## About
BGDPbES BAU Guaranteed Dispatch Percentage by Electricity Source | Iowa | 2024-07-26 |  | State | State
| IA |  |  | Alabama | AL
Source: | Petroleum |  |  | Alaska | AK
| Weighted Average Expected Capacity Factors (calculated EPS variable) |  |  | Arizona | AZ
|  |  |  | Arkansas | AR
|  |  |  | California | CA
|  |  |  | Colorado | CO
|  |  |  | Connecticut | CT
Notes: |  |  |  | Delaware | DE
This variable is used to specify the percentage of potential electricity output from each |  |  |  | Florida | FL
source that is guaranteed (e.g. dispatched before any least-cost dispatching |  |  |  | Georgia | GA
begins) in the BAU case. |  |  |  | Hawaii | HI
|  |  |  | Idaho | ID
For nuclear plants, we guarantee full dispatch, as regulators and utilities often run |  |  |  | Illinois | IL
these plants as baseload irresective of cost, rather than ramping them up and down. |  |  |  | Indiana | IN
|  |  |  | Iowa | IA
For petroleum, we use the weighted average expected capacity factor. |  |  |  | Kansas | KS
In reality, petroleum is primarily used in fuel-switching applications in New England |  |  |  | Kentucky | KY
(where there can be specific, unusual hours of NG shortage due to pipeline congestion) |  |  |  | Louisiana | LA
and in places like Hawaii, without much NG access, where it is easier to transport petroleum |  |  |  | Maine | ME
by ship due to its higher volumetric energy density. |  |  |  | Maryland | MD
We can't capture some of these unusual hours and sub-regional dynamics directly, so |  |  |  | Massachusetts | MA
we use guaranteed dispatch to align modeled petroleum dispatch with real-world experience. |  |  |  | Michigan | MI
|  |  |  | Minnesota | MN
|  |  |  | Mississippi | MS
|  |  |  | Missouri | MO
|  |  |  | Montana | MT
|  |  |  | Nebraska | NE
|  |  |  | Nevada | NV
|  |  |  | New Hampshire | NH
|  |  |  | New Jersey | NJ
|  |  |  | New Mexico | NM
|  |  |  | New York | NY
|  |  |  | North Carolina | NC
|  |  |  | North Dakota | ND
|  |  |  | Ohio | OH
|  |  |  | Oklahoma | OK
|  |  |  | Oregon | OR
|  |  |  | Pennsylvania | PA
|  |  |  | Rhode Island | RI
|  |  |  | South Carolina | SC
|  |  |  | South Dakota | SD
|  |  |  | Tennessee | TN
|  |  |  | Texas | TX
|  |  |  | Utah | UT
|  |  |  | Vermont | VT
|  |  |  | Virginia | VA
|  |  |  | Washington | WA
|  |  |  | West Virginia | WV
|  |  |  | Wisconsin | WI
|  |  |  | Wyoming | WY
State
| Tot production | Cap factor | Percent of total
RICE | 5172 | 18.2 | 0.01226
Steam turbine | 74000 | 12.5 | 0.17541
Gas turbine | 130100 | 11.7 | 0.3084
CCGT | 212587 | 55 | 0.50393
Total | 421859
These are the overall national capacity factors across the US
Need to combine RICE and gas turbine into one weighted category
RICE is so small though, that keeping the gas turbine as the peaker capacity it reasonable
Steam Turbine | 12.5
CCGT | 55
Peaker | 11.7
Now I have a capacity factor in general, and I need to then shape that around the actual capacity factor (which I only have for the overall natural gas generation)
If this is not precisely correct, then use the ratio to normalize to the correct total value
Then, if CCGT is greater than 80%, take the excess and move evenly to steam turbine
If steam turbine is greater than 80% move to peaker
Need to reallocate the excess if CCGT is greater than 80%. Mostly can allocate to steam turbine using the equation: excess / (steam turbine capacity * 8760) = new capacity factor
This can then be added to the steam turbine capacity factor

## 860
2021 Form EIA-860 Data - Schedule 3, 'Generator Data' (Operable Units Only)
Vintage | Model Energy Source | Include? | Utility ID | Utility Name | Plant Code | Plant Name | State | County | Generator ID | Technology | Prime Mover | Unit Code | Ownership | Duct Burners | Can Bypass Heat Recovery Steam Generator? | RTO/ISO LMP Node Designation | RTO/ISO Location Designation for Reporting Wholesale Sales Data to FERC | Nameplate Capacity (MW) | Nameplate Power Factor | Summer Capacity (MW) | Winter Capacity (MW) | Minimum Load (MW) | Uprate or Derate Completed During Year | Month Uprate or Derate Completed | Year Uprate or Derate Completed | Status | Synchronized to Transmission Grid | Operating Month | Operating Year | Planned Retirement Month | Planned Retirement Year | Associated with Combined Heat and Power System | Sector Name | Sector | Topping or Bottoming | Energy Source 1 | Energy Source 2 | Energy Source 3 | Energy Source 4 | Energy Source 5 | Energy Source 6 | Startup Source 1 | Startup Source 2 | Startup Source 3 | Startup Source 4 | Solid Fuel Gasification System? | Carbon Capture Technology? | Turbines or Hydrokinetic Buoys | Time from Cold Shutdown to Full Load | Fluidized Bed Technology? | Pulverized Coal Technology? | Stoker Technology? | Other Combustion Technology? | Subcritical Technology? | Supercritical Technology? | Ultrasupercritical Technology? | Planned Net Summer Capacity Uprate (MW) | Planned Net Winter Capacity Uprate (MW) | Planned Uprate Month | Planned Uprate Year | Planned Net Summer Capacity Derate (MW) | Planned Net Winter Capacity Derate (MW) | Planned Derate Month | Planned Derate Year | Planned New Prime Mover | Planned Energy Source 1 | Planned New Nameplate Capacity (MW) | Planned Repower Month | Planned Repower Year | Other Planned Modifications? | Other Modifications Month | Other Modifications Year | Multiple Fuels? | Cofire Fuels? | Switch Between Oil and Natural Gas?
Vintage2000 | petroleum | TRUE | 63560 | TDX Sand Point Generating, LLC | 1 | Sand Point | AK | Aleutians East | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.4 | 0.4 | 0.4 | N |  |  | SB | Y | 12 | 2000 |  |  | N | Electric Utility | 1 | X | DFO | [12 empty] | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 63560 | TDX Sand Point Generating, LLC | 1 | Sand Point | AK | Aleutians East | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.3 | 0.3 | 0.3 | N |  |  | OP | X | 12 | 2000 |  |  | N | Electric Utility | 1 | X | DFO | [12 empty] | 10M | [23 empty] | N
Vintage2010 | petroleum | TRUE | 63560 | TDX Sand Point Generating, LLC | 1 | Sand Point | AK | Aleutians East | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.3 | 0.3 | 0.3 | N |  |  | OP | X | 12 | 2010 |  |  | N | Electric Utility | 1 | X | DFO | [12 empty] | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 63560 | TDX Sand Point Generating, LLC | 1 | Sand Point | AK | Aleutians East | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.7 | 0.8 | 0.4 | 0.3 | 0.3 | N |  |  | OS | X | 12 | 2000 |  |  | N | Electric Utility | 1 | X | DFO | [12 empty] | 10M | [23 empty] | N
Vintage2011 | onshore wind | TRUE | 63560 | TDX Sand Point Generating, LLC | 1 | Sand Point | AK | Aleutians East | WT1 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 0.5 | 0.89 | 0.1 | 0.1 | 0.1 | N |  |  | OS | X | 10 | 2011 |  |  | N | Electric Utility | 1 | X | WND | [11 empty] | 1
Vintage2011 | onshore wind | TRUE | 63560 | TDX Sand Point Generating, LLC | 1 | Sand Point | AK | Aleutians East | WT2 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 0.5 | 0.89 | 0.3 | 0.3 | 0.3 | N |  |  | OA | X | 10 | 2011 |  |  | N | Electric Utility | 1 | X | WND | [11 empty] | 1
Vintage1963 | hydro | TRUE | 195 | Alabama Power Co | 2 | Bankhead Dam | AL | Tuscaloosa | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 53.9 | 0.92 | 53 | 53 | 52 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1954 | natural gas steam turbine | TRUE | 195 | Alabama Power Co | 3 | Barry | AL | Mobile | 1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 153.1 | 0.85 | 80 | 80 | 55 | N |  |  | OP | X | 2 | 1954 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG | [6 empty] | OVER | [23 empty] | N | N
Vintage1954 | natural gas steam turbine | TRUE | 195 | Alabama Power Co | 3 | Barry | AL | Mobile | 2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 153.1 | 0.85 | 80 | 80 | 55 | N |  |  | OP | X | 7 | 1954 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG | [6 empty] | OVER | [23 empty] | N
Vintage1969 | hard coal | TRUE | 195 | Alabama Power Co | 3 | Barry | AL | Mobile | 4 | Conventional Steam Coal | ST |  | S | X | X |  |  | 403.7 | 0.85 | 362 | 362 | 200 | N |  |  | OP | X | 12 | 1969 |  |  | N | Electric Utility | 1 | X | BIT | [5 empty] | NG | [6 empty] | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1971 | hard coal | TRUE | 195 | Alabama Power Co | 3 | Barry | AL | Mobile | 5 | Conventional Steam Coal | ST |  | S | X | X |  |  | 788.8 | 0.85 | 756.5 | 756.5 | 465 | N |  |  | OP | X | 10 | 1971 |  |  | N | Electric Utility | 1 | X | BIT | [5 empty] | NG | [6 empty] | OVER |  | Y |  |  |  | Y | [17 empty] | N
Vintage2000 | natural gas combined cycle | TRUE | 195 | Alabama Power Co | 3 | Barry | AL | Mobile | A1CT | Natural Gas Fired Combined Cycle | CT | G521 | S | X | N |  |  | 170.1 | 0.85 | 184.4 | 194.5 | 90 | N |  |  | OP | X | 5 | 2000 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 12H | [23 empty] | N
Vintage2000 | natural gas combined cycle | TRUE | 195 | Alabama Power Co | 3 | Barry | AL | Mobile | A1CT2 | Natural Gas Fired Combined Cycle | CT | G521 | S | X | N |  |  | 170.1 | 0.85 | 184.4 | 194.5 | 90 | N |  |  | OP | X | 5 | 2000 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 12H | [23 empty] | N
Vintage2000 | natural gas combined cycle | TRUE | 195 | Alabama Power Co | 3 | Barry | AL | Mobile | A1ST | Natural Gas Fired Combined Cycle | CA | G521 | S | Y | X |  |  | 195.2 | 0.85 | 200 | 205 | 136 | N |  |  | OP | X | 5 | 2000 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 12H | [23 empty] | N
Vintage2000 | natural gas combined cycle | TRUE | 195 | Alabama Power Co | 3 | Barry | AL | Mobile | A2C1 | Natural Gas Fired Combined Cycle | CT | G522 | S | X | N |  |  | 170.1 | 0.85 | 186.2 | 190 | 86 | N |  |  | OP | X | 5 | 2000 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 12H | [23 empty] | N
Vintage2000 | natural gas combined cycle | TRUE | 195 | Alabama Power Co | 3 | Barry | AL | Mobile | A2C2 | Natural Gas Fired Combined Cycle | CT | G522 | S | X | N |  |  | 170.1 | 0.85 | 186.2 | 190 | 86 | N |  |  | OP | X | 5 | 2000 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 12H | [23 empty] | N
Vintage2000 | natural gas combined cycle | TRUE | 195 | Alabama Power Co | 3 | Barry | AL | Mobile | A2ST | Natural Gas Fired Combined Cycle | CA | G522 | S | Y | X |  |  | 195.2 | 0.85 | 195 | 200 | 128 | N |  |  | OP | X | 5 | 2000 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 12H | [23 empty] | N
Vintage1967 | hydro | TRUE | 195 | Alabama Power Co | 4 | Walter Bouldin Dam | AL | Elmore | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 75 | 0.857 | 74.7 | 74.7 | 74 | N |  |  | OP | X | 7 | 1967 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1967 | hydro | TRUE | 195 | Alabama Power Co | 4 | Walter Bouldin Dam | AL | Elmore | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 75 | 0.857 | 74.7 | 74.7 | 74 | N |  |  | OP | X | 8 | 1967 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1967 | hydro | TRUE | 195 | Alabama Power Co | 4 | Walter Bouldin Dam | AL | Elmore | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 75 | 0.857 | 74.7 | 74.7 | 74 | N |  |  | OP | X | 8 | 1967 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1949 | natural gas steam turbine | TRUE | 195 | Alabama Power Co | 7 | Gadsden | AL | Etowah | 1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 69 | 0.85 | 64 | 64 | 28 | N |  |  | OP | X | 4 | 1949 |  |  | Y | Electric Utility | 1 | B | NG | [5 empty] | NG |  |  |  | N |  |  | OVER | [23 empty] | N
Vintage1949 | natural gas steam turbine | TRUE | 195 | Alabama Power Co | 7 | Gadsden | AL | Etowah | 2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 69 | 0.85 | 66 | 66 | 28 | N |  |  | OP | X | 7 | 1949 |  |  | Y | Electric Utility | 1 | B | NG | [5 empty] | NG |  |  |  | N |  |  | OVER | [23 empty] | N
Vintage1980 | natural gas peaker | TRUE | 5701 | El Paso Electric Co | 9 | Copper | TX | El Paso | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 86.9 | 0.9 | 63 | 65 | 3 | N |  |  | OP | X | 7 | 1980 | 12 | 2030 | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 10M | [23 empty] | N |  | N
Vintage1965 | natural gas steam turbine | TRUE | 195 | Alabama Power Co | 10 | Greene County | AL | Greene | 1 | Natural Gas Steam Turbine | ST |  | J | X | X |  |  | 299.2 | 0.85 | 257.8 | 257.8 | 110 | N |  |  | OP | X | 6 | 1965 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N |  |  | 12H | [23 empty] | N
Vintage1966 | natural gas steam turbine | TRUE | 195 | Alabama Power Co | 10 | Greene County | AL | Greene | 2 | Natural Gas Steam Turbine | ST |  | J | X | X |  |  | 269.2 | 0.85 | 258.3 | 258.3 | 110 | N |  |  | OP | X | 7 | 1966 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N |  |  | 12H | [23 empty] | N
Vintage1996 | natural gas peaker | TRUE | 195 | Alabama Power Co | 10 | Greene County | AL | Greene | GT10 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 80 | 0.85 | 85 | 101 | 66 | N |  |  | OP | X | 5 | 1996 |  |  | N | Electric Utility | 1 | X | NG | DFO | [11 empty] | 1H | [23 empty] | Y | N | Y
Vintage1996 | natural gas peaker | TRUE | 195 | Alabama Power Co | 10 | Greene County | AL | Greene | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 80 | 0.85 | 84 | 100 | 66 | N |  |  | OP | X | 5 | 1996 |  |  | N | Electric Utility | 1 | X | NG | DFO | [11 empty] | 1H | [23 empty] | Y | N | Y
Vintage1995 | natural gas peaker | TRUE | 195 | Alabama Power Co | 10 | Greene County | AL | Greene | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 80 | 0.85 | 82 | 98 | 66 | N |  |  | OP | X | 5 | 1995 |  |  | N | Electric Utility | 1 | X | NG | DFO | [11 empty] | 1H | [23 empty] | Y | N | Y
Vintage1995 | natural gas peaker | TRUE | 195 | Alabama Power Co | 10 | Greene County | AL | Greene | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 80 | 0.85 | 81 | 97 | 66 | N |  |  | OP | X | 5 | 1995 |  |  | N | Electric Utility | 1 | X | NG | DFO | [11 empty] | 1H | [23 empty] | Y | N | Y
Vintage1995 | natural gas peaker | TRUE | 195 | Alabama Power Co | 10 | Greene County | AL | Greene | GT5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 80 | 0.85 | 82 | 98 | 66 | N |  |  | OP | X | 5 | 1995 |  |  | N | Electric Utility | 1 | X | NG | DFO | [11 empty] | 1H | [23 empty] | Y | N | Y
Vintage1995 | natural gas peaker | TRUE | 195 | Alabama Power Co | 10 | Greene County | AL | Greene | GT6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 80 | 0.85 | 81 | 97 | 66 | N |  |  | OP | X | 5 | 1995 |  |  | N | Electric Utility | 1 | X | NG | DFO | [11 empty] | 1H | [23 empty] | Y | N | Y
Vintage1995 | natural gas peaker | TRUE | 195 | Alabama Power Co | 10 | Greene County | AL | Greene | GT7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 80 | 0.85 | 80 | 96 | 66 | N |  |  | OP | X | 5 | 1995 |  |  | N | Electric Utility | 1 | X | NG | DFO | [11 empty] | 1H | [23 empty] | Y | N | Y
Vintage1996 | natural gas peaker | TRUE | 195 | Alabama Power Co | 10 | Greene County | AL | Greene | GT8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 80 | 0.85 | 83 | 99 | 66 | N |  |  | OP | X | 5 | 1996 |  |  | N | Electric Utility | 1 | X | NG | DFO | [11 empty] | 1H | [23 empty] | Y | N | Y
Vintage1996 | natural gas peaker | TRUE | 195 | Alabama Power Co | 10 | Greene County | AL | Greene | GT9 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 80 | 0.85 | 82 | 98 | 66 | N |  |  | OP | X | 5 | 1996 |  |  | N | Electric Utility | 1 | X | NG | DFO | [11 empty] | 1H | [23 empty] | Y | N | Y
Vintage1966 | hydro | TRUE | 195 | Alabama Power Co | 11 | H Neely Henry Dam | AL | Calhoun | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 24.3 | 0.9 | 23.7 | 22.7 | 22.3 | N |  |  | OP | X | 6 | 1966 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1966 | hydro | TRUE | 195 | Alabama Power Co | 11 | H Neely Henry Dam | AL | Calhoun | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 24.3 | 0.9 | 23.7 | 22.7 | 22.3 | N |  |  | OP | X | 6 | 1966 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1966 | hydro | TRUE | 195 | Alabama Power Co | 11 | H Neely Henry Dam | AL | Calhoun | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 24.3 | 0.9 | 23.7 | 22.7 | 22.4 | N |  |  | OP | X | 6 | 1966 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1968 | hydro | TRUE | 195 | Alabama Power Co | 12 | Holt Dam | AL | Tuscaloosa | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 46.9 | 0.89 | 48 | 48 | 45 | N |  |  | OP | X | 8 | 1968 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1929 | hydro | TRUE | 195 | Alabama Power Co | 13 | Jordan Dam | AL | Elmore | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 25 | 0.862 | 32.3 | 32.5 | 25 | N |  |  | OP | X | 1 | 1929 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1929 | hydro | TRUE | 195 | Alabama Power Co | 13 | Jordan Dam | AL | Elmore | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 25 | 0.862 | 32.3 | 32.5 | 25 | N |  |  | OP | X | 1 | 1929 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1929 | hydro | TRUE | 195 | Alabama Power Co | 13 | Jordan Dam | AL | Elmore | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 25 | 0.862 | 32.3 | 32.5 | 25 | N |  |  | OP | X | 1 | 1929 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1929 | hydro | TRUE | 195 | Alabama Power Co | 13 | Jordan Dam | AL | Elmore | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 25 | 0.862 | 32.3 | 32.5 | 25 | N |  |  | OP | X | 1 | 1929 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1964 | hydro | TRUE | 195 | Alabama Power Co | 14 | Logan Martin Dam | AL | Talladega | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 42.7 | 0.9 | 43 | 39.7 | 41.6 | N |  |  | OP | X | 8 | 1964 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1964 | hydro | TRUE | 195 | Alabama Power Co | 14 | Logan Martin Dam | AL | Talladega | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 42.7 | 0.9 | 43 | 39.7 | 41.6 | N |  |  | OP | X | 8 | 1964 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1964 | hydro | TRUE | 195 | Alabama Power Co | 14 | Logan Martin Dam | AL | Talladega | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 42.7 | 0.9 | 43 | 39.7 | 41.8 | N |  |  | OP | X | 8 | 1964 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1968 | hydro | TRUE | 195 | Alabama Power Co | 15 | Lay Dam | AL | Chilton | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 29.5 | 0.9 | 30 | 30.3 | 29 | N |  |  | OP | X | 4 | 1968 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1968 | hydro | TRUE | 195 | Alabama Power Co | 15 | Lay Dam | AL | Chilton | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 29.5 | 0.9 | 30 | 30.3 | 29 | N |  |  | OP | X | 4 | 1968 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1967 | hydro | TRUE | 195 | Alabama Power Co | 15 | Lay Dam | AL | Chilton | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 29.5 | 0.9 | 30 | 30.3 | 29 | N |  |  | OP | X | 12 | 1967 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1967 | hydro | TRUE | 195 | Alabama Power Co | 15 | Lay Dam | AL | Chilton | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 29.5 | 0.9 | 30 | 30.3 | 29 | N |  |  | OP | X | 10 | 1967 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1967 | hydro | TRUE | 195 | Alabama Power Co | 15 | Lay Dam | AL | Chilton | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 29.5 | 0.9 | 30 | 30.3 | 29 | N |  |  | OP | X | 5 | 1967 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1967 | hydro | TRUE | 195 | Alabama Power Co | 15 | Lay Dam | AL | Chilton | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 29.5 | 0.9 | 30 | 30.3 | 29 | N |  |  | OP | X | 2 | 1967 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1927 | hydro | TRUE | 195 | Alabama Power Co | 16 | Martin Dam | AL | Elmore | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 50.2 | 0.95 | 41.5 | 39.4 | 40 | N |  |  | OP | X | 1 | 1927 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1927 | hydro | TRUE | 195 | Alabama Power Co | 16 | Martin Dam | AL | Elmore | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 50.2 | 0.95 | 41.5 | 39.4 | 40 | N |  |  | OP | X | 1 | 1927 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1927 | hydro | TRUE | 195 | Alabama Power Co | 16 | Martin Dam | AL | Elmore | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 50.2 | 0.95 | 41.5 | 39.4 | 40 | N |  |  | OP | X | 1 | 1927 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1952 | hydro | TRUE | 195 | Alabama Power Co | 16 | Martin Dam | AL | Elmore | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 60 | 0.95 | 57.6 | 54.7 | 40 | N |  |  | OP | X | 7 | 1952 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1949 | hydro | TRUE | 195 | Alabama Power Co | 17 | Mitchell Dam | AL | Coosa | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 20 | 0.8 | 22.4 | 22.7 | 19 | N |  |  | OP | X | 11 | 1949 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1985 | hydro | TRUE | 195 | Alabama Power Co | 17 | Mitchell Dam | AL | Coosa | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 50 | 0.8 | 46.9 | 47.4 | 46 | N |  |  | OP | X | 4 | 1985 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1985 | hydro | TRUE | 195 | Alabama Power Co | 17 | Mitchell Dam | AL | Coosa | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 50 | 0.8 | 46.9 | 47.4 | 46 | N |  |  | OP | X | 4 | 1985 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1985 | hydro | TRUE | 195 | Alabama Power Co | 17 | Mitchell Dam | AL | Coosa | 7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 50 | 0.8 | 46.9 | 47.4 | 46 | N |  |  | OP | X | 4 | 1985 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1961 | hydro | TRUE | 195 | Alabama Power Co | 18 | Lewis Smith Dam | AL | Walker | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 90.5 | 0.9 | 89 | 87.5 | 83 | N |  |  | OP | X | 9 | 1961 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M | [23 empty] | N
Vintage1962 | hydro | TRUE | 195 | Alabama Power Co | 18 | Lewis Smith Dam | AL | Walker | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 90.5 | 0.9 | 89 | 87.5 | 83 | N |  |  | OP | X | 7 | 1962 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M | [23 empty] | N
Vintage1931 | hydro | TRUE | 195 | Alabama Power Co | 19 | Thurlow Dam | AL | Elmore | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40.5 | 0.95 | 36.2 | 35.3 | 32 | N |  |  | OP | X | 1 | 1931 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1931 | hydro | TRUE | 195 | Alabama Power Co | 19 | Thurlow Dam | AL | Elmore | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40.5 | 0.95 | 36.2 | 35.3 | 32 | N |  |  | OP | X | 1 | 1931 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1931 | hydro | TRUE | 195 | Alabama Power Co | 19 | Thurlow Dam | AL | Elmore | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 0.8 | 7.5 | 7.3 | 7 | N |  |  | OP | X | 1 | 1931 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1962 | hydro | TRUE | 195 | Alabama Power Co | 20 | Weiss Dam | AL | Cherokee | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 29.2 | 0.9 | 27 | 24.3 | 22.3 | N |  |  | OP | X | 7 | 1962 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1961 | hydro | TRUE | 195 | Alabama Power Co | 20 | Weiss Dam | AL | Cherokee | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 29.2 | 0.9 | 27 | 24.3 | 22.3 | N |  |  | OP | X | 6 | 1961 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1961 | hydro | TRUE | 195 | Alabama Power Co | 20 | Weiss Dam | AL | Cherokee | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 29.2 | 0.9 | 27 | 24.3 | 22.3 | N |  |  | OP | X | 6 | 1961 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1928 | hydro | TRUE | 195 | Alabama Power Co | 21 | Yates Dam | AL | Elmore | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 25.5 | 0.901 | 22 | 22.5 | 21 | N |  |  | OP | X | 7 | 1928 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1928 | hydro | TRUE | 195 | Alabama Power Co | 21 | Yates Dam | AL | Elmore | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 25 | 0.901 | 22 | 22.5 | 21 | N |  |  | OP | X | 7 | 1928 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1960 | natural gas steam turbine | TRUE | 195 | Alabama Power Co | 26 | E C Gaston | AL | Shelby | 1 | Natural Gas Steam Turbine | ST |  | J | X | X |  |  | 272 | 0.85 | 254 | 254 | 70 | N |  |  | OP | X | 5 | 1960 |  |  | N | Electric Utility | 1 | X | NG | BIT |  |  |  |  | NG |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1960 | natural gas steam turbine | TRUE | 195 | Alabama Power Co | 26 | E C Gaston | AL | Shelby | 2 | Natural Gas Steam Turbine | ST |  | J | X | X |  |  | 272 | 0.85 | 256 | 256 | 70 | N |  |  | OP | X | 7 | 1960 |  |  | N | Electric Utility | 1 | X | NG | BIT |  |  |  |  | NG |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1961 | natural gas steam turbine | TRUE | 195 | Alabama Power Co | 26 | E C Gaston | AL | Shelby | 3 | Natural Gas Steam Turbine | ST |  | J | X | X |  |  | 272 | 0.85 | 254 | 254 | 70 | N |  |  | OP | X | 6 | 1961 |  |  | N | Electric Utility | 1 | X | NG | BIT |  |  |  |  | NG |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1974 | hard coal | TRUE | 195 | Alabama Power Co | 26 | E C Gaston | AL | Shelby | 5 | Conventional Steam Coal | ST |  | S | X | X |  |  | 952 | 0.85 | 832 | 832 | 700 | N |  |  | OP | X | 8 | 1974 |  |  | N | Electric Utility | 1 | X | BIT | NG |  |  |  |  | NG |  |  |  | N |  |  | OVER |  | Y |  |  |  | Y | [17 empty] | N
Vintage1970 | petroleum | TRUE | 195 | Alabama Power Co | 26 | E C Gaston | AL | Shelby | GT4 | Petroleum Liquids | GT |  | J | X | X |  |  | 21.2 | 0.85 | 16 | 20 | 16 | N |  |  | OP | X | 6 | 1970 |  |  | N | Electric Utility | 1 | X | DFO | [12 empty] | 1H | [23 empty] | N
Vintage1962 | natural gas steam turbine | TRUE | 195 | Alabama Power Co | 26 | E C Gaston | AL | Shelby | ST4 | Natural Gas Steam Turbine | ST |  | J | X | X |  |  | 244.8 | 0.85 | 256 | 256 | 70 | N |  |  | OP | X | 6 | 1962 |  |  | N | Electric Utility | 1 | X | NG | BIT |  |  |  |  | NG |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage2001 | petroleum | TRUE | 29305 | City of Madelia - (MN) | 30 | Madelia | MN | Watonwan | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.1 | 0.8 | 3.1 | 3.1 | 1.6 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1965 | petroleum | TRUE | 29305 | City of Madelia - (MN) | 30 | Madelia | MN | Watonwan | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 2 | 1 | N |  |  | OP | X | 6 | 1965 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1959 | petroleum | TRUE | 29305 | City of Madelia - (MN) | 30 | Madelia | MN | Watonwan | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 0.9 | 1 | 0.6 | N |  |  | OP | X | 1 | 1959 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1973 | petroleum | TRUE | 29305 | City of Madelia - (MN) | 30 | Madelia | MN | Watonwan | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.3 | 0.8 | 3.7 | 4 | 1.7 | N |  |  | OP | X | 6 | 1973 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1954 | petroleum | TRUE | 29305 | City of Madelia - (MN) | 30 | Madelia | MN | Watonwan | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.1 | 1.2 | 0.7 | N |  |  | OP | X | 3 | 1954 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1980 | hydro | TRUE | 13402 | Nevada Irrigation District | 34 | Rollins | CA | Placer | 1P | Conventional Hydroelectric | HY |  | S | X | X |  |  | 12.1 | 0.99 | 12.1 | 12.1 | 0.5 | N |  |  | OP | X | 8 | 1980 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 12H | [23 empty] | N
Vintage1970 | hydro | TRUE | 27813 | USCE-Mobile District | 38 | Millers Ferry | AL | Wilcox | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 33.7 | 0.95 | 30 | 30 | 24 | N |  |  | OP | X | 4 | 1970 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage1970 | hydro | TRUE | 27813 | USCE-Mobile District | 38 | Millers Ferry | AL | Wilcox | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 33.7 | 0.95 | 30 | 30 | 24 | N |  |  | OP | X | 4 | 1970 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage1970 | hydro | TRUE | 27813 | USCE-Mobile District | 38 | Millers Ferry | AL | Wilcox | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 33.7 | 0.95 | 30 | 30 | 24 | N |  |  | OP | X | 5 | 1970 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage1974 | nuclear | TRUE | 18642 | Tennessee Valley Authority | 46 | Browns Ferry | AL | Limestone | 1 | Nuclear | ST |  | S | X | X |  |  | 1263.5 | 0.95 | 1227.4 | 1254.8 | 1227.4 | N |  |  | OP | X | 8 | 1974 |  |  | N | Electric Utility | 1 | X | NUC | [9 empty] | N |  |  | OVER | [23 empty] | N
Vintage1975 | nuclear | TRUE | 18642 | Tennessee Valley Authority | 46 | Browns Ferry | AL | Limestone | 2 | Nuclear | ST |  | S | X | X |  |  | 1152 | 0.9 | 1207.7 | 1242 | 1103.7 | N |  |  | OP | X | 3 | 1975 |  |  | N | Electric Utility | 1 | X | NUC | [9 empty] | N |  |  | OVER | [23 empty] | N
Vintage1977 | nuclear | TRUE | 18642 | Tennessee Valley Authority | 46 | Browns Ferry | AL | Limestone | 3 | Nuclear | ST |  | S | X | X |  |  | 1152 | 0.9 | 1226.6 | 1259 | 1226.6 | N |  |  | OP | X | 3 | 1977 |  |  | N | Electric Utility | 1 | X | NUC | [9 empty] | N |  |  | OVER | [23 empty] | N
Vintage1972 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 47 | Colbert | AL | Colbert | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 59.5 | 0.9 | 45.4 | 60.8 | 10 | N |  |  | OP | X | 9 | 1972 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 10M | [23 empty] | Y | N | Y
Vintage1972 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 47 | Colbert | AL | Colbert | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 59.5 | 0.9 | 45.4 | 60.8 | 10 | N |  |  | OP | X | 9 | 1972 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 10M | [23 empty] | Y | N | Y
Vintage1972 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 47 | Colbert | AL | Colbert | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 59.5 | 0.9 | 45.4 | 60.8 | 10 | N |  |  | OP | X | 9 | 1972 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 10M | [23 empty] | Y | N | Y
Vintage1972 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 47 | Colbert | AL | Colbert | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 59.5 | 0.9 | 45.4 | 60.8 | 10 | N |  |  | OP | X | 9 | 1972 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 10M | [23 empty] | Y | N | Y
Vintage1972 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 47 | Colbert | AL | Colbert | GT5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 59.5 | 0.9 | 45.4 | 60.8 | 10 | N |  |  | OP | X | 9 | 1972 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 10M | [23 empty] | Y | N | Y
Vintage1972 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 47 | Colbert | AL | Colbert | GT6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 59.5 | 0.9 | 45.4 | 60.8 | 10 | N |  |  | OP | X | 9 | 1972 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 10M | [23 empty] | Y | N | Y
Vintage1972 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 47 | Colbert | AL | Colbert | GT7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 59.5 | 0.9 | 45.4 | 60.8 | 10 | N |  |  | OP | X | 9 | 1972 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 10M | [23 empty] | Y | N | Y
Vintage1972 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 47 | Colbert | AL | Colbert | GT8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 59.5 | 0.9 | 45.4 | 60.8 | 10 | N |  |  | OP | X | 9 | 1972 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 10M | [23 empty] | Y | N | Y
Vintage1939 | hydro | TRUE | 18642 | Tennessee Valley Authority | 48 | Guntersville | AL | Marshall | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 28.8 | 0.9 | 31 | 31.4 | 9.7 | N |  |  | OP | X | 8 | 1939 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1939 | hydro | TRUE | 18642 | Tennessee Valley Authority | 48 | Guntersville | AL | Marshall | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 28.8 | 0.9 | 30.6 | 31.1 | 12.9 | N |  |  | OP | X | 10 | 1939 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1939 | hydro | TRUE | 18642 | Tennessee Valley Authority | 48 | Guntersville | AL | Marshall | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 28.8 | 0.9 | 29.8 | 30.3 | 9.7 | N |  |  | OP | X | 12 | 1939 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1952 | hydro | TRUE | 18642 | Tennessee Valley Authority | 48 | Guntersville | AL | Marshall | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 28.8 | 0.9 | 31.3 | 31.7 | 14.6 | N |  |  | OP | X | 3 | 1952 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1936 | hydro | TRUE | 18642 | Tennessee Valley Authority | 49 | Wheeler Dam | AL | Lawrence | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 35.1 | 0.9 | 34.1 | 35.6 | 23.5 | N |  |  | OP | X | 11 | 1936 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H
Vintage1963 | hydro | TRUE | 18642 | Tennessee Valley Authority | 49 | Wheeler Dam | AL | Lawrence | 10 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 36 | 0.9 | 41.9 | 38.3 | 27.2 | N |  |  | OP | X | 6 | 1963 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H
Vintage1963 | hydro | TRUE | 18642 | Tennessee Valley Authority | 49 | Wheeler Dam | AL | Lawrence | 11 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 43.6 | 0.9 | 41.9 | 38.2 | 27.9 | N |  |  | OP | X | 12 | 1963 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H
Vintage1937 | hydro | TRUE | 18642 | Tennessee Valley Authority | 49 | Wheeler Dam | AL | Lawrence | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 35.1 | 0.9 | 33.2 | 30.1 | 27.6 | N |  |  | OP | X | 4 | 1937 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1941 | hydro | TRUE | 18642 | Tennessee Valley Authority | 49 | Wheeler Dam | AL | Lawrence | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 35.1 | 0.9 | 33.6 | 30.4 | 23 | N |  |  | OP | X | 1 | 1941 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1941 | hydro | TRUE | 18642 | Tennessee Valley Authority | 49 | Wheeler Dam | AL | Lawrence | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 35.1 | 0.9 | 33.4 | 30.2 | 25.4 | N |  |  | OP | X | 3 | 1941 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1948 | hydro | TRUE | 18642 | Tennessee Valley Authority | 49 | Wheeler Dam | AL | Lawrence | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 35.1 | 0.9 | 34.7 | 31.4 | 23.3 | N |  |  | OP | X | 10 | 1948 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1949 | hydro | TRUE | 18642 | Tennessee Valley Authority | 49 | Wheeler Dam | AL | Lawrence | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 35.1 | 0.9 | 34.6 | 31.3 | 23.4 | N |  |  | OP | X | 2 | 1949 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1949 | hydro | TRUE | 18642 | Tennessee Valley Authority | 49 | Wheeler Dam | AL | Lawrence | 7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 35.1 | 0.9 | 34.4 | 31.1 | 25 | N |  |  | OP | X | 12 | 1949 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1950 | hydro | TRUE | 18642 | Tennessee Valley Authority | 49 | Wheeler Dam | AL | Lawrence | 8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 35.1 | 0.9 | 34.5 | 31.2 | 23.4 | N |  |  | OP | X | 3 | 1950 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1962 | hydro | TRUE | 18642 | Tennessee Valley Authority | 49 | Wheeler Dam | AL | Lawrence | 9 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 43.6 | 0.9 | 41.9 | 38.2 | 28 | N |  |  | OP | X | 12 | 1962 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1926 | hydro | TRUE | 189 | PowerSouth Energy Cooperative | 53 | Gantt | AL | Covington | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.8 | 1 | 1 | 0.1 | N |  |  | OP | X | 1 | 1926 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 189 | PowerSouth Energy Cooperative | 53 | Gantt | AL | Covington | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.1 | N |  |  | OP | X | 2 | 1985 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 10M | [23 empty] | N
Vintage1999 | natural gas peaker | TRUE | 5580 | East Kentucky Power Coop, Inc | 54 | J K Smith | KY | Clark | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 1123180710 | 88122101 | 149 | 0.9 | 104 | 142 | 70 | N |  |  | OP | X | 3 | 1999 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2010 | natural gas peaker | TRUE | 5580 | East Kentucky Power Coop, Inc | 54 | J K Smith | KY | Clark | GT10 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 1123180711 | 8122110 | 98 | 0.85 | 74 | 103 | 33 | N |  |  | OP | X | 5 | 2010 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1999 | natural gas peaker | TRUE | 5580 | East Kentucky Power Coop, Inc | 54 | J K Smith | KY | Clark | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 1123180712 | 88122102 | 149 | 0.9 | 104 | 142 | 70 | N |  |  | OP | X | 1 | 1999 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1999 | natural gas peaker | TRUE | 5580 | East Kentucky Power Coop, Inc | 54 | J K Smith | KY | Clark | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 1123180713 | 88122103 | 149 | 0.9 | 104 | 142 | 70 | N |  |  | OP | X | 4 | 1999 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2001 | natural gas peaker | TRUE | 5580 | East Kentucky Power Coop, Inc | 54 | J K Smith | KY | Clark | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 1123180714 | 88122104 | 108 | 0.9 | 73 | 93 | 54 | N |  |  | OP | X | 11 | 2001 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2001 | natural gas peaker | TRUE | 5580 | East Kentucky Power Coop, Inc | 54 | J K Smith | KY | Clark | GT5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 1123180715 | 88122105 | 108 | 0.9 | 73 | 88 | 54 | N |  |  | OP | X | 11 | 2001 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2005 | natural gas peaker | TRUE | 5580 | East Kentucky Power Coop, Inc | 54 | J K Smith | KY | Clark | GT6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 1123180716 | 88122106 | 98 | 0.9 | 73 | 88 | 54 | N |  |  | OP | X | 1 | 2005 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2005 | natural gas peaker | TRUE | 5580 | East Kentucky Power Coop, Inc | 54 | J K Smith | KY | Clark | GT7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 1123180717 | 88122107 | 98 | 0.9 | 73 | 88 | 54 | N |  |  | OP | X | 1 | 2005 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2010 | natural gas peaker | TRUE | 5580 | East Kentucky Power Coop, Inc | 54 | J K Smith | KY | Clark | GT9 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 1123180718 | 88122109 | 98 | 0.85 | 75 | 103 | 33 | N |  |  | OP | X | 5 | 2010 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1925 | hydro | TRUE | 189 | PowerSouth Energy Cooperative | 55 | Point A | AL | Covington | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.8 | 1.8 | 1.8 | 0.1 | N |  |  | OP | X | 1 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 10M | [23 empty] | N
Vintage1925 | hydro | TRUE | 189 | PowerSouth Energy Cooperative | 55 | Point A | AL | Covington | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.8 | 1.8 | 1.8 | 0.1 | N |  |  | OP | X | 1 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 10M | [23 empty] | N
Vintage1949 | hydro | TRUE | 189 | PowerSouth Energy Cooperative | 55 | Point A | AL | Covington | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 0.1 | N |  |  | OP | X | 1 | 1949 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 10M | [23 empty] | N
Vintage1982 | hard coal | TRUE | 40606 | City of Grand Island - (NE) | 59 | Platte | NE | Hall | 1 | Conventional Steam Coal | ST |  | S | X | X | NPPDGI_SUB-DUNGRIS_PGS1_RA | NPPDGI_SUB-DUNGRIS_PGS1_RA | 109.8 | 0.9 | 100 | 100 | 40 | N |  |  | OP | X | 12 | 1982 |  |  | N | Electric Utility | 1 | X | SUB | [5 empty] | DFO |  |  |  | N | N |  | OVER | N | Y |  |  | Y | [15 empty] | N |  |  | N | N | N
Vintage1981 | hard coal | TRUE | 8245 | City of Hastings - (NE) | 60 | Whelan Energy Center | NE | Adams | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 76.3 | 0.9 | 77 | 77 | 38 | N |  |  | OP | X | 7 | 1981 |  |  | N | Electric Utility | 1 | X | RC | [5 empty] | DFO |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage2011 | hard coal | TRUE | 8245 | City of Hastings - (NE) | 60 | Whelan Energy Center | NE | Adams | 2 | Conventional Steam Coal | ST |  | J | X | X |  |  | 248 | 0.85 | 232 | 232 | 125 | N |  |  | OP | X | 6 | 2011 |  |  | N | Electric Utility | 1 | X | SUB | RC |  |  |  |  | DFO |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1915 | hydro | TRUE | 213 | Alaska Electric Light & Power Co. | 62 | Annex Creek | AK | Juneau | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.1 | N |  |  | OP | X | 12 | 1915 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1915 | hydro | TRUE | 213 | Alaska Electric Light & Power Co. | 62 | Annex Creek | AK | Juneau | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 0.8 | 1.8 | 1.8 | 0.1 | N |  |  | OP | X | 12 | 1915 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1951 | hydro | TRUE | 213 | Alaska Electric Light & Power Co. | 63 | Gold Creek | AK | Juneau | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.1 | N |  |  | OP | X | 9 | 1951 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1914 | hydro | TRUE | 213 | Alaska Electric Light & Power Co. | 63 | Gold Creek | AK | Juneau | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 11 | 1914 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1914 | hydro | TRUE | 213 | Alaska Electric Light & Power Co. | 63 | Gold Creek | AK | Juneau | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 11 | 1914 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1952 | petroleum | TRUE | 213 | Alaska Electric Light & Power Co. | 63 | Gold Creek | AK | Juneau | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 0.3 | N |  |  | SB | Y | 6 | 1952 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1954 | petroleum | TRUE | 213 | Alaska Electric Light & Power Co. | 63 | Gold Creek | AK | Juneau | IC2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 0.3 | N |  |  | SB | Y | 8 | 1954 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1961 | petroleum | TRUE | 213 | Alaska Electric Light & Power Co. | 63 | Gold Creek | AK | Juneau | IC3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.3 | N |  |  | SB | Y | 8 | 1961 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1963 | petroleum | TRUE | 213 | Alaska Electric Light & Power Co. | 63 | Gold Creek | AK | Juneau | IC4 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.5 | 0.8 | 3.5 | 3.5 | 2 | N |  |  | SB | Y | 9 | 1963 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1966 | petroleum | TRUE | 213 | Alaska Electric Light & Power Co. | 63 | Gold Creek | AK | Juneau | IC5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.3 | N |  |  | SB | Y | 10 | 1966 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1969 | petroleum | TRUE | 213 | Alaska Electric Light & Power Co. | 64 | Lemon Creek | AK | Juneau | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | SB | Y | 8 | 1969 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1969 | petroleum | TRUE | 213 | Alaska Electric Light & Power Co. | 64 | Lemon Creek | AK | Juneau | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.6 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | SB | Y | 9 | 1969 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N |  | N
Vintage1974 | petroleum | TRUE | 213 | Alaska Electric Light & Power Co. | 64 | Lemon Creek | AK | Juneau | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.6 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | SB | Y | 9 | 1974 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1980 | petroleum | TRUE | 213 | Alaska Electric Light & Power Co. | 64 | Lemon Creek | AK | Juneau | 5 | Petroleum Liquids | GT |  | S | X | X |  |  | 18.6 | 0.85 | 17.5 | 17.5 | 4 | N |  |  | SB | Y | 9 | 1980 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N | N | N
Vintage1983 | petroleum | TRUE | 213 | Alaska Electric Light & Power Co. | 64 | Lemon Creek | AK | Juneau | 6 | Petroleum Liquids | GT |  | S | X | X |  |  | 18.6 | 0.85 | 17.5 | 17.5 | 4 | N |  |  | SB | Y | 8 | 1983 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N | N | N
Vintage1983 | petroleum | TRUE | 213 | Alaska Electric Light & Power Co. | 64 | Lemon Creek | AK | Juneau | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.8 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | SB | Y | 8 | 1983 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1984 | petroleum | TRUE | 213 | Alaska Electric Light & Power Co. | 64 | Lemon Creek | AK | Juneau | IC10 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.8 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | SB | Y | 9 | 1984 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1984 | petroleum | TRUE | 213 | Alaska Electric Light & Power Co. | 64 | Lemon Creek | AK | Juneau | IC11 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.8 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | SB | Y | 9 | 1984 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1984 | petroleum | TRUE | 213 | Alaska Electric Light & Power Co. | 64 | Lemon Creek | AK | Juneau | IC12 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.8 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | SB | Y | 9 | 1984 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1985 | petroleum | TRUE | 213 | Alaska Electric Light & Power Co. | 64 | Lemon Creek | AK | Juneau | IC8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.8 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | SB | Y | 8 | 1985 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1985 | petroleum | TRUE | 213 | Alaska Electric Light & Power Co. | 64 | Lemon Creek | AK | Juneau | IC9 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.8 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | SB | Y | 8 | 1985 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1984 | hydro | TRUE | 213 | Alaska Electric Light & Power Co. | 65 | Salmon Creek 1 | AK | Juneau | HY7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8.5 | 0.8 | 5.2 | 5.2 | 0.5 | N |  |  | OP | X | 12 | 1984 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1957 | hydro | TRUE | 219 | Alaska Power and Telephone Co | 66 | Skagway | AK | Skagway Hoonah Angoon | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0 | N |  |  | OP | X | 7 | 1957 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1909 | hydro | TRUE | 219 | Alaska Power and Telephone Co | 66 | Skagway | AK | Skagway Hoonah Angoon | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0 | N |  |  | OP | X | 7 | 1909 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1981 | hydro | TRUE | 219 | Alaska Power and Telephone Co | 66 | Skagway | AK | Skagway Hoonah Angoon | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0 | N |  |  | OP | X | 7 | 1981 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1987 | hydro | TRUE | 219 | Alaska Power and Telephone Co | 66 | Skagway | AK | Skagway Hoonah Angoon | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0 | N |  |  | OP | X | 7 | 1987 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1986 | petroleum | TRUE | 219 | Alaska Power and Telephone Co | 66 | Skagway | AK | Skagway Hoonah Angoon | 6A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 4 | 1986 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1996 | petroleum | TRUE | 219 | Alaska Power and Telephone Co | 66 | Skagway | AK | Skagway Hoonah Angoon | 7A | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.5 | N |  |  | OP | X | 5 | 1996 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1991 | petroleum | TRUE | 219 | Alaska Power and Telephone Co | 66 | Skagway | AK | Skagway Hoonah Angoon | 8A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.2 | N |  |  | OP | X | 9 | 1991 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage2009 | petroleum | TRUE | 219 | Alaska Power and Telephone Co | 66 | Skagway | AK | Skagway Hoonah Angoon | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.4 | N |  |  | OP | X | 4 | 2009 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1991 | petroleum | TRUE | 219 | Alaska Power and Telephone Co | 69 | Haines | AK | Haines | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 0.5 | N |  |  | OP | X | 5 | 1991 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage2006 | petroleum | TRUE | 219 | Alaska Power and Telephone Co | 69 | Haines | AK | Haines | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.9 | 0.8 | 1.9 | 1.9 | 0.7 | N |  |  | OP | X | 1 | 2006 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage2021 | petroleum | TRUE | 219 | Alaska Power and Telephone Co | 69 | Haines | AK | Haines | 12 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.6 | N |  |  | OP | X | 1 | 2021 |  |  | N | Electric Utility | 1 | X | DFO | [10 empty] | N |  | 10M | [23 empty] | N
Vintage1968 | petroleum | TRUE | 219 | Alaska Power and Telephone Co | 69 | Haines | AK | Haines | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.2 | N |  |  | OS | X | 6 | 1968 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1995 | petroleum | TRUE | 219 | Alaska Power and Telephone Co | 69 | Haines | AK | Haines | 7A | Petroleum Liquids | IC |  | S | X | X |  |  | 2.8 | 0.8 | 2.8 | 2.8 | 1.1 | N |  |  | OP | X | 12 | 1995 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1996 | petroleum | TRUE | 219 | Alaska Power and Telephone Co | 69 | Haines | AK | Haines | IC8A | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.6 | N |  |  | OP | X | 10 | 1996 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1984 | hydro | FALSE | 60123 | Southeast Alaska Power Agency | 70 | Swan Lake | AK | Ketchikan Gateway | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 11.3 | 0.9 | 11.3 | 11.3 | 1 | N |  |  | OP | X | 6 | 1984 |  |  | N | Commercial Non-CHP | 4 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1984 | hydro | FALSE | 60123 | Southeast Alaska Power Agency | 70 | Swan Lake | AK | Ketchikan Gateway | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 11.3 | 0.9 | 11.3 | 11.3 | 1 | N |  |  | OP | X | 6 | 1984 |  |  | N | Commercial Non-CHP | 4 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1984 | hydro | TRUE | 10433 | Kodiak Electric Assn Inc | 71 | Terror Lake Microgrid | AK | Kodiak Island | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 11.2 | 0.9 | 11.2 | 11.2 | 0.3 | N |  |  | OP | X | 12 | 1984 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 12H | [23 empty] | N
Vintage1984 | hydro | TRUE | 10433 | Kodiak Electric Assn Inc | 71 | Terror Lake Microgrid | AK | Kodiak Island | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 11.2 | 0.9 | 11.2 | 11.2 | 0.3 | N |  |  | OP | X | 12 | 1984 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 12H | [23 empty] | N
Vintage2014 | hydro | TRUE | 10433 | Kodiak Electric Assn Inc | 71 | Terror Lake Microgrid | AK | Kodiak Island | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 11.2 | 0.9 | 11.2 | 11.2 | 0.3 | N |  |  | OP | X | 2 | 2014 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 12H | [23 empty] | N
Vintage1982 | hydro | TRUE | 12397 | Metropolitan Water District of S CA | 72 | Venice Hydro | CA | Los Angeles | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10.1 | 1 | 10.1 | 10.1 | 3.8 | N |  |  | SB | Y | 8 | 1982 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 12H
Vintage2007 | natural gas peaker | TRUE | 3522 | Chugach Electric Assn Inc | 75 | Hank Nikkels Plant 1 | AK | Anchorage | 3R | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 48.9 | 0.85 | 29.3 | 32.9 | 3 | N |  |  | OP | X | 8 | 2007 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N
Vintage1972 | natural gas peaker | TRUE | 3522 | Chugach Electric Assn Inc | 75 | Hank Nikkels Plant 1 | AK | Anchorage | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 27 | 0.85 | 31.1 | 33.2 | 5 | N |  |  | OS | X | 3 | 1972 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2012 | petroleum | TRUE | 3522 | Chugach Electric Assn Inc | 75 | Hank Nikkels Plant 1 | AK | Anchorage | P1 BS | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | OP | X | 2 | 2012 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1955 | hydro | TRUE | 3522 | Chugach Electric Assn Inc | 77 | Eklutna Hydro Project | AK | Matanuska Susitna | 1 | Conventional Hydroelectric | HY |  | J | X | X |  |  | 22.2 | 0.9 | 22.2 | 22.2 | 3 | N |  |  | OP | X | 1 | 1955 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1955 | hydro | TRUE | 3522 | Chugach Electric Assn Inc | 77 | Eklutna Hydro Project | AK | Matanuska Susitna | 2 | Conventional Hydroelectric | HY |  | J | X | X |  |  | 22.2 | 0.9 | 22.2 | 22.2 | 3 | N |  |  | OP | X | 4 | 1955 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1973 | hydro | TRUE | 213 | Alaska Electric Light & Power Co. | 78 | Snettisham | AK | Juneau | 1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 23.6 | 0.9 | 23.5 | 23.5 | 2 | N |  |  | OP | X | 11 | 1973 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1973 | hydro | TRUE | 213 | Alaska Electric Light & Power Co. | 78 | Snettisham | AK | Juneau | 2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 23.6 | 0.9 | 23.5 | 23.5 | 2 | N |  |  | OP | X | 11 | 1973 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1990 | hydro | TRUE | 213 | Alaska Electric Light & Power Co. | 78 | Snettisham | AK | Juneau | 3 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 31 | 0.9 | 31 | 31 | 3 | N |  |  | OP | X | 12 | 1990 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1952 | hard coal | TRUE | 986 | Aurora Energy LLC | 79 | Aurora Energy LLC Chena | AK | Fairbanks North Star | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 5 | 0.8 | 4.7 | 4.3 | 1 | N |  |  | OP | X | 6 | 1952 |  |  | Y | IPP CHP | 3 | T | SUB | [5 empty] | WDS | DFO |  |  | N | N |  | 12H |  | N | Y | N | Y | [18 empty] | N | N | N
Vintage1952 | hard coal | TRUE | 986 | Aurora Energy LLC | 79 | Aurora Energy LLC Chena | AK | Fairbanks North Star | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 2.5 | 0.8 | 2 | 2 | 1 | N |  |  | OP | X | 6 | 1952 |  |  | Y | IPP CHP | 3 | T | SUB | [5 empty] | WDS | DFO |  |  | N | N |  | 12H |  | N | Y | N | Y | [18 empty] | N | N | N
Vintage1975 | hard coal | TRUE | 986 | Aurora Energy LLC | 79 | Aurora Energy LLC Chena | AK | Fairbanks North Star | 5 | Conventional Steam Coal | ST |  | S | X | X |  |  | 20 | 0.85 | 19 | 18.8 | 8 | N |  |  | OP | X | 6 | 1975 |  |  | Y | IPP CHP | 3 | T | SUB | [5 empty] | AB | DFO |  |  | N | N |  | 12H |  | N | Y |  | Y | [18 empty] | N | N | N
Vintage1952 | hydro | TRUE | 10210 | Ketchikan Public Utilities | 84 | Ketchikan | AK | Ketchikan Gateway | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.4 | 0.8 | 1.4 | 1.1 | 0.3 | N |  |  | OP | X | 1 | 1952 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 1H
Vintage1938 | hydro | TRUE | 10210 | Ketchikan Public Utilities | 84 | Ketchikan | AK | Ketchikan Gateway | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.4 | 0.8 | 1.4 | 1.1 | 0.3 | N |  |  | OP | X | 1 | 1938 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 1H
Vintage1954 | hydro | TRUE | 10210 | Ketchikan Public Utilities | 84 | Ketchikan | AK | Ketchikan Gateway | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.4 | 0.8 | 1.4 | 1.1 | 0.3 | N |  |  | OP | X | 1 | 1954 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 1H
Vintage1969 | petroleum | TRUE | 10210 | Ketchikan Public Utilities | 85 | S W Bailey | AK | Ketchikan Gateway | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.5 | 0.8 | 3.5 | 3.5 | 2 | N |  |  | OP | X | 1 | 1969 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1970 | petroleum | TRUE | 10210 | Ketchikan Public Utilities | 85 | S W Bailey | AK | Ketchikan Gateway | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.5 | 0.8 | 3.5 | 3.5 | 2 | N |  |  | OP | X | 1 | 1970 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1976 | petroleum | TRUE | 10210 | Ketchikan Public Utilities | 85 | S W Bailey | AK | Ketchikan Gateway | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 6.4 | 0.8 | 5.5 | 5.5 | 3 | N |  |  | OP | X | 1 | 1976 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1998 | petroleum | TRUE | 10210 | Ketchikan Public Utilities | 85 | S W Bailey | AK | Ketchikan Gateway | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 10.5 | 0.8 | 10.5 | 10.5 | 3.5 | N |  |  | OP | X | 10 | 1998 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1982 | hydro | TRUE | 15296 | New York Power Authority | 88 | Ashokan | NY | Ulster | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.3 | 1 | 2.3 | 2.3 | 1 | N |  |  | OP | X | 11 | 1982 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1982 | hydro | TRUE | 15296 | New York Power Authority | 88 | Ashokan | NY | Ulster | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.3 | 1 | 2.3 | 2.3 | 1 | N |  |  | OP | X | 11 | 1982 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1991 | petroleum | TRUE | 13642 | Nome Joint Utility Systems | 90 | Snake River | AK | Nome | 12 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.8 | 0.8 | 3.7 | 3.7 | 2.8 | N |  |  | OP | X | 4 | 1991 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 12H | [23 empty] | N
Vintage1999 | petroleum | TRUE | 13642 | Nome Joint Utility Systems | 90 | Snake River | AK | Nome | 14 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.9 | 1.9 | 1.4 | N |  |  | OP | X | 12 | 1999 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 12H | [23 empty] | N
Vintage2007 | petroleum | TRUE | 13642 | Nome Joint Utility Systems | 90 | Snake River | AK | Nome | 15 | Petroleum Liquids | IC |  | S | X | X |  |  | 5.2 | 0.8 | 5.2 | 5.2 | 3.4 | N |  |  | OP | X | 11 | 2007 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | OVER | [23 empty] | N
Vintage2007 | petroleum | TRUE | 13642 | Nome Joint Utility Systems | 90 | Snake River | AK | Nome | 16 | Petroleum Liquids | IC |  | S | X | X |  |  | 5.2 | 0.8 | 5.2 | 5.2 | 3.4 | N |  |  | OP | X | 11 | 2007 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | OVER | [23 empty] | N
Vintage2013 | petroleum | TRUE | 13642 | Nome Joint Utility Systems | 90 | Snake River | AK | Nome | 18 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 1 | 2013 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 12H | [23 empty] | N
Vintage2013 | onshore wind | TRUE | 13642 | Nome Joint Utility Systems | 90 | Snake River | AK | Nome | EWT 1 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 0.9 |  | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 7 | 2013 |  |  | N | Electric Utility | 1 | X | WND | [9 empty] | N | N | 1 | [24 empty] | N
Vintage2013 | onshore wind | TRUE | 13642 | Nome Joint Utility Systems | 90 | Snake River | AK | Nome | EWT 2 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 0.9 |  | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 7 | 2013 |  |  | N | Electric Utility | 1 | X | WND | [9 empty] | N | N | 1 | [24 empty] | N
Vintage1954 | hydro | TRUE | 14856 | Petersburg Borough - (AK) | 91 | Petersburg | AK | Wrangell Petersburg | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.7 | N |  |  | OP | X | 3 | 1954 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1972 | petroleum | TRUE | 14856 | Petersburg Borough - (AK) | 91 | Petersburg | AK | Wrangell Petersburg | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.6 | 0.8 | 1.7 | 1.7 | 1.4 | N |  |  | OP | X | 12 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1965 | petroleum | TRUE | 14856 | Petersburg Borough - (AK) | 91 | Petersburg | AK | Wrangell Petersburg | IC3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1 | 1 | 0.5 | N |  |  | OP | X | 10 | 1965 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1979 | petroleum | TRUE | 14856 | Petersburg Borough - (AK) | 91 | Petersburg | AK | Wrangell Petersburg | IC4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.3 | N |  |  | OP | X | 3 | 1979 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1979 | petroleum | TRUE | 14856 | Petersburg Borough - (AK) | 91 | Petersburg | AK | Wrangell Petersburg | IC5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.7 | 0.7 | 0.4 | N |  |  | OP | X | 3 | 1979 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1993 | petroleum | TRUE | 14856 | Petersburg Borough - (AK) | 91 | Petersburg | AK | Wrangell Petersburg | IC6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.6 | 0.8 | 2.3 | 2.3 | 1.5 | N |  |  | OP | X | 9 | 1993 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2001 | petroleum | TRUE | 14856 | Petersburg Borough - (AK) | 91 | Petersburg | AK | Wrangell Petersburg | IC7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.6 | 0.8 | 2.3 | 2.3 | 1.5 | N |  |  | OP | X | 8 | 2001 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2012 | petroleum | TRUE | 14856 | Petersburg Borough - (AK) | 91 | Petersburg | AK | Wrangell Petersburg | IC8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.2 | 2.2 | 1.2 | N |  |  | OP | X | 10 | 2012 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1975 | petroleum | TRUE | 16955 | City of Seward - (AK) | 92 | Seward (AK) | AK | Kenai Peninsula | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 4 | 1975 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1986 | petroleum | TRUE | 16955 | City of Seward - (AK) | 92 | Seward (AK) | AK | Kenai Peninsula | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 3 | 1986 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1985 | petroleum | TRUE | 16955 | City of Seward - (AK) | 92 | Seward (AK) | AK | Kenai Peninsula | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 3 | 1985 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2000 | petroleum | TRUE | 16955 | City of Seward - (AK) | 92 | Seward (AK) | AK | Kenai Peninsula | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.8 | 0.8 | 2.8 | 2.8 | 0.5 | N |  |  | OP | X | 12 | 2000 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2010 | petroleum | TRUE | 16955 | City of Seward - (AK) | 92 | Seward (AK) | AK | Kenai Peninsula | N1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.8 | 0.8 | 2.8 | 2.8 | 0.5 | N |  |  | OP | X | 7 | 2010 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2010 | petroleum | TRUE | 16955 | City of Seward - (AK) | 92 | Seward (AK) | AK | Kenai Peninsula | N2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 7 | 2010 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2014 | hydro | TRUE | 17271 | City & Borough of Sitka - (AK) | 93 | Blue Lake Hydro | AK | Sitka | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.3 | 0.8 | 5.3 | 5.3 | 1 | N |  |  | OP | X | 10 | 2014 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 1H | [23 empty] | N
Vintage2014 | hydro | TRUE | 17271 | City & Borough of Sitka - (AK) | 93 | Blue Lake Hydro | AK | Sitka | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.3 | 0.8 | 5.3 | 5.3 | 1 | N |  |  | OP | X | 10 | 2014 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 1H | [23 empty] | N
Vintage2014 | hydro | TRUE | 17271 | City & Borough of Sitka - (AK) | 93 | Blue Lake Hydro | AK | Sitka | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.3 | 0.8 | 5.3 | 5.3 | 1 | N |  |  | OP | X | 10 | 2014 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 1H | [23 empty] | N
Vintage2000 | petroleum | TRUE | 21015 | City of Wrangell - (AK) | 95 | Wrangell | AK | Wrangell Petersburg | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | OP | X | 9 | 2000 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage2000 | petroleum | TRUE | 21015 | City of Wrangell - (AK) | 95 | Wrangell | AK | Wrangell Petersburg | 12 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | OP | X | 9 | 2000 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage2002 | petroleum | TRUE | 21015 | City of Wrangell - (AK) | 95 | Wrangell | AK | Wrangell Petersburg | 13 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1987 | petroleum | TRUE | 21015 | City of Wrangell - (AK) | 95 | Wrangell | AK | Wrangell Petersburg | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 0.1 | N |  |  | OP | X | 6 | 1987 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N | N | N
Vintage1968 | natural gas peaker | TRUE | 3522 | Chugach Electric Assn Inc | 96 | Beluga | AK | Kenai Peninsula | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 16 | 0.85 | 18.9 | 19.6 | 1 | N |  |  | OP | X | 1 | 1968 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1968 | natural gas peaker | TRUE | 3522 | Chugach Electric Assn Inc | 96 | Beluga | AK | Kenai Peninsula | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 16 | 0.85 | 18.9 | 19.6 | 1 | N |  |  | OS | X | 1 | 1968 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1972 | natural gas peaker | TRUE | 3522 | Chugach Electric Assn Inc | 96 | Beluga | AK | Kenai Peninsula | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 59.1 | 0.9 | 58 | 64.8 | 2 | N |  |  | OP | X | 5 | 1972 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1975 | natural gas peaker | TRUE | 3522 | Chugach Electric Assn Inc | 96 | Beluga | AK | Kenai Peninsula | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 68.3 | 0.9 | 61.4 | 68.7 | 2 | N |  |  | OP | X | 10 | 1975 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1976 | natural gas peaker | TRUE | 3522 | Chugach Electric Assn Inc | 96 | Beluga | AK | Kenai Peninsula | 6 | Natural Gas Fired Combustion Turbine | GT | BCC8 | S | X | X |  |  | 76.5 | 0.9 | 72.6 | 79.2 | 2 | N |  |  | OS | X | 5 | 1976 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N
Vintage1978 | natural gas peaker | TRUE | 3522 | Chugach Electric Assn Inc | 96 | Beluga | AK | Kenai Peninsula | 7 | Natural Gas Fired Combustion Turbine | GT | BCC8 | S | X | X |  |  | 76.5 | 0.9 | 70.6 | 80.1 | 2 | N |  |  | OP | X | 12 | 1978 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | PG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1981 | natural gas peaker | TRUE | 15500 | Puget Sound Energy Inc | 99 | Frederickson | WA | Pierce | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 88.9 | 0.9 | 67 | 81.1 | 5 | N |  |  | OP | X | 11 | 1981 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1981 | natural gas peaker | TRUE | 15500 | Puget Sound Energy Inc | 99 | Frederickson | WA | Pierce | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 88.9 | 0.9 | 67 | 81.1 | 5 | N |  |  | OP | X | 11 | 1981 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1981 | hydro | TRUE | 16572 | Salt River Project | 100 | South Consolidated | AZ | Maricopa | SC1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.4 | 0.9 | 1.4 | 1.4 | 0.1 | N |  |  | OP | X | 9 | 1981 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 10M | [23 empty] | N
Vintage1987 | other | TRUE | 17609 | Southern California Edison Co | 104 | J S Eastwood | CA | Fresno | 1 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 199.8 | 0.9 | 199.8 | 199.8 | 0 | N |  |  | OP | X | 12 | 1987 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1983 | hard coal | TRUE | 18315 | Sunflower Electric Power Corp | 108 | Holcomb | KS | Finney | 1 | Conventional Steam Coal | ST |  | S | X | X | SECIHOLCOM1UN1 | SECIHOLCOM1UN1 | 348.7 | 0.9 | 359.1 | 359.1 | 95 | N |  |  | OP | X | 8 | 1983 |  |  | N | Electric Utility | 1 | X | SUB | NG |  |  |  |  | NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1988 | petroleum | TRUE | 13870 | Nushagak Electric Coop, Inc | 109 | Dillingham | AK | Dillingham | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.5 | N |  |  | OP | X | 5 | 1988 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2001 | petroleum | TRUE | 13870 | Nushagak Electric Coop, Inc | 109 | Dillingham | AK | Dillingham | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.5 | N |  |  | OP | X | 11 | 2001 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2006 | petroleum | TRUE | 13870 | Nushagak Electric Coop, Inc | 109 | Dillingham | AK | Dillingham | 12 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.5 | N |  |  | OP | X | 3 | 2006 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2006 | petroleum | TRUE | 13870 | Nushagak Electric Coop, Inc | 109 | Dillingham | AK | Dillingham | 13 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.5 | N |  |  | OP | X | 4 | 2006 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N | N | N
Vintage2008 | petroleum | TRUE | 13870 | Nushagak Electric Coop, Inc | 109 | Dillingham | AK | Dillingham | 14 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.5 | N |  |  | OP | X | 3 | 2008 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N | N | N
Vintage2008 | petroleum | TRUE | 13870 | Nushagak Electric Coop, Inc | 109 | Dillingham | AK | Dillingham | 15 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.5 | N |  |  | OP | X | 5 | 2008 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N | N | N
Vintage2009 | petroleum | TRUE | 13870 | Nushagak Electric Coop, Inc | 109 | Dillingham | AK | Dillingham | 16 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 12 | 2009 |  |  | N | Electric Utility | 1 | X | DFO | [12 empty] | 10M | [23 empty] | N | N | N
Vintage2019 | petroleum | TRUE | 13870 | Nushagak Electric Coop, Inc | 109 | Dillingham | AK | Dillingham | 17 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.2 | 0.8 | 2.2 | 2.2 | 1 | N |  |  | OP | X | 6 | 2019 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage2019 | petroleum | TRUE | 13870 | Nushagak Electric Coop, Inc | 109 | Dillingham | AK | Dillingham | 18 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.2 | 0.8 | 2.2 | 2.2 | 1 | N |  |  | OP | X | 6 | 2019 |  |  | N | Electric Utility | 1 | X | DFO | [12 empty] | 10M | [23 empty] | N
Vintage1962 | hard coal | TRUE | 803 | Arizona Public Service Co | 113 | Cholla | AZ | Navajo | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 113.6 | 0.85 | 116 | 116 | 30 | N |  |  | OP | X | 5 | 1962 |  |  | N | Electric Utility | 1 | X | SUB | NG |  |  |  |  | NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1980 | hard coal | TRUE | 803 | Arizona Public Service Co | 113 | Cholla | AZ | Navajo | 3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 312.3 | 0.94 | 271 | 271 | 75 | N |  |  | OP | X | 5 | 1980 |  |  | N | Electric Utility | 1 | X | SUB | DFO | BIT |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1972 | petroleum | TRUE | 803 | Arizona Public Service Co | 114 | Douglas | AZ | Cochise | 1 | Petroleum Liquids | GT |  | S | X | X |  |  | 26.1 | 0.9 | 15 | 19 | 2 | N |  |  | OP | X | 5 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1972 | natural gas peaker | TRUE | 803 | Arizona Public Service Co | 116 | Ocotillo | AZ | Maricopa | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 53.1 | 0.85 | 50 | 62 | 4 | N |  |  | OP | X | 5 | 1972 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1973 | natural gas peaker | TRUE | 803 | Arizona Public Service Co | 116 | Ocotillo | AZ | Maricopa | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 53.1 | 0.85 | 50 | 62 | 4 | N |  |  | OP | X | 7 | 1973 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage2019 | natural gas peaker | TRUE | 803 | Arizona Public Service Co | 116 | Ocotillo | AZ | Maricopa | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 161.9 | 0.85 | 104.7 | 105.8 | 45 | N |  |  | OP | X | 4 | 2019 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage2019 | natural gas peaker | TRUE | 803 | Arizona Public Service Co | 116 | Ocotillo | AZ | Maricopa | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 161.9 | 0.85 | 104.7 | 105.8 | 45 | N |  |  | OP | X | 4 | 2019 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage2019 | natural gas peaker | TRUE | 803 | Arizona Public Service Co | 116 | Ocotillo | AZ | Maricopa | GT5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 161.9 | 0.85 | 104.7 | 105.8 | 45 | N |  |  | OP | X | 5 | 2019 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 10M | [23 empty] | N
Vintage2019 | natural gas peaker | TRUE | 803 | Arizona Public Service Co | 116 | Ocotillo | AZ | Maricopa | GT6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 161.9 | 0.85 | 104.7 | 105.8 | 45 | N |  |  | OP | X | 4 | 2019 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 10M | [23 empty] | N
Vintage2019 | natural gas peaker | TRUE | 803 | Arizona Public Service Co | 116 | Ocotillo | AZ | Maricopa | GT7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 161.9 | 0.85 | 104.7 | 105.8 | 45 | N |  |  | OP | X | 4 | 2019 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 10M | [23 empty] | N
Vintage1976 | natural gas combined cycle | TRUE | 803 | Arizona Public Service Co | 117 | West Phoenix | AZ | Maricopa | 1B | Natural Gas Fired Combined Cycle | CS |  | S | N | N |  |  | 132 | 0.9 | 85 | 92 | 10 | N |  |  | OP | X | 6 | 1976 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1976 | natural gas combined cycle | TRUE | 803 | Arizona Public Service Co | 117 | West Phoenix | AZ | Maricopa | 2B | Natural Gas Fired Combined Cycle | CS |  | S | N | N |  |  | 132 | 0.9 | 85 | 92 | 10 | N |  |  | OP | X | 6 | 1976 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1976 | natural gas combined cycle | TRUE | 803 | Arizona Public Service Co | 117 | West Phoenix | AZ | Maricopa | 3B | Natural Gas Fired Combined Cycle | CS |  | S | N | N |  |  | 132 | 0.9 | 85 | 92 | 50 | N |  |  | OP | X | 6 | 1976 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage2001 | natural gas combined cycle | TRUE | 803 | Arizona Public Service Co | 117 | West Phoenix | AZ | Maricopa | C4-1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 91 | 0.85 | 68 | 80 | 40 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage2001 | natural gas combined cycle | TRUE | 803 | Arizona Public Service Co | 117 | West Phoenix | AZ | Maricopa | C4-2 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 44.6 | 0.85 | 39 | 40 | 0 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage2003 | natural gas combined cycle | TRUE | 803 | Arizona Public Service Co | 117 | West Phoenix | AZ | Maricopa | C5-1 | Natural Gas Fired Combined Cycle | CT | CC2 | S | X | Y |  |  | 184.5 | 0.85 | 155 | 160 | 85 | N |  |  | OP | X | 8 | 2003 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage2003 | natural gas combined cycle | TRUE | 803 | Arizona Public Service Co | 117 | West Phoenix | AZ | Maricopa | C5-2 | Natural Gas Fired Combined Cycle | CT | CC2 | S | X | Y |  |  | 184.5 | 0.85 | 153 | 160 | 85 | N |  |  | OP | X | 8 | 2003 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage2003 | natural gas combined cycle | TRUE | 803 | Arizona Public Service Co | 117 | West Phoenix | AZ | Maricopa | C5-3 | Natural Gas Fired Combined Cycle | CA | CC2 | S | Y | X |  |  | 200.6 | 0.85 | 150 | 166 | 0 | N |  |  | OP | X | 8 | 2003 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1972 | natural gas peaker | TRUE | 803 | Arizona Public Service Co | 117 | West Phoenix | AZ | Maricopa | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 53.1 | 0.85 | 50 | 62 | 4 | N |  |  | OP | X | 5 | 1972 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1973 | natural gas peaker | TRUE | 803 | Arizona Public Service Co | 117 | West Phoenix | AZ | Maricopa | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 53.1 | 0.85 | 50 | 62 | 4 | N |  |  | OP | X | 7 | 1973 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2002 | natural gas peaker | TRUE | 803 | Arizona Public Service Co | 118 | Saguaro | AZ | Pinal | GE1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 78.3 | 0.9 | 76 | 79 | 40 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1972 | natural gas peaker | TRUE | 803 | Arizona Public Service Co | 118 | Saguaro | AZ | Pinal | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 53.1 | 0.85 | 50 | 62 | 4 | N |  |  | OP | X | 5 | 1972 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1973 | natural gas peaker | TRUE | 803 | Arizona Public Service Co | 118 | Saguaro | AZ | Pinal | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 53.1 | 0.85 | 50 | 62 | 4 | N |  |  | OP | X | 7 | 1973 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1971 | natural gas peaker | TRUE | 803 | Arizona Public Service Co | 120 | Yucca | AZ | Yuma | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 23.6 | 0.9 | 18 | 22 | 2 | N |  |  | OP | X | 7 | 1971 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1971 | natural gas peaker | TRUE | 803 | Arizona Public Service Co | 120 | Yucca | AZ | Yuma | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 23.6 | 0.9 | 18 | 22 | 2 | N |  |  | OP | X | 7 | 1971 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1978 | petroleum | TRUE | 803 | Arizona Public Service Co | 120 | Yucca | AZ | Yuma | GT21 | Petroleum Liquids | GT |  | W | X | X |  |  | 25.3 | 0.9 | 20 | 22 | 2 | N |  |  | OP | X | 12 | 1978 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N |  | N
Vintage1973 | natural gas peaker | TRUE | 803 | Arizona Public Service Co | 120 | Yucca | AZ | Yuma | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 72.4 | 0.9 | 52 | 62 | 5 | N |  |  | OP | X | 6 | 1973 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | N |  | N
Vintage1974 | petroleum | TRUE | 803 | Arizona Public Service Co | 120 | Yucca | AZ | Yuma | GT4 | Petroleum Liquids | GT |  | S | X | X |  |  | 72.4 | 0.9 | 51 | 61 | 5 | N |  |  | OP | X | 7 | 1974 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage2008 | natural gas peaker | TRUE | 803 | Arizona Public Service Co | 120 | Yucca | AZ | Yuma | GT5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 60.5 | 0.85 | 47 | 49 | 20 | N |  |  | OP | X | 6 | 2008 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | N | N | N
Vintage2008 | natural gas peaker | TRUE | 803 | Arizona Public Service Co | 120 | Yucca | AZ | Yuma | GT6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 60.5 | 0.85 | 47 | 49 | 20 | N |  |  | OP | X | 6 | 2008 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | N | N | N
Vintage1959 | natural gas steam turbine | TRUE | 803 | Arizona Public Service Co | 120 | Yucca | AZ | Yuma | ST1 | Natural Gas Steam Turbine | ST |  | W | X | X |  |  | 86.7 | 0.9 | 75 | 75 | 2 | N |  |  | OP | X | 4 | 1959 |  |  | N | Electric Utility | 1 | X | NG | RFO |  |  |  |  | NG |  |  |  | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 24211 | Tucson Electric Power Co | 124 | Demoss Petrie | AZ | Pima | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 85 | 0.85 | 75 | 77.4 | 40 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1967 | natural gas steam turbine | TRUE | 24211 | Tucson Electric Power Co | 126 | H Wilson Sundt Generating Station | AZ | Pima | 4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 173.3 | 0.85 | 156 | 156 | 40 | N |  |  | OP | X | 7 | 1967 |  |  | N | Electric Utility | 1 | X | NG | LFG |  |  |  |  | NG |  |  |  | N | N |  | OVER |  | N | [21 empty] | Y | Y | N
Vintage1972 | natural gas peaker | TRUE | 24211 | Tucson Electric Power Co | 126 | H Wilson Sundt Generating Station | AZ | Pima | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 27 | 0.85 | 24 | 26.8 | 5 | N |  |  | OP | X | 12 | 1972 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H |  |  |  |  | N | [18 empty] | Y | N | Y
Vintage1972 | natural gas peaker | TRUE | 24211 | Tucson Electric Power Co | 126 | H Wilson Sundt Generating Station | AZ | Pima | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 27 | 0.85 | 24 | 26.8 | 5 | N |  |  | OP | X | 12 | 1972 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M |  |  |  |  | N | [18 empty] | Y | N | Y
Vintage2020 | natural gas peaker | TRUE | 24211 | Tucson Electric Power Co | 126 | H Wilson Sundt Generating Station | AZ | Pima | RIC1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 18.8 | 0.8 | 18.2 | 18.7 | 4.7 | N |  |  | OP | X | 3 | 2020 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2019 | natural gas peaker | TRUE | 24211 | Tucson Electric Power Co | 126 | H Wilson Sundt Generating Station | AZ | Pima | RIC10 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 18.8 | 0.8 | 18.2 | 18.7 | 4.7 | N |  |  | OP | X | 12 | 2019 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2020 | natural gas peaker | TRUE | 24211 | Tucson Electric Power Co | 126 | H Wilson Sundt Generating Station | AZ | Pima | RIC2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 18.8 | 0.8 | 18.2 | 18.7 | 4.7 | N |  |  | OP | X | 3 | 2020 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2020 | natural gas peaker | TRUE | 24211 | Tucson Electric Power Co | 126 | H Wilson Sundt Generating Station | AZ | Pima | RIC3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 18.8 | 0.8 | 18.2 | 18.7 | 4.7 | N |  |  | OP | X | 3 | 2020 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2020 | natural gas peaker | TRUE | 24211 | Tucson Electric Power Co | 126 | H Wilson Sundt Generating Station | AZ | Pima | RIC4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 18.8 | 0.8 | 18.2 | 18.7 | 4.7 | N |  |  | OP | X | 3 | 2020 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2020 | natural gas peaker | TRUE | 24211 | Tucson Electric Power Co | 126 | H Wilson Sundt Generating Station | AZ | Pima | RIC5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 18.8 | 0.8 | 18.2 | 18.7 | 4.7 | N |  |  | OP | X | 3 | 2020 |  |  | Y | Electric Utility | 1 | T | NG | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2019 | natural gas peaker | TRUE | 24211 | Tucson Electric Power Co | 126 | H Wilson Sundt Generating Station | AZ | Pima | RIC6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 18.8 | 0.8 | 18.2 | 18.7 | 4.7 | N |  |  | OP | X | 12 | 2019 |  |  | Y | Electric Utility | 1 | T | NG | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2019 | natural gas peaker | TRUE | 24211 | Tucson Electric Power Co | 126 | H Wilson Sundt Generating Station | AZ | Pima | RIC7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 18.8 | 0.8 | 18.2 | 18.7 | 4.7 | N |  |  | OP | X | 12 | 2019 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2019 | natural gas peaker | TRUE | 24211 | Tucson Electric Power Co | 126 | H Wilson Sundt Generating Station | AZ | Pima | RIC8 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 18.8 | 0.8 | 18.2 | 18.7 | 4.7 | N |  |  | OP | X | 12 | 2019 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2019 | natural gas peaker | TRUE | 24211 | Tucson Electric Power Co | 126 | H Wilson Sundt Generating Station | AZ | Pima | RIC9 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 18.8 | 0.8 | 18.2 | 18.7 | 4.7 | N |  |  | OP | X | 12 | 2019 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1962 | natural gas steam turbine | TRUE | 24211 | Tucson Electric Power Co | 126 | H Wilson Sundt Generating Station | AZ | Pima | ST3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 113.6 | 0.85 | 104 | 104 | 20 | N |  |  | OP | X | 6 | 1962 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1995 | hard coal | TRUE | 17543 | South Carolina Public Service Authority | 130 | Cross | SC | Berkeley | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 590.9 | 0.9 | 580 | 585 | 260 | N |  |  | OP | X | 5 | 1995 |  |  | N | Electric Utility | 1 | X | RC | BIT |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1984 | hard coal | TRUE | 17543 | South Carolina Public Service Authority | 130 | Cross | SC | Berkeley | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 556.2 | 0.9 | 565 | 570 | 250 | N |  |  | OP | X | 5 | 1984 |  |  | N | Electric Utility | 1 | X | RC | BIT |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage2007 | hard coal | TRUE | 17543 | South Carolina Public Service Authority | 130 | Cross | SC | Berkeley | 3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 591 | 0.9 | 610 | 610 | 250 | N |  |  | OP | X | 1 | 2007 |  |  | N | Electric Utility | 1 | X | RC | BIT |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage2008 | hard coal | TRUE | 17543 | South Carolina Public Service Authority | 130 | Cross | SC | Berkeley | 4 | Conventional Steam Coal | ST |  | S | X | X |  |  | 652 | 0.9 | 615 | 615 | 250 | N |  |  | OP | X | 10 | 2008 |  |  | N | Electric Utility | 1 | X | RC | BIT |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1984 | hard coal | TRUE | 21554 | Seminole Electric Cooperative Inc | 136 | Seminole (FL) | FL | Putnam | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 714.6 | 0.9 | 626 | 639 | 300 | N |  |  | OP | X | 2 | 1984 | 1 | 2023 | N | Electric Utility | 1 | X | BIT | [5 empty] | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1984 | hard coal | TRUE | 21554 | Seminole Electric Cooperative Inc | 136 | Seminole (FL) | FL | Putnam | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 714.6 | 0.9 | 634 | 640 | 300 | N |  |  | OP | X | 12 | 1984 |  |  | N | Electric Utility | 1 | X | BIT | [5 empty] | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1958 | natural gas steam turbine | TRUE | 16572 | Salt River Project | 141 | Agua Fria | AZ | Maricopa | AF1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 113.6 | 0.85 | 113 | 114 | 113 | N |  |  | OP | X | 1 | 1958 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | NG | DFO |  |  | N | N |  | 12H | [20 empty] | N |  |  | Y | Y | Y
Vintage1957 | natural gas steam turbine | TRUE | 16572 | Salt River Project | 141 | Agua Fria | AZ | Maricopa | AF2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 113.6 | 0.85 | 113 | 114 | 113 | N |  |  | OP | X | 4 | 1957 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | DFO | NG |  |  | N | N |  | 12H | [20 empty] | N |  |  | Y | Y | Y
Vintage1961 | natural gas steam turbine | TRUE | 16572 | Salt River Project | 141 | Agua Fria | AZ | Maricopa | AF3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 163.2 | 0.85 | 181 | 184 | 181 | N |  |  | OP | X | 4 | 1961 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | DFO | NG |  |  | N | N | 0 | OVER | [20 empty] | N |  |  | Y | Y | Y
Vintage1975 | natural gas peaker | TRUE | 16572 | Salt River Project | 141 | Agua Fria | AZ | Maricopa | AF4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 80.5 | 0.9 | 73 | 87 | 73 | N |  |  | OP | X | 5 | 1975 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [20 empty] | N |  |  | Y | Y | Y
Vintage1974 | natural gas peaker | TRUE | 16572 | Salt River Project | 141 | Agua Fria | AZ | Maricopa | AF5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 71.2 | 0.9 | 73 | 82 | 73 | N |  |  | OP | X | 7 | 1974 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [20 empty] | N |  |  | Y | Y | Y
Vintage1974 | natural gas peaker | TRUE | 16572 | Salt River Project | 141 | Agua Fria | AZ | Maricopa | AF6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 71.2 | 0.9 | 73 | 82 | 73 | N |  |  | OP | X | 7 | 1974 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [20 empty] | N |  |  | Y | Y | Y
Vintage2021 | other | TRUE | 16572 | Salt River Project | 141 | Agua Fria | AZ | Maricopa | AFSB1 | Batteries | BA |  | S | X | X |  |  | 25 |  | 25 | 25 | 25 | N |  |  | OP | X | 9 | 2021 |  |  | N | Electric Utility | 1 | X | MWH | [12 empty] | 10M
Vintage2001 | solar pv | TRUE | 16572 | Salt River Project | 141 | Agua Fria | AZ | Maricopa | PV-3 | Solar Photovoltaic | PV |  | S | X | X |  |  | 0.2 |  | 0.2 | 0.2 |  | N |  |  | OA | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X | SUN | [9 empty] | N | N | 0 | [24 empty] | N
Vintage1939 | hydro | TRUE | 16572 | Salt River Project | 143 | Crosscut | AZ | Maricopa | CC5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.9 | 3 | 3 | 0.1 | N |  |  | OS | X | 7 | 1939 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 10M | [23 empty] | N
Vintage1927 | hydro | TRUE | 16572 | Salt River Project | 145 | Horse Mesa | AZ | Maricopa | HM1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9.9 | 0.9 | 10 | 10 | 3 | N |  |  | OP | X | 4 | 1927 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1927 | hydro | TRUE | 16572 | Salt River Project | 145 | Horse Mesa | AZ | Maricopa | HM2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9.9 | 0.9 | 10 | 10 | 3 | N |  |  | OP | X | 4 | 1927 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1927 | hydro | TRUE | 16572 | Salt River Project | 145 | Horse Mesa | AZ | Maricopa | HM3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9.9 | 0.9 | 10 | 10 | 3 | N |  |  | OP | X | 4 | 1927 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [20 empty] | Y | 7 | 2023 | N
Vintage1972 | other | TRUE | 16572 | Salt River Project | 145 | Horse Mesa | AZ | Maricopa | HM4 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 99.8 | 0.9 | 119 | 119 | 80 | N |  |  | OP | X | 6 | 1972 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1952 | natural gas steam turbine | TRUE | 16572 | Salt River Project | 147 | Kyrene | AZ | Maricopa | KY1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 34.5 | 0.85 | 34 | 34 | 4 | N |  |  | OS | X | 7 | 1952 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | NG |  |  |  | N | N |  | OVER | [20 empty] | N |  |  | Y | N | Y
Vintage1954 | natural gas steam turbine | TRUE | 16572 | Salt River Project | 147 | Kyrene | AZ | Maricopa | KY2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 73.5 | 0.85 | 72 | 72 | 4 | N |  |  | OS | X | 6 | 1954 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | NG |  |  |  | N | N |  | OVER | [20 empty] | N |  |  | Y | N | Y
Vintage1971 | natural gas peaker | TRUE | 16572 | Salt River Project | 147 | Kyrene | AZ | Maricopa | KY4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 53.1 | 0.85 | 59 | 62.5 | 6 | N |  |  | OP | X | 12 | 1971 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | NG |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1973 | natural gas peaker | TRUE | 16572 | Salt River Project | 147 | Kyrene | AZ | Maricopa | KY5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 60.3 | 0.9 | 53 | 62 | 6 | N |  |  | OP | X | 7 | 1973 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | NG |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1973 | natural gas peaker | TRUE | 16572 | Salt River Project | 147 | Kyrene | AZ | Maricopa | KY6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 60.3 | 0.9 | 53 | 62 | 6 | N |  |  | OP | X | 6 | 1973 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | NG |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage2002 | natural gas combined cycle | TRUE | 16572 | Salt River Project | 147 | Kyrene | AZ | Maricopa | KY7 | Natural Gas Fired Combined Cycle | CT | KYS7 | S | X | N |  |  | 170 | 0.85 | 148 | 167 | 90 | N |  |  | OP | X | 10 | 2002 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | 12H | [20 empty] | Y | 4 | 2026 | N | N | N
Vintage2002 | natural gas combined cycle | TRUE | 16572 | Salt River Project | 147 | Kyrene | AZ | Maricopa | KY7A | Natural Gas Fired Combined Cycle | CA | KYS7 | S | Y | X |  |  | 122 | 0.85 | 106 | 110 | 90 | N |  |  | OP | X | 10 | 2002 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | 12H | [20 empty] | Y | 4 | 2026 | N | N | N
Vintage1926 | hydro | TRUE | 16572 | Salt River Project | 148 | Mormon Flat | AZ | Maricopa | MF1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9.2 | 0.9 | 11.5 | 11.5 | 8 | N |  |  | OP | X | 5 | 1926 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1971 | other | TRUE | 16572 | Salt River Project | 148 | Mormon Flat | AZ | Maricopa | MF2 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 54.3 | 0.9 | 57.3 | 57.3 | 10 | N |  |  | OP | X | 6 | 1971 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1973 | hydro | TRUE | 16572 | Salt River Project | 149 | Roosevelt | AZ | Maricopa | ROOS | Conventional Hydroelectric | HY |  | S | X | X |  |  | 36 | 0.9 | 36 | 36 | 10 | N |  |  | OP | X | 3 | 1973 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [20 empty] | Y | 3 | 2022 | N
Vintage1930 | hydro | TRUE | 16572 | Salt River Project | 150 | Stewart Mountain | AZ | Maricopa | SM | Conventional Hydroelectric | HY |  | S | X | X |  |  | 13 | 0.8 | 13 | 13 | 0.1 | N |  |  | OP | X | 3 | 1930 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1980 | petroleum | TRUE | 12745 | Modesto Irrigation District | 151 | McClure | CA | Stanislaus | 1 | Petroleum Liquids | GT |  | S | X | X |  |  | 71.2 | 0.9 | 53.5 | 53.5 | 20 | N |  |  | OP | X | 7 | 1980 |  |  | N | Electric Utility | 1 | X | DFO | NG |  |  |  |  | DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1981 | natural gas peaker | TRUE | 12745 | Modesto Irrigation District | 151 | McClure | CA | Stanislaus | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 71.2 | 0.9 | 53.5 | 53.5 | 20 | N |  |  | OP | X | 7 | 1981 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1951 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 152 | Davis Dam | AZ | Mohave | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 51.7 | 1 | 51.7 | 51.7 | 0 | N |  |  | OP | X | 1 | 1951 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1951 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 152 | Davis Dam | AZ | Mohave | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 51.7 | 1 | 51.7 | 51.7 | 0 | N |  |  | OP | X | 4 | 1951 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1951 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 152 | Davis Dam | AZ | Mohave | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 48 | 1 | 48 | 48 | 0 | N |  |  | OP | X | 4 | 1951 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1951 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 152 | Davis Dam | AZ | Mohave | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 51.7 | 1 | 51.7 | 51.7 | 0 | N |  |  | OP | X | 5 | 1951 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1951 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 152 | Davis Dam | AZ | Mohave | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 51.7 | 1 | 51.7 | 51.7 | 0 | N |  |  | OP | X | 6 | 1951 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1964 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 153 | Glen Canyon Dam | AZ | Coconino | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 165 | 0.95 | 165 | 165 | 0 | N |  |  | OP | X | 9 | 1964 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1964 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 153 | Glen Canyon Dam | AZ | Coconino | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 165 | 0.95 | 165 | 165 | 0 | N |  |  | OP | X | 9 | 1964 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1964 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 153 | Glen Canyon Dam | AZ | Coconino | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 165 | 0.95 | 165 | 165 | 0 | N |  |  | OP | X | 12 | 1964 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1965 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 153 | Glen Canyon Dam | AZ | Coconino | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 165 | 0.95 | 165 | 165 | 0 | N |  |  | OP | X | 2 | 1965 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1965 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 153 | Glen Canyon Dam | AZ | Coconino | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 165 | 0.95 | 165 | 165 | 0 | N |  |  | OP | X | 7 | 1965 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1965 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 153 | Glen Canyon Dam | AZ | Coconino | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 165 | 0.95 | 165 | 165 | 0 | N |  |  | OP | X | 10 | 1965 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1966 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 153 | Glen Canyon Dam | AZ | Coconino | 7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 157 | 0.95 | 157 | 157 | 0 | N |  |  | OP | X | 1 | 1966 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1966 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 153 | Glen Canyon Dam | AZ | Coconino | 8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 165 | 0.95 | 165 | 165 | 0 | N |  |  | OP | X | 2 | 1966 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1936 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 154 | Hoover Dam (NV) | NV | Clark | N0 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 2.4 | 2.4 | 0 | N |  |  | OP | X | 9 | 1936 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1936 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 154 | Hoover Dam (NV) | NV | Clark | N1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 130 | 0.98 | 130 | 130 | 0 | N |  |  | OP | X | 12 | 1936 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1936 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 154 | Hoover Dam (NV) | NV | Clark | N2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 130 | 0.98 | 130 | 130 | 0 | N |  |  | OP | X | 10 | 1936 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1937 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 154 | Hoover Dam (NV) | NV | Clark | N3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 130 | 0.98 | 130 | 130 | 0 | N |  |  | OP | X | 3 | 1937 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1936 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 154 | Hoover Dam (NV) | NV | Clark | N4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 130 | 0.98 | 130 | 130 | 0 | N |  |  | OP | X | 11 | 1936 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1938 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 154 | Hoover Dam (NV) | NV | Clark | N5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 130 | 0.98 | 130 | 130 | 0 | N |  |  | OP | X | 6 | 1938 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1938 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 154 | Hoover Dam (NV) | NV | Clark | N6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 130 | 0.98 | 130 | 130 | 0 | N |  |  | OP | X | 8 | 1938 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1944 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 154 | Hoover Dam (NV) | NV | Clark | N7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 127 | 0.97 | 127 | 127 | 0 | N |  |  | OP | X | 11 | 1944 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1961 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 154 | Hoover Dam (NV) | NV | Clark | N8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 130 | 0.98 | 130 | 130 | 0 | N |  |  | OP | X | 12 | 1961 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1981 | hydro | TRUE | 8366 | Heber Light & Power Company | 159 | Lake Creek Dam | UT | Wasatch | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 1 | 1 | 1 | 0.2 | N |  |  | OP | X | 5 | 1981 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1963 | natural gas peaker | TRUE | 796 | Arizona Electric Pwr Coop Inc | 160 | Apache Station | AZ | Cochise | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 11.5 | 0.85 | 10 | 10 | 1 | N |  |  | SB | Y | 2 | 1963 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1972 | natural gas peaker | TRUE | 796 | Arizona Electric Pwr Coop Inc | 160 | Apache Station | AZ | Cochise | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 20.4 | 0.9 | 18.5 | 20 | 2 | N |  |  | SB | Y | 6 | 1972 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1975 | natural gas peaker | TRUE | 796 | Arizona Electric Pwr Coop Inc | 160 | Apache Station | AZ | Cochise | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 78.7 | 0.9 | 60 | 63 | 7 | N |  |  | SB | Y | 6 | 1975 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2002 | natural gas peaker | TRUE | 796 | Arizona Electric Pwr Coop Inc | 160 | Apache Station | AZ | Cochise | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 60.5 | 0.85 | 38 | 44 | 5 | N |  |  | SB | Y | 10 | 2002 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1964 | natural gas steam turbine | TRUE | 796 | Arizona Electric Pwr Coop Inc | 160 | Apache Station | AZ | Cochise | ST1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 81.6 | 0.85 | 72 | 72 | 20 | N |  |  | SB | Y | 11 | 1964 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1979 | natural gas steam turbine | TRUE | 796 | Arizona Electric Pwr Coop Inc | 160 | Apache Station | AZ | Cochise | ST2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 204 | 0.85 | 175 | 175 | 50 | N |  |  | OP | X | 1 | 1979 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER |  | N |  |  | N | [18 empty] | N | N | N
Vintage1979 | hard coal | TRUE | 796 | Arizona Electric Pwr Coop Inc | 160 | Apache Station | AZ | Cochise | ST3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 204 | 0.85 | 175 | 175 | 50 | N |  |  | OP | X | 9 | 1979 |  |  | N | Electric Utility | 1 | X | SUB | NG | BIT |  |  |  | NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1980 | hydro | TRUE | 19281 | Turlock Irrigation District | 161 | Turlock Lake | CA | Stanislaus | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.1 | 0.95 | 1.1 | 1.1 | 0.3 | N |  |  | OP | X | 7 | 1980 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1980 | hydro | TRUE | 19281 | Turlock Irrigation District | 161 | Turlock Lake | CA | Stanislaus | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.1 | 0.95 | 1.1 | 1.1 | 0.3 | N |  |  | OP | X | 7 | 1980 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1980 | hydro | TRUE | 19281 | Turlock Irrigation District | 161 | Turlock Lake | CA | Stanislaus | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.1 | 0.95 | 1.1 | 1.1 | 0.3 | N |  |  | OP | X | 7 | 1980 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1979 | hydro | TRUE | 19281 | Turlock Irrigation District | 162 | Hickman | CA | Stanislaus | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.95 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 9 | 1979 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1979 | hydro | TRUE | 19281 | Turlock Irrigation District | 162 | Hickman | CA | Stanislaus | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.95 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 9 | 1979 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1985 | hard coal | TRUE | 7490 | Grand River Dam Authority | 165 | GREC | OK | Mayes | 2 | Conventional Steam Coal | ST |  | S | X | X | GRDAGRDA17UN2 | GRDAGRDA17UN2_RA | 594 | 0.9 | 492 | 492 | 150 | N |  |  | OP | X | 10 | 1985 |  |  | N | Electric Utility | 1 | X | SUB | [5 empty] | NG |  |  |  | N | N | 0 | OVER |  | Y |  |  | Y | [15 empty] | N |  |  | N | N | N
Vintage2017 | natural gas combined cycle | TRUE | 7490 | Grand River Dam Authority | 165 | GREC | OK | Mayes | 3CT | Natural Gas Fired Combined Cycle | CT | CT03 | S | X | N | GRDAGREC3UNGREC3 | GRDAGREC3UNGREC3 | 369 | 0.9 | 310.3 | 327.3 | 160 | N |  |  | OP | X | 12 | 2017 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N | 0 | 12H | [20 empty] | N |  |  | N | N | N
Vintage2017 | natural gas combined cycle | TRUE | 7490 | Grand River Dam Authority | 165 | GREC | OK | Mayes | 3ST | Natural Gas Fired Combined Cycle | CA | CT03 | S | Y | X | GRDAGREC3UNGREC3 | GRDAGREC3UNGREC3 | 231.3 | 0.9 | 166.7 | 175.7 | 100 | N |  |  | OP | X | 12 | 2017 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N | 0 | 12H |  |  |  |  | N | [15 empty] | N |  |  | N | N | N
Vintage1932 | hydro | TRUE | 814 | Entergy Arkansas LLC | 166 | Carpenter | AR | Garland | 1 | Conventional Hydroelectric | HY |  | S | X | X | EAI.CARPEN1 | EAI.CARPEN1 | 28 | 0.9 | 30.9 | 30.9 | 15 | N |  |  | OP | X | 1 | 1932 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1932 | hydro | TRUE | 814 | Entergy Arkansas LLC | 166 | Carpenter | AR | Garland | 2 | Conventional Hydroelectric | HY |  | S | X | X | EAI.CARPEN2 | EAI.CARPEN2 | 28 | 0.9 | 30.8 | 30.8 | 15 | N |  |  | OP | X | 1 | 1932 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1970 | natural gas steam turbine | TRUE | 814 | Entergy Arkansas LLC | 170 | Lake Catherine | AR | Hot Spring | 4 | Natural Gas Steam Turbine | ST |  | S | X | X | EAI.LK_CATH4 | EAI.LK_CATH4 | 552.5 | 0.85 | 522 | 522 | 45 | N |  |  | OP | X | 4 | 1970 | 6 | 2025 | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N |  |  | OVER | [23 empty] | N |  | N
Vintage1992 | petroleum | TRUE | 14216 | City of Osceola - (AR) | 172 | Osceola (AR) | AR | Mississippi | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 1 | 1.6 | 1.6 | 1.6 | N |  |  | SB | N | 5 | 1992 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1925 | hydro | TRUE | 814 | Entergy Arkansas LLC | 174 | Remmel | AR | Hot Spring | 1 | Conventional Hydroelectric | HY |  | S | X | X | EAI.REMMEL123 | EAI.REMMEL123 | 3 | 0.85 | 3.9 | 3.9 | 1 | N |  |  | OP | X | 1 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M | [23 empty] | N
Vintage1925 | hydro | TRUE | 814 | Entergy Arkansas LLC | 174 | Remmel | AR | Hot Spring | 2 | Conventional Hydroelectric | HY |  | S | X | X | EAI.REMMEL123 | EAI.REMMEL123 | 3 | 0.85 | 3.7 | 3.7 | 1 | N |  |  | OP | X | 1 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M | [23 empty] | N
Vintage1925 | hydro | TRUE | 814 | Entergy Arkansas LLC | 174 | Remmel | AR | Hot Spring | 3 | Conventional Hydroelectric | HY |  | S | X | X | EAI.REMMEL123 | EAI.REMMEL123 | 3 | 0.85 | 3.8 | 3.8 | 1 | N |  |  | OP | X | 1 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M | [23 empty] | N
Vintage1981 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 180 | Volta 2 | CA | Shasta | 1 | Conventional Hydroelectric | HY |  | S | X | X | VOLTA2_7_N002 | VOLTA2_7_N002 | 1 | 0.84 | 0.9 | 0.9 | 0 | N |  |  | OP | X | 11 | 1981 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1965 | hydro | TRUE | 19647 | USCE-Little Rock District | 182 | Beaver Dam | AR | Carroll | 1 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 56 | 0.95 | 64.4 | 64.4 | 20 | N |  |  | OA | X | 5 | 1965 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1965 | hydro | TRUE | 19647 | USCE-Little Rock District | 182 | Beaver Dam | AR | Carroll | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 56 | 0.95 | 64.4 | 64.4 | 20 | N |  |  | OS | X | 5 | 1965 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1972 | hydro | TRUE | 19406 | USCE -Vickburg District | 187 | Degray | AR | Clark | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40 | 0.95 | 40 | 40 | 15 | N |  |  | OP | X | 2 | 1972 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H
Vintage1972 | other | TRUE | 19406 | USCE -Vickburg District | 187 | Degray | AR | Clark | 2 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 30 | 0.95 | 30 | 30 | 15 | N |  |  | OP | X | 2 | 1972 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H
Vintage1964 | hydro | TRUE | 19647 | USCE-Little Rock District | 188 | Greers Ferry Lake | AR | Cleburne | 1 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 48 | 0.95 | 50 | 50 | 15 | N |  |  | OP | X | 3 | 1964 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1964 | hydro | TRUE | 19647 | USCE-Little Rock District | 188 | Greers Ferry Lake | AR | Cleburne | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 48 | 0.95 | 40 | 40 | 15 | N |  |  | OP | X | 5 | 1964 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1963 | petroleum | TRUE | 15043 | City of Piggott - (AR) | 193 | Municipal Light | AR | Clay | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 1 | 2 | 2 | 1.2 | N |  |  | OS | X | 10 | 1963 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1952 | petroleum | TRUE | 15043 | City of Piggott - (AR) | 193 | Municipal Light | AR | Clay | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 1 | 0.6 | 0.6 | 0.4 | N |  |  | OS | X | 4 | 1952 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1976 | petroleum | TRUE | 15043 | City of Piggott - (AR) | 193 | Municipal Light | AR | Clay | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.2 | 1 | 2.2 | 2.2 | 1.4 | N |  |  | OS | X | 3 | 1976 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1959 | petroleum | TRUE | 15043 | City of Piggott - (AR) | 193 | Municipal Light | AR | Clay | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 1 | 1.3 | 1.3 | 0.7 | N |  |  | OS | X | 3 | 1959 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1955 | petroleum | TRUE | 15043 | City of Piggott - (AR) | 193 | Municipal Light | AR | Clay | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 1 | 1.1 | 1.1 | 0.6 | N |  |  | OS | X | 1 | 1955 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1950 | hydro | TRUE | 19406 | USCE -Vickburg District | 195 | Narrows (AR) | AR | Pike | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8.5 | 0.9 | 9.7 | 9.7 | 5 | N |  |  | OP | X | 5 | 1950 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 1H
Vintage1950 | hydro | TRUE | 19406 | USCE -Vickburg District | 195 | Narrows (AR) | AR | Pike | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8.5 | 0.9 | 9.7 | 9.7 | 5 | N |  |  | OP | X | 5 | 1950 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 1H
Vintage1969 | hydro | TRUE | 19406 | USCE -Vickburg District | 195 | Narrows (AR) | AR | Pike | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8.5 | 0.9 | 9.7 | 9.7 | 5 | N |  |  | OP | X | 9 | 1969 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 1H
Vintage1950 | hydro | TRUE | 19647 | USCE-Little Rock District | 196 | Norfork | AR | Baxter | 1 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 40.2 | 0.9 | 40 | 40 | 10 | N |  |  | OP | X | 2 | 1950 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1944 | hydro | TRUE | 19647 | USCE-Little Rock District | 196 | Norfork | AR | Baxter | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40.2 | 0.9 | 40 | 40 | 10 | N |  |  | OP | X | 6 | 1944 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1955 | hydro | TRUE | 19406 | USCE -Vickburg District | 197 | Blakely Mountain | AR | Garland | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 37.5 | 0.9 | 37.5 | 37.5 | 20 | N |  |  | OP | X | 9 | 1955 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1955 | hydro | TRUE | 19406 | USCE -Vickburg District | 197 | Blakely Mountain | AR | Garland | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 37.5 | 0.9 | 37.5 | 37.5 | 20 | N |  |  | OP | X | 10 | 1955 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1952 | hydro | TRUE | 19647 | USCE-Little Rock District | 198 | Bull Shoals | AR | Marion | 1 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 40 | 0.95 | 45 | 45 | 10 | N |  |  | OP | X | 9 | 1952 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1952 | hydro | TRUE | 19647 | USCE-Little Rock District | 198 | Bull Shoals | AR | Marion | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40 | 0.95 | 45 | 45 | 10 | N |  |  | OP | X | 9 | 1952 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1952 | hydro | TRUE | 19647 | USCE-Little Rock District | 198 | Bull Shoals | AR | Marion | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40 | 0.95 | 35 | 35 | 10 | N |  |  | OP | X | 12 | 1952 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1953 | hydro | TRUE | 19647 | USCE-Little Rock District | 198 | Bull Shoals | AR | Marion | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40 | 0.95 | 45 | 45 | 10 | N |  |  | OP | X | 6 | 1953 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1962 | hydro | TRUE | 19647 | USCE-Little Rock District | 198 | Bull Shoals | AR | Marion | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 45 | 0.95 | 50 | 50 | 10 | N |  |  | OP | X | 1 | 1962 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1962 | hydro | TRUE | 19647 | USCE-Little Rock District | 198 | Bull Shoals | AR | Marion | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 45 | 0.95 | 50 | 50 | 10 | N |  |  | OP | X | 2 | 1962 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1963 | hydro | TRUE | 19647 | USCE-Little Rock District | 198 | Bull Shoals | AR | Marion | 7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 45 | 0.95 | 50 | 50 | 10 | N |  |  | OP | X | 8 | 1963 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1963 | hydro | TRUE | 19647 | USCE-Little Rock District | 198 | Bull Shoals | AR | Marion | 8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 45 | 0.95 | 50 | 50 | 10 | N |  |  | OP | X | 9 | 1963 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1965 | hydro | TRUE | 19647 | USCE-Little Rock District | 199 | Dardanelle | AR | Pope | 1 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 40.2 | 0.95 | 35 | 35 | 10 | N |  |  | OP | X | 4 | 1965 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1965 | hydro | TRUE | 19647 | USCE-Little Rock District | 199 | Dardanelle | AR | Pope | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40.2 | 0.95 | 35 | 35 | 10 | N |  |  | OP | X | 5 | 1965 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1965 | hydro | TRUE | 19647 | USCE-Little Rock District | 199 | Dardanelle | AR | Pope | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40.2 | 0.95 | 35 | 35 | 10 | N |  |  | OP | X | 9 | 1965 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1966 | hydro | TRUE | 19647 | USCE-Little Rock District | 199 | Dardanelle | AR | Pope | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40.2 | 0.95 | 35 | 35 | 10 | N |  |  | OP | X | 1 | 1966 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1963 | natural gas combined cycle | TRUE | 807 | Arkansas Electric Coop Corp | 201 | Thomas Fitzhugh | AR | Franklin | 1 | Natural Gas Fired Combined Cycle | CA | FIT1 | S | Y | X | AECC_FITZHUGH | SWPP | 59 | 0.88 | 61 | 62 | 25 | N |  |  | OP | X | 5 | 1963 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2002 | natural gas combined cycle | TRUE | 807 | Arkansas Electric Coop Corp | 201 | Thomas Fitzhugh | AR | Franklin | 2 | Natural Gas Fired Combined Cycle | CT | FIT1 | S | X | Y | AECC_FITZHUGH | SWPP | 126 | 0.9 | 101 | 110 | 65 | N |  |  | OP | X | 12 | 2002 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1966 | natural gas steam turbine | TRUE | 807 | Arkansas Electric Coop Corp | 202 | Carl Bailey | AR | Woodruff | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | EAI.AECCBAILEY | EIA | 120 | 0.85 | 122 | 122 | 25 | N |  |  | OS | X | 7 | 1966 |  |  | N | Electric Utility | 1 | X | NG | RFO |  |  |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1972 | natural gas steam turbine | TRUE | 807 | Arkansas Electric Coop Corp | 203 | McClellan (AR) | AR | Ouachita | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | EAI.AECCMCCLLN | EIA | 136 | 0.85 | 134 | 134 | 35 | N |  |  | OP | X | 5 | 1972 |  |  | N | Electric Utility | 1 | X | NG | RFO |  |  |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1987 | nuclear | TRUE | 55951 | Exelon Nuclear | 204 | Clinton Power Station | IL | DeWitt | 1 | Nuclear | ST |  | S | X | X | 20589649 | 20589649 | 1138.3 | 0.9 | 1065 | 1078 | 296.9 | N |  |  | OP | X | 11 | 1987 |  |  | N | IPP Non-CHP | 2 | X | NUC | [9 empty] | N | N |  | OVER | [23 empty] | N
Vintage1985 | nuclear | TRUE | 20893 | Wolf Creek Nuclear Optg Corp | 210 | Wolf Creek Generating Station | KS | Coffey | 1 | Nuclear | ST |  | J | X | X |  |  | 1267.7 | 0.9 | 1225 | 1255 | 50 | N |  |  | OP | X | 9 | 1985 |  |  | N | Electric Utility | 1 | X | NUC | [9 empty] | N | N |  | OVER | [23 empty] | N | N | N
Vintage1902 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 214 | Alta Powerhouse | CA | Placer | 1 | Conventional Hydroelectric | HY |  | S | X | X | BONNIEN_7_N002 | BONNIEN_7_N002 | 1 | 1 | 1 | 1 | 0 | N |  |  | OP | X | 11 | 1902 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1940 | hydro | TRUE | 19586 | Utica Water & Power Authority | 215 | Angels | CA | Calaveras | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.4 | 0.8 | 0.7 | 1 | 0.3 | N |  |  | OP | X | 1 | 1940 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1927 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 217 | Balch 1 | CA | Fresno | 1 | Conventional Hydroelectric | HY |  | S | X | X | BALCH1_7_B2 | BALCH1_7_B2 | 31 | 0.94 | 34 | 34 | 0 | N |  |  | OP | X | 2 | 1927 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1958 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 218 | Balch 2 | CA | Fresno | 2 | Conventional Hydroelectric | HY |  | S | X | X | BLCH38750_7_B1 | BLCH38750_7_B1 | 48.6 | 0.9 | 52.5 | 52.5 | 0 | N |  |  | OP | X | 11 | 1958 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1958 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 218 | Balch 2 | CA | Fresno | 3 | Conventional Hydroelectric | HY |  | S | X | X | BLCH38751_7_B1 | BLCH38751_7_B1 | 48.6 | 0.9 | 52.5 | 52.5 | 0 | N |  |  | OP | X | 12 | 1958 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1969 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 219 | Belden | CA | Plumas | 1 | Conventional Hydroelectric | HY |  | S | X | X | BELDEN_7_B1 | BELDEN_7_B1 | 117.9 | 0.9 | 125 | 125 | 0 | N |  |  | OP | X | 9 | 1969 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1928 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 220 | Bucks Creek | CA | Plumas | H1 | Conventional Hydroelectric | HY |  | S | X | X | BUCKCK_7_PL1X2-APND | BUCKCK_7_PL1X2-APND | 33 | 1 | 32.5 | 32.5 | 0 | N |  |  | OP | X | 3 | 1928 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1928 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 220 | Bucks Creek | CA | Plumas | H2 | Conventional Hydroelectric | HY |  | S | X | X | BUCKCK_7_PL1X2-APND | BUCKCK_7_PL1X2-APND | 33 | 1 | 32.5 | 32.5 | 0 | N |  |  | OP | X | 3 | 1928 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1958 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 221 | Butt Valley | CA | Plumas | 1 | Conventional Hydroelectric | HY |  | S | X | X | BUTTVLLY_7_B1 | BUTTVLLY_7_B1 | 40 | 0.9 | 41 | 41 | 0 | N |  |  | OP | X | 12 | 1958 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1921 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 222 | Caribou 1 | CA | Plumas | 1 | Conventional Hydroelectric | HY |  | S | X | X | CARABOU_7_B12 | CARABOU_7_B12 | 23.8 | 0.9 | 25 | 25 | 0 | N |  |  | OP | X | 6 | 1921 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1921 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 222 | Caribou 1 | CA | Plumas | 2 | Conventional Hydroelectric | HY |  | S | X | X | CARBOU_7_PL2X3-APND | CARBOU_7_PL2X3-APND | 25 | 0.9 | 25 | 25 | 0 | N |  |  | OP | X | 6 | 1921 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1924 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 222 | Caribou 1 | CA | Plumas | 3 | Conventional Hydroelectric | HY |  | S | X | X | CARBOU_7_PL2X3-APND | CARBOU_7_PL2X3-APND | 25 | 0.9 | 25 | 25 | 0 | N |  |  | OP | X | 5 | 1924 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1958 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 223 | Caribou 2 | CA | Plumas | 4 | Conventional Hydroelectric | HY |  | S | X | X | CARBOU_7_PL4X5-APND | CARBOU_7_PL4X5-APND | 60.3 | 0.9 | 60 | 60 | 0 | N |  |  | OP | X | 11 | 1958 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1958 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 223 | Caribou 2 | CA | Plumas | 5 | Conventional Hydroelectric | HY |  | S | X | X | CARBOU_7_PL4X5-APND | CARBOU_7_PL4X5-APND | 57.6 | 0.9 | 60 | 60 | 0 | N |  |  | OP | X | 11 | 1958 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1900 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 224 | Centerville PH | CA | Butte | 1 | Conventional Hydroelectric | HY |  | S | X | X | CNTRVL12_7_N002 | CNTRVL12_7_N002 | 5.5 | 1 | 5.5 | 5.5 | 0 | N |  |  | OS | X | 5 | 1900 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1900 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 224 | Centerville PH | CA | Butte | 2 | Conventional Hydroelectric | HY |  | S | X | X | CNTRVL12_7_N002 | CNTRVL12_7_N002 | 0.9 | 1 | 0.9 | 0.9 | 0 | N |  |  | OS | X | 5 | 1900 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1965 | hydro | TRUE | 16534 | Sacramento Municipal Util Dist | 225 | Chili Bar | CA | El Dorado | 1 | Conventional Hydroelectric | HY |  | S | X | X | PLCRVLB2_7_N001 | PLCRVLB2_7_N001 | 8.3 | 0.9 | 7 | 7 | 0 | N |  |  | OP | X | 3 | 1965 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1979 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 227 | Coleman PH | CA | Shasta | 1 | Conventional Hydroelectric | HY |  | S | X | X | COLEMAN_7_B1 | COLEMAN_7_B1 | 12.1 | 0.9 | 13 | 13 | 0 | N |  |  | OP | X | 6 | 1979 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1907 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 229 | Cow Creek | CA | Shasta | 1 | Conventional Hydroelectric | HY |  | S | X | X | COWCREEK_6_N001 | COWCREEK_6_N001 | 0.7 | 0.8 | 0.9 | 0.9 | 0 | N |  |  | OP | X | 1 | 1907 | 12 | 2023 | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1907 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 229 | Cow Creek | CA | Shasta | 2 | Conventional Hydroelectric | HY |  | S | X | X | COWCREEK_6_N001 | COWCREEK_6_N001 | 0.7 | 0.8 | 0.9 | 0.9 | 0 | N |  |  | OP | X | 1 | 1907 | 12 | 2023 | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1949 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 231 | Cresta | CA | Butte | 1 | Conventional Hydroelectric | HY |  | S | X | X | CRESTA_7_PL1X2-APND | CRESTA_7_PL1X2-APND | 36.9 | 0.9 | 35 | 35 | 0 | N |  |  | OP | X | 11 | 1949 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1950 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 231 | Cresta | CA | Butte | 2 | Conventional Hydroelectric | HY |  | S | X | X | CRESTA_7_PL1X2-APND | CRESTA_7_PL1X2-APND | 36.9 | 0.9 | 35 | 35 | 0 | N |  |  | OP | X | 1 | 1950 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1963 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 232 | De Sabla | CA | Butte | 1 | Conventional Hydroelectric | HY |  | S | X | X | DESABLA_7_B1 | DESABLA_7_B1 | 18.4 | 0.9 | 18.5 | 18.5 | 0 | N |  |  | OP | X | 2 | 1963 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1908 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 233 | Deer Creek PH | CA | Nevada | 1 | Conventional Hydroelectric | HY |  | S | X | X | DEERCRK_7_B1 | DEERCRK_7_B1 | 5.5 | 0.8 | 5.7 | 5.7 | 0 | N |  |  | OP | X | 5 | 1908 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1913 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 235 | Drum 1 | CA | Placer | 1 | Conventional Hydroelectric | HY |  | S | X | X | DRUM_7_PL1X2-APND | DRUM_7_PL1X2-APND | 12 | 0.9 | 13.2 | 13.2 | 0 | N |  |  | OP | X | 11 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1913 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 235 | Drum 1 | CA | Placer | 2 | Conventional Hydroelectric | HY |  | S | X | X | DRUM_7_PL1X2-APND | DRUM_7_PL1X2-APND | 12 | 0.9 | 13.2 | 13.2 | 0 | N |  |  | OP | X | 11 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1922 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 235 | Drum 1 | CA | Placer | 3 | Conventional Hydroelectric | HY |  | S | X | X | DRUM_7_PL3X4-APND | DRUM_7_PL3X4-APND | 12 | 0.9 | 13.2 | 13.2 | 0 | N |  |  | OP | X | 4 | 1922 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1928 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 235 | Drum 1 | CA | Placer | 4 | Conventional Hydroelectric | HY |  | S | X | X | DRUM_7_PL3X4-APND | DRUM_7_PL3X4-APND | 13.2 | 0.9 | 14.4 | 14.4 | 0 | N |  |  | OP | X | 6 | 1928 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1965 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 236 | Drum 2 | CA | Placer | 5 | Conventional Hydroelectric | HY |  | S | X | X | DRUM5_7_B1 | DRUM5_7_B1 | 53.1 | 0.9 | 49.5 | 49.5 | 0 | N |  |  | OP | X | 12 | 1965 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1943 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 237 | Dutch Flat | CA | Placer | 1 | Conventional Hydroelectric | HY |  | S | X | X | DTCHFLT1_7_B1 | DTCHFLT1_7_B1 | 22 | 0.8 | 22 | 22 | 0 | N |  |  | OP | X | 3 | 1943 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1924 | hydro | TRUE | 25915 | El Dorado Irrigation District | 238 | El Dorado | CA | El Dorado | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 0.8 | 10.4 | 10.6 | 2.5 | N |  |  | OP | X | 1 | 1924 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 12H | [23 empty] | N |  | N
Vintage1924 | hydro | TRUE | 25915 | El Dorado Irrigation District | 238 | El Dorado | CA | El Dorado | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 0.8 | 10.4 | 10.5 | 2.5 | N |  |  | OP | X | 1 | 1924 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 12H | [23 empty] | N |  | N
Vintage1948 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 239 | Electra | CA | Amador | 1 | Conventional Hydroelectric | HY |  | S | X | X | ELECTR_7_PL1X3-APND | ELECTR_7_PL1X3-APND | 32.3 | 0.9 | 30.7 | 30.7 | 0 | N |  |  | OP | X | 6 | 1948 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1948 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 239 | Electra | CA | Amador | 2 | Conventional Hydroelectric | HY |  | S | X | X | ELECTR_7_PL1X3-APND | ELECTR_7_PL1X3-APND | 35.1 | 0.9 | 30.7 | 30.7 | 0 | N |  |  | OP | X | 6 | 1948 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1948 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 239 | Electra | CA | Amador | 3 | Conventional Hydroelectric | HY |  | S | X | X | ELECTR_7_PL1X3-APND | ELECTR_7_PL1X3-APND | 35.1 | 0.9 | 36.6 | 36.6 | 0 | N |  |  | OP | X | 6 | 1948 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1958 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 240 | Haas | CA | Fresno | H1 | Conventional Hydroelectric | HY |  | S | X | X | HAASPH_7_PL1X2-APND | HAASPH_7_PL1X2-APND | 67.5 | 0.9 | 72 | 72 | 0 | N |  |  | OP | X | 12 | 1958 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1958 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 240 | Haas | CA | Fresno | H2 | Conventional Hydroelectric | HY |  | S | X | X | HAASPH_7_PL1X2-APND | HAASPH_7_PL1X2-APND | 67.5 | 0.9 | 72 | 72 | 0 | N |  |  | OP | X | 12 | 1958 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1916 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 241 | Halsey | CA | Placer | 1 | Conventional Hydroelectric | HY |  | S | X | X | HALSEYF_7_B1 | HALSEYF_7_B1 | 13.6 | 0.8 | 11 | 11 | 0 | N |  |  | OP | X | 12 | 1916 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1921 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 242 | Hamilton Branch | CA | Plumas | 1 | Conventional Hydroelectric | HY |  | S | X | X | HAMILBR_7_N002 | HAMILBR_7_N002 | 2.6 | 0.8 | 2.4 | 2.4 | 0 | N |  |  | OS | X | 8 | 1921 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1921 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 242 | Hamilton Branch | CA | Plumas | 2 | Conventional Hydroelectric | HY |  | S | X | X | HAMILBR_7_N002 | HAMILBR_7_N002 | 2.7 | 0.85 | 2.4 | 2.4 | 0 | N |  |  | OS | X | 8 | 1921 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1921 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 243 | Hat Creek 1 | CA | Shasta | 1 | Conventional Hydroelectric | HY |  | S | X | X | HATCRK1_7_B1 | HATCRK1_7_B1 | 10 | 0.8 | 8.5 | 8.5 | 0 | N |  |  | OP | X | 8 | 1921 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1921 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 244 | Hat Creek 2 | CA | Shasta | 1 | Conventional Hydroelectric | HY |  | S | X | X | HATCRK2_7_B1 | HATCRK2_7_B1 | 10 | 0.8 | 8.5 | 8.5 | 0 | N |  |  | OP | X | 9 | 1921 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage2010 | natural gas peaker | TRUE | 14328 | Pacific Gas & Electric Co. | 246 | Humboldt Bay | CA | Humboldt | IC1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | HMBUNIT1_7_GN010 | HMBUNIT1_7_GN010 | 16.7 | 0.8 | 16.3 | 16.3 | 14.5 | N |  |  | OP | X | 9 | 2010 |  |  | N | Electric Utility | 1 | X | NG | DFO | OBG | [7 empty] | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage2010 | natural gas peaker | TRUE | 14328 | Pacific Gas & Electric Co. | 246 | Humboldt Bay | CA | Humboldt | IC10 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | HMBUNIT2_7_GN010 | HMBUNIT2_7_GN010 | 16.7 | 0.8 | 16.3 | 16.3 | 14.5 | N |  |  | OP | X | 9 | 2010 |  |  | N | Electric Utility | 1 | X | NG | DFO | OBG | [7 empty] | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage2010 | natural gas peaker | TRUE | 14328 | Pacific Gas & Electric Co. | 246 | Humboldt Bay | CA | Humboldt | IC2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | HMBUNIT1_7_GN010 | HMBUNIT1_7_GN010 | 16.7 | 0.8 | 16.3 | 16.3 | 14.5 | N |  |  | OP | X | 9 | 2010 |  |  | N | Electric Utility | 1 | X | NG | DFO | OBG | [7 empty] | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage2011 | natural gas peaker | TRUE | 14328 | Pacific Gas & Electric Co. | 246 | Humboldt Bay | CA | Humboldt | IC3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | HMBUNIT1_7_GN010 | HMBUNIT1_7_GN010 | 16.7 | 0.8 | 16.3 | 16.3 | 14.5 | N |  |  | OP | X | 3 | 2011 |  |  | N | Electric Utility | 1 | X | NG | DFO | OBG | [7 empty] | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage2010 | natural gas peaker | TRUE | 14328 | Pacific Gas & Electric Co. | 246 | Humboldt Bay | CA | Humboldt | IC4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | HMBUNIT3_7_GN010 | HMBUNIT3_7_GN010 | 16.7 | 0.8 | 16.3 | 16.3 | 14.5 | N |  |  | OP | X | 9 | 2010 |  |  | N | Electric Utility | 1 | X | NG | DFO | OBG | [7 empty] | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage2010 | natural gas peaker | TRUE | 14328 | Pacific Gas & Electric Co. | 246 | Humboldt Bay | CA | Humboldt | IC5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | HMBUNIT3_7_GN010 | HMBUNIT3_7_GN010 | 16.7 | 0.8 | 16.3 | 16.3 | 15.4 | N |  |  | OP | X | 9 | 2010 |  |  | N | Electric Utility | 1 | X | NG | DFO | OBG | [7 empty] | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage2010 | natural gas peaker | TRUE | 14328 | Pacific Gas & Electric Co. | 246 | Humboldt Bay | CA | Humboldt | IC6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | HMBUNIT3_7_GN010 | HMBUNIT3_7_GN010 | 16.7 | 0.8 | 16.3 | 16.3 | 14.5 | N |  |  | OP | X | 9 | 2010 |  |  | N | Electric Utility | 1 | X | NG | DFO | OBG | [7 empty] | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage2010 | natural gas peaker | TRUE | 14328 | Pacific Gas & Electric Co. | 246 | Humboldt Bay | CA | Humboldt | IC7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | HMBUNIT3_7_GN010 | HMBUNIT3_7_GN010 | 16.7 | 0.8 | 16.3 | 16.3 | 14.5 | N |  |  | OP | X | 9 | 2010 |  |  | N | Electric Utility | 1 | X | NG | DFO | OBG | [7 empty] | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage2010 | natural gas peaker | TRUE | 14328 | Pacific Gas & Electric Co. | 246 | Humboldt Bay | CA | Humboldt | IC8 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | HMBUNIT2_7_GN010 | HMBUNIT2_7_GN010 | 16.7 | 0.8 | 16.3 | 16.3 | 14.5 | N |  |  | OP | X | 9 | 2010 |  |  | N | Electric Utility | 1 | X | NG | DFO | OBG | [7 empty] | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage2010 | natural gas peaker | TRUE | 14328 | Pacific Gas & Electric Co. | 246 | Humboldt Bay | CA | Humboldt | IC9 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | HMBUNIT2_7_GN010 | HMBUNIT2_7_GN010 | 16.7 | 0.8 | 16.7 | 16.7 | 14.5 | N |  |  | OP | X | 9 | 2010 |  |  | N | Electric Utility | 1 | X | NG | DFO | OBG | [7 empty] | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1979 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 248 | Inskip | CA | Tehama | 1 | Conventional Hydroelectric | HY |  | S | X | X | INSKIP_7_B1 | INSKIP_7_B1 | 7.6 | 0.9 | 8 | 8 | 0 | N |  |  | OS | X | 10 | 1979 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1966 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 249 | James B Black | CA | Shasta | 1 | Conventional Hydroelectric | HY |  | S | X | X | JBBLACK1_7_B1 | JBBLACK1_7_B1 | 85.1 | 0.9 | 86 | 86 | 0 | N |  |  | OP | X | 2 | 1966 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1965 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 249 | James B Black | CA | Shasta | 2 | Conventional Hydroelectric | HY |  | S | X | X | JBBLACK2_7_B1 | JBBLACK2_7_B1 | 83.5 | 0.9 | 86 | 86 | 0 | N |  |  | OP | X | 12 | 1965 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1920 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 250 | Kerckhoff | CA | Fresno | H1 | Conventional Hydroelectric | HY |  | S | X | X | KERCK1G1_7_B2 | KERCK1G1_7_B2 | 11.3 | 1 | 12.6 | 12.6 | 0.5 | N |  |  | OS | X | 8 | 1920 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1920 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 250 | Kerckhoff | CA | Fresno | H3 | Conventional Hydroelectric | HY |  | S | X | X | KERCK1G3_7_B1 | KERCK1G3_7_B1 | 11.3 | 1 | 12.6 | 12.6 | 0.5 | N |  |  | OS | X | 8 | 1920 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1904 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 253 | Kilarc | CA | Shasta | 1 | Conventional Hydroelectric | HY |  | S | X | X | KILRC1-2_7_B1 | KILRC1-2_7_B1 | 1.5 | 1 | 1.6 | 1.6 | 0 | N |  |  | OP | X | 6 | 1904 | 12 | 2023 | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1962 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 254 | Kings River PH | CA | Fresno | H1 | Conventional Hydroelectric | HY |  | S | X | X | KINGSRIV_7_B1 | KINGSRIV_7_B1 | 48.6 | 0.9 | 52 | 52 | 0 | N |  |  | OP | X | 3 | 1962 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1906 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 255 | Lime Saddle | CA | Butte | 1 | Conventional Hydroelectric | HY |  | S | X | X | CLARKRD_7_N003 | CLARKRD_7_N003 | 1 | 1 | 1 | 1 | 0 | N |  |  | OS | X | 8 | 1906 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1906 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 255 | Lime Saddle | CA | Butte | 2 | Conventional Hydroelectric | HY |  | S | X | X | CLARKRD_7_N003 | CLARKRD_7_N003 | 1 | 1 | 1 | 1 | 0 | N |  |  | OS | X | 8 | 1906 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1930 | hydro | TRUE | 12312 | Merced Irrigation District | 258 | Merced Falls | CA | Merced | 1 | Conventional Hydroelectric | HY |  | S | X | X | MERCEDFL_7_N001 |  | 3.4 | 0.86 | 3.5 | 3.5 | 0 | N |  |  | OP | X | 7 | 1930 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage2021 | other | TRUE | 54802 | Dynegy -Moss Landing LLC | 260 | Dynegy Moss Landing Power Plant Hybrid | CA | Monterey | BAT1 | Batteries | BA |  | S | X | X |  |  | 300 |  | 300 | 300 | 0.2 | N |  |  | OP | X | 5 | 2021 |  |  | N | IPP Non-CHP | 2 | X | MWH | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | N
Vintage2021 | other | TRUE | 54802 | Dynegy -Moss Landing LLC | 260 | Dynegy Moss Landing Power Plant Hybrid | CA | Monterey | BAT2 | Batteries | BA |  | S | X | X |  |  | 100 |  | 100 | 100 | 0.2 | N |  |  | OP | X | 5 | 2021 |  |  | N | IPP Non-CHP | 2 | X | MWH | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | N
Vintage2002 | natural gas combined cycle | TRUE | 54802 | Dynegy -Moss Landing LLC | 260 | Dynegy Moss Landing Power Plant Hybrid | CA | Monterey | CT1A | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 233 | 0.85 | 165 | 165 | 80 | N |  |  | OP | X | 7 | 2002 |  |  | N | IPP Non-CHP | 2 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage2002 | natural gas combined cycle | TRUE | 54802 | Dynegy -Moss Landing LLC | 260 | Dynegy Moss Landing Power Plant Hybrid | CA | Monterey | CT1B | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 233 | 0.85 | 165 | 165 | 80 | N |  |  | OP | X | 7 | 2002 |  |  | N | IPP Non-CHP | 2 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage2002 | natural gas combined cycle | TRUE | 54802 | Dynegy -Moss Landing LLC | 260 | Dynegy Moss Landing Power Plant Hybrid | CA | Monterey | CT2A | Natural Gas Fired Combined Cycle | CT | CC2 | S | X | N |  |  | 233 | 0.85 | 165 | 165 | 80 | N |  |  | OP | X | 7 | 2002 |  |  | N | IPP Non-CHP | 2 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage2002 | natural gas combined cycle | TRUE | 54802 | Dynegy -Moss Landing LLC | 260 | Dynegy Moss Landing Power Plant Hybrid | CA | Monterey | CT2B | Natural Gas Fired Combined Cycle | CT | CC2 | S | X | N |  |  | 233 | 0.85 | 165 | 165 | 80 | N |  |  | OP | X | 7 | 2002 |  |  | N | IPP Non-CHP | 2 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage2002 | natural gas combined cycle | TRUE | 54802 | Dynegy -Moss Landing LLC | 260 | Dynegy Moss Landing Power Plant Hybrid | CA | Monterey | ST1 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X |  |  | 233 | 0.85 | 180 | 180 | 60 | N |  |  | OP | X | 7 | 2002 |  |  | N | IPP Non-CHP | 2 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage2002 | natural gas combined cycle | TRUE | 54802 | Dynegy -Moss Landing LLC | 260 | Dynegy Moss Landing Power Plant Hybrid | CA | Monterey | ST2 | Natural Gas Fired Combined Cycle | CA | CC2 | S | N | X |  |  | 233 | 0.85 | 180 | 180 | 60 | N |  |  | OP | X | 7 | 2002 |  |  | N | IPP Non-CHP | 2 | X | NG | [9 empty] | N | N | 0 | 12H | [23 empty] | N | N | N
Vintage1954 | hydro | TRUE | 19586 | Utica Water & Power Authority | 261 | Murphys | CA | Calaveras | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.6 | 0.8 | 1.7 | 2 | 0.7 | N |  |  | OP | X | 3 | 1954 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1942 | hydro | TRUE | 21140 | Yuba County Water Agency | 262 | Narrows PH | CA | Nevada | 1 | Conventional Hydroelectric | HY |  | S | X | X | NARROWS1_7_B1 | NARROWS1_7_B1 | 10.2 | 0.86 | 12 | 12 | 0 | N |  |  | OP | X | 12 | 1942 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1940 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 264 | Phoenix | CA | Tuolumne | 1 | Conventional Hydroelectric | HY |  | S | X | X | PHOENIX_7_N001 | PHOENIX_7_N001 | 1.6 | 0.8 | 2 | 2 | 0 | N |  |  | OP | X | 2 | 1940 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1922 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 265 | Pit 1 | CA | Shasta | H1 | Conventional Hydroelectric | HY |  | S | X | X | PIT1U1_7_B1 | PIT1U1_7_B1 | 34.6 | 0.9 | 30.5 | 30.5 | 0 | N |  |  | OP | X | 9 | 1922 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1922 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 265 | Pit 1 | CA | Shasta | H2 | Conventional Hydroelectric | HY |  | S | X | X | PIT1U1_7_B2 | PIT1U1_7_B2 | 34.6 | 0.9 | 30.5 | 30.5 | 0 | N |  |  | OP | X | 9 | 1922 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1925 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 266 | Pit 3 | CA | Shasta | H1 | Conventional Hydroelectric | HY |  | S | X | X | PIT3_7_PL1X3-APND | PIT3_7_PL1X3-APND | 26.7 | 0.9 | 23.3 | 23.3 | 0 | N |  |  | OP | X | 7 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1925 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 266 | Pit 3 | CA | Shasta | H2 | Conventional Hydroelectric | HY |  | S | X | X | PIT3_7_PL1X3-APND | PIT3_7_PL1X3-APND | 26.7 | 0.9 | 23.3 | 23.3 | 0 | N |  |  | OP | X | 7 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1925 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 266 | Pit 3 | CA | Shasta | H3 | Conventional Hydroelectric | HY |  | S | X | X | PIT3_7_PL1X3-APND | PIT3_7_PL1X3-APND | 26.7 | 0.9 | 23.3 | 23.3 | 0 | N |  |  | OP | X | 7 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1955 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 267 | Pit 4 | CA | Shasta | 1 | Conventional Hydroelectric | HY |  | S | X | X | PIT4_7_PL1X2-APND | PIT4_7_PL1X2-APND | 51.7 | 0.9 | 47.5 | 47.5 | 0 | N |  |  | OP | X | 10 | 1955 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1955 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 267 | Pit 4 | CA | Shasta | 2 | Conventional Hydroelectric | HY |  | S | X | X | PIT4_7_PL1X2-APND | PIT4_7_PL1X2-APND | 51.7 | 0.9 | 47.5 | 47.5 | 0 | N |  |  | OP | X | 7 | 1955 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1944 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 268 | Pit 5 | CA | Shasta | H1 | Conventional Hydroelectric | HY |  | S | X | X | PIT5_7_PL1X2-APND | PIT5_7_PL1X2-APND | 38.2 | 0.87 | 40 | 40 | 0 | N |  |  | OP | X | 4 | 1944 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1944 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 268 | Pit 5 | CA | Shasta | H2 | Conventional Hydroelectric | HY |  | S | X | X | PIT5_7_PL1X2-APND | PIT5_7_PL1X2-APND | 38.2 | 0.87 | 40 | 40 | 0 | N |  |  | OP | X | 4 | 1944 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1944 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 268 | Pit 5 | CA | Shasta | H3 | Conventional Hydroelectric | HY |  | S | X | X | PIT5_7_PL3X4-APND | PIT5_7_PL3X4-APND | 33.2 | 0.8 | 40 | 40 | 0 | N |  |  | OP | X | 4 | 1944 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1944 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 268 | Pit 5 | CA | Shasta | H4 | Conventional Hydroelectric | HY |  | S | X | X | PIT5_7_PL3X4-APND | PIT5_7_PL3X4-APND | 32 | 0.8 | 40 | 40 | 0 | N |  |  | OP | X | 4 | 1944 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1965 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 269 | Pit 6 | CA | Shasta | H1 | Conventional Hydroelectric | HY |  | S | X | X | PIT6U1_7_B1 | PIT6U1_7_B1 | 39.6 | 0.9 | 40 | 40 | 0 | N |  |  | OP | X | 8 | 1965 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1965 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 269 | Pit 6 | CA | Shasta | H2 | Conventional Hydroelectric | HY |  | S | X | X | PIT6U2_7_B1 | PIT6U2_7_B1 | 39.6 | 0.9 | 40 | 40 | 0 | N |  |  | OP | X | 8 | 1965 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1965 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 270 | Pit 7 | CA | Shasta | H1 | Conventional Hydroelectric | HY |  | S | X | X | PIT7U1_7_B1 | PIT7U1_7_B1 | 57.6 | 0.9 | 56 | 56 | 0 | N |  |  | OP | X | 9 | 1965 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1965 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 270 | Pit 7 | CA | Shasta | H2 | Conventional Hydroelectric | HY |  | S | X | X | PIT7U2_7_B1 | PIT7U2_7_B1 | 52.2 | 0.9 | 57 | 57 | 0 | N |  |  | OP | X | 9 | 1965 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1958 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 272 | Poe | CA | Butte | 1 | Conventional Hydroelectric | HY |  | S | X | X | POE1_7_B1 | POE1_7_B1 | 71.4 | 0.9 | 60 | 60 | 0 | N |  |  | OP | X | 10 | 1958 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1958 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 272 | Poe | CA | Butte | 2 | Conventional Hydroelectric | HY |  | S | X | X | POE2_7_B1 | POE2_7_B1 | 71.4 | 0.9 | 60 | 60 | 0 | N |  |  | OP | X | 10 | 1958 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1939 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 274 | Potter Valley | CA | Mendocino | 1 | Conventional Hydroelectric | HY |  | S | X | X | POTTRVLY_7_N002 | POTTRVLY_7_N002 | 4.4 | 0.8 | 4.5 | 4.5 | 0 | N |  |  | OP | X | 2 | 1939 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1910 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 274 | Potter Valley | CA | Mendocino | 2 | Conventional Hydroelectric | HY |  | S | X | X | POTTRVLY_7_N002 | POTTRVLY_7_N002 | 2 | 0.8 | 2 | 2 | 0 | N |  |  | OP | X | 3 | 1910 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1917 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 274 | Potter Valley | CA | Mendocino | 3 | Conventional Hydroelectric | HY |  | S | X | X | POTTRVLY_7_N002 | POTTRVLY_7_N002 | 3 | 1 | 2.7 | 2.7 | 0 | N |  |  | OP | X | 9 | 1917 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1950 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 275 | Rock Creek | CA | Plumas | H1 | Conventional Hydroelectric | HY |  | S | X | X | ROCKCK1_7_B1 | ROCKCK1_7_B1 | 63 | 0.9 | 63 | 63 | 0 | N |  |  | OP | X | 3 | 1950 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1950 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 275 | Rock Creek | CA | Plumas | H2 | Conventional Hydroelectric | HY |  | S | X | X | ROCKCK2_7_B1 | ROCKCK2_7_B1 | 63 | 0.9 | 63 | 63 | 0 | N |  |  | OP | X | 3 | 1950 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1917 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 276 | San Joaquin 2 | CA | Madera | 1 | Conventional Hydroelectric | HY |  | S | X | X | SJNO2_6_N002 | SJNO2_6_N002 | 2.8 | 0.8 | 3.2 | 3.2 | 0 | N |  |  | OP | X | 9 | 1917 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1923 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 277 | San Joaquin 3 | CA | Madera | 3 | Conventional Hydroelectric | HY |  | S | X | X | CRANEVLY_6_N002 | CRANEVLY_6_N002 | 4 | 0.8 | 4.2 | 4.2 | 0 | N |  |  | OS | X | 8 | 1923 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1931 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 279 | Salt Springs | CA | Amador | 1 | Conventional Hydroelectric | HY |  | S | X | X | SALTSP_7_UNITS-APND | SALTSP_7_UNITS-APND | 12.3 | 0.85 | 11 | 11 | 0 | N |  |  | OP | X | 6 | 1931 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1953 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 279 | Salt Springs | CA | Amador | 2 | Conventional Hydroelectric | HY |  | S | X | X | SALTSP_7_UNITS-APND | SALTSP_7_UNITS-APND | 29.7 | 0.9 | 33 | 33 | 0 | N |  |  | OP | X | 4 | 1953 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1979 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 280 | South | CA | Tehama | 1 | Conventional Hydroelectric | HY |  | S | X | X | SOUTHG_7_B1 | SOUTHG_7_B1 | 6.7 | 0.9 | 7 | 7 | 0 | N |  |  | OP | X | 12 | 1979 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1928 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 281 | Spaulding 1 | CA | Nevada | 1 | Conventional Hydroelectric | HY |  | S | X | X | SPAULD_6_UNIT12-APND | SPAULD_6_UNIT12-APND | 7 | 0.8 | 7 | 7 | 0 | N |  |  | OP | X | 5 | 1928 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1928 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 282 | Spaulding 2 | CA | Nevada | 1 | Conventional Hydroelectric | HY |  | S | X | X | SPAULD_6_UNIT12-APND | SPAULD_6_UNIT12-APND | 3.7 | 0.9 | 4.4 | 4.4 | 0 | N |  |  | OP | X | 7 | 1928 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1929 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 283 | Spaulding 3 | CA | Nevada | 1 | Conventional Hydroelectric | HY |  | S | X | X | SPAULD3_7_B1 | SPAULD3_7_B1 | 6.6 | 0.9 | 5.8 | 5.8 | 0 | N |  |  | OP | X | 2 | 1929 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1921 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 284 | Spring Gap | CA | Tuolumne | 1 | Conventional Hydroelectric | HY |  | S | X | X | SPRNGGP_7_B1 | SPRNGGP_7_B1 | 6 | 0.8 | 7 | 7 | 0 | N |  |  | OP | X | 9 | 1921 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1963 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 285 | Stanislaus | CA | Tuolumne | HC1 | Conventional Hydroelectric | HY |  | S | X | X | STANISLS_7_B1 | STANISLS_7_B1 | 81.9 | 0.9 | 91 | 91 | 0 | N |  |  | OP | X | 3 | 1963 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1975 | geothermal | TRUE | 7160 | Geysers Power Co LLC | 286 | Geysers Unit 5-20 | CA | Sonoma | U11 | Geothermal | ST |  | S | X | X |  |  | 110 | 1 | 68 | 68 | 22 | N |  |  | OP | X | 12 | 1975 |  |  | N | IPP Non-CHP | 2 | X | GEO | [5 empty] | GEO |  |  |  | N |  |  | 12H | [23 empty] | N
Vintage1979 | geothermal | TRUE | 7160 | Geysers Power Co LLC | 286 | Geysers Unit 5-20 | CA | Sonoma | U12 | Geothermal | ST |  | S | X | X |  |  | 110 | 1 | 51 | 56 | 22 | N |  |  | OP | X | 8 | 1979 |  |  | N | IPP Non-CHP | 2 | X | GEO | [5 empty] | GEO |  |  |  | N |  |  | 12H | [23 empty] | N | N
Vintage1980 | geothermal | TRUE | 7160 | Geysers Power Co LLC | 286 | Geysers Unit 5-20 | CA | Sonoma | U13 | Geothermal | ST |  | S | X | X |  |  | 138 | 1 | 65 | 68 | 22 | N |  |  | OP | X | 4 | 1980 |  |  | N | IPP Non-CHP | 2 | X | GEO | [5 empty] | GEO |  |  |  | N |  |  | 12H | [23 empty] | N | N
Vintage1980 | geothermal | TRUE | 7160 | Geysers Power Co LLC | 286 | Geysers Unit 5-20 | CA | Sonoma | U14 | Geothermal | ST |  | S | X | X |  |  | 113 | 1 | 60 | 62 | 22 | N |  |  | OP | X | 2 | 1980 |  |  | N | IPP Non-CHP | 2 | X | GEO | [5 empty] | GEO |  |  |  | N |  |  | 12H | [23 empty] | N | N
Vintage1985 | geothermal | TRUE | 7160 | Geysers Power Co LLC | 286 | Geysers Unit 5-20 | CA | Sonoma | U16 | Geothermal | ST |  | S | X | X |  |  | 118 | 1 | 60 | 60 | 22 | N |  |  | OP | X | 10 | 1985 |  |  | N | IPP Non-CHP | 2 | X | GEO | [5 empty] | GEO |  |  |  | N |  |  | 12H | [23 empty] | N | N
Vintage1982 | geothermal | TRUE | 7160 | Geysers Power Co LLC | 286 | Geysers Unit 5-20 | CA | Sonoma | U17 | Geothermal | ST |  | S | X | X |  |  | 118 | 1 | 60 | 65 | 22 | N |  |  | OP | X | 11 | 1982 |  |  | N | IPP Non-CHP | 2 | X | GEO | [5 empty] | GEO |  |  |  | N |  |  | 12H | [23 empty] | N | N
Vintage1983 | geothermal | TRUE | 7160 | Geysers Power Co LLC | 286 | Geysers Unit 5-20 | CA | Sonoma | U18 | Geothermal | ST |  | S | X | X |  |  | 118 | 1 | 60 | 60 | 22 | N |  |  | OP | X | 11 | 1983 |  |  | N | IPP Non-CHP | 2 | X | GEO | [5 empty] | GEO |  |  |  | N |  |  | 12H | [23 empty] | N | N
Vintage1985 | geothermal | TRUE | 7160 | Geysers Power Co LLC | 286 | Geysers Unit 5-20 | CA | Sonoma | U20 | Geothermal | ST |  | S | X | X |  |  | 118 | 1 | 50 | 50 | 22 | N |  |  | OP | X | 10 | 1985 |  |  | N | IPP Non-CHP | 2 | X | GEO | [5 empty] | GEO |  |  |  | N |  |  | 12H | [23 empty] | N | N
Vintage1971 | geothermal | TRUE | 7160 | Geysers Power Co LLC | 286 | Geysers Unit 5-20 | CA | Sonoma | U5 | Geothermal | ST |  | S | X | X |  |  | 55 | 1 | 45 | 50 | 20 | N |  |  | OP | X | 4 | 1971 |  |  | N | IPP Non-CHP | 2 | X | GEO | [5 empty] | GEO |  |  |  | N |  |  | 12H | [23 empty] | N | N
Vintage1971 | geothermal | TRUE | 7160 | Geysers Power Co LLC | 286 | Geysers Unit 5-20 | CA | Sonoma | U6 | Geothermal | ST |  | S | X | X |  |  | 55 | 1 | 45 | 50 | 20 | N |  |  | OP | X | 4 | 1971 |  |  | N | IPP Non-CHP | 2 | X | GEO | [5 empty] | GEO |  |  |  | N |  |  | 12H | [23 empty] | N | N
Vintage1972 | geothermal | TRUE | 7160 | Geysers Power Co LLC | 286 | Geysers Unit 5-20 | CA | Sonoma | U7 | Geothermal | ST |  | S | X | X |  |  | 55 | 1 | 40 | 42 | 20 | N |  |  | OP | X | 7 | 1972 |  |  | N | IPP Non-CHP | 2 | X | GEO | [5 empty] | GEO |  |  |  | N |  |  | 12H | [23 empty] | N | N
Vintage1972 | geothermal | TRUE | 7160 | Geysers Power Co LLC | 286 | Geysers Unit 5-20 | CA | Sonoma | U8 | Geothermal | ST |  | S | X | X |  |  | 55 | 1 | 40 | 42 | 20 | N |  |  | OP | X | 7 | 1972 |  |  | N | IPP Non-CHP | 2 | X | GEO | [5 empty] | GEO |  |  |  | N |  |  | 12H | [23 empty] | N | N
Vintage1931 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 287 | Tiger Creek | CA | Amador | H1 | Conventional Hydroelectric | HY |  | S | X | X | TIGRCK_7_UNITS-APND | TIGRCK_7_UNITS-APND | 25.5 | 0.85 | 29 | 29 | 0 | N |  |  | OP | X | 8 | 1931 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1931 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 287 | Tiger Creek | CA | Amador | H2 | Conventional Hydroelectric | HY |  | S | X | X | TIGRCK_7_UNITS-APND | TIGRCK_7_UNITS-APND | 26.7 | 0.85 | 29 | 29 | 0 | N |  |  | OP | X | 6 | 1931 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1914 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 289 | Tule River | CA | Tulare | 1 | Conventional Hydroelectric | HY |  | S | X | X | SPRINGVL_6_N002 | SPRINGVL_6_N002 | 4.2 | 1 | 3.2 | 3.2 | 0 | N |  |  | OS | X | 1 | 1914 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1914 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 289 | Tule River | CA | Tulare | 2 | Conventional Hydroelectric | HY |  | S | X | X | SPRINGVL_6_N002 | SPRINGVL_6_N002 | 4.2 | 1 | 3.2 | 3.2 | 0 | N |  |  | OS | X | 1 | 1914 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1980 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 290 | Volta 1 | CA | Shasta | 1 | Conventional Hydroelectric | HY |  | S | X | X | VOLTA1_7_B1 | VOLTA1_7_B1 | 8.5 | 0.9 | 9 | 9 | 0 | N |  |  | OP | X | 4 | 1980 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1948 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 291 | West Point PH | CA | Amador | 1 | Conventional Hydroelectric | HY |  | S | X | X | WESTPNT_7_B2 | WESTPNT_7_B2 | 13.6 | 0.85 | 14.5 | 14.5 | 0 | N |  |  | OP | X | 11 | 1948 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1917 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 292 | Wise | CA | Placer | 1 | Conventional Hydroelectric | HY |  | S | X | X | WISE1_7_B1 | WISE1_7_B1 | 13.6 | 0.8 | 14 | 14 | 0 | N |  |  | OP | X | 3 | 1917 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1986 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 292 | Wise | CA | Placer | 2 | Conventional Hydroelectric | HY |  | S | X | X | WISE2_7_B1 | WISE2_7_B1 | 2.8 | 0.9 | 3.2 | 3.2 | 0 | N |  |  | OP | X | 12 | 1986 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1910 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 293 | A G Wishon | CA | Madera | 1 | Conventional Hydroelectric | HY |  | S | X | X | WISHON_6_UNITS-APND | WISHON_6_UNITS-APND | 3.2 | 0.8 | 5 | 5 | 0 | N |  |  | OP | X | 9 | 1910 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1910 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 293 | A G Wishon | CA | Madera | 2 | Conventional Hydroelectric | HY |  | S | X | X | WISHON_6_UNITS-APND | WISHON_6_UNITS-APND | 3.2 | 0.8 | 5 | 5 | 0 | N |  |  | OP | X | 9 | 1910 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1910 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 293 | A G Wishon | CA | Madera | 3 | Conventional Hydroelectric | HY |  | S | X | X | WISHON_6_UNITS-APND | WISHON_6_UNITS-APND | 3.2 | 0.8 | 5 | 5 | 0 | N |  |  | OP | X | 9 | 1910 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1910 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 293 | A G Wishon | CA | Madera | 4 | Conventional Hydroelectric | HY |  | S | X | X | WISHON_6_UNITS-APND | WISHON_6_UNITS-APND | 3.2 | 0.8 | 5 | 5 | 0 | N |  |  | OP | X | 9 | 1910 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1918 | hydro | TRUE | 14354 | PacifiCorp | 294 | Copco 1 | CA | Siskiyou | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 0.8 | 14 | 14 | 0 | N |  |  | OP | X | 1 | 1918 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | OVER | [23 empty] | N
Vintage1918 | hydro | TRUE | 14354 | PacifiCorp | 294 | Copco 1 | CA | Siskiyou | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 0.8 | 14 | 14 | 0 | N |  |  | OP | X | 11 | 1918 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | OVER | [23 empty] | N
Vintage1925 | hydro | TRUE | 14354 | PacifiCorp | 295 | Copco 2 | CA | Siskiyou | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 13.5 | 0.9 | 17 | 17 | 0 | N |  |  | OP | X | 7 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1925 | hydro | TRUE | 14354 | PacifiCorp | 295 | Copco 2 | CA | Siskiyou | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 13.5 | 0.9 | 17 | 17 | 0 | N |  |  | OP | X | 8 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1903 | hydro | TRUE | 14354 | PacifiCorp | 296 | Fall Creek | CA | Siskiyou | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 1 | 0.4 | 0.4 | 0 | N |  |  | OP | X | 9 | 1903 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1907 | hydro | TRUE | 14354 | PacifiCorp | 296 | Fall Creek | CA | Siskiyou | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 1 | 0.4 | 0.4 | 0 | N |  |  | OP | X | 8 | 1907 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1910 | hydro | TRUE | 14354 | PacifiCorp | 296 | Fall Creek | CA | Siskiyou | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 1 | 1.1 | 1.1 | 0 | N |  |  | OP | X | 1 | 1910 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1962 | hydro | TRUE | 14354 | PacifiCorp | 297 | Iron Gate | CA | Siskiyou | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18 | 0.95 | 18.8 | 18.8 | 0 | N |  |  | OP | X | 2 | 1962 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1985 | hard coal | TRUE | 54888 | NRG Texas Power LLC | 298 | Limestone | TX | Limestone | 1 | Conventional Steam Coal | ST |  | S | X | X | LEG_LEG_G1 | LEG_LEG_G1 | 893 | 0.94 | 831 | 831 | 300 | N |  |  | OP | X | 12 | 1985 | 12 | 2029 | N | IPP Non-CHP | 2 | X | SUB | NG | LIG | PC |  |  | NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1986 | hard coal | TRUE | 54888 | NRG Texas Power LLC | 298 | Limestone | TX | Limestone | 2 | Conventional Steam Coal | ST |  | S | X | X | LEG_LEG_G2 | LEG_LEG_G2 | 956.8 | 0.92 | 858 | 858 | 300 | N |  |  | OP | X | 12 | 1986 | 12 | 2029 | N | IPP Non-CHP | 2 | X | SUB | NG | LIG | PC |  |  | NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1984 | geothermal | TRUE | 14354 | PacifiCorp | 299 | Blundell | UT | Beaver | 1 | Geothermal | ST |  | S | X | X |  |  | 30.7 | 0.85 | 23 | 23 | 4 | N |  |  | OP | X | 7 | 1984 |  |  | N | Electric Utility | 1 | X | GEO | [5 empty] | GEO |  |  |  | N |  |  | 12H | [23 empty] | N
Vintage2007 | geothermal | TRUE | 14354 | PacifiCorp | 299 | Blundell | UT | Beaver | 2 | Geothermal | ST |  | S | X | X |  |  | 14.1 | 0.85 | 8.7 | 10.8 | 4 | N |  |  | OP | X | 12 | 2007 |  |  | N | Electric Utility | 1 | X | GEO | [5 empty] | GEO | [6 empty] | 12H | [23 empty] | N
Vintage1982 | hydro | TRUE | 17271 | City & Borough of Sitka - (AK) | 313 | Green Lake | AK | Sitka | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9.3 | 0.8 | 9.3 | 9.3 | 4 | N |  |  | OP | X | 4 | 1982 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 1H | [23 empty] | N
Vintage1982 | hydro | TRUE | 17271 | City & Borough of Sitka - (AK) | 313 | Green Lake | AK | Sitka | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9.3 | 0.8 | 9.3 | 9.3 | 4 | N |  |  | OP | X | 10 | 1982 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 1H | [23 empty] | N
Vintage1982 | hydro | TRUE | 9216 | Imperial Irrigation District | 314 | Drop 5 | CA | Imperial | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.8 | 1.9 | 0.9 | 0.1 | N |  |  | OP | X | 3 | 1982 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1982 | hydro | TRUE | 9216 | Imperial Irrigation District | 314 | Drop 5 | CA | Imperial | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.8 | 1.9 | 0.9 | 0.1 | N |  |  | OP | X | 3 | 1982 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1961 | natural gas steam turbine | TRUE | 22148 | AES Alamitos LLC | 315 | AES Alamitos LLC | CA | Los Angeles | 3 | Natural Gas Steam Turbine | ST |  | S | X | X | ALAMT3G_7_B1 | ALAMT3G_7_B1 | 310 | 1 | 332 | 332 | 10 | N |  |  | OP | X | 12 | 1961 | 12 | 2023 | N | IPP Non-CHP | 2 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1962 | natural gas steam turbine | TRUE | 22148 | AES Alamitos LLC | 315 | AES Alamitos LLC | CA | Los Angeles | 4 | Natural Gas Steam Turbine | ST |  | S | X | X | ALAMT4G_7_B1 | ALAMT4G_7_B1 | 310 | 1 | 335 | 335 | 20 | N |  |  | OP | X | 6 | 1962 | 12 | 2023 | N | IPP Non-CHP | 2 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1964 | natural gas steam turbine | TRUE | 22148 | AES Alamitos LLC | 315 | AES Alamitos LLC | CA | Los Angeles | 5 | Natural Gas Steam Turbine | ST |  | S | X | X | ALAMT5G_7_B1 | ALAMT5G_7_B1 | 495 | 1 | 485 | 485 | 70 | N |  |  | OP | X | 3 | 1964 | 12 | 2023 | N | IPP Non-CHP | 2 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1982 | hydro | TRUE | 12397 | Metropolitan Water District of S CA | 316 | Sepulveda Canyon | CA | Los Angeles | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8.5 | 1 | 8.5 | 8.5 | 1.5 | N |  |  | SB | Y | 6 | 1982 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 12H
Vintage1913 | hydro | TRUE | 17609 | Southern California Edison Co | 317 | Big Creek 1 | CA | Fresno | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 19.8 | 0.9 | 19.8 | 19.8 | 2 | N |  |  | OP | X | 11 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1913 | hydro | TRUE | 17609 | Southern California Edison Co | 317 | Big Creek 1 | CA | Fresno | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15.8 | 0.9 | 15.8 | 15.8 | 1.6 | N |  |  | OP | X | 11 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1923 | hydro | TRUE | 17609 | Southern California Edison Co | 317 | Big Creek 1 | CA | Fresno | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 21.6 | 0.9 | 21.6 | 21.6 | 2.2 | N |  |  | OP | X | 7 | 1923 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1925 | hydro | TRUE | 17609 | Southern California Edison Co | 317 | Big Creek 1 | CA | Fresno | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 31.2 | 1 | 31.2 | 31.2 | 3.1 | N |  |  | OP | X | 6 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1913 | hydro | TRUE | 17609 | Southern California Edison Co | 318 | Big Creek 2 | CA | Fresno | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15.8 | 0.9 | 15.8 | 15.8 | 1.6 | N |  |  | OA | X | 12 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1914 | hydro | TRUE | 17609 | Southern California Edison Co | 318 | Big Creek 2 | CA | Fresno | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15.8 | 0.9 | 15.8 | 15.8 | 1.6 | N |  |  | OA | X | 1 | 1914 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1921 | hydro | TRUE | 17609 | Southern California Edison Co | 318 | Big Creek 2 | CA | Fresno | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 17.5 | 1 | 17.5 | 17.5 | 1.8 | N |  |  | OA | X | 2 | 1921 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1925 | hydro | TRUE | 17609 | Southern California Edison Co | 318 | Big Creek 2 | CA | Fresno | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 17.5 | 1 | 17.5 | 17.5 | 1.8 | N |  |  | OA | X | 3 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1923 | hydro | TRUE | 17609 | Southern California Edison Co | 319 | Big Creek 3 | CA | Fresno | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 34 | 1 | 34 | 34 | 3.4 | N |  |  | OP | X | 10 | 1923 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1923 | hydro | TRUE | 17609 | Southern California Edison Co | 319 | Big Creek 3 | CA | Fresno | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 34 | 1 | 34 | 34 | 3.4 | N |  |  | OP | X | 9 | 1923 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1923 | hydro | TRUE | 17609 | Southern California Edison Co | 319 | Big Creek 3 | CA | Fresno | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 34 | 1 | 33 | 33 | 3.4 | N |  |  | OP | X | 10 | 1923 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1948 | hydro | TRUE | 17609 | Southern California Edison Co | 319 | Big Creek 3 | CA | Fresno | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 36 | 0.9 | 36 | 36 | 3.6 | N |  |  | OP | X | 4 | 1948 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1980 | hydro | TRUE | 17609 | Southern California Edison Co | 319 | Big Creek 3 | CA | Fresno | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 36.5 | 0.9 | 36.5 | 36.5 | 3.6 | N |  |  | OP | X | 2 | 1980 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1951 | hydro | TRUE | 17609 | Southern California Edison Co | 320 | Big Creek 4 | CA | Madera | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 50 | 1 | 50 | 50 | 5 | N |  |  | OP | X | 6 | 1951 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1951 | hydro | TRUE | 17609 | Southern California Edison Co | 320 | Big Creek 4 | CA | Madera | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 50 | 1 | 50 | 50 | 5 | N |  |  | OP | X | 7 | 1951 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1921 | hydro | TRUE | 17609 | Southern California Edison Co | 321 | Big Creek 8 | CA | Fresno | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 30 | 1 | 25.8 | 25.8 | 2.6 | N |  |  | OA | X | 8 | 1921 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1929 | hydro | TRUE | 17609 | Southern California Edison Co | 321 | Big Creek 8 | CA | Fresno | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 45 | 0.9 | 45 | 45 | 4.5 | N |  |  | OS | X | 6 | 1929 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1928 | hydro | TRUE | 17609 | Southern California Edison Co | 322 | Big Creek 2A | CA | Fresno | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 55 | 1 | 50 | 50 | 5.5 | N |  |  | OS | X | 8 | 1928 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1928 | hydro | TRUE | 17609 | Southern California Edison Co | 322 | Big Creek 2A | CA | Fresno | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 55 | 1 | 50 | 50 | 5.5 | N |  |  | OS | X | 12 | 1928 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1908 | hydro | TRUE | 17609 | Southern California Edison Co | 323 | Bishop Creek 2 | CA | Inyo | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 0 | N |  |  | OP | X | 11 | 1908 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1908 | hydro | TRUE | 17609 | Southern California Edison Co | 323 | Bishop Creek 2 | CA | Inyo | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 0 | N |  |  | OP | X | 11 | 1908 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1911 | hydro | TRUE | 17609 | Southern California Edison Co | 323 | Bishop Creek 2 | CA | Inyo | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.3 | 0.8 | 2.3 | 2.3 | 0 | N |  |  | OP | X | 6 | 1911 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1913 | hydro | TRUE | 17609 | Southern California Edison Co | 324 | Bishop Creek 3 | CA | Inyo | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.8 | 1 | 2.8 | 2.8 | 0 | N |  |  | OP | X | 6 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1913 | hydro | TRUE | 17609 | Southern California Edison Co | 324 | Bishop Creek 3 | CA | Inyo | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.8 | 1 | 2.8 | 2.8 | 0 | N |  |  | OP | X | 6 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1913 | hydro | TRUE | 17609 | Southern California Edison Co | 324 | Bishop Creek 3 | CA | Inyo | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.8 | 1 | 2.8 | 2.8 | 0 | N |  |  | OP | X | 6 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1905 | hydro | TRUE | 17609 | Southern California Edison Co | 325 | Bishop Creek 4 | CA | Inyo | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 1 | 1 | 1 | 0 | N |  |  | OP | X | 9 | 1905 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1905 | hydro | TRUE | 17609 | Southern California Edison Co | 325 | Bishop Creek 4 | CA | Inyo | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 1 | 1 | 1 | 0 | N |  |  | OP | X | 9 | 1905 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1906 | hydro | TRUE | 17609 | Southern California Edison Co | 325 | Bishop Creek 4 | CA | Inyo | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.91 | 2 | 2 | 0 | N |  |  | OP | X | 6 | 1906 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1907 | hydro | TRUE | 17609 | Southern California Edison Co | 325 | Bishop Creek 4 | CA | Inyo | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 1 | 2.2 | 2.2 | 0 | N |  |  | OP | X | 10 | 1907 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1909 | hydro | TRUE | 17609 | Southern California Edison Co | 325 | Bishop Creek 4 | CA | Inyo | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.91 | 2 | 2 | 0 | N |  |  | OP | X | 6 | 1909 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1943 | hydro | TRUE | 17609 | Southern California Edison Co | 326 | Bishop Creek 5 | CA | Inyo | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | OP | X | 5 | 1943 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1919 | hydro | TRUE | 17609 | Southern California Edison Co | 326 | Bishop Creek 5 | CA | Inyo | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 0.9 | 1.8 | 1.8 | 0.1 | N |  |  | OP | X | 6 | 1919 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1913 | hydro | TRUE | 17609 | Southern California Edison Co | 327 | Bishop Creek 6 | CA | Inyo | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0 | N |  |  | OP | X | 3 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1917 | hydro | TRUE | 17609 | Southern California Edison Co | 332 | Fontana | CA | San Bernardino | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 1 | 1.5 | 1.5 | 0 | N |  |  | OP | X | 12 | 1917 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1917 | hydro | TRUE | 17609 | Southern California Edison Co | 332 | Fontana | CA | San Bernardino | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 1 | 1.5 | 1.5 | 0 | N |  |  | OP | X | 12 | 1917 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1958 | natural gas steam turbine | TRUE | 23693 | AES Huntington Beach LLC | 335 | AES Huntington Beach LLC | CA | Orange | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | HUNT2G_7_B1 | HUNT2G_7_B1 | 218 | 1 | 225.8 | 225.8 | 20 | N |  |  | OP | X | 12 | 1958 | 12 | 2023 | N | IPP Non-CHP | 2 | X | NG | [5 empty] | NG |  |  |  |  | N |  | OVER | [23 empty] | N | N
Vintage1929 | hydro | TRUE | 17609 | Southern California Edison Co | 336 | Kaweah 2 | CA | Tulare | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 0.9 | 1.8 | 1.8 | 0.1 | N |  |  | OP | X | 9 | 1929 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1929 | hydro | TRUE | 17609 | Southern California Edison Co | 337 | Kaweah 1 | CA | Tulare | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.3 | 0.9 | 2.3 | 2.3 | 0 | N |  |  | OS | X | 5 | 1929 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1913 | hydro | TRUE | 17609 | Southern California Edison Co | 338 | Kaweah 3 | CA | Tulare | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 1 | 2.4 | 2.4 | 0 | N |  |  | OS | X | 5 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1913 | hydro | TRUE | 17609 | Southern California Edison Co | 338 | Kaweah 3 | CA | Tulare | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 1 | 2.1 | 2.1 | 0 | N |  |  | OS | X | 5 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1921 | hydro | TRUE | 17609 | Southern California Edison Co | 339 | Kern River 3 | CA | Kern | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 20.5 | 0.9 | 20.5 | 20.5 | 0.8 | N |  |  | OP | X | 5 | 1921 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1921 | hydro | TRUE | 17609 | Southern California Edison Co | 339 | Kern River 3 | CA | Kern | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 19.8 | 0.9 | 19.7 | 19.7 | 0.8 | N |  |  | OP | X | 3 | 1921 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1907 | hydro | TRUE | 17609 | Southern California Edison Co | 340 | Kern River 1 | CA | Kern | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.6 | 0.9 | 6.6 | 6.6 | 0 | N |  |  | OP | X | 5 | 1907 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1907 | hydro | TRUE | 17609 | Southern California Edison Co | 340 | Kern River 1 | CA | Kern | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.6 | 0.9 | 6.6 | 6.6 | 0 | N |  |  | OP | X | 6 | 1907 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1907 | hydro | TRUE | 17609 | Southern California Edison Co | 340 | Kern River 1 | CA | Kern | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.6 | 0.9 | 6.6 | 6.6 | 0 | N |  |  | OP | X | 7 | 1907 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1907 | hydro | TRUE | 17609 | Southern California Edison Co | 340 | Kern River 1 | CA | Kern | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.6 | 0.9 | 6.6 | 6.6 | 0 | N |  |  | OP | X | 6 | 1907 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1976 | natural gas peaker | TRUE | 11181 | Long Beach Generation LLC | 341 | Long Beach Generation LLC | CA | Los Angeles | CT1 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 63 | 0.9 | 65 | 65 | 47 | N |  |  | OP | X | 12 | 1976 |  |  | N | IPP Non-CHP | 2 | X | NG | [5 empty] | NG |  |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage1976 | natural gas peaker | TRUE | 11181 | Long Beach Generation LLC | 341 | Long Beach Generation LLC | CA | Los Angeles | CT2 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 63 | 0.9 | 65 | 65 | 47 | N |  |  | OP | X | 12 | 1976 |  |  | N | IPP Non-CHP | 2 | X | NG | [5 empty] | NG |  |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage1976 | natural gas peaker | TRUE | 11181 | Long Beach Generation LLC | 341 | Long Beach Generation LLC | CA | Los Angeles | CT3 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 63 | 0.9 | 65 | 65 | 47 | N |  |  | OP | X | 12 | 1976 |  |  | N | IPP Non-CHP | 2 | X | NG | [5 empty] | NG |  |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage1976 | natural gas peaker | TRUE | 11181 | Long Beach Generation LLC | 341 | Long Beach Generation LLC | CA | Los Angeles | CT4 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 63 | 0.9 | 65 | 65 | 47 | N |  |  | OP | X | 12 | 1976 |  |  | N | IPP Non-CHP | 2 | X | NG | [5 empty] | NG |  |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage1911 | hydro | TRUE | 17609 | Southern California Edison Co | 342 | Lundy | CA | Mono | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0 | N |  |  | OP | X | 12 | 1911 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1912 | hydro | TRUE | 17609 | Southern California Edison Co | 342 | Lundy | CA | Mono | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0 | N |  |  | OP | X | 2 | 1912 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1960 | hydro | TRUE | 17609 | Southern California Edison Co | 344 | Mammoth Pool | CA | Madera | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 95 | 1 | 95 | 95 | 0 | N |  |  | OA | X | 3 | 1960 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1960 | hydro | TRUE | 17609 | Southern California Edison Co | 344 | Mammoth Pool | CA | Madera | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 95 | 1 | 95 | 95 | 0 | N |  |  | OA | X | 3 | 1960 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1971 | natural gas steam turbine | TRUE | 63843 | Ormond Beach Power, LLC | 350 | Ormond Beach | CA | Ventura | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | ORMOND_7_UNIT 1_ | ORMOND1G_7_B1 | 806 | 0.85 | 741 | 741 | 100 | N |  |  | OP | X | 8 | 1971 | 1 | 2024 | N | IPP Non-CHP | 2 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER | [20 empty] | N |  |  | N
Vintage1973 | natural gas steam turbine | TRUE | 63843 | Ormond Beach Power, LLC | 350 | Ormond Beach | CA | Ventura | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | ORMOND_7_UNIT 2 | ORMOND2G_7_B1 | 806 | 0.85 | 750 | 750 | 50 | N |  |  | OP | X | 3 | 1973 | 1 | 2024 | N | IPP Non-CHP | 2 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER | [20 empty] | N |  |  | N
Vintage1924 | hydro | TRUE | 17609 | Southern California Edison Co | 353 | Poole | CA | Mono | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 11.3 | 0.9 | 11.3 | 11.3 | 0 | N |  |  | OP | X | 5 | 1924 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1956 | hydro | TRUE | 17609 | Southern California Edison Co | 354 | Portal | CA | Fresno | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10.8 | 0.9 | 10.8 | 10.8 | 1.1 | N |  |  | OA | X | 12 | 1956 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1954 | natural gas steam turbine | TRUE | 22484 | AES Redondo Beach LLC | 356 | AES Redondo Beach LLC | CA | Los Angeles | 5 | Natural Gas Steam Turbine | ST |  | S | X | X | REDON5G_7_B1 | REDON5G_7_B1 | 163.2 | 1 | 175 | 178.9 | 10 | N |  |  | OP | X | 10 | 1954 | 12 | 2023 | N | IPP Non-CHP | 2 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1957 | natural gas steam turbine | TRUE | 22484 | AES Redondo Beach LLC | 356 | AES Redondo Beach LLC | CA | Los Angeles | 6 | Natural Gas Steam Turbine | ST |  | S | X | X | REDON6G_7_B1 | REDON6G_7_B1 | 163.2 | 1 | 175 | 175 | 10 | N |  |  | OP | X | 7 | 1957 | 12 | 2023 | N | IPP Non-CHP | 2 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1967 | natural gas steam turbine | TRUE | 22484 | AES Redondo Beach LLC | 356 | AES Redondo Beach LLC | CA | Los Angeles | 8 | Natural Gas Steam Turbine | ST |  | S | X | X | REDON8G_7_B1 | REDON8G_7_B1 | 495 | 1 | 480 | 486.9 | 130 | N |  |  | OP | X | 7 | 1967 | 12 | 2023 | N | IPP Non-CHP | 2 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1916 | hydro | TRUE | 17609 | Southern California Edison Co | 357 | Rush Creek | CA | Mono | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.9 | 0.9 | 5.9 | 5.9 | 0 | N |  |  | OP | X | 10 | 1916 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1917 | hydro | TRUE | 17609 | Southern California Edison Co | 357 | Rush Creek | CA | Mono | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7.2 | 0.9 | 5.5 | 5.5 | 0 | N |  |  | OP | X | 12 | 1917 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage2005 | natural gas combined cycle | TRUE | 17609 | Southern California Edison Co | 358 | Mountainview Generating Station | CA | San Bernardino | MV3A | Natural Gas Fired Combined Cycle | CT | 3 | S | X | N |  |  | 164.6 | 0.8 | 156 | 182 | 60 | N |  |  | OP | X | 12 | 2005 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 12H | [23 empty] | N
Vintage2005 | natural gas combined cycle | TRUE | 17609 | Southern California Edison Co | 358 | Mountainview Generating Station | CA | San Bernardino | MV3B | Natural Gas Fired Combined Cycle | CT | 3 | S | X | N |  |  | 164.6 | 0.8 | 156 | 182 | 60 | N |  |  | OP | X | 12 | 2005 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 12H | [23 empty] | N
Vintage2005 | natural gas combined cycle | TRUE | 17609 | Southern California Edison Co | 358 | Mountainview Generating Station | CA | San Bernardino | MV3C | Natural Gas Fired Combined Cycle | CA | 3 | S | Y | X |  |  | 189.2 | 0.83 | 197 | 191 | 90 | N |  |  | OP | X | 12 | 2005 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 12H | [23 empty] | N
Vintage2006 | natural gas combined cycle | TRUE | 17609 | Southern California Edison Co | 358 | Mountainview Generating Station | CA | San Bernardino | MV4A | Natural Gas Fired Combined Cycle | CT | 4 | S | X | N |  |  | 164.6 | 0.8 | 156 | 182 | 60 | N |  |  | OP | X | 1 | 2006 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 12H | [23 empty] | N
Vintage2006 | natural gas combined cycle | TRUE | 17609 | Southern California Edison Co | 358 | Mountainview Generating Station | CA | San Bernardino | MV4B | Natural Gas Fired Combined Cycle | CT | 4 | S | X | N |  |  | 164.6 | 0.8 | 156 | 182 | 60 | N |  |  | OP | X | 1 | 2006 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 12H | [23 empty] | N
Vintage2006 | natural gas combined cycle | TRUE | 17609 | Southern California Edison Co | 358 | Mountainview Generating Station | CA | San Bernardino | MV4C | Natural Gas Fired Combined Cycle | CA | 4 | S | Y | X |  |  | 189.2 | 0.83 | 197 | 191 | 90 | N |  |  | OP | X | 1 | 2006 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 12H | [23 empty] | N
Vintage1899 | hydro | TRUE | 17609 | Southern California Edison Co | 361 | Santa Ana 1 | CA | San Bernardino | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0 | N |  |  | OP | X | 2 | 1899 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1899 | hydro | TRUE | 17609 | Southern California Edison Co | 361 | Santa Ana 1 | CA | San Bernardino | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0 | N |  |  | OP | X | 2 | 1899 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1899 | hydro | TRUE | 17609 | Southern California Edison Co | 361 | Santa Ana 1 | CA | San Bernardino | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0 | N |  |  | OP | X | 1 | 1899 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1899 | hydro | TRUE | 17609 | Southern California Edison Co | 361 | Santa Ana 1 | CA | San Bernardino | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0 | N |  |  | OP | X | 1 | 1899 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1999 | hydro | TRUE | 17609 | Southern California Edison Co | 363 | Santa Ana 3 | CA | San Bernardino | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.1 | 0.9 | 3.1 | 3.1 | 0 | N |  |  | OP | X | 9 | 1999 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1909 | hydro | TRUE | 17609 | Southern California Edison Co | 365 | Lower Tule River | CA | Tulare | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 0.9 | 1.3 | 1.3 | 0 | N |  |  | OS | X | 9 | 1909 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1909 | hydro | TRUE | 17609 | Southern California Edison Co | 365 | Lower Tule River | CA | Tulare | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 0.9 | 1.3 | 1.3 | 0 | N |  |  | OS | X | 9 | 1909 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1984 | nuclear | TRUE | 20160 | Energy Northwest | 371 | Columbia Generating Station | WA | Benton | 2 | Nuclear | ST |  | S | X | X |  |  | 1200 | 0.975 | 1151 | 1172 | 120 | N |  |  | OP | X | 12 | 1984 |  |  | N | Electric Utility | 1 | X | NUC | [9 empty] | N | N |  | OVER | [23 empty] | N | N | N
Vintage1930 | hydro | TRUE | 5571 | East Bay Municipal Util Dist | 376 | Pardee | CA | Calaveras | 1 | Conventional Hydroelectric | HY |  | S | X | X | Pardeb_6_units |  | 7.5 | 0.8 | 8.9 | 8.9 | 5 | N |  |  | OP | X | 7 | 1930 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1930 | hydro | TRUE | 5571 | East Bay Municipal Util Dist | 376 | Pardee | CA | Calaveras | 2 | Conventional Hydroelectric | HY |  | S | X | X | Pardeb_6_units |  | 7.5 | 0.8 | 8.9 | 8.9 | 5 | N |  |  | OP | X | 7 | 1930 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1983 | hydro | TRUE | 5571 | East Bay Municipal Util Dist | 376 | Pardee | CA | Calaveras | 3 | Conventional Hydroelectric | HY |  | S | X | X | Pardeb_6_units |  | 8.6 | 0.95 | 9.9 | 9.9 | 5 | N |  |  | OP | X | 6 | 1983 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1977 | natural gas combined cycle | TRUE | 7294 | City of Glendale - (CA) | 377 | Grayson | CA | Los Angeles | 1 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X |  |  | 20 | 0.85 | 19 | 19 | 1 | N |  |  | OP | X | 7 | 1977 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage1977 | natural gas combined cycle | TRUE | 7294 | City of Glendale - (CA) | 377 | Grayson | CA | Los Angeles | 2 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X |  |  | 20 | 0.85 | 19 | 19 | 1 | N |  |  | OP | X | 7 | 1977 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage1953 | natural gas steam turbine | TRUE | 7294 | City of Glendale - (CA) | 377 | Grayson | CA | Los Angeles | 3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 23 | 0.85 | 18 | 18 | 7 | N |  |  | OS | X | 12 | 1953 |  |  | N | Electric Utility | 1 | X | NG | LFG |  |  |  |  | NG |  |  |  | N | N |  | 12H | [5 empty] | N | [17 empty] | Y | Y | N
Vintage1959 | natural gas steam turbine | TRUE | 7294 | City of Glendale - (CA) | 377 | Grayson | CA | Los Angeles | 4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 50 | 0.85 | 40 | 40 | 15 | N |  |  | OP | X | 9 | 1959 |  |  | N | Electric Utility | 1 | X | NG | LFG |  |  |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1964 | natural gas steam turbine | TRUE | 7294 | City of Glendale - (CA) | 377 | Grayson | CA | Los Angeles | 5 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 50 | 0.85 | 40 | 40 | 15 | N |  |  | OP | X | 11 | 1964 |  |  | N | Electric Utility | 1 | X | NG | LFG |  |  |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1977 | natural gas combined cycle | TRUE | 7294 | City of Glendale - (CA) | 377 | Grayson | CA | Los Angeles | 8A | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 25.4 | 0.9 | 26 | 30 | 16 | N |  |  | OP | X | 7 | 1977 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1977 | natural gas combined cycle | TRUE | 7294 | City of Glendale - (CA) | 377 | Grayson | CA | Los Angeles | 8BC | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 55.1 | 0.9 | 46 | 50 | 34 | N |  |  | OP | X | 7 | 1977 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2004 | natural gas peaker | TRUE | 7294 | City of Glendale - (CA) | 377 | Grayson | CA | Los Angeles | 9 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 57.4 | 0.85 | 48 | 48 | 25 | N |  |  | OP | X | 1 | 2004 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1920 | hydro | TRUE | 12647 | ALLETE, Inc. | 378 | Prairie River | MN | Itasca | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 4 | 1920 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1920 | hydro | TRUE | 12647 | ALLETE, Inc. | 378 | Prairie River | MN | Itasca | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 4 | 1920 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1960 | hydro | TRUE | 16612 | City & County of San Francisco | 380 | Dion R Holm | CA | Tuolumne | 1 | Conventional Hydroelectric | HY |  | S | X | X | INTKEP_2_UNITS-APND | INTKEP_2_UNITS | 78.4 | 0.95 | 78.4 | 78.4 | 0 | N |  |  | OP | X | 8 | 1960 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1960 | hydro | TRUE | 16612 | City & County of San Francisco | 380 | Dion R Holm | CA | Tuolumne | 2 | Conventional Hydroelectric | HY |  | S | X | X | INTKEP_2_UNITS-APND | INTKEP_2_UNITS | 78.4 | 0.95 | 78.4 | 78.4 | 0 | N |  |  | OP | X | 8 | 1960 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1969 | hydro | TRUE | 16612 | City & County of San Francisco | 381 | Moccasin | CA | Tuolumne | 1 | Conventional Hydroelectric | HY |  | S | X | X | INTKEP_2_UNITS-APND | INTKEP_2_UNITS | 50 | 0.9 | 50 | 50 | 0 | N |  |  | OP | X | 8 | 1969 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1969 | hydro | TRUE | 16612 | City & County of San Francisco | 381 | Moccasin | CA | Tuolumne | 2 | Conventional Hydroelectric | HY |  | S | X | X | INTKEP_2_UNITS-APND | INTKEP_2_UNITS | 50 | 0.9 | 50 | 50 | 0 | N |  |  | OP | X | 9 | 1969 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1967 | hydro | TRUE | 16612 | City & County of San Francisco | 382 | R C Kirkwood | CA | Tuolumne | 1 | Conventional Hydroelectric | HY |  | S | X | X | INTKEP_2_UNITS-APND | INTKEP_2_UNITS | 39.5 | 0.95 | 39.5 | 39.5 | 0 | N |  |  | OP | X | 2 | 1967 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1967 | hydro | TRUE | 16612 | City & County of San Francisco | 382 | R C Kirkwood | CA | Tuolumne | 2 | Conventional Hydroelectric | HY |  | S | X | X | INTKEP_2_UNITS-APND | INTKEP_2_UNITS | 39.5 | 0.95 | 39.5 | 39.5 | 0 | N |  |  | OP | X | 2 | 1967 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1987 | hydro | TRUE | 16612 | City & County of San Francisco | 382 | R C Kirkwood | CA | Tuolumne | 3 | Conventional Hydroelectric | HY |  | S | X | X | INTKEP_2_UNITS-APND | INTKEP_2_UNITS | 36.5 | 0.9 | 36.5 | 36.5 | 0 | N |  |  | OP | X | 9 | 1987 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1965 | natural gas steam turbine | TRUE | 12384 | Midwest Generations EME LLC | 384 | Joliet 29 | IL | Will | 7 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 660 | 0.9 | 518 | 522 | 120 | N |  |  | OP | X | 4 | 1965 |  |  | N | IPP Non-CHP | 2 | X | NG | [5 empty] | NG | [6 empty] | OVER | [23 empty] | N
Vintage1966 | natural gas steam turbine | TRUE | 12384 | Midwest Generations EME LLC | 384 | Joliet 29 | IL | Will | 8 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 660 | 0.9 | 518 | 522 | 120 | N |  |  | OP | X | 3 | 1966 |  |  | N | IPP Non-CHP | 2 | X | NG | [5 empty] | NG | [6 empty] | OVER | [23 empty] | N
Vintage1953 | hydro | TRUE | 9216 | Imperial Irrigation District | 385 | Drop 2 (CA) | CA | Imperial | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5 | 0.8 | 4.9 | 2.5 | 0.7 | N |  |  | OP | X | 12 | 1953 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1953 | hydro | TRUE | 9216 | Imperial Irrigation District | 385 | Drop 2 (CA) | CA | Imperial | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5 | 0.8 | 4.9 | 2.5 | 0.7 | N |  |  | OP | X | 12 | 1953 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1941 | hydro | TRUE | 9216 | Imperial Irrigation District | 386 | Drop 3 (CA) | CA | Imperial | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.8 | 0.8 | 4.5 | 3.6 | 1 | N |  |  | OP | X | 2 | 1941 |  |  | N | Electric Utility | 1 | X | WAT | [10 empty] | N |  | 1H | [23 empty] | N
Vintage1966 | hydro | TRUE | 9216 | Imperial Irrigation District | 386 | Drop 3 (CA) | CA | Imperial | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.4 | 0.8 | 4.4 | 4.6 | 1 | N |  |  | OP | X | 11 | 1966 |  |  | N | Electric Utility | 1 | X | WAT | [10 empty] | N |  | 1H | [23 empty] | N
Vintage1950 | hydro | TRUE | 9216 | Imperial Irrigation District | 387 | Drop 4 | CA | Imperial | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 0.8 | 10 | 10 | 0.6 | N |  |  | OP | X | 8 | 1950 |  |  | N | Electric Utility | 1 | X | WAT | [10 empty] | N |  | 1H | [23 empty] | N
Vintage1941 | hydro | TRUE | 9216 | Imperial Irrigation District | 387 | Drop 4 | CA | Imperial | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9.6 | 0.8 | 10 | 8 | 1 | N |  |  | OP | X | 2 | 1941 |  |  | N | Electric Utility | 1 | X | WAT | [10 empty] | N |  | 1H | [23 empty] | N
Vintage1957 | hydro | TRUE | 9216 | Imperial Irrigation District | 388 | Pilot Knob | CA | Imperial | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 16.5 | 0.8 |  | 10.4 | 0.7 | N |  |  | OP | X | 1 | 1957 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1957 | hydro | TRUE | 9216 | Imperial Irrigation District | 388 | Pilot Knob | CA | Imperial | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 16.5 | 0.8 |  | 7.7 | 0.7 | N |  |  | OP | X | 1 | 1957 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1952 | natural gas combined cycle | TRUE | 9216 | Imperial Irrigation District | 389 | El Centro Hybrid | CA | Imperial | 2 | Natural Gas Fired Combined Cycle | CA | STM2 | S | N | X |  |  | 34.5 | 0.85 | 32.5 | 32.5 | 22 | N |  |  | OP | X | 8 | 1952 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage1993 | natural gas combined cycle | TRUE | 9216 | Imperial Irrigation District | 389 | El Centro Hybrid | CA | Imperial | 2A | Natural Gas Fired Combined Cycle | CT | STM2 | S | X | N |  |  | 89.9 | 0.85 | 73 | 73 | 48 | N |  |  | OP | X | 6 | 1993 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | NG | DFO |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage2012 | natural gas combined cycle | TRUE | 9216 | Imperial Irrigation District | 389 | El Centro Hybrid | CA | Imperial | 30 | Natural Gas Fired Combined Cycle | CA | STM3 | S | Y | X |  |  | 65.9 | 0.85 | 42 | 53 | 28 | N |  |  | OP | X | 10 | 2012 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2012 | natural gas combined cycle | TRUE | 9216 | Imperial Irrigation District | 389 | El Centro Hybrid | CA | Imperial | 31 | Natural Gas Fired Combined Cycle | CT | STM3 | S | X | N |  |  | 43.2 | 0.8 | 39 | 46 | 24 | N |  |  | OP | X | 10 | 2012 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2012 | natural gas combined cycle | TRUE | 9216 | Imperial Irrigation District | 389 | El Centro Hybrid | CA | Imperial | 32 | Natural Gas Fired Combined Cycle | CT | STM3 | S | X | N |  |  | 43.2 | 0.8 | 39 | 46 | 24 | N |  |  | OP | X | 10 | 2012 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1968 | natural gas steam turbine | TRUE | 9216 | Imperial Irrigation District | 389 | El Centro Hybrid | CA | Imperial | 4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 81.6 | 0.85 | 67.6 | 72 | 20 | N |  |  | OP | X | 8 | 1968 |  |  | N | Electric Utility | 1 | X | NG | RFO |  |  |  |  | NG | RFO |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage2016 | other | TRUE | 9216 | Imperial Irrigation District | 389 | El Centro Hybrid | CA | Imperial | BESS | Batteries | BA |  | S | X | X |  |  | 30 |  | 18.9 | 29 | 0 | N |  |  | OP | X | 10 | 2016 |  |  | N | Electric Utility | 1 | X | MWH | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1982 | hydro | TRUE | 4329 | Copper Valley Elec Assn, Inc | 390 | Solomon Gulch | AK | Valdez Cordova | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6 | 0.8 | 6 | 6 | 0.5 | N |  |  | OP | X | 1 | 1982 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1982 | hydro | TRUE | 4329 | Copper Valley Elec Assn, Inc | 390 | Solomon Gulch | AK | Valdez Cordova | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6 | 0.8 | 6 | 6 | 0.5 | N |  |  | OP | X | 1 | 1982 |  |  | N | Electric Utility | 1 | X | WAT | [10 empty] | N |  | 1H | [23 empty] | N
Vintage1925 | hydro | TRUE | 11208 | Los Angeles Department of Water & Power | 391 | Big Pine Creek | CA | Inyo | 1 | Conventional Hydroelectric | HY |  | S | X | X | none | none | 3.2 | 0.8 | 3 | 3 | 0.3 | N |  |  | OP | X | 7 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 12H | [23 empty] | N
Vintage1973 | other | TRUE | 11208 | Los Angeles Department of Water & Power | 392 | Castaic | CA | Los Angeles | 1 | Hydroelectric Pumped Storage | PS |  | S | X | X | none | none | 271 | 0.943 | 270.5 | 270.5 | 10 | N |  |  | OP | X | 9 | 1973 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1974 | other | TRUE | 11208 | Los Angeles Department of Water & Power | 392 | Castaic | CA | Los Angeles | 2 | Hydroelectric Pumped Storage | PS |  | S | X | X | none | none | 271 | 0.943 | 270.5 | 270.5 | 10 | N |  |  | OP | X | 7 | 1974 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1976 | other | TRUE | 11208 | Los Angeles Department of Water & Power | 392 | Castaic | CA | Los Angeles | 3 | Hydroelectric Pumped Storage | PS |  | S | X | X | none | none | 271 | 0.943 | 270.5 | 270.5 | 10 | N |  |  | OP | X | 7 | 1976 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1977 | other | TRUE | 11208 | Los Angeles Department of Water & Power | 392 | Castaic | CA | Los Angeles | 4 | Hydroelectric Pumped Storage | PS |  | S | X | X | none | none | 271 | 0.943 | 270.5 | 270.5 | 10 | N |  |  | OP | X | 6 | 1977 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1977 | other | TRUE | 11208 | Los Angeles Department of Water & Power | 392 | Castaic | CA | Los Angeles | 5 | Hydroelectric Pumped Storage | PS |  | S | X | X | none | none | 271 | 0.943 | 270.5 | 270.5 | 10 | N |  |  | OP | X | 12 | 1977 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1978 | other | TRUE | 11208 | Los Angeles Department of Water & Power | 392 | Castaic | CA | Los Angeles | 6 | Hydroelectric Pumped Storage | PS |  | S | X | X | none | none | 271 | 0.943 | 270.5 | 270.5 | 10 | N |  |  | OP | X | 8 | 1978 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1972 | hydro | TRUE | 11208 | Los Angeles Department of Water & Power | 392 | Castaic | CA | Los Angeles | 7 | Conventional Hydroelectric | HY |  | S | X | X | none | none | 56 | 0.8 | 51.5 | 51.5 | 2 | N |  |  | OP | X | 1 | 1972 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1952 | hydro | TRUE | 11208 | Los Angeles Department of Water & Power | 393 | Control Gorge | CA | Inyo | 1 | Conventional Hydroelectric | HY |  | S | X | X | none | none | 37.5 | 1 | 37.5 | 37.5 | 0.5 | N |  |  | OP | X | 4 | 1952 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1908 | hydro | TRUE | 11208 | Los Angeles Department of Water & Power | 394 | Cottonwood | CA | Inyo | 1 | Conventional Hydroelectric | HY |  | S | X | X | none | none | 0.8 | 0.8 | 1.2 | 1.2 | 0.1 | N |  |  | OP | X | 11 | 1908 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1909 | hydro | TRUE | 11208 | Los Angeles Department of Water & Power | 394 | Cottonwood | CA | Inyo | 2 | Conventional Hydroelectric | HY |  | S | X | X | none | none | 0.8 | 0.8 | 1.2 | 1.2 | 0.1 | N |  |  | OP | X | 10 | 1909 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1971 | hydro | TRUE | 11208 | Los Angeles Department of Water & Power | 396 | Foothill | CA | Los Angeles | 1 | Conventional Hydroelectric | HY |  | S | X | X | none | none | 8.8 | 0.8 | 8.6 | 8.6 | 0.1 | N |  |  | OP | X | 10 | 1971 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1921 | hydro | TRUE | 11208 | Los Angeles Department of Water & Power | 397 | Franklin (CA) | CA | Los Angeles | 1 | Conventional Hydroelectric | HY |  | S | X | X | none | none | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | OP | X | 6 | 1921 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1927 | hydro | TRUE | 11208 | Los Angeles Department of Water & Power | 398 | Haiwee | CA | Inyo | 1 | Conventional Hydroelectric | HY |  | S | X | X | none | none | 2.8 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 7 | 1927 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1927 | hydro | TRUE | 11208 | Los Angeles Department of Water & Power | 398 | Haiwee | CA | Inyo | 2 | Conventional Hydroelectric | HY |  | S | X | X | none | none | 2.8 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 7 | 1927 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1995 | natural gas combined cycle | TRUE | 11208 | Los Angeles Department of Water & Power | 399 | Harbor | CA | Los Angeles | 10A | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | none | none | 85.3 | 0.85 | 73 | 73 | 36 | N |  |  | OP | X | 1 | 1995 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1995 | natural gas combined cycle | TRUE | 11208 | Los Angeles Department of Water & Power | 399 | Harbor | CA | Los Angeles | 10B | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | none | none | 85.3 | 0.85 | 73 | 73 | 36 | N |  |  | OP | X | 1 | 1995 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1995 | natural gas combined cycle | TRUE | 11208 | Los Angeles Department of Water & Power | 399 | Harbor | CA | Los Angeles | 5 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X | none | none | 75 | 0.8 | 56 | 60 | 17 | N |  |  | OP | X | 1 | 1995 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage2002 | natural gas peaker | TRUE | 11208 | Los Angeles Department of Water & Power | 399 | Harbor | CA | Los Angeles | GT10 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | none | none | 60.5 | 0.85 | 47.4 | 47.4 | 15 | N |  |  | OP | X | 1 | 2002 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2002 | natural gas peaker | TRUE | 11208 | Los Angeles Department of Water & Power | 399 | Harbor | CA | Los Angeles | GT11 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | none | none | 60.5 | 0.85 | 47.4 | 47.4 | 15 | N |  |  | OP | X | 1 | 2002 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2002 | natural gas peaker | TRUE | 11208 | Los Angeles Department of Water & Power | 399 | Harbor | CA | Los Angeles | GT12 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | none | none | 60.5 | 0.85 | 47.4 | 47.4 | 15 | N |  |  | OP | X | 1 | 2002 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2002 | natural gas peaker | TRUE | 11208 | Los Angeles Department of Water & Power | 399 | Harbor | CA | Los Angeles | GT13 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | none | none | 60.5 | 0.85 | 47.4 | 47.4 | 15 | N |  |  | OP | X | 1 | 2002 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2002 | natural gas peaker | TRUE | 11208 | Los Angeles Department of Water & Power | 399 | Harbor | CA | Los Angeles | GT14 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | none | none | 60.5 | 0.85 | 47.4 | 47.4 | 15 | N |  |  | OP | X | 1 | 2002 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1962 | natural gas steam turbine | TRUE | 11208 | Los Angeles Department of Water & Power | 400 | Haynes | CA | Los Angeles | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | none | none | 230 | 0.85 | 222 | 222 | 50 | N |  |  | OP | X | 9 | 1962 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage2005 | natural gas combined cycle | TRUE | 11208 | Los Angeles Department of Water & Power | 400 | Haynes | CA | Los Angeles | 10 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | none | none | 182.8 | 0.85 | 162.5 | 162.5 | 105 | N |  |  | OP | X | 1 | 2005 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage2013 | natural gas peaker | TRUE | 11208 | Los Angeles Department of Water & Power | 400 | Haynes | CA | Los Angeles | 11 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | none | none | 108.2 | 0.85 | 99.2 | 99.2 | 52 | N |  |  | OP | X | 6 | 2013 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2013 | natural gas peaker | TRUE | 11208 | Los Angeles Department of Water & Power | 400 | Haynes | CA | Los Angeles | 12 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | none | none | 108.2 | 0.85 | 99.2 | 99.2 | 52 | N |  |  | OP | X | 6 | 2013 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2013 | natural gas peaker | TRUE | 11208 | Los Angeles Department of Water & Power | 400 | Haynes | CA | Los Angeles | 13 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | none | none | 108.2 | 0.85 | 99.2 | 99.2 | 52 | N |  |  | OP | X | 6 | 2013 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2013 | natural gas peaker | TRUE | 11208 | Los Angeles Department of Water & Power | 400 | Haynes | CA | Los Angeles | 14 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | none | none | 108.2 | 0.85 | 99.2 | 99.2 | 52 | N |  |  | OP | X | 6 | 2013 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2013 | natural gas peaker | TRUE | 11208 | Los Angeles Department of Water & Power | 400 | Haynes | CA | Los Angeles | 15 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | none | none | 108.2 | 0.85 | 99.2 | 99.2 | 52 | N |  |  | OP | X | 6 | 2013 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2013 | natural gas peaker | TRUE | 11208 | Los Angeles Department of Water & Power | 400 | Haynes | CA | Los Angeles | 16 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | none | none | 108.2 | 0.85 | 99.2 | 99.2 | 52 | N |  |  | OP | X | 6 | 2013 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1963 | natural gas steam turbine | TRUE | 11208 | Los Angeles Department of Water & Power | 400 | Haynes | CA | Los Angeles | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | none | none | 230 | 0.85 | 222 | 222 | 50 | N |  |  | OP | X | 4 | 1963 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage2005 | natural gas combined cycle | TRUE | 11208 | Los Angeles Department of Water & Power | 400 | Haynes | CA | Los Angeles | 8 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | none | none | 264.3 | 0.85 | 235 | 250 | 73 | N |  |  | OP | X | 1 | 2005 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage2005 | natural gas combined cycle | TRUE | 11208 | Los Angeles Department of Water & Power | 400 | Haynes | CA | Los Angeles | 9 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | none | none | 182.8 | 0.85 | 162.5 | 162.5 | 105 | N |  |  | OP | X | 1 | 2005 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1952 | hydro | TRUE | 11208 | Los Angeles Department of Water & Power | 401 | Middle Gorge | CA | Mono | 1 | Conventional Hydroelectric | HY |  | S | X | X | none | none | 37.5 | 1 | 37.5 | 37.5 | 0.5 | N |  |  | OP | X | 5 | 1952 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1958 | hydro | TRUE | 11208 | Los Angeles Department of Water & Power | 402 | Pleasant Valley Hydro | CA | Inyo | 1 | Conventional Hydroelectric | HY |  | S | X | X | none | none | 3.2 | 0.8 | 2.7 | 2.7 | 0.3 | N |  |  | OP | X | 2 | 1958 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1922 | hydro | TRUE | 11208 | Los Angeles Department of Water & Power | 403 | San Fernando | CA | Los Angeles | 1 | Conventional Hydroelectric | HY |  | S | X | X | none | none | 2.8 | 0.8 | 3.2 | 3.2 | 0.1 | N |  |  | OP | X | 10 | 1922 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1922 | hydro | TRUE | 11208 | Los Angeles Department of Water & Power | 403 | San Fernando | CA | Los Angeles | 2 | Conventional Hydroelectric | HY |  | S | X | X | none | none | 2.8 | 0.8 | 2.9 | 2.9 | 0.1 | N |  |  | OP | X | 10 | 1922 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1958 | natural gas steam turbine | TRUE | 11208 | Los Angeles Department of Water & Power | 404 | Scattergood | CA | Los Angeles | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | none | none | 163.2 | 0.85 | 105 | 105 | 40 | N |  |  | OP | X | 12 | 1958 | 12 | 2024 | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1959 | natural gas steam turbine | TRUE | 11208 | Los Angeles Department of Water & Power | 404 | Scattergood | CA | Los Angeles | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | none | none | 163.2 | 0.85 | 156.3 | 156.3 | 40 | N |  |  | OP | X | 7 | 1959 | 12 | 2024 | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage2015 | natural gas combined cycle | TRUE | 11208 | Los Angeles Department of Water & Power | 404 | Scattergood | CA | Los Angeles | 4 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | none | none | 216.9 | 0.85 | 206 | 206 | 75 | N |  |  | OP | X | 10 | 2015 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage2015 | natural gas combined cycle | TRUE | 11208 | Los Angeles Department of Water & Power | 404 | Scattergood | CA | Los Angeles | 5 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X | none | none | 118.9 | 0.85 | 107 | 107 | 65 | N |  |  | OP | X | 11 | 2015 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2015 | natural gas peaker | TRUE | 11208 | Los Angeles Department of Water & Power | 404 | Scattergood | CA | Los Angeles | 6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | none | none | 106.9 | 0.85 | 102 | 102 | 28 | N |  |  | OP | X | 8 | 2015 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2015 | natural gas peaker | TRUE | 11208 | Los Angeles Department of Water & Power | 404 | Scattergood | CA | Los Angeles | 7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | none | none | 106.9 | 0.85 | 102 | 102 | 28 | N |  |  | OP | X | 9 | 2015 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 219 | Alaska Power and Telephone Co | 406 | Tok | AK | Southeast Fairbanks | 3A | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 0.5 | N |  |  | OP | X | 11 | 1999 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1989 | petroleum | TRUE | 219 | Alaska Power and Telephone Co | 406 | Tok | AK | Southeast Fairbanks | 4A | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.5 | N |  |  | OP | X | 12 | 1989 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1996 | petroleum | TRUE | 219 | Alaska Power and Telephone Co | 406 | Tok | AK | Southeast Fairbanks | 5A | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.5 | N |  |  | OP | X | 1 | 1996 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage2010 | petroleum | TRUE | 219 | Alaska Power and Telephone Co | 406 | Tok | AK | Southeast Fairbanks | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.2 | N |  |  | OS | X | 12 | 2010 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1985 | petroleum | TRUE | 219 | Alaska Power and Telephone Co | 406 | Tok | AK | Southeast Fairbanks | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 10 | 1985 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1985 | petroleum | TRUE | 219 | Alaska Power and Telephone Co | 406 | Tok | AK | Southeast Fairbanks | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 1 | 1 | 0.4 | N |  |  | OP | X | 10 | 1985 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1953 | hydro | TRUE | 11208 | Los Angeles Department of Water & Power | 407 | Upper Gorge | CA | Mono | 1 | Conventional Hydroelectric | HY |  | S | X | X | none | none | 37.5 | 1 | 36.5 | 36.5 | 0.5 | N |  |  | OP | X | 6 | 1953 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage2001 | natural gas peaker | TRUE | 11208 | Los Angeles Department of Water & Power | 408 | Valley (CA) | CA | Los Angeles | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | none | none | 60.5 | 0.85 | 44 | 44 | 15 | N |  |  | OP | X | 8 | 2001 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2003 | natural gas combined cycle | TRUE | 11208 | Los Angeles Department of Water & Power | 408 | Valley (CA) | CA | Los Angeles | 6 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | none | none | 182.8 | 0.85 | 155 | 155 | 85 | N |  |  | OP | X | 9 | 2003 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage2003 | natural gas combined cycle | TRUE | 11208 | Los Angeles Department of Water & Power | 408 | Valley (CA) | CA | Los Angeles | 7 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | none | none | 182.8 | 0.85 | 155 | 155 | 85 | N |  |  | OP | X | 9 | 2003 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage2003 | natural gas combined cycle | TRUE | 11208 | Los Angeles Department of Water & Power | 408 | Valley (CA) | CA | Los Angeles | 8 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | none | none | 264.4 | 0.85 | 209 | 209 | 60 | N |  |  | OP | X | 11 | 2003 |  |  | N | Electric Utility | 1 | X | NG | DFO | OBG |  |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1967 | hydro | TRUE | 12312 | Merced Irrigation District | 409 | Exchequer | CA | Mariposa | 1 | Conventional Hydroelectric | HY |  | S | X | X | POD_EXCHEC_7_UNIT 1-APND |  | 94.5 | 0.9 | 94.5 | 94.5 | 0.1 | N |  |  | OP | X | 7 | 1967 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1967 | hydro | TRUE | 12312 | Merced Irrigation District | 410 | McSwain | CA | Mariposa | 1 | Conventional Hydroelectric | HY |  | S | X | X | MCSWAIN_6_N001 |  | 9 | 0.9 | 9 | 9 | 0.1 | N |  |  | OP | X | 7 | 1967 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1965 | hydro | TRUE | 13402 | Nevada Irrigation District | 412 | Chicago Park | CA | Nevada | 2P | Conventional Hydroelectric | HY |  | S | X | X |  |  | 44 | 0.99 | 44 | 44 | 5 | N |  |  | OP | X | 11 | 1965 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 12H | [23 empty] | N
Vintage1965 | hydro | TRUE | 13402 | Nevada Irrigation District | 413 | Dutch Flat 2 | CA | Nevada | 3P | Conventional Hydroelectric | HY |  | S | X | X |  |  | 27.3 | 0.99 | 27.3 | 27.3 | 5 | N |  |  | OP | X | 11 | 1965 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 12H | [23 empty] | N
Vintage1957 | hydro | TRUE | 13935 | Oakdale&South San Joaquin Irrigation D. | 414 | Beardsley | CA | Tuolumne | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 0.9 | 11 | 8.5 | 1 | N |  |  | OP | X | 5 | 1957 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1957 | hydro | TRUE | 13935 | Oakdale&South San Joaquin Irrigation D. | 415 | Donnells | CA | Tuolumne | H1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 72 | 0.9 | 72 | 61.2 | 5 | N |  |  | OP | X | 6 | 1957 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1958 | hydro | TRUE | 13935 | Oakdale&South San Joaquin Irrigation D. | 416 | Tulloch | CA | Tuolumne | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 11.7 | 0.9 | 9 | 8 | 1 | N |  |  | OP | X | 6 | 1958 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1958 | hydro | TRUE | 13935 | Oakdale&South San Joaquin Irrigation D. | 416 | Tulloch | CA | Tuolumne | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 11.7 | 0.9 | 10 | 8.5 | 1 | N |  |  | OP | X | 6 | 1958 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage2012 | hydro | TRUE | 13935 | Oakdale&South San Joaquin Irrigation D. | 416 | Tulloch | CA | Tuolumne | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.5 | 0.9 | 6.5 | 6 | 1 | N |  |  | OP | X | 3 | 2012 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1963 | hydro | TRUE | 14191 | South Feather Water and Power Agency | 417 | Forbestown | CA | Butte | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 41.9 | 0.9 | 37.5 | 37.5 | 0 | N |  |  | OP | X | 10 | 1963 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1963 | hydro | TRUE | 14191 | South Feather Water and Power Agency | 418 | Kelly Ridge | CA | Butte | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 0.9 | 10 | 10 | 0 | N |  |  | OP | X | 9 | 1963 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1963 | hydro | TRUE | 14191 | South Feather Water and Power Agency | 419 | Woodleaf | CA | Butte | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 67.2 | 0.9 | 60 | 60 | 0 | N |  |  | OP | X | 11 | 1963 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1984 | petroleum | TRUE | 219 | Alaska Power and Telephone Co | 421 | Craig (AK) | AK | Prince of Wales Ketchikan | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.3 | N |  |  | OP | X | 9 | 1984 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage2015 | petroleum | TRUE | 219 | Alaska Power and Telephone Co | 421 | Craig (AK) | AK | Prince of Wales Ketchikan | 3B | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.7 | N |  |  | OP | X | 8 | 2015 |  |  | N | Electric Utility | 1 | X | DFO | [10 empty] | N |  | 10M | [23 empty] | N
Vintage1983 | petroleum | TRUE | 219 | Alaska Power and Telephone Co | 421 | Craig (AK) | AK | Prince of Wales Ketchikan | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.5 | N |  |  | OP | X | 9 | 1983 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1989 | petroleum | TRUE | 219 | Alaska Power and Telephone Co | 421 | Craig (AK) | AK | Prince of Wales Ketchikan | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.5 | N |  |  | OP | X | 10 | 1989 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1976 | natural gas peaker | TRUE | 14534 | City of Pasadena - (CA) | 422 | Glenarm | CA | Los Angeles | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | Unit 1 | Unit 1 | 28.8 | 0.85 | 22 | 22 | 15 | Y | 7 | 2021 | OP | X | 1 | 1976 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1976 | natural gas peaker | TRUE | 14534 | City of Pasadena - (CA) | 422 | Glenarm | CA | Los Angeles | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | Unit 2 | Unit 2 | 28.8 | 0.85 | 22 | 22 | 15 | Y | 7 | 2021 | OP | X | 1 | 1976 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2004 | natural gas peaker | TRUE | 14534 | City of Pasadena - (CA) | 422 | Glenarm | CA | Los Angeles | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | Unit 3 | Unit 3 | 60.5 | 0.85 | 47.2 | 47.2 | 15.4 | N |  |  | OP | X | 1 | 2004 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2004 | natural gas peaker | TRUE | 14534 | City of Pasadena - (CA) | 422 | Glenarm | CA | Los Angeles | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | Unit 4 | Unit 4 | 60.5 | 0.85 | 47.2 | 47.2 | 15.4 | N |  |  | OP | X | 1 | 2004 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2016 | natural gas combined cycle | TRUE | 14534 | City of Pasadena - (CA) | 422 | Glenarm | CA | Los Angeles | GT5 | Natural Gas Fired Combined Cycle | CT | 1 | S | X | Y | Unit 5 | Unit 5 | 71 | 0.85 | 68 | 68 | 18 | N |  |  | OP | X | 12 | 2016 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2016 | natural gas combined cycle | TRUE | 14534 | City of Pasadena - (CA) | 422 | Glenarm | CA | Los Angeles | ST1 | Natural Gas Fired Combined Cycle | CA | 1 | S | N | X | Unit 5 | Unit 5 | 16 | 0.9 | 16 | 16 | 6 | N |  |  | OP | X | 12 | 2016 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage1990 | petroleum | TRUE | 219 | Alaska Power and Telephone Co | 423 | Hydaburg | AK | Prince of Wales Ketchikan | 1A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 10 | 1990 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage2001 | petroleum | TRUE | 219 | Alaska Power and Telephone Co | 423 | Hydaburg | AK | Prince of Wales Ketchikan | 3A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 10 | 2001 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1985 | petroleum | TRUE | 219 | Alaska Power and Telephone Co | 423 | Hydaburg | AK | Prince of Wales Ketchikan | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 9 | 1985 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1966 | hydro | TRUE | 15127 | Placer County Water Agency | 424 | French Meadows | CA | Placer | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15.3 | 0.9 | 16 | 16 | 0 | N |  |  | OP | X | 10 | 1966 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1966 | hydro | TRUE | 15127 | Placer County Water Agency | 425 | Middle Fork | CA | Placer | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 61.2 | 0.9 | 66 | 66 | 0 | N |  |  | OP | X | 10 | 1966 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1966 | hydro | TRUE | 15127 | Placer County Water Agency | 425 | Middle Fork | CA | Placer | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 61.2 | 0.9 | 66 | 66 | 0 | N |  |  | OP | X | 10 | 1966 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1966 | hydro | TRUE | 15127 | Placer County Water Agency | 426 | Oxbow (CA) | CA | Placer | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.1 | 0.9 | 6 | 6 | 0 | N |  |  | OP | X | 10 | 1966 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1966 | hydro | TRUE | 15127 | Placer County Water Agency | 427 | Ralston | CA | Placer | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 79.2 | 0.9 | 86 | 86 | 0 | N |  |  | OP | X | 10 | 1966 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1982 | hydro | TRUE | 12312 | Merced Irrigation District | 428 | Parker | CA | Merced | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.7 | 0.95 | 2.7 | 2.7 | 0.1 | N |  |  | OP | X | 4 | 1982 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1963 | hydro | TRUE | 16534 | Sacramento Municipal Util Dist | 430 | Camino | CA | El Dorado | H1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 78.9 | 0.95 | 78.9 | 78.9 | 1 | N |  |  | OP | X | 10 | 1963 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1968 | hydro | TRUE | 16534 | Sacramento Municipal Util Dist | 430 | Camino | CA | El Dorado | H2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 78.9 | 0.95 | 77 | 77 | 1 | N |  |  | OP | X | 8 | 1968 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1961 | hydro | TRUE | 16534 | Sacramento Municipal Util Dist | 431 | Jaybird | CA | El Dorado | H1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 80.8 | 0.95 | 78.1 | 78.1 | 1 | N |  |  | OP | X | 4 | 1961 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1962 | hydro | TRUE | 16534 | Sacramento Municipal Util Dist | 431 | Jaybird | CA | El Dorado | H2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 80.8 | 0.95 | 78.1 | 78.1 | 1 | N |  |  | OP | X | 3 | 1962 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1971 | hydro | TRUE | 16534 | Sacramento Municipal Util Dist | 432 | Loon Lake | CA | El Dorado | H1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 74.1 | 0.95 | 74.1 | 74.1 | 1 | N |  |  | OP | X | 9 | 1971 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1965 | hydro | TRUE | 16534 | Sacramento Municipal Util Dist | 433 | Robbs Peak | CA | El Dorado | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 25.5 | 0.95 | 25.5 | 25.5 | 1 | N |  |  | OP | X | 10 | 1965 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1968 | hydro | TRUE | 16534 | Sacramento Municipal Util Dist | 435 | White Rock/Slab Creek | CA | El Dorado | H1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 133 | 0.95 | 108 | 108 | 1 | N |  |  | OP | X | 6 | 1968 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1968 | hydro | TRUE | 16534 | Sacramento Municipal Util Dist | 435 | White Rock/Slab Creek | CA | El Dorado | H2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 133 | 0.95 | 133 | 133 | 1 | N |  |  | OP | X | 2 | 1968 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage2020 | hydro | TRUE | 16534 | Sacramento Municipal Util Dist | 435 | White Rock/Slab Creek | CA | El Dorado | H3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.7 | 0.95 | 2.7 | 2.7 | 0.4 | N |  |  | OP | X | 12 | 2020 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1983 | hydro | TRUE | 16534 | Sacramento Municipal Util Dist | 435 | White Rock/Slab Creek | CA | El Dorado | H4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.86 | 0.5 | 0.5 | 0.5 | N |  |  | OS | X | 6 | 1983 | 12 | 2022 | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M | [23 empty] | N
Vintage1972 | hydro | TRUE | 3255 | California Dept. of Water Resources | 436 | Devil Canyon | CA | San Bernardino | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 59.8 | 0.95 | 57 | 57 | 15 | N |  |  | OP | X | 12 | 1972 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1976 | hydro | TRUE | 3255 | California Dept. of Water Resources | 436 | Devil Canyon | CA | San Bernardino | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 59.8 | 0.95 | 57 | 57 | 15 | N |  |  | OP | X | 7 | 1976 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1994 | hydro | TRUE | 3255 | California Dept. of Water Resources | 436 | Devil Canyon | CA | San Bernardino | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 78.3 | 0.95 | 74 | 74 | 15 | N |  |  | OP | X | 7 | 1994 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1992 | hydro | TRUE | 3255 | California Dept. of Water Resources | 436 | Devil Canyon | CA | San Bernardino | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 78.3 | 0.95 | 74 | 74 | 15 | N |  |  | OP | X | 7 | 1992 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1968 | hydro | TRUE | 3255 | California Dept. of Water Resources | 437 | Edward C Hyatt | CA | Butte | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 117 | 0.95 | 135.3 | 131.3 | 115 | N |  |  | OP | X | 3 | 1968 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1968 | other | TRUE | 3255 | California Dept. of Water Resources | 437 | Edward C Hyatt | CA | Butte | 2 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 97.7 | 0.85 | 112.4 | 122.6 | 97 | N |  |  | OP | X | 11 | 1968 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1968 | hydro | TRUE | 3255 | California Dept. of Water Resources | 437 | Edward C Hyatt | CA | Butte | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 117 | 0.95 | 135.3 | 131.3 | 115 | N |  |  | OP | X | 6 | 1968 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1968 | other | TRUE | 3255 | California Dept. of Water Resources | 437 | Edward C Hyatt | CA | Butte | 4 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 97.7 | 0.85 | 112.4 | 122.6 | 97 | N |  |  | OP | X | 12 | 1968 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1968 | hydro | TRUE | 3255 | California Dept. of Water Resources | 437 | Edward C Hyatt | CA | Butte | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 117 | 0.95 | 135.3 | 131.3 | 115 | N |  |  | OP | X | 8 | 1968 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1969 | other | TRUE | 3255 | California Dept. of Water Resources | 437 | Edward C Hyatt | CA | Butte | 6 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 97.7 | 0.85 | 112.4 | 122.6 | 97 | N |  |  | OP | X | 2 | 1969 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1968 | hydro | TRUE | 3255 | California Dept. of Water Resources | 438 | Thermalito | CA | Butte | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 32.6 | 0.95 | 32.6 | 30 | 30 | N |  |  | OP | X | 11 | 1968 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1968 | other | TRUE | 3255 | California Dept. of Water Resources | 438 | Thermalito | CA | Butte | 2 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 27.5 | 0.9 | 27.5 | 27.3 | 27 | N |  |  | OP | X | 7 | 1968 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1968 | other | TRUE | 3255 | California Dept. of Water Resources | 438 | Thermalito | CA | Butte | 3 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 27.5 | 0.9 | 27.5 | 27.3 | 27 | N |  |  | OP | X | 7 | 1968 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1968 | other | TRUE | 3255 | California Dept. of Water Resources | 438 | Thermalito | CA | Butte | 4 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 27.5 | 0.9 | 27.5 | 27.3 | 27 | N |  |  | OP | X | 2 | 1968 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1971 | hydro | TRUE | 19281 | Turlock Irrigation District | 439 | Don Pedro | CA | Tuolumne | 1 | Conventional Hydroelectric | HY |  | J | X | X |  |  | 45.5 | 0.95 | 55 | 55 | 10 | N |  |  | OP | X | 5 | 1971 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1971 | hydro | TRUE | 19281 | Turlock Irrigation District | 439 | Don Pedro | CA | Tuolumne | 2 | Conventional Hydroelectric | HY |  | J | X | X |  |  | 45.5 | 0.95 | 55 | 55 | 10 | N |  |  | OP | X | 5 | 1971 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1971 | hydro | TRUE | 19281 | Turlock Irrigation District | 439 | Don Pedro | CA | Tuolumne | 3 | Conventional Hydroelectric | HY |  | J | X | X |  |  | 45.5 | 0.95 | 55 | 55 | 10 | N |  |  | OP | X | 5 | 1971 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1989 | hydro | TRUE | 19281 | Turlock Irrigation District | 439 | Don Pedro | CA | Tuolumne | 4 | Conventional Hydroelectric | HY |  | J | X | X |  |  | 34.3 | 0.9 | 38.2 | 38.2 | 8 | N |  |  | OP | X | 4 | 1989 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1924 | hydro | TRUE | 19281 | Turlock Irrigation District | 440 | La Grange | CA | Stanislaus | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.8 | 1 | 1 | 0.1 | N |  |  | OP | X | 12 | 1924 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1924 | hydro | TRUE | 19281 | Turlock Irrigation District | 440 | La Grange | CA | Stanislaus | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.3 | 0.8 | 3.3 | 3.3 | 0.1 | N |  |  | OP | X | 12 | 1924 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1955 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 441 | Folsom | CA | Sacramento | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 66.2 | 1 | 71.7 | 71.7 | 0 | N |  |  | OP | X | 6 | 1955 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1955 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 441 | Folsom | CA | Sacramento | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 66.2 | 1 | 71.7 | 71.7 | 0 | N |  |  | OP | X | 10 | 1955 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1955 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 441 | Folsom | CA | Sacramento | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 66.2 | 1 | 71.7 | 71.7 | 0 | N |  |  | OP | X | 5 | 1955 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1963 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 442 | Judge F Carr | CA | Shasta | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 77.2 | 0.91 | 88.7 | 88.7 | 0 | N |  |  | OP | X | 5 | 1963 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1963 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 442 | Judge F Carr | CA | Shasta | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 77.2 | 0.91 | 88.7 | 88.7 | 0 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1950 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 443 | Keswick | CA | Shasta | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 39 | 1 | 39 | 39 | 0 | N |  |  | OP | X | 3 | 1950 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1949 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 443 | Keswick | CA | Shasta | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 39 | 1 | 39 | 39 | 0 | N |  |  | OP | X | 12 | 1949 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1949 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 443 | Keswick | CA | Shasta | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 39 | 1 | 39 | 39 | 0 | N |  |  | OP | X | 10 | 1949 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1955 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 444 | Nimbus | CA | Sacramento | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.7 | 0.9 | 8.3 | 8.3 | 0 | N |  |  | OP | X | 5 | 1955 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1955 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 444 | Nimbus | CA | Sacramento | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.7 | 0.9 | 8.3 | 8.3 | 0 | N |  |  | OP | X | 6 | 1955 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1949 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 445 | Shasta | CA | Shasta | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 142 | 1 | 142 | 142 | 0 | N |  |  | OP | X | 4 | 1949 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1948 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 445 | Shasta | CA | Shasta | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 142 | 1 | 142 | 142 | 0 | N |  |  | OP | X | 7 | 1948 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1944 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 445 | Shasta | CA | Shasta | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 142 | 1 | 142 | 142 | 0 | N |  |  | OP | X | 6 | 1944 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1944 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 445 | Shasta | CA | Shasta | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 142 | 1 | 142 | 142 | 0 | N |  |  | OP | X | 6 | 1944 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1948 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 445 | Shasta | CA | Shasta | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 142 | 1 | 142 | 142 | 0 | N |  |  | OP | X | 3 | 1948 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1944 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 445 | Shasta | CA | Shasta | S1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0 | N |  |  | OP | X | 6 | 1944 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1944 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 445 | Shasta | CA | Shasta | S2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0 | N |  |  | OP | X | 6 | 1944 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1968 | other | TRUE | 2518 | U S Bureau of Reclamation | 446 | ONeill | CA | Merced | 1 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 4.2 | 1 | 2.4 | 2.4 | 0 | N |  |  | OP | X | 1 | 1968 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1968 | other | TRUE | 2518 | U S Bureau of Reclamation | 446 | ONeill | CA | Merced | 2 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 4.2 | 1 | 2.4 | 2.4 | 0 | N |  |  | OP | X | 2 | 1968 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1967 | other | TRUE | 2518 | U S Bureau of Reclamation | 446 | ONeill | CA | Merced | 3 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 4.2 | 1 | 2.4 | 2.4 | 0 | N |  |  | OP | X | 11 | 1967 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1967 | other | TRUE | 2518 | U S Bureau of Reclamation | 446 | ONeill | CA | Merced | 4 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 4.2 | 1 | 2.4 | 2.4 | 0 | N |  |  | OP | X | 11 | 1967 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1968 | other | TRUE | 2518 | U S Bureau of Reclamation | 446 | ONeill | CA | Merced | 5 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 4.2 | 1 | 2.4 | 2.4 | 0 | N |  |  | OP | X | 2 | 1968 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1967 | other | TRUE | 2518 | U S Bureau of Reclamation | 446 | ONeill | CA | Merced | 6 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 4.2 | 1 | 2.4 | 2.4 | 0 | N |  |  | OP | X | 12 | 1967 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1942 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 447 | Parker Dam | CA | San Bernardino | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 30 | 1 | 30 | 30 | 0 | N |  |  | OP | X | 12 | 1942 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1943 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 447 | Parker Dam | CA | San Bernardino | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 30 | 1 | 30 | 30 | 0 | N |  |  | OP | X | 1 | 1943 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1942 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 447 | Parker Dam | CA | San Bernardino | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 30 | 1 | 30 | 30 | 0 | N |  |  | OP | X | 12 | 1942 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1943 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 447 | Parker Dam | CA | San Bernardino | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 30 | 1 | 30 | 30 | 0 | N |  |  | OP | X | 5 | 1943 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1968 | other | TRUE | 3255 | California Dept. of Water Resources | 448 | W R Gianelli | CA | Merced | 1 | Hydroelectric Pumped Storage | PS |  | J | X | X |  |  | 53 | 0.95 | 51 | 51 | 0 | N |  |  | OP | X | 6 | 1968 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1968 | other | TRUE | 3255 | California Dept. of Water Resources | 448 | W R Gianelli | CA | Merced | 2 | Hydroelectric Pumped Storage | PS |  | J | X | X |  |  | 53 | 0.95 | 50 | 50 | 0 | N |  |  | OP | X | 3 | 1968 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1967 | other | TRUE | 3255 | California Dept. of Water Resources | 448 | W R Gianelli | CA | Merced | 3 | Hydroelectric Pumped Storage | PS |  | J | X | X |  |  | 53 | 0.95 | 50 | 50 | 0 | N |  |  | OP | X | 11 | 1967 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1967 | other | TRUE | 3255 | California Dept. of Water Resources | 448 | W R Gianelli | CA | Merced | 4 | Hydroelectric Pumped Storage | PS |  | J | X | X |  |  | 53 | 0.95 | 50 | 50 | 0 | N |  |  | OP | X | 9 | 1967 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1967 | other | TRUE | 3255 | California Dept. of Water Resources | 448 | W R Gianelli | CA | Merced | 5 | Hydroelectric Pumped Storage | PS |  | J | X | X |  |  | 53 | 0.95 | 50 | 50 | 0 | N |  |  | OP | X | 8 | 1967 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1967 | other | TRUE | 3255 | California Dept. of Water Resources | 448 | W R Gianelli | CA | Merced | 6 | Hydroelectric Pumped Storage | PS |  | J | X | X |  |  | 53 | 0.95 | 50 | 50 | 0 | N |  |  | OP | X | 7 | 1967 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1967 | other | TRUE | 3255 | California Dept. of Water Resources | 448 | W R Gianelli | CA | Merced | 7 | Hydroelectric Pumped Storage | PS |  | J | X | X |  |  | 53 | 0.95 | 50 | 50 | 0 | N |  |  | OP | X | 5 | 1967 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1967 | other | TRUE | 3255 | California Dept. of Water Resources | 448 | W R Gianelli | CA | Merced | 8 | Hydroelectric Pumped Storage | PS |  | J | X | X |  |  | 53 | 0.95 | 50 | 50 | 0 | N |  |  | OP | X | 3 | 1967 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1964 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 450 | Spring Creek | CA | Shasta | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 90 | 0.95 | 90 | 90 | 0 | N |  |  | OP | X | 1 | 1964 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1964 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 450 | Spring Creek | CA | Shasta | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 90 | 0.95 | 90 | 90 | 0 | N |  |  | OP | X | 3 | 1964 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1964 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 451 | Trinity | CA | Trinity | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 70 | 1 | 70 | 70 | 0 | N |  |  | OP | X | 2 | 1964 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1964 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 451 | Trinity | CA | Trinity | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 70 | 1 | 70 | 70 | 0 | N |  |  | OP | X | 2 | 1964 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1969 | hydro | TRUE | 21140 | Yuba County Water Agency | 454 | Colgate | CA | Yuba | 1 | Conventional Hydroelectric | HY |  | S | X | X | COLGATE 1_7_B1 | COLGATE 1_7_B1 | 157.5 | 0.9 | 176.7 | 176.7 | 0 | N |  |  | OP | X | 10 | 1969 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1969 | hydro | TRUE | 21140 | Yuba County Water Agency | 454 | Colgate | CA | Yuba | 2 | Conventional Hydroelectric | HY |  | S | X | X | COLGATE 2_7_B1 | COLGATE 2_7_B1 | 157.5 | 0.9 | 175.7 | 175.7 | 0 | N |  |  | OP | X | 10 | 1969 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1969 | hydro | TRUE | 21140 | Yuba County Water Agency | 455 | Narrows 2 | CA | Yuba | 1 | Conventional Hydroelectric | HY |  | S | X | X | NARROWS 2_7_B1 | NARROWS 2_7_B1 | 46.7 | 0.9 | 55 | 55 | 4 | N |  |  | OP | X | 12 | 1969 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1986 | hydro | TRUE | 5969 | City of Escondido - (CA) | 457 | Bear Valley | CA | San Diego | HC1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.85 | 0.7 | 0.7 | 0.2 | N |  |  | OP | X | 6 | 1986 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1986 | hydro | TRUE | 5969 | City of Escondido - (CA) | 457 | Bear Valley | CA | San Diego | HC2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.85 | 0.7 | 0.7 | 0.2 | N |  |  | OP | X | 6 | 1986 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1964 | petroleum | TRUE | 56146 | Black Hills Colorado Electric, LLC | 460 | Pueblo | CO | Pueblo | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 2 | 1964 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1964 | petroleum | TRUE | 56146 | Black Hills Colorado Electric, LLC | 460 | Pueblo | CO | Pueblo | IC3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 2 | 1964 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1964 | petroleum | TRUE | 56146 | Black Hills Colorado Electric, LLC | 460 | Pueblo | CO | Pueblo | IC4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 2 | 1964 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1964 | petroleum | TRUE | 56146 | Black Hills Colorado Electric, LLC | 460 | Pueblo | CO | Pueblo | IC5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 2 | 1964 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1973 | natural gas peaker | TRUE | 15466 | Public Service Co of Colorado | 464 | Alamosa | CO | Alamosa | CT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 26.6 | 0.9 | 13 | 17 | 5 | N |  |  | OP | X | 6 | 1973 | 12 | 2026 | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1977 | natural gas peaker | TRUE | 15466 | Public Service Co of Colorado | 464 | Alamosa | CO | Alamosa | CT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 26.6 | 0.9 | 14 | 18 | 5 | N |  |  | OP | X | 6 | 1977 | 12 | 2026 | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage2013 | hydro | TRUE | 1994 | Boulder City of | 466 | Boulder Canyon Hydro | CO | Boulder | 1A | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5 | 0.9 | 5 | 5 | 0.3 | N |  |  | OP | X | 6 | 2013 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1967 | other | TRUE | 15466 | Public Service Co of Colorado | 467 | Cabin Creek | CO | Clear Creek | A | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 150 | 0.9 | 180.3 | 180.3 | 75 | N |  |  | OP | X | 6 | 1967 |  |  | N | Electric Utility | 1 | X | WAT | [10 empty] | N |  | 1H | [23 empty] | N
Vintage1967 | other | TRUE | 15466 | Public Service Co of Colorado | 467 | Cabin Creek | CO | Clear Creek | B | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 150 | 0.9 | 162 | 162 | 75 | N |  |  | OP | X | 6 | 1967 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [7 empty] | 9.6 | 9.6 | 12 | 2022 | [12 empty] | N
Vintage1968 | natural gas steam turbine | TRUE | 15466 | Public Service Co of Colorado | 469 | Cherokee | CO | Adams | 4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 380.8 | 0.85 | 310 | 310 | 220 | N |  |  | OP | X | 6 | 1968 | 12 | 2027 | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER | N | N | [21 empty] | N | N | N
Vintage2015 | natural gas combined cycle | TRUE | 15466 | Public Service Co of Colorado | 469 | Cherokee | CO | Adams | 5 | Natural Gas Fired Combined Cycle | CT | CHR0 | S | X | Y |  |  | 185.3 | 0.85 | 168 | 176 | 32 | N |  |  | OP | X | 8 | 2015 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage2015 | natural gas combined cycle | TRUE | 15466 | Public Service Co of Colorado | 469 | Cherokee | CO | Adams | 6 | Natural Gas Fired Combined Cycle | CT | CHR0 | S | X | Y |  |  | 185.3 | 0.85 | 168 | 176 | 32 | N |  |  | OP | X | 8 | 2015 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 12H | [23 empty] | N | N | N
Vintage2015 | natural gas combined cycle | TRUE | 15466 | Public Service Co of Colorado | 469 | Cherokee | CO | Adams | 7 | Natural Gas Fired Combined Cycle | CA | CHR0 | S | Y | X |  |  | 255 | 0.85 | 240 | 248 | 104 | N |  |  | OP | X | 8 | 2015 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 12H | [23 empty] | N | N | N
Vintage1973 | hard coal | TRUE | 15466 | Public Service Co of Colorado | 470 | Comanche (CO) | CO | Pueblo | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 382.5 | 0.85 | 325 | 325 | 170 | N |  |  | OP | X | 6 | 1973 | 12 | 2022 | N | Electric Utility | 1 | X | SUB | NG |  |  |  |  | NG |  |  |  | N | N |  | OVER | N | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1975 | hard coal | TRUE | 15466 | Public Service Co of Colorado | 470 | Comanche (CO) | CO | Pueblo | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 396 | 0.9 | 335 | 335 | 170 | N |  |  | OP | X | 6 | 1975 | 12 | 2025 | N | Electric Utility | 1 | X | SUB | NG |  |  |  |  | NG |  |  |  | N | N |  | OVER | N | Y |  |  | Y | [18 empty] | Y | N | N
Vintage2010 | hard coal | TRUE | 15466 | Public Service Co of Colorado | 470 | Comanche (CO) | CO | Pueblo | 3 | Conventional Steam Coal | ST |  | J | X | X |  |  | 856.8 | 0.85 | 750 | 766 | 450 | N |  |  | OP | X | 7 | 2010 |  |  | N | Electric Utility | 1 | X | SUB | NG |  |  |  |  | NG |  |  |  | N | N |  | 1H | N | Y |  |  |  | Y | [17 empty] | Y | N | N
Vintage1973 | natural gas peaker | TRUE | 15466 | Public Service Co of Colorado | 471 | Fruita | CO | Mesa | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 26.6 | 0.9 | 14 | 18 | 5 | N |  |  | OP | X | 6 | 1973 | 12 | 2026 | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1906 | hydro | TRUE | 15466 | Public Service Co of Colorado | 472 | Georgetown Hydro | CO | Clear Creek | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.9 | 0.8 | 0.6 | 0.6 | N |  |  | OP | X | 1 | 1906 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1908 | hydro | TRUE | 15466 | Public Service Co of Colorado | 472 | Georgetown Hydro | CO | Clear Creek | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.9 | 0.8 | 0.6 | 0.6 | N |  |  | OP | X | 1 | 1908 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1932 | hydro | TRUE | 57301 | Orchard Mesa Irrigation District | 473 | Grand Valley Project Power Plant | CO | Mesa | 1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.5 | 0.8 | 1.5 | 3 | 0.5 | N |  |  | OA | X | 4 | 1932 | 3 | 2023 | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1908 | hydro | TRUE | 15466 | Public Service Co of Colorado | 474 | Salida | CO | Chaffee | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.6 | N |  |  | OP | X | 6 | 1908 | 12 | 2027 | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1909 | hydro | TRUE | 15466 | Public Service Co of Colorado | 476 | Shoshone (CO) | CO | Garfield | A | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7.2 | 0.9 | 7.5 | 4 | 1 | N |  |  | OP | X | 6 | 1909 |  |  | N | Electric Utility | 1 | X | WAT | [10 empty] | N |  | 10M | [23 empty] | N
Vintage1909 | hydro | TRUE | 15466 | Public Service Co of Colorado | 476 | Shoshone (CO) | CO | Garfield | B | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7.2 | 0.9 | 7.5 | 4 | 1 | N |  |  | OP | X | 6 | 1909 |  |  | N | Electric Utility | 1 | X | WAT | [10 empty] | N |  | 10M | [23 empty] | N
Vintage1973 | natural gas peaker | TRUE | 15466 | Public Service Co of Colorado | 477 | Valmont | CO | Boulder | 6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 59.3 | 0.9 | 43 | 51 | 18 | N |  |  | OP | X | 5 | 1973 | 12 | 2026 | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1983 | hydro | TRUE | 12397 | Metropolitan Water District of S CA | 479 | Temescal | CA | Riverside | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.9 | 0.85 | 2.8 | 2.8 | 1.5 | N |  |  | OP | X | 7 | 1983 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 12H
Vintage1983 | hydro | TRUE | 12397 | Metropolitan Water District of S CA | 480 | Corona | CA | Riverside | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.9 | 0.85 | 2.8 | 2.8 | 1.4 | N |  |  | OP | X | 8 | 1983 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 12H
Vintage1983 | hydro | TRUE | 12397 | Metropolitan Water District of S CA | 481 | Perris | CA | Riverside | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7.9 | 1 | 7.9 | 7.9 | 1.5 | N |  |  | OP | X | 5 | 1983 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 12H
Vintage1984 | hydro | TRUE | 12397 | Metropolitan Water District of S CA | 482 | Rio Hondo | CA | Los Angeles | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.9 | 0.87 | 1.9 | 1.9 | 0.5 | N |  |  | OP | X | 3 | 1984 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 12H
Vintage1984 | hydro | TRUE | 12397 | Metropolitan Water District of S CA | 483 | Coyote Creek | CA | Orange | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.1 | 0.87 | 3.1 | 3.1 | 0.7 | N |  |  | OP | X | 6 | 1984 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 12H
Vintage1985 | hydro | TRUE | 12397 | Metropolitan Water District of S CA | 484 | Red Mountain | CA | San Diego | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.9 | 1 | 5.9 | 5.9 | 1 | N |  |  | OP | X | 6 | 1985 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 12H
Vintage1985 | hydro | TRUE | 12397 | Metropolitan Water District of S CA | 487 | Valley View | CA | Orange | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.1 | 1 | 4.1 | 4.1 | 1.2 | N |  |  | OP | X | 11 | 1985 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 12H
Vintage1983 | hydro | TRUE | 19281 | Turlock Irrigation District | 489 | Upper Dawson | CA | Tuolumne | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.4 | 0.95 | 5.5 | 5.5 | 0.6 | N |  |  | OP | X | 11 | 1983 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1968 | natural gas steam turbine | TRUE | 3989 | City of Colorado Springs - (CO) | 492 | Martin Drake | CO | El Paso | 6 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 75 | 0.85 | 77 | 77 | 38 | N |  |  | OP | X | 10 | 1968 | 9 | 2022 | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER |  | N |  |  | N | [18 empty] | N | N | N
Vintage1974 | natural gas steam turbine | TRUE | 3989 | City of Colorado Springs - (CO) | 492 | Martin Drake | CO | El Paso | 7 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 132.3 | 0.9 | 131 | 131 | 40 | N |  |  | OP | X | 7 | 1974 | 9 | 2022 | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1953 | natural gas steam turbine | TRUE | 3989 | City of Colorado Springs - (CO) | 493 | George Birdsall | CO | El Paso | 1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 17.3 | 0.85 | 16 | 16 | 5 | N |  |  | OP | X | 8 | 1953 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | NG |  |  |  | N | N |  | 12H |  |  |  |  | N | [15 empty] | N |  |  | Y | Y | Y
Vintage1954 | natural gas steam turbine | TRUE | 3989 | City of Colorado Springs - (CO) | 493 | George Birdsall | CO | El Paso | 2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 18.8 | 0.85 | 16 | 16 | 5 | N |  |  | OP | X | 3 | 1954 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | NG |  |  |  | N | N |  | 12H | N |  |  |  | N | [15 empty] | N |  |  | Y | Y | Y
Vintage1957 | natural gas steam turbine | TRUE | 3989 | City of Colorado Springs - (CO) | 493 | George Birdsall | CO | El Paso | 3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 25 | 0.85 | 23 | 23 | 6 | N |  |  | OP | X | 3 | 1957 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | NG |  |  |  | N | N |  | 12H |  |  |  |  | N | [15 empty] | N |  |  | Y | Y | Y
Vintage1939 | hydro | TRUE | 3989 | City of Colorado Springs - (CO) | 494 | Manitou Springs | CO | El Paso | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 0.1 | N |  |  | OP | X | 5 | 1939 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1927 | hydro | TRUE | 3989 | City of Colorado Springs - (CO) | 494 | Manitou Springs | CO | El Paso | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 0.1 | N |  |  | OP | X | 5 | 1927 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage2006 | hydro | TRUE | 3989 | City of Colorado Springs - (CO) | 494 | Manitou Springs | CO | El Paso | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.81 | 0.5 | 0.5 | 0 | N |  |  | OP | X | 3 | 2006 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1925 | hydro | TRUE | 3989 | City of Colorado Springs - (CO) | 495 | Ruxton Park | CO | El Paso | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.1 | N |  |  | OP | X | 5 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage2000 | petroleum | TRUE | 8751 | Town of Holly - (CO) | 502 | Holly | CO | Prowers | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.8 | 0.3 | 0.3 |  | N |  |  | SB | Y | 6 | 2000 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage2007 | petroleum | TRUE | 8751 | Town of Holly - (CO) | 502 | Holly | CO | Prowers | CAT | Petroleum Liquids | IC |  | J | X | X |  |  | 1.8 | 0.8 | 1.7 | 1.8 |  | N |  |  | SB | Y | 9 | 2007 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N | N
Vintage1993 | petroleum | TRUE | 8751 | Town of Holly - (CO) | 502 | Holly | CO | Prowers | EMD | Petroleum Liquids | IC |  | S | X | X |  |  | 0.7 | 0.8 | 0.7 | 0.8 |  | N |  |  | SB | Y | 1 | 1993 |  |  | N | Electric Utility | 1 | X | DFO | [12 empty] | 10M | [23 empty] | N | N
Vintage1951 | petroleum | TRUE | 9928 | City of Julesburg - (CO) | 504 | Julesburg | CO | Sedgwick | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.7 | 0.7 | 0.1 | N |  |  | SB | N | 11 | 1951 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1945 | petroleum | TRUE | 9928 | City of Julesburg - (CO) | 504 | Julesburg | CO | Sedgwick | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | SB | N | 2 | 1945 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1964 | petroleum | TRUE | 9928 | City of Julesburg - (CO) | 504 | Julesburg | CO | Sedgwick | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.1 | 1.1 | 0.1 | N |  |  | SB | N | 12 | 1964 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1946 | petroleum | TRUE | 9928 | City of Julesburg - (CO) | 504 | Julesburg | CO | Sedgwick | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | SB | N | 4 | 1946 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1952 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 505 | Boysen | WY | Fremont | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7.5 | 0.9 | 8.6 | 8.6 | 0 | N |  |  | OP | X | 8 | 1952 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1952 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 505 | Boysen | WY | Fremont | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7.5 | 0.9 | 8.6 | 8.6 | 0 | N |  |  | OP | X | 9 | 1952 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1941 | petroleum | TRUE | 10730 | City of Las Animas - (CO) | 507 | Las Animas | CO | Bent | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 11 | 1941 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1941 | petroleum | TRUE | 10730 | City of Las Animas - (CO) | 507 | Las Animas | CO | Bent | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 11 | 1941 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1951 | petroleum | TRUE | 10730 | City of Las Animas - (CO) | 507 | Las Animas | CO | Bent | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.5 | N |  |  | OP | X | 1 | 1951 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1951 | petroleum | TRUE | 10730 | City of Las Animas - (CO) | 507 | Las Animas | CO | Bent | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.5 | N |  |  | OP | X | 1 | 1951 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1967 | petroleum | TRUE | 10730 | City of Las Animas - (CO) | 507 | Las Animas | CO | Bent | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.8 | 2.5 | 2.5 | 1 | N |  |  | OP | X | 3 | 1967 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1949 | petroleum | TRUE | 10633 | City of Lamar - (CO) | 508 | Lamar Plant | CO | Prowers | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.5 | N |  |  | OS | X | 1 | 1949 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 12H | [23 empty] | N
Vintage1946 | petroleum | TRUE | 10633 | City of Lamar - (CO) | 508 | Lamar Plant | CO | Prowers | IC2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.5 | N |  |  | OS | X | 1 | 1946 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 12H | [23 empty] | N
Vintage2004 | onshore wind | TRUE | 10633 | City of Lamar - (CO) | 508 | Lamar Plant | CO | Prowers | T1-T3 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 4.5 |  | 4 | 4 | 1 | N |  |  | OP | X | 2 | 2004 |  |  | N | Electric Utility | 1 | X | WND | [9 empty] | N |  | 3
Vintage2004 | onshore wind | TRUE | 10633 | City of Lamar - (CO) | 508 | Lamar Plant | CO | Prowers | T4 | Onshore Wind Turbine | WT |  | W | X | X |  |  | 1.5 |  | 1.5 | 1.5 | 1 | N |  |  | OP | X | 2 | 2004 |  |  | N | Electric Utility | 1 | X | WND | [9 empty] | N |  | 1 | [24 empty] | N
Vintage1983 | geothermal | TRUE | 7160 | Geysers Power Co LLC | 510 | Sonoma California Geothermal | CA | Lake | 1 | Geothermal | ST |  | S | X | X |  |  | 78 | 1 | 50 | 55 | 10 | N |  |  | OP | X | 12 | 1983 |  |  | N | IPP Non-CHP | 2 | X | GEO | [5 empty] | GEO |  |  |  | N |  |  | 12H | [23 empty] | N | N
Vintage1966 | natural gas peaker | TRUE | 19204 | City of Trinidad - (CO) | 511 | Trinidad (CO) | CO | Las Animas | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.9 | 1 | 1.9 | 1.9 | 1.9 | N |  |  | SB | Y | 5 | 1966 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | N
Vintage1966 | natural gas peaker | TRUE | 19204 | City of Trinidad - (CO) | 511 | Trinidad (CO) | CO | Las Animas | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.9 | 1 | 1.9 | 1.9 | 1.9 | N |  |  | SB | Y | 5 | 1966 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | N
Vintage1999 | petroleum | TRUE | 19204 | City of Trinidad - (CO) | 511 | Trinidad (CO) | CO | Las Animas | 5 | Petroleum Liquids | IC |  | W | X | X |  |  | 1.8 | 1 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 1 | 1999 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | N | N |  |  | N | N | N | [16 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 19204 | City of Trinidad - (CO) | 511 | Trinidad (CO) | CO | Las Animas | 6 | Petroleum Liquids | IC |  | W | X | X |  |  | 1.8 | 1 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 1 | 1999 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 19204 | City of Trinidad - (CO) | 511 | Trinidad (CO) | CO | Las Animas | 7 | Petroleum Liquids | IC |  | W | X | X |  |  | 1.8 | 1 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 1 | 1999 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N | N | N
Vintage1967 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 512 | Blue Mesa | CO | Gunnison | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 43.2 | 0.9 | 43.2 | 43.2 | 0 | N |  |  | OP | X | 9 | 1967 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1967 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 512 | Blue Mesa | CO | Gunnison | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 43.2 | 0.9 | 43.2 | 43.2 | 0 | N |  |  | OP | X | 11 | 1967 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1950 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 513 | Estes | CO | Larimer | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.9 | 17.2 | 17.2 | 0 | N |  |  | OP | X | 9 | 1950 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1950 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 513 | Estes | CO | Larimer | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.9 | 17.2 | 17.2 | 0 | N |  |  | OP | X | 12 | 1950 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1950 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 513 | Estes | CO | Larimer | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.9 | 17.2 | 17.2 | 0 | N |  |  | OP | X | 12 | 1950 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1970 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 514 | Morrow Point | CO | Montrose | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 86.6 | 0.9 | 86.6 | 86.6 | 0 | N |  |  | OP | X | 12 | 1970 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1971 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 514 | Morrow Point | CO | Montrose | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 86.6 | 0.9 | 86.6 | 86.6 | 0 | N |  |  | OP | X | 1 | 1971 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1959 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 515 | Big Thompson | CO | Larimer | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.5 | 1 | 5.2 | 4.1 | 0 | N |  |  | OP | X | 4 | 1959 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1943 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 516 | Green Mountain | CO | Summit | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 13 | 0.9 | 13 | 13 | 0 | N |  |  | OP | X | 5 | 1943 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1943 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 516 | Green Mountain | CO | Summit | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 13 | 0.9 | 13 | 13 | 0 | N |  |  | OP | X | 5 | 1943 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1951 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 517 | Marys Lake | CO | Larimer | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8.1 | 0.9 | 9.3 | 9.3 | 0 | N |  |  | OP | X | 5 | 1951 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1954 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 518 | Flatiron | CO | Larimer | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 43 | 0.94 | 43 | 43 | 0 | N |  |  | OP | X | 1 | 1954 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1954 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 518 | Flatiron | CO | Larimer | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 43 | 0.94 | 43 | 43 | 0 | N |  |  | OP | X | 1 | 1954 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1954 | other | TRUE | 2518 | U S Bureau of Reclamation | 518 | Flatiron | CO | Larimer | 3 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 8.5 | 0.94 | 8.5 | 8.5 | 0 | N |  |  | OP | X | 5 | 1954 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1954 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 519 | Pole Hill | CO | Larimer | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 38.2 | 0.95 | 38.2 | 38.2 | 0 | N |  |  | OP | X | 1 | 1954 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1962 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 520 | Lower Molina | CO | Mesa | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.6 | 0.9 | 5.6 | 5.6 | 0 | N |  |  | OP | X | 12 | 1962 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1962 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 521 | Upper Molina | CO | Mesa | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9.9 | 0.9 | 9.9 | 9.9 | 0 | N |  |  | OP | X | 12 | 1962 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1965 | hard coal | TRUE | 15466 | Public Service Co of Colorado | 525 | Hayden | CO | Routt | 1 | Conventional Steam Coal | ST |  | J | X | X |  |  | 190 | 0.94 | 179 | 179 | 110 | N |  |  | OP | X | 7 | 1965 | 12 | 2028 | N | Electric Utility | 1 | X | BIT | NG | DFO |  |  |  | DFO |  |  |  | N | N |  | 12H | N | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1976 | hard coal | TRUE | 15466 | Public Service Co of Colorado | 525 | Hayden | CO | Routt | 2 | Conventional Steam Coal | ST |  | J | X | X |  |  | 275.4 | 0.9 | 262 | 262 | 120 | N |  |  | OP | X | 9 | 1976 | 12 | 2027 | N | Electric Utility | 1 | X | BIT | DFO |  |  |  |  | DFO |  |  |  | N | N |  | 12H | N | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1985 | hydro | TRUE | 16534 | Sacramento Municipal Util Dist | 531 | Camp Far West | CA | Placer | 1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 7.2 | 0.95 | 7.2 | 7.2 | 1 | N |  |  | OP | X | 2 | 1985 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1954 | natural gas combined cycle | TRUE | 189 | PowerSouth Energy Cooperative | 533 | McWilliams | AL | Covington | 1 | Natural Gas Fired Combined Cycle | CA | MCWM | S | Y | X |  |  | 7.5 | 0.8 | 9 | 9 | 2.5 | N |  |  | OP | X | 12 | 1954 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage1954 | natural gas combined cycle | TRUE | 189 | PowerSouth Energy Cooperative | 533 | McWilliams | AL | Covington | 2 | Natural Gas Fired Combined Cycle | CA | MCWM | S | Y | X |  |  | 7.5 | 0.8 | 9 | 9 | 2.5 | N |  |  | OP | X | 12 | 1954 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage1959 | natural gas combined cycle | TRUE | 189 | PowerSouth Energy Cooperative | 533 | McWilliams | AL | Covington | 3 | Natural Gas Fired Combined Cycle | CA | MCWM | S | Y | X |  |  | 25 | 0.85 | 22 | 22 | 5 | N |  |  | OP | X | 8 | 1959 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage1996 | natural gas combined cycle | TRUE | 189 | PowerSouth Energy Cooperative | 533 | McWilliams | AL | Covington | 4 | Natural Gas Fired Combined Cycle | CT | MCWM | S | X | Y |  |  | 107 | 0.85 | 109 | 116 | 6 | N |  |  | OP | X | 12 | 1996 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas combined cycle | TRUE | 189 | PowerSouth Energy Cooperative | 533 | McWilliams | AL | Covington | VAN1 | Natural Gas Fired Combined Cycle | CT | VANN | S | X | N |  |  | 165 | 0.85 | 171 | 205 | 90 | N |  |  | OP | X | 1 | 2002 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N |  | N
Vintage2002 | natural gas combined cycle | TRUE | 189 | PowerSouth Energy Cooperative | 533 | McWilliams | AL | Covington | VAN2 | Natural Gas Fired Combined Cycle | CT | VANN | S | X | N |  |  | 165 | 0.85 | 168 | 205 | 90 | N |  |  | OP | X | 1 | 2002 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N |  | N
Vintage2002 | natural gas combined cycle | TRUE | 189 | PowerSouth Energy Cooperative | 533 | McWilliams | AL | Covington | VAN3 | Natural Gas Fired Combined Cycle | CA | VANN | S | N | X |  |  | 177 | 0.9 | 176 | 185 | 60 | N |  |  | OP | X | 1 | 2002 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N |  | N
Vintage1985 | hydro | TRUE | 16534 | Sacramento Municipal Util Dist | 534 | Jones Fork | CA | El Dorado | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 0.95 | 10 | 10 | 1 | N |  |  | OP | X | 6 | 1985 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1986 | natural gas peaker | TRUE | 16534 | Sacramento Municipal Util Dist | 535 | McClellan (CA) | CA | Sacramento | 1 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 77 | 0.85 | 77 | 77 | 55 | N |  |  | OP | X | 3 | 1986 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1983 | hydro | TRUE | 5571 | East Bay Municipal Util Dist | 537 | Camanche | CA | San Joaquin | 1 | Conventional Hydroelectric | HY |  | S | X | X | Camche_1_PL1X3 |  | 3.6 | 0.95 | 3.5 | 3.5 | 0.8 | N |  |  | OP | X | 7 | 1983 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1983 | hydro | TRUE | 5571 | East Bay Municipal Util Dist | 537 | Camanche | CA | San Joaquin | 2 | Conventional Hydroelectric | HY |  | S | X | X | Camche_1_PL1X3 |  | 3.6 | 0.95 | 3.5 | 3.5 | 0.8 | N |  |  | OP | X | 7 | 1983 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1983 | hydro | TRUE | 5571 | East Bay Municipal Util Dist | 537 | Camanche | CA | San Joaquin | 3 | Conventional Hydroelectric | HY |  | S | X | X | Camche_1_PL1X3 |  | 3.6 | 0.95 | 3.5 | 3.5 | 0.8 | N |  |  | OP | X | 8 | 1983 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1929 | other | TRUE | 54895 | FirstLight Power Resources Services LLC | 539 | Rocky River (CT) | CT | Litchfield | 1 | Hydroelectric Pumped Storage | PS |  | W | X | X |  |  | 3.5 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 1 | 1929 |  |  | N | IPP Non-CHP | 2 | X | WAT | [12 empty] | 1H
Vintage1928 | other | TRUE | 54895 | FirstLight Power Resources Services LLC | 539 | Rocky River (CT) | CT | Litchfield | 2 | Hydroelectric Pumped Storage | PS |  | W | X | X |  |  | 3.5 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 1 | 1928 |  |  | N | IPP Non-CHP | 2 | X | WAT | [12 empty] | 1H
Vintage1928 | other | TRUE | 54895 | FirstLight Power Resources Services LLC | 539 | Rocky River (CT) | CT | Litchfield | 3 | Hydroelectric Pumped Storage | PS |  | W | X | X |  |  | 24 | 0.8 | 25.4 | 25 | 23 | N |  |  | OP | X | 1 | 1928 |  |  | N | IPP Non-CHP | 2 | X | WAT | [12 empty] | 1H
Vintage1967 | other | TRUE | 22379 | Connecticut Jet Power LLC | 540 | Branford | CT | New Haven | UN10 | Petroleum Liquids | GT |  | S | X | X |  |  | 21.8 | 0.85 | 17.4 | 22.5 | 17.4 | N |  |  | OP | X | 11 | 1967 |  |  | N | IPP Non-CHP | 2 | X | KER | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1903 | hydro | TRUE | 54895 | FirstLight Power Resources Services LLC | 541 | Bulls Bridge | CT | Litchfield | 1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.2 | 0.8 | 1.4 | 1.4 | 0.3 | N |  |  | OP | X | 1 | 1903 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 1H
Vintage1903 | hydro | TRUE | 54895 | FirstLight Power Resources Services LLC | 541 | Bulls Bridge | CT | Litchfield | 2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.2 | 0.8 | 1.4 | 1.4 | 0.3 | N |  |  | OP | X | 1 | 1903 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 1H
Vintage1903 | hydro | TRUE | 54895 | FirstLight Power Resources Services LLC | 541 | Bulls Bridge | CT | Litchfield | 3 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.2 | 0.8 | 1.4 | 1.4 | 0.3 | N |  |  | OP | X | 1 | 1903 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 1H
Vintage1903 | hydro | TRUE | 54895 | FirstLight Power Resources Services LLC | 541 | Bulls Bridge | CT | Litchfield | 4 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.2 | 0.8 | 1.4 | 1.4 | 0.3 | N |  |  | OP | X | 1 | 1903 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 1H
Vintage1903 | hydro | TRUE | 54895 | FirstLight Power Resources Services LLC | 541 | Bulls Bridge | CT | Litchfield | 5 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.2 | 0.8 | 1.4 | 1.4 | 0.3 | N |  |  | OP | X | 1 | 1903 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 1H
Vintage1903 | hydro | TRUE | 54895 | FirstLight Power Resources Services LLC | 541 | Bulls Bridge | CT | Litchfield | 6 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.2 | 0.8 | 1.4 | 1.4 | 0.3 | N |  |  | OP | X | 1 | 1903 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 1H
Vintage1969 | other | TRUE | 22379 | Connecticut Jet Power LLC | 542 | Cos Cob | CT | Fairfield | UN10 | Petroleum Liquids | GT |  | S | X | X |  |  | 25 | 0.85 | 19.1 | 24 | 19.1 | N |  |  | OP | X | 9 | 1969 |  |  | N | IPP Non-CHP | 2 | X | KER | [10 empty] | N |  | 10M | [23 empty] | N | N | N
Vintage1969 | other | TRUE | 22379 | Connecticut Jet Power LLC | 542 | Cos Cob | CT | Fairfield | UN11 | Petroleum Liquids | GT |  | S | X | X |  |  | 25 | 0.85 | 18.7 | 23.6 | 18.7 | N |  |  | OP | X | 9 | 1969 |  |  | N | IPP Non-CHP | 2 | X | KER | [10 empty] | N |  | 10M | [23 empty] | N | N | N
Vintage1969 | other | TRUE | 22379 | Connecticut Jet Power LLC | 542 | Cos Cob | CT | Fairfield | UN12 | Petroleum Liquids | GT |  | S | X | X |  |  | 25 | 0.85 | 19.1 | 24 | 19.1 | N |  |  | OP | X | 10 | 1969 |  |  | N | IPP Non-CHP | 2 | X | KER | [10 empty] | N |  | 10M | [23 empty] | N | N | N
Vintage2008 | other | TRUE | 22379 | Connecticut Jet Power LLC | 542 | Cos Cob | CT | Fairfield | UN13 | Petroleum Liquids | GT |  | S | X | X |  |  | 20 | 0.85 | 19.1 | 24 | 19.1 | N |  |  | OP | X | 6 | 2008 |  |  | N | IPP Non-CHP | 2 | X | KER | [10 empty] | N |  | 10M | [23 empty] | N | N | N
Vintage2008 | other | TRUE | 22379 | Connecticut Jet Power LLC | 542 | Cos Cob | CT | Fairfield | un14 | Petroleum Liquids | GT |  | S | X | X |  |  | 20 | 0.85 | 19.6 | 23.5 | 19.6 | N |  |  | OP | X | 6 | 2008 |  |  | N | IPP Non-CHP | 2 | X | KER | [10 empty] | N |  | 10M | [23 empty] | N | N | N
Vintage1985 | other | TRUE | 22350 | Devon Power LLC | 544 | Devon Station | CT | New Haven | 10 | Petroleum Liquids | GT |  | S | X | X | UN.DEVON 13.8DV10 | UN.DEVON 13.8DV10 | 18.6 | 0.85 | 14.4 | 19.2 | 14.4 | N |  |  | OP | X | 1 | 1985 |  |  | N | IPP Non-CHP | 2 | X | KER | DFO | JF | [7 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1996 | other | TRUE | 22350 | Devon Power LLC | 544 | Devon Station | CT | New Haven | 11 | Petroleum Liquids | GT |  | S | X | X | UN.DEVON 13.2DV11 | UN.DEVON 13.2DV11 | 51 | 0.85 | 29.3 | 38.8 | 16 | N |  |  | OP | X | 7 | 1996 |  |  | N | IPP Non-CHP | 2 | X | KER | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1996 | other | TRUE | 22350 | Devon Power LLC | 544 | Devon Station | CT | New Haven | 12 | Petroleum Liquids | GT |  | S | X | X | UN.DEVON 13.2DV12 | UN.DEVON 13.2DV12 | 51 | 0.85 | 29.2 | 38.4 | 16 | N |  |  | OP | X | 7 | 1996 |  |  | N | IPP Non-CHP | 2 | X | KER | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1996 | other | TRUE | 22350 | Devon Power LLC | 544 | Devon Station | CT | New Haven | 13 | Petroleum Liquids | GT |  | S | X | X | UN.DEVON 13.2DV13 | UN.DEVON 13.2DV13 | 51 | 0.85 | 29.9 | 38.9 | 16 | N |  |  | OP | X | 7 | 1996 |  |  | N | IPP Non-CHP | 2 | X | KER | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1996 | other | TRUE | 22350 | Devon Power LLC | 544 | Devon Station | CT | New Haven | 14 | Petroleum Liquids | GT |  | S | X | X | UN.DEVON 13.2DV14 | UN.DEVON 13.2DV14 | 51 | 0.85 | 29.7 | 40.3 | 16 | N |  |  | OP | X | 7 | 1996 |  |  | N | IPP Non-CHP | 2 | X | KER | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1967 | petroleum | TRUE | 22380 | NRG Montville Operations Inc | 546 | Montville Station | CT | New London | 10 | Petroleum Liquids | IC |  | S | X | X | UN.MONTVLLE69 MO10 | UN.MONTVLLE69 MO10 | 2.7 | 0.8 | 2.7 | 2.7 | 1 | N |  |  | SB | Y | 1 | 1967 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1967 | petroleum | TRUE | 22380 | NRG Montville Operations Inc | 546 | Montville Station | CT | New London | 11 | Petroleum Liquids | IC |  | S | X | X | UN.MONTVLLE69 MO10 | UN.MONTVLLE69 MO10 | 2.7 | 0.8 | 2.7 | 2.7 | 1 | N |  |  | SB | Y | 1 | 1967 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1954 | natural gas steam turbine | TRUE | 22380 | NRG Montville Operations Inc | 546 | Montville Station | CT | New London | 5 | Natural Gas Steam Turbine | ST |  | S | X | X | UN.MONTVLLE13.8MON5 | UN.MONTVLLE13.8MON5 | 75 | 0.8 | 81 | 83 | 40 | N |  |  | OP | X | 1 | 1954 |  |  | N | IPP Non-CHP | 2 | X | NG | RFO |  |  |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1971 | petroleum | TRUE | 22380 | NRG Montville Operations Inc | 546 | Montville Station | CT | New London | 6 | Petroleum Liquids | ST |  | S | X | X | UN.MONTVLLE22.0MON6 | UN.MONTVLLE22.0MON6 | 414.9 | 0.9 | 410 | 410 | 125 | N |  |  | OP | X | 1 | 1971 |  |  | N | IPP Non-CHP | 2 | X | RFO | [5 empty] | DFO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1973 | other | TRUE | 58185 | FirstLight Power Resources, Inc. - MA | 547 | Northfield Mountain | MA | Franklin | 1 | Hydroelectric Pumped Storage | PS |  | S | X | X | NFD1 | NFD1 | 292 | 0.95 | 292 | 292 | 125 | N |  |  | OP | X | 2 | 1973 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1973 | other | TRUE | 58185 | FirstLight Power Resources, Inc. - MA | 547 | Northfield Mountain | MA | Franklin | 2 | Hydroelectric Pumped Storage | PS |  | S | X | X | NFD2 | NFD2 | 292 | 0.95 | 292 | 292 | 125 | N |  |  | OP | X | 10 | 1973 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1973 | other | TRUE | 58185 | FirstLight Power Resources, Inc. - MA | 547 | Northfield Mountain | MA | Franklin | 3 | Hydroelectric Pumped Storage | PS |  | S | X | X | NFD3 | NFD3 | 292 | 0.95 | 292 | 292 | 125 | N |  |  | OP | X | 7 | 1973 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1972 | other | TRUE | 58185 | FirstLight Power Resources, Inc. - MA | 547 | Northfield Mountain | MA | Franklin | 4 | Hydroelectric Pumped Storage | PS |  | S | X | X | NFD4 | NFD4 | 292 | 0.95 | 292 | 292 | 125 | N |  |  | OP | X | 11 | 1972 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1983 | biomass | TRUE | 20169 | Avista Corp | 550 | Kettle Falls Generating Station | WA | Stevens | 1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 50.7 | 0.95 | 50 | 50.7 | 12 | N |  |  | OP | X | 12 | 1983 |  |  | N | Electric Utility | 1 | X | WDS | NG |  |  |  |  | NG |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | Y | Y | N
Vintage2002 | natural gas peaker | TRUE | 20169 | Avista Corp | 550 | Kettle Falls Generating Station | WA | Stevens | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 7.2 | 0.8 | 6.2 | 8 | 1 | N |  |  | OP | X | 5 | 2002 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1937 | hydro | TRUE | 54895 | FirstLight Power Resources Services LLC | 551 | Scotland Dam | CT | Windham | 1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 2 | 0.8 | 1.7 | 2.2 | 0.2 | N |  |  | OP | X | 1 | 1937 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 1H
Vintage1955 | hydro | TRUE | 54895 | FirstLight Power Resources Services LLC | 552 | Shepaug | CT | New Haven | 1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 37.2 | 0.85 | 41.5 | 42.6 | 35 | N |  |  | OP | X | 1 | 1955 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1919 | hydro | TRUE | 54895 | FirstLight Power Resources Services LLC | 553 | Stevenson | CT | Fairfield | 1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 7.5 | 0.9 | 7.1 | 7.1 | 0.8 | N |  |  | OP | X | 1 | 1919 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1919 | hydro | TRUE | 54895 | FirstLight Power Resources Services LLC | 553 | Stevenson | CT | Fairfield | 2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 7.5 | 0.9 | 7.1 | 7.1 | 0.8 | N |  |  | OP | X | 1 | 1919 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1919 | hydro | TRUE | 54895 | FirstLight Power Resources Services LLC | 553 | Stevenson | CT | Fairfield | 3 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 7.5 | 0.9 | 7.1 | 7.1 | 0.8 | N |  |  | OP | X | 1 | 1919 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1936 | hydro | TRUE | 54895 | FirstLight Power Resources Services LLC | 553 | Stevenson | CT | Fairfield | 4 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 8 | 0.8 | 7.6 | 7.6 | 0.8 | N |  |  | OP | X | 1 | 1936 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1926 | hydro | TRUE | 54895 | FirstLight Power Resources Services LLC | 554 | Taftville | CT | New London | 1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 1 | 1926 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 1H
Vintage1906 | hydro | TRUE | 54895 | FirstLight Power Resources Services LLC | 554 | Taftville | CT | New London | 2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.3 | 0.8 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 1 | 1906 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 1H
Vintage1906 | hydro | TRUE | 54895 | FirstLight Power Resources Services LLC | 554 | Taftville | CT | New London | 3 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.3 | 0.8 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 1 | 1906 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 1H
Vintage1949 | hydro | TRUE | 54895 | FirstLight Power Resources Services LLC | 554 | Taftville | CT | New London | 4 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.3 | 0.8 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 1 | 1949 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 1H
Vintage1949 | hydro | TRUE | 54895 | FirstLight Power Resources Services LLC | 554 | Taftville | CT | New London | 5 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.3 | 0.8 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 1 | 1949 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 1H
Vintage1919 | hydro | TRUE | 54895 | FirstLight Power Resources Services LLC | 557 | Tunnel | CT | New London | 1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1 | 0.85 | 0.8 | 1.1 | 0.3 | N |  |  | OP | X | 1 | 1919 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1969 | petroleum | TRUE | 54895 | FirstLight Power Resources Services LLC | 557 | Tunnel | CT | New London | 10 | Petroleum Liquids | GT |  | W | X | X |  |  | 18.5 | 0.85 | 16.5 | 21.8 | 5 | N |  |  | SB | Y | 1 | 1969 |  |  | N | IPP Non-CHP | 2 | X | JF | [12 empty] | 1H | [23 empty] | N | N | N
Vintage1949 | hydro | TRUE | 54895 | FirstLight Power Resources Services LLC | 557 | Tunnel | CT | New London | 2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1 | 0.85 | 0.8 | 1.1 | 0.3 | N |  |  | OP | X | 1 | 1949 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1925 | hydro | TRUE | 6207 | Farmington River Power Company | 559 | Rainbow (CT) | CT | Hartford | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4 | 1 | 4 | 4 | 4 | N |  |  | OP | X | 12 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M | [23 empty] | N
Vintage1925 | hydro | TRUE | 6207 | Farmington River Power Company | 559 | Rainbow (CT) | CT | Hartford | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4 | 1 | 4 | 4 | 4 | N |  |  | OP | X | 12 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M | [23 empty] | N
Vintage1914 | hydro | TRUE | 54895 | FirstLight Power Resources Services LLC | 560 | Falls Village | CT | Litchfield | 1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 3 | 0.8 | 3.3 | 3.7 | 0.3 | N |  |  | OP | X | 1 | 1914 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 1H
Vintage1914 | hydro | TRUE | 54895 | FirstLight Power Resources Services LLC | 560 | Falls Village | CT | Litchfield | 2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 3 | 0.8 | 3.3 | 3.7 | 0.3 | N |  |  | OP | X | 1 | 1914 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 1H
Vintage1914 | hydro | TRUE | 54895 | FirstLight Power Resources Services LLC | 560 | Falls Village | CT | Litchfield | 3 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 3 | 0.8 | 3.3 | 3.7 | 0.3 | N |  |  | OP | X | 1 | 1914 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 1H
Vintage1968 | other | TRUE | 22379 | Connecticut Jet Power LLC | 561 | Franklin Drive | CT | Litchfield | UN19 | Petroleum Liquids | GT |  | S | X | X |  |  | 21.8 | 0.85 | 16.1 | 21.2 | 16.1 | N |  |  | OP | X | 11 | 1968 |  |  | N | IPP Non-CHP | 2 | X | KER | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1966 | other | TRUE | 12490 | Middletown Power LLC | 562 | Middletown | CT | Middlesex | 10 | Petroleum Liquids | GT |  | S | X | X | un.middletn115 mi10 | un.middletn115 mi10 | 18.5 | 0.85 | 17.2 | 22.1 | 5 | N |  |  | OP | X | 8 | 1966 |  |  | N | IPP Non-CHP | 2 | X | KER | [9 empty] | N | N |  | 10M | [23 empty] | N | N
Vintage1958 | natural gas steam turbine | TRUE | 12490 | Middletown Power LLC | 562 | Middletown | CT | Middlesex | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | un.middletn13.2 mid2 | un.middletn13.2 mid2 | 113.6 | 0.85 | 117 | 120 | 45 | N |  |  | OP | X | 10 | 1958 |  |  | N | IPP Non-CHP | 2 | X | NG | RFO |  |  |  |  | DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1964 | natural gas steam turbine | TRUE | 12490 | Middletown Power LLC | 562 | Middletown | CT | Middlesex | 3 | Natural Gas Steam Turbine | ST |  | S | X | X | un.middletn20.9 mid3 | un.middletn20.9 mid3 | 239.4 | 0.85 | 236 | 245 | 100 | N |  |  | OP | X | 1 | 1964 |  |  | N | IPP Non-CHP | 2 | X | NG | RFO |  |  |  |  | DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1973 | petroleum | TRUE | 12490 | Middletown Power LLC | 562 | Middletown | CT | Middlesex | 4 | Petroleum Liquids | ST |  | S | X | X | un.laurel 22 mid4 | un.laurel 22 mid4 | 414.9 | 0.9 | 400 | 402 | 125 | N |  |  | OP | X | 5 | 1973 |  |  | N | IPP Non-CHP | 2 | X | RFO | [5 empty] | DFO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1970 | other | TRUE | 4426 | NAES Corp | 563 | South Meadow | CT | Hartford | 11 | Petroleum Liquids | GT |  | W | X | X | SO11 |  | 41.8 | 0.8 | 35.7 | 46.9 | 10 | N |  |  | SB | Y | 8 | 1970 | 6 | 2023 | N | IPP Non-CHP | 2 | X | KER | [12 empty] | 10M | [23 empty] | N | N | N
Vintage1970 | other | TRUE | 4426 | NAES Corp | 563 | South Meadow | CT | Hartford | 12 | Petroleum Liquids | GT |  | W | X | X | SO12 |  | 41.8 | 0.9 | 37.7 | 47.8 | 10 | N |  |  | SB | Y | 8 | 1970 | 6 | 2023 | N | IPP Non-CHP | 2 | X | KER | [12 empty] | 10M | [23 empty] | N | N | N
Vintage1970 | other | TRUE | 4426 | NAES Corp | 563 | South Meadow | CT | Hartford | 13 | Petroleum Liquids | GT |  | W | X | X | SO13 |  | 41.8 | 0.9 | 38.3 | 47.9 | 10 | N |  |  | SB | Y | 8 | 1970 | 6 | 2023 | N | IPP Non-CHP | 2 | X | KER | [12 empty] | 10M | [23 empty] | N | N | N
Vintage1970 | other | TRUE | 4426 | NAES Corp | 563 | South Meadow | CT | Hartford | 14 | Petroleum Liquids | GT |  | W | X | X | SO14 |  | 41.8 | 0.9 | 36.7 | 46.3 | 10 | N |  |  | SB | Y | 8 | 1970 | 6 | 2023 | N | IPP Non-CHP | 2 | X | KER | [12 empty] | 10M | [23 empty] | N | N | N
Vintage1987 | hard coal | TRUE | 14610 | Orlando Utilities Comm | 564 | Stanton Energy Center | FL | Orange | 1 | Conventional Steam Coal | ST |  | J | X | X |  |  | 464.5 | 0.9 | 455 | 455 | 90 | N |  |  | OP | X | 7 | 1987 | 12 | 2025 | N | Electric Utility | 1 | X | BIT | NG | LFG |  |  |  | NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1996 | hard coal | TRUE | 14610 | Orlando Utilities Comm | 564 | Stanton Energy Center | FL | Orange | 2 | Conventional Steam Coal | ST |  | J | X | X |  |  | 464.5 | 0.9 | 467 | 467 | 95 | N |  |  | OP | X | 6 | 1996 |  |  | N | Electric Utility | 1 | X | BIT | NG | LFG |  |  |  | NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage2010 | natural gas combined cycle | TRUE | 14610 | Orlando Utilities Comm | 564 | Stanton Energy Center | FL | Orange | B | Natural Gas Fired Combined Cycle | CA | OUC | S | Y | X |  |  | 129.8 | 0.85 | 128 | 130 |  | N |  |  | OP | X | 2 | 2010 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 12H | [5 empty] | N | [17 empty] | Y | N | Y
Vintage2010 | natural gas combined cycle | TRUE | 14610 | Orlando Utilities Comm | 564 | Stanton Energy Center | FL | Orange | B1 | Natural Gas Fired Combined Cycle | CT | OUC | S | X | N |  |  | 203.2 | 0.85 | 167 | 170 | 155 | N |  |  | OP | X | 2 | 2010 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1967 | other | TRUE | 22379 | Connecticut Jet Power LLC | 565 | Torrington Terminal | CT | Litchfield | UN10 | Petroleum Liquids | GT |  | S | X | X |  |  | 21.8 | 0.85 | 17.4 | 22.5 | 17.4 | N |  |  | OP | X | 11 | 1967 |  |  | N | IPP Non-CHP | 2 | X | KER | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1975 | nuclear | TRUE | 5221 | Dominion Energy Nuclear Conn Inc | 566 | Millstone | CT | New London | 2 | Nuclear | ST |  | S | X | X | UN.MILSTONE24.0MIL2 | UN.MILSTONE24.0MIL2 | 909.9 | 0.9 | 872.3 | 869.8 | 50 | N |  |  | OP | X | 12 | 1975 |  |  | N | IPP Non-CHP | 2 | X | NUC | [5 empty] | NUC |  |  |  | N | N |  | OVER | [23 empty] | N
Vintage1986 | nuclear | TRUE | 5221 | Dominion Energy Nuclear Conn Inc | 566 | Millstone | CT | New London | 3 | Nuclear | ST |  | J | X | X | UN.MILSTONE24.0MIL3 | UN.MILSTONE24.0MIL3 | 1253 | 0.93 | 1225 | 1234.3 | 65 | N |  |  | OP | X | 4 | 1986 |  |  | N | IPP Non-CHP | 2 | X | NUC | [5 empty] | NUC |  |  |  | N | N |  | OVER | [7 empty] | 21 | 21 | 5 | 2022 | [12 empty] | N
Vintage2019 | natural gas combined cycle | TRUE | 15452 | PSEG Power Connecticut LLC | 568 | Bridgeport Station | CT | Fairfield | 501 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 375.7 | 0.85 | 342 | 364 | 155 | N |  |  | OP | X | 6 | 2019 |  |  | N | IPP Non-CHP | 2 | X | NG | [10 empty] | N |  | 1H | [23 empty] | N |  | N
Vintage2019 | natural gas combined cycle | TRUE | 15452 | PSEG Power Connecticut LLC | 568 | Bridgeport Station | CT | Fairfield | 502 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 200.6 | 0.85 | 154.6 | 150.8 | 82 | N |  |  | OP | X | 6 | 2019 |  |  | N | IPP Non-CHP | 2 | X | NG | [10 empty] | N |  | 12H | [23 empty] | N | N | N
Vintage1986 | hydro | TRUE | 3249 | Central Hudson Gas & Elec Corp | 579 | Central Hudson High Falls | NY | Ulster | 1 | Conventional Hydroelectric | HY |  | S | X | X | 23754 | 23754 | 3.2 | 0.89 | 3.2 | 3.2 | 0.2 | N |  |  | OP | X | 12 | 1986 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1972 | petroleum | TRUE | 13831 | City of Norwich - (CT) | 581 | North Main Street | CT | New London | 5 | Petroleum Liquids | GT |  | S | X | X | UN.TUNNEL 69 NORJ | UN.TUNNEL 69 NORJ | 19 | 0.9 | 15.3 | 18.8 | 2 | N |  |  | OP | X | 8 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H |  |  |  | N | [19 empty] | N | N
Vintage1967 | hydro | TRUE | 13831 | City of Norwich - (CT) | 583 | Tenth Street | CT | New London | 1 | Conventional Hydroelectric | HY |  | S | X | X | UN.TUNNEL 69 NORJ | UN.TUNNEL 69 NORJ | 1.4 | 0.9 | 1 | 1.2 | 0.1 | N |  |  | OP | X | 5 | 1967 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1989 | hydro | TRUE | 6204 | City of Farmington - (NM) | 584 | Navajo Dam | NM | San Juan | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.9 | 15 | 15 | 6 | N |  |  | OP | X | 1 | 1989 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 12H
Vintage1989 | hydro | TRUE | 6204 | City of Farmington - (NM) | 584 | Navajo Dam | NM | San Juan | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.9 | 15 | 15 | 6 | N |  |  | OP | X | 1 | 1989 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 12H
Vintage1984 | hydro | TRUE | 9216 | Imperial Irrigation District | 585 | Drop 1 | CA | Imperial | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.9 | 0.8 | 1.3 | 1.5 | 0.2 | N |  |  | OP | X | 11 | 1984 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1984 | hydro | TRUE | 9216 | Imperial Irrigation District | 585 | Drop 1 | CA | Imperial | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.9 | 0.8 | 1.2 | 1.1 | 0.2 | N |  |  | OP | X | 11 | 1984 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1984 | hydro | TRUE | 9216 | Imperial Irrigation District | 585 | Drop 1 | CA | Imperial | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.9 | 0.8 | 1.3 | 1.1 | 0.2 | N |  |  | OP | X | 10 | 1984 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1984 | hydro | TRUE | 9216 | Imperial Irrigation District | 586 | East Highline | CA | Imperial | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 1 | 0.8 | 0.3 | N |  |  | OP | X | 9 | 1984 |  |  | N | Electric Utility | 1 | X | WAT | [10 empty] | N |  | 1H | [23 empty] | N
Vintage1984 | biomass | TRUE | 2548 | City of Burlington Electric - (VT) | 589 | J C McNeil | VT | Chittenden | 1 | Wood/Wood Waste Biomass | ST |  | J | X | X | 474 | 474 | 59.5 | 0.9 | 52 | 54 | 15 | N |  |  | OP | X | 6 | 1984 |  |  | N | Electric Utility | 1 | X | WDS | NG | DFO |  |  |  | DFO | NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1973 | petroleum | TRUE | 56609 | Calpine Mid-Atlantic Generation LLC | 591 | Christiana | DE | New Castle | CH11 | Petroleum Liquids | GT |  | S | X | X | 510440 | 510440 | 26 | 0.8 | 25 | 25 | 20 | N |  |  | SB | Y | 6 | 1973 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 1H |  |  |  |  | N | [18 empty] | N
Vintage1973 | petroleum | TRUE | 56609 | Calpine Mid-Atlantic Generation LLC | 591 | Christiana | DE | New Castle | CH14 | Petroleum Liquids | GT |  | S | X | X | 510441 | 510441 | 26 | 0.8 | 25 | 25 | 20 | N |  |  | SB | Y | 6 | 1973 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 1H |  |  |  |  | N | [18 empty] | N
Vintage1968 | petroleum | TRUE | 56609 | Calpine Mid-Atlantic Generation LLC | 592 | Delaware City 10 | DE | New Castle | DC10 | Petroleum Liquids | GT |  | S | X | X | 50524 | 50524 | 18.5 | 0.85 | 18 | 18 | 15 | N |  |  | SB | Y | 4 | 1968 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1963 | petroleum | TRUE | 56609 | Calpine Mid-Atlantic Generation LLC | 593 | Edge Moor | DE | New Castle | 10 | Petroleum Liquids | GT |  | S | X | X | 50887 | 50887 | 12.5 | 0.85 | 15 | 15 | 12.5 | N |  |  | SB | Y | 6 | 1963 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1954 | natural gas steam turbine | TRUE | 56609 | Calpine Mid-Atlantic Generation LLC | 593 | Edge Moor | DE | New Castle | 3 | Natural Gas Steam Turbine | ST |  | S | X | X | 50888 | 50888 | 75 | 0.85 | 86 | 86 | 25 | N |  |  | OP | X | 12 | 1954 |  |  | N | IPP Non-CHP | 2 | X | NG | RFO | DFO |  |  |  | NG | DFO |  |  | N | N |  | OVER |  | N |  |  | N | [18 empty] | Y | Y | Y
Vintage1966 | natural gas steam turbine | TRUE | 56609 | Calpine Mid-Atlantic Generation LLC | 593 | Edge Moor | DE | New Castle | 4 | Natural Gas Steam Turbine | ST |  | S | X | X | 50893 | 50893 | 176.8 | 0.85 | 174 | 174 | 50 | N |  |  | OP | X | 4 | 1966 |  |  | N | IPP Non-CHP | 2 | X | NG | RFO | DFO |  |  |  | NG | DFO |  |  | N | N |  | OVER |  | N |  |  | N | [18 empty] | Y | Y | Y
Vintage1973 | natural gas steam turbine | TRUE | 56609 | Calpine Mid-Atlantic Generation LLC | 593 | Edge Moor | DE | New Castle | 5 | Natural Gas Steam Turbine | ST |  | S | X | X | 50894 | 50894 | 446 | 0.9 | 450 | 450 | 65 | N |  |  | OP | X | 8 | 1973 |  |  | N | IPP Non-CHP | 2 | X | NG | RFO | DFO |  |  |  | NG | DFO |  |  | N |  |  | OVER | [23 empty] | Y | Y | Y
Vintage1967 | petroleum | TRUE | 9332 | Indian River Operations Inc | 594 | Indian River Generating Station | DE | Sussex | 10 | Petroleum Liquids | GT |  | W | X | X |  |  | 18.6 | 0.85 | 16.1 | 16.1 | 14 | N |  |  | OP | X | 6 | 1967 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1980 | hard coal | TRUE | 9332 | Indian River Operations Inc | 594 | Indian River Generating Station | DE | Sussex | 4 | Conventional Steam Coal | ST |  | W | X | X |  |  | 445.5 | 0.9 | 410 | 410 | 190 | N |  |  | OP | X | 10 | 1980 | 12 | 2026 | N | IPP Non-CHP | 2 | X | BIT | DFO |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | N |  |  | N | N | N
Vintage1964 | petroleum | TRUE | 56609 | Calpine Mid-Atlantic Generation LLC | 597 | West Station (DE) | DE | New Castle | WEST | Petroleum Liquids | GT |  | S | X | X | 50871 | 50871 | 20 | 0.85 | 15 | 19 | 15 | N |  |  | SB | Y | 6 | 1964 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1984 | hard coal | TRUE | 60421 | Brandon Shores LLC | 602 | Brandon Shores | MD | Anne Arundel | 1 | Conventional Steam Coal | ST |  | S | X | X | 50659 | 50659 | 685.1 | 0.9 | 635 | 635 | 220 | N |  |  | OP | X | 5 | 1984 |  |  | N | IPP Non-CHP | 2 | X | BIT | [5 empty] | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | N |  |  | N | N | N
Vintage1991 | hard coal | TRUE | 60421 | Brandon Shores LLC | 602 | Brandon Shores | MD | Anne Arundel | 2 | Conventional Steam Coal | ST |  | S | X | X | 50660 | 50660 | 685.1 | 0.9 | 638 | 638 | 220 | N |  |  | OP | X | 5 | 1991 |  |  | N | IPP Non-CHP | 2 | X | BIT | [5 empty] | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | N |  |  | N | N | N
Vintage1984 | natural gas peaker | TRUE | 15500 | Puget Sound Energy Inc | 607 | Fredonia | WA | Skagit | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 129.1 | 0.9 | 93 | 114 | 40 | N |  |  | SB | Y | 5 | 1984 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1984 | natural gas peaker | TRUE | 15500 | Puget Sound Energy Inc | 607 | Fredonia | WA | Skagit | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 129.1 | 0.9 | 93 | 114 | 40 | N |  |  | SB | Y | 5 | 1984 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 15500 | Puget Sound Energy Inc | 607 | Fredonia | WA | Skagit | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 58.9 | 0.9 | 47 | 60 | 20 | N |  |  | SB | Y | 7 | 2001 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 15500 | Puget Sound Energy Inc | 607 | Fredonia | WA | Skagit | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 58.9 | 0.9 | 47 | 60 | 20 | N |  |  | SB | Y | 7 | 2001 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2013 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 609 | Cape Canaveral | FL | Brevard | 3A | Natural Gas Fired Combined Cycle | CT | PCC | S | X | N |  |  | 265 | 0.85 | 270.4 | 300.8 | 189 | N |  |  | OP | X | 4 | 2013 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage2013 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 609 | Cape Canaveral | FL | Brevard | 3B | Natural Gas Fired Combined Cycle | CT | PCC | S | X | N |  |  | 265 | 0.85 | 270.4 | 300.8 | 189 | N |  |  | OP | X | 4 | 2013 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage2013 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 609 | Cape Canaveral | FL | Brevard | 3C | Natural Gas Fired Combined Cycle | CT | PCC | S | X | N |  |  | 265 | 0.85 | 270.4 | 300.8 | 189 | N |  |  | OP | X | 4 | 2013 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage2013 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 609 | Cape Canaveral | FL | Brevard | 3ST | Natural Gas Fired Combined Cycle | CA | PCC | S | N | X |  |  | 500 | 0.85 | 478.8 | 490.6 | 189 | N |  |  | OP | X | 4 | 2013 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage2000 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 612 | Fort Myers | FL | Lee | 2A | Natural Gas Fired Combined Cycle | CT | F901 | S | X | Y |  |  | 188.2 | 0.85 | 199.5 | 207 | 90 | N |  |  | OP | X | 12 | 2000 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y |  | N
Vintage2000 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 612 | Fort Myers | FL | Lee | 2B | Natural Gas Fired Combined Cycle | CT | F901 | S | X | Y |  |  | 188.2 | 0.85 | 197.4 | 207 | 90 | N |  |  | OP | X | 12 | 2000 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y |  | N
Vintage2000 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 612 | Fort Myers | FL | Lee | 2C | Natural Gas Fired Combined Cycle | CT | F901 | S | X | Y |  |  | 188.2 | 0.85 | 197.4 | 207 | 90 | N |  |  | OP | X | 12 | 2000 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y |  | N
Vintage2001 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 612 | Fort Myers | FL | Lee | 2D | Natural Gas Fired Combined Cycle | CT | F901 | S | X | Y |  |  | 188.2 | 0.85 | 197.4 | 207 | 90 | N |  |  | OP | X | 4 | 2001 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y |  | N
Vintage2001 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 612 | Fort Myers | FL | Lee | 2E | Natural Gas Fired Combined Cycle | CT | F901 | S | X | Y |  |  | 188.2 | 0.85 | 197.4 | 207 | 90 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y |  | N
Vintage2001 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 612 | Fort Myers | FL | Lee | 2F | Natural Gas Fired Combined Cycle | CT | F901 | S | X | Y |  |  | 188.2 | 0.85 | 197.4 | 207 | 90 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y |  | N
Vintage1974 | petroleum | TRUE | 6452 | Florida Power & Light Co | 612 | Fort Myers | FL | Lee | 9 | Petroleum Liquids | GT |  | S | X | X |  |  | 62 | 0.9 | 54 | 61.5 | 5 | N |  |  | OP | X | 5 | 1974 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage2003 | natural gas peaker | TRUE | 6452 | Florida Power & Light Co | 612 | Fort Myers | FL | Lee | CT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 188.2 | 0.85 | 182 | 200 | 90 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage2003 | natural gas peaker | TRUE | 6452 | Florida Power & Light Co | 612 | Fort Myers | FL | Lee | CT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 188.2 | 0.85 | 182 | 200 | 90 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1974 | petroleum | TRUE | 6452 | Florida Power & Light Co | 612 | Fort Myers | FL | Lee | GT1 | Petroleum Liquids | GT |  | S | X | X |  |  | 62 | 0.9 | 54 | 61.5 | 5 | N |  |  | OP | X | 5 | 1974 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage2016 | natural gas peaker | TRUE | 6452 | Florida Power & Light Co | 612 | Fort Myers | FL | Lee | PFM3C | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 229.5 | 0.85 | 231 | 223 | 90 | N |  |  | OP | X | 12 | 2016 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2016 | natural gas peaker | TRUE | 6452 | Florida Power & Light Co | 612 | Fort Myers | FL | Lee | PFM3D | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 229.5 | 0.85 | 231 | 223 | 90 | N |  |  | OP | X | 12 | 2016 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1958 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 612 | Fort Myers | FL | Lee | ST1 | Natural Gas Fired Combined Cycle | CA | F901 | S | N | X |  |  | 156.2 | 0.85 | 155.8 | 141 | 27.8 | N |  |  | OP | X | 11 | 1958 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1969 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 612 | Fort Myers | FL | Lee | ST2 | Natural Gas Fired Combined Cycle | CA | F901 | S | N | X |  |  | 436.1 | 0.89 | 459.2 | 404 | 146.6 | N |  |  | OP | X | 7 | 1969 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1970 | natural gas peaker | TRUE | 6452 | Florida Power & Light Co | 613 | Lauderdale | FL | Broward | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 34.2 | 0.85 | 34.3 | 37.2 | 5 | N |  |  | OP | X | 8 | 1970 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 10M | [23 empty] | Y | N | Y
Vintage1970 | natural gas peaker | TRUE | 6452 | Florida Power & Light Co | 613 | Lauderdale | FL | Broward | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 34.2 | 0.8 | 34.3 | 37.2 | 5 | N |  |  | OP | X | 8 | 1970 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 10M | [23 empty] | Y | N | Y
Vintage2016 | natural gas peaker | TRUE | 6452 | Florida Power & Light Co | 613 | Lauderdale | FL | Broward | 6A | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 229.5 | 0.85 | 231 | 222 | 90 | N |  |  | OP | X | 12 | 2016 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2016 | natural gas peaker | TRUE | 6452 | Florida Power & Light Co | 613 | Lauderdale | FL | Broward | 6B | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 229.5 | 0.85 | 231 | 222 | 90 | N |  |  | OP | X | 12 | 2016 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2016 | natural gas peaker | TRUE | 6452 | Florida Power & Light Co | 613 | Lauderdale | FL | Broward | 6C | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 229.5 | 0.85 | 231 | 222 | 90 | N |  |  | OP | X | 12 | 2016 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2016 | natural gas peaker | TRUE | 6452 | Florida Power & Light Co | 613 | Lauderdale | FL | Broward | 6D | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 229.5 | 0.85 | 231 | 222 | 90 | N |  |  | OP | X | 12 | 2016 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2016 | natural gas peaker | TRUE | 6452 | Florida Power & Light Co | 613 | Lauderdale | FL | Broward | 6E | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 229.5 | 0.85 | 231 | 222 | 90 | N |  |  | OP | X | 12 | 2016 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2016 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 617 | Port Everglades | FL | Broward | 5A | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 296 | 0.85 | 271.9 | 297.1 | 100 | N |  |  | OP | X | 4 | 2016 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage2016 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 617 | Port Everglades | FL | Broward | 5B | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 296 | 0.85 | 271.9 | 297.1 | 100 | N |  |  | OP | X | 4 | 2016 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage2016 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 617 | Port Everglades | FL | Broward | 5C | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 296 | 0.85 | 271.9 | 297.1 | 100 | N |  |  | OP | X | 4 | 2016 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage2016 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 617 | Port Everglades | FL | Broward | 5ST | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X |  |  | 464 | 0.85 | 421.3 | 446.7 | 100 | N |  |  | OP | X | 4 | 2016 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage2014 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 619 | Riviera | FL | Palm Beach | 5A | Natural Gas Fired Combined Cycle | CT | PRV | S | X | N |  |  | 265 | 0.85 | 270.5 | 300.9 |  | N |  |  | OP | X | 4 | 2014 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage2014 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 619 | Riviera | FL | Palm Beach | 5B | Natural Gas Fired Combined Cycle | CT | PRV | S | X | N |  |  | 265 | 0.85 | 270.5 | 300.9 |  | N |  |  | OP | X | 4 | 2014 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage2014 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 619 | Riviera | FL | Palm Beach | 5C | Natural Gas Fired Combined Cycle | CT | PRV | S | X | N |  |  | 265 | 0.85 | 270.5 | 300.9 |  | N |  |  | OP | X | 4 | 2014 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage2014 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 619 | Riviera | FL | Palm Beach | 5ST | Natural Gas Fired Combined Cycle | CA | PRV | S | Y | X |  |  | 500 | 0.85 | 478.5 | 490.3 |  | N |  |  | OP | X | 4 | 2014 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage1969 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 620 | Sanford | FL | Volusia | 4 | Natural Gas Fired Combined Cycle | CA | G160 | S | N | X |  |  | 436.1 | 0.89 | 388 | 360 | 132.6 | N |  |  | OP | X | 7 | 1969 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 12H | [23 empty] | N
Vintage2002 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 620 | Sanford | FL | Volusia | 4A | Natural Gas Fired Combined Cycle | CT | G160 | S | X | N |  |  | 188.2 | 0.85 | 197 | 207 | 95 | N |  |  | OP | X | 12 | 2002 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 12H | [23 empty] | N |  | N
Vintage2002 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 620 | Sanford | FL | Volusia | 4B | Natural Gas Fired Combined Cycle | CT | G160 | S | X | N |  |  | 188.2 | 0.85 | 197 | 207 | 95 | N |  |  | OP | X | 12 | 2002 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 12H | [23 empty] | N |  | N
Vintage2002 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 620 | Sanford | FL | Volusia | 4C | Natural Gas Fired Combined Cycle | CT | G160 | S | X | N |  |  | 188.2 | 0.85 | 197 | 207 | 95 | N |  |  | OP | X | 12 | 2002 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 12H | [23 empty] | N |  | N
Vintage2003 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 620 | Sanford | FL | Volusia | 4D | Natural Gas Fired Combined Cycle | CT | G160 | S | X | N |  |  | 188.2 | 0.85 | 197 | 207 | 95 | N |  |  | OP | X | 1 | 2003 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 12H | [23 empty] | N |  | N
Vintage1974 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 620 | Sanford | FL | Volusia | 5 | Natural Gas Fired Combined Cycle | CA | G161 | S | N | X |  |  | 436.1 | 0.89 | 388 | 360 | 132.6 | N |  |  | OP | X | 5 | 1974 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 12H | [23 empty] | N |  | N
Vintage2002 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 620 | Sanford | FL | Volusia | 5A | Natural Gas Fired Combined Cycle | CT | G161 | S | X | N |  |  | 188.2 | 0.85 | 197 | 207 | 95 | N |  |  | OP | X | 5 | 2002 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 12H | [23 empty] | N |  | N
Vintage2002 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 620 | Sanford | FL | Volusia | 5B | Natural Gas Fired Combined Cycle | CT | G161 | S | X | N |  |  | 188.2 | 0.85 | 197 | 207 | 95 | N |  |  | OP | X | 5 | 2002 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 12H | [23 empty] | N |  | N
Vintage2002 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 620 | Sanford | FL | Volusia | 5C | Natural Gas Fired Combined Cycle | CT | G161 | S | X | N |  |  | 188.2 | 0.85 | 197 | 207 | 95 | N |  |  | OP | X | 5 | 2002 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 12H | [23 empty] | N |  | N
Vintage2002 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 620 | Sanford | FL | Volusia | 5D | Natural Gas Fired Combined Cycle | CT | G161 | S | X | N |  |  | 188.2 | 0.85 | 197 | 207 | 95 | N |  |  | OP | X | 5 | 2002 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 12H | [23 empty] | N |  | N
Vintage1972 | nuclear | TRUE | 6452 | Florida Power & Light Co | 621 | Turkey Point | FL | Miami Dade | 3 | Nuclear | ST |  | S | X | X |  |  | 877.2 | 0.9 | 837 | 859 | 420 | N |  |  | OP | X | 12 | 1972 |  |  | N | Electric Utility | 1 | X | NUC | [9 empty] | N |  |  | OVER | [23 empty] | N
Vintage1973 | nuclear | TRUE | 6452 | Florida Power & Light Co | 621 | Turkey Point | FL | Miami Dade | 4 | Nuclear | ST |  | S | X | X |  |  | 760 | 0.9 | 861 | 888 | 424 | N |  |  | OP | X | 9 | 1973 |  |  | N | Electric Utility | 1 | X | NUC | [9 empty] | N |  |  | OVER | [23 empty] | N
Vintage2007 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 621 | Turkey Point | FL | Miami Dade | 5CA | Natural Gas Fired Combined Cycle | CA | G901 | S | N | X |  |  | 472 | 0.85 | 466.2 | 460 |  | N |  |  | OP | X | 5 | 2007 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage2007 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 621 | Turkey Point | FL | Miami Dade | 5CTA | Natural Gas Fired Combined Cycle | CT | G901 | S | X | N |  |  | 188 | 0.85 | 197.8 | 207 | 90 | N |  |  | OP | X | 5 | 2007 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage2007 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 621 | Turkey Point | FL | Miami Dade | 5CTB | Natural Gas Fired Combined Cycle | CT | G901 | S | X | N |  |  | 188 | 0.85 | 196.7 | 207 | 90 | N |  |  | OP | X | 5 | 2007 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage2007 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 621 | Turkey Point | FL | Miami Dade | 5CTC | Natural Gas Fired Combined Cycle | CT | G901 | S | X | N |  |  | 188 | 0.85 | 196.7 | 207 | 90 | N |  |  | OP | X | 5 | 2007 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage2007 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 621 | Turkey Point | FL | Miami Dade | 5CTD | Natural Gas Fired Combined Cycle | CT | G901 | S | X | N |  |  | 188 | 0.85 | 196.7 | 207 | 90 | N |  |  | OP | X | 5 | 2007 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage1995 | hydro | TRUE | 16868 | City of Seattle - (WA) | 622 | South Fork Tolt | WA | King | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 16.8 | 0.9 | 16.8 | 16.8 | 0 | N |  |  | OP | X | 11 | 1995 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 12H | [23 empty] | N
Vintage1983 | hydro | TRUE | 13511 | New York State Elec & Gas Corp | 625 | Upper Mechanicville | NY | Saratoga | 1 | Conventional Hydroelectric | HY |  | S | X | X | 23645 | 23645 | 8.2 | 0.95 | 9.2 | 9.2 | 0 | N |  |  | OP | X | 9 | 1983 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1983 | hydro | TRUE | 13511 | New York State Elec & Gas Corp | 625 | Upper Mechanicville | NY | Saratoga | 2 | Conventional Hydroelectric | HY |  | S | X | X | 23645 | 23645 | 8.2 | 0.95 | 9.2 | 9.2 | 0 | N |  |  | OA | X | 9 | 1983 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1985 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 626 | Oak Flat | CA | Plumas | 1 | Conventional Hydroelectric | HY |  | S | X | X | BCKSCRK_7_N002 | BCKSCRK_7_N002 | 1.4 | 0.86 | 1.3 | 1.3 | 0 | N |  |  | OP | X | 11 | 1985 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1973 | petroleum | TRUE | 6455 | Duke Energy Florida, LLC | 627 | Bayboro | FL | Pinellas | P1 | Petroleum Liquids | GT |  | S | X | X |  |  | 56.7 | 0.9 | 44 | 58 | 30 | N |  |  | OP | X | 4 | 1973 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1973 | petroleum | TRUE | 6455 | Duke Energy Florida, LLC | 627 | Bayboro | FL | Pinellas | P2 | Petroleum Liquids | GT |  | S | X | X |  |  | 56.7 | 0.9 | 41 | 55 | 22 | N |  |  | OP | X | 4 | 1973 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1973 | petroleum | TRUE | 6455 | Duke Energy Florida, LLC | 627 | Bayboro | FL | Pinellas | P3 | Petroleum Liquids | GT |  | S | X | X |  |  | 56.7 | 0.9 | 43 | 57 | 30 | N |  |  | OP | X | 4 | 1973 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1973 | petroleum | TRUE | 6455 | Duke Energy Florida, LLC | 627 | Bayboro | FL | Pinellas | P4 | Petroleum Liquids | GT |  | S | X | X |  |  | 56.7 | 0.9 | 43 | 56 | 30 | N |  |  | OP | X | 4 | 1973 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage2018 | natural gas combined cycle | TRUE | 6455 | Duke Energy Florida, LLC | 628 | Crystal River | FL | Citrus | 1GTA | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 310.3 | 0.85 | 243 | 295 | 243 | N |  |  | OP | X | 10 | 2018 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 12H | [23 empty] | N | N | N
Vintage2018 | natural gas combined cycle | TRUE | 6455 | Duke Energy Florida, LLC | 628 | Crystal River | FL | Citrus | 1GTB | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 310.3 | 0.85 | 242 | 295 | 242 | N |  |  | OP | X | 10 | 2018 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 12H | [23 empty] | N | N | N
Vintage2018 | natural gas combined cycle | TRUE | 6455 | Duke Energy Florida, LLC | 628 | Crystal River | FL | Citrus | 2GTA | Natural Gas Fired Combined Cycle | CT | CC2 | S | X | N |  |  | 310.3 | 0.85 | 241 | 296 | 241 | N |  |  | OP | X | 11 | 2018 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 12H | [23 empty] | N | N | N
Vintage2018 | natural gas combined cycle | TRUE | 6455 | Duke Energy Florida, LLC | 628 | Crystal River | FL | Citrus | 2GTB | Natural Gas Fired Combined Cycle | CT | CC2 | S | X | N |  |  | 310.3 | 0.85 | 242 | 297 | 242 | N |  |  | OP | X | 11 | 2018 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 12H | [23 empty] | N | N | N
Vintage1984 | hard coal | TRUE | 6455 | Duke Energy Florida, LLC | 628 | Crystal River | FL | Citrus | 5 | Conventional Steam Coal | ST |  | S | X | X |  |  | 739.2 | 0.9 | 698 | 721 | 225 | N |  |  | OP | X | 10 | 1984 |  |  | N | Electric Utility | 1 | X | BIT | [5 empty] | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage2018 | natural gas combined cycle | TRUE | 6455 | Duke Energy Florida, LLC | 628 | Crystal River | FL | Citrus | CC1ST | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 364.7 | 0.85 | 322 | 335 | 322 | N |  |  | OP | X | 10 | 2018 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 12H | [23 empty] | N | N | N
Vintage2018 | natural gas combined cycle | TRUE | 6455 | Duke Energy Florida, LLC | 628 | Crystal River | FL | Citrus | CC2ST | Natural Gas Fired Combined Cycle | CA | CC2 | S | Y | X |  |  | 364.7 | 0.85 | 320 | 336 | 320 | N |  |  | OP | X | 11 | 2018 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 12H | [23 empty] | N | N | N
Vintage1982 | hard coal | TRUE | 6455 | Duke Energy Florida, LLC | 628 | Crystal River | FL | Citrus | ST4 | Conventional Steam Coal | ST |  | S | X | X |  |  | 739.2 | 0.9 | 712 | 721 | 225 | N |  |  | OP | X | 12 | 1982 |  |  | N | Electric Utility | 1 | X | BIT | [5 empty] | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1986 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 632 | Newcastle | CA | Placer | 1 | Conventional Hydroelectric | HY |  | S | X | X | NEWCSTLE_7_B1 | NEWCSTLE_7_B1 | 12.7 | 0.9 | 11.5 | 11.5 | 0 | N |  |  | OP | X | 12 | 1986 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage2009 | natural gas combined cycle | TRUE | 6455 | Duke Energy Florida, LLC | 634 | P L Bartow | FL | Pinellas | 4AGT | Natural Gas Fired Combined Cycle | CT | G981 | S | X | Y |  |  | 208.2 | 0.85 | 181 | 216 | 181 | N |  |  | OP | X | 6 | 2009 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2009 | natural gas combined cycle | TRUE | 6455 | Duke Energy Florida, LLC | 634 | P L Bartow | FL | Pinellas | 4BGT | Natural Gas Fired Combined Cycle | CT | G981 | S | X | Y |  |  | 208.2 | 0.85 | 165 | 214 | 165 | N |  |  | OP | X | 6 | 2009 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2009 | natural gas combined cycle | TRUE | 6455 | Duke Energy Florida, LLC | 634 | P L Bartow | FL | Pinellas | 4CGT | Natural Gas Fired Combined Cycle | CT | G981 | S | X | Y |  |  | 208.2 | 0.85 | 181 | 197 | 181 | N |  |  | OP | X | 6 | 2009 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2009 | natural gas combined cycle | TRUE | 6455 | Duke Energy Florida, LLC | 634 | P L Bartow | FL | Pinellas | 4DGT | Natural Gas Fired Combined Cycle | CT | G981 | S | X | Y |  |  | 208.2 | 0.85 | 183 | 203 | 183 | N |  |  | OP | X | 6 | 2009 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2009 | natural gas combined cycle | TRUE | 6455 | Duke Energy Florida, LLC | 634 | P L Bartow | FL | Pinellas | 4ST | Natural Gas Fired Combined Cycle | CA | G981 | S | Y | X |  |  | 421.2 | 0.9 | 402 | 429 | 402 | N |  |  | OP | X | 6 | 2009 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1972 | petroleum | TRUE | 6455 | Duke Energy Florida, LLC | 634 | P L Bartow | FL | Pinellas | P1 | Petroleum Liquids | GT |  | S | X | X |  |  | 55.4 | 0.9 | 41 | 50 | 20 | N |  |  | OP | X | 5 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1972 | natural gas peaker | TRUE | 6455 | Duke Energy Florida, LLC | 634 | P L Bartow | FL | Pinellas | P2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 55.4 | 0.9 | 41 | 53 | 20 | N |  |  | OP | X | 6 | 1972 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1972 | petroleum | TRUE | 6455 | Duke Energy Florida, LLC | 634 | P L Bartow | FL | Pinellas | P3 | Petroleum Liquids | GT |  | S | X | X |  |  | 55.4 | 0.9 | 41 | 51 | 20 | N |  |  | OP | X | 6 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1972 | natural gas peaker | TRUE | 6455 | Duke Energy Florida, LLC | 634 | P L Bartow | FL | Pinellas | P4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 55.4 | 0.9 | 45 | 58 | 20 | N |  |  | OP | X | 6 | 1972 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1980 | natural gas peaker | TRUE | 6455 | Duke Energy Florida, LLC | 638 | Suwannee River | FL | Suwannee | P1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 65.9 | 0.9 | 48 | 65 | 30 | N |  |  | OP | X | 10 | 1980 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1980 | petroleum | TRUE | 6455 | Duke Energy Florida, LLC | 638 | Suwannee River | FL | Suwannee | P2 | Petroleum Liquids | GT |  | S | X | X |  |  | 65.9 | 0.9 | 48 | 64 | 30 | N |  |  | OP | X | 10 | 1980 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1980 | natural gas peaker | TRUE | 6455 | Duke Energy Florida, LLC | 638 | Suwannee River | FL | Suwannee | P3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 65.9 | 0.9 | 49 | 65 | 30 | N |  |  | OP | X | 11 | 1980 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1959 | natural gas steam turbine | TRUE | 7801 | Gulf Power Co | 641 | Gulf Clean Energy Center | FL | Escambia | 4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 93.7 | 0.85 | 75 | 75 | 45 | N |  |  | OP | X | 7 | 1959 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | DFO |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1961 | natural gas steam turbine | TRUE | 7801 | Gulf Power Co | 641 | Gulf Clean Energy Center | FL | Escambia | 5 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 93.7 | 0.85 | 75 | 75 | 45 | N |  |  | OP | X | 6 | 1961 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | DFO |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1970 | natural gas steam turbine | TRUE | 7801 | Gulf Power Co | 641 | Gulf Clean Energy Center | FL | Escambia | 6 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 369.7 | 0.85 | 299 | 299 | 220 | N |  |  | OP | X | 5 | 1970 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1973 | natural gas steam turbine | TRUE | 7801 | Gulf Power Co | 641 | Gulf Clean Energy Center | FL | Escambia | 7 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 578 | 0.85 | 475 | 475 | 280 | N |  |  | OP | X | 8 | 1973 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage2021 | natural gas peaker | TRUE | 7801 | Gulf Power Co | 641 | Gulf Clean Energy Center | FL | Escambia | 8A | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 243.1 | 0.85 | 236 | 233 | 94 | N |  |  | OP | X | 12 | 2021 |  |  | N | Electric Utility | 1 | X | NG | DFO | [9 empty] | N |  | 1H | [23 empty] | Y | N | Y
Vintage2021 | natural gas peaker | TRUE | 7801 | Gulf Power Co | 641 | Gulf Clean Energy Center | FL | Escambia | 8B | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 243.1 | 0.85 | 236 | 233 | 94 | N |  |  | OP | X | 12 | 2021 |  |  | N | Electric Utility | 1 | X | NG | DFO | [9 empty] | N |  | 1H | [23 empty] | Y | N | Y
Vintage2021 | natural gas peaker | TRUE | 7801 | Gulf Power Co | 641 | Gulf Clean Energy Center | FL | Escambia | 8C | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 243.1 | 0.85 | 231.1 | 231.1 | 94 | N |  |  | OP | X | 12 | 2021 |  |  | N | Electric Utility | 1 | X | NG | DFO | [9 empty] | N |  | 1H | [23 empty] | Y | N | Y
Vintage2021 | natural gas peaker | TRUE | 7801 | Gulf Power Co | 641 | Gulf Clean Energy Center | FL | Escambia | 8D | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 243.1 | 0.85 | 231.1 | 231.1 | 94 | N |  |  | OP | X | 12 | 2021 |  |  | N | Electric Utility | 1 | X | NG | DFO | [9 empty] | N |  | 1H | [23 empty] | Y |  | Y
Vintage2002 | natural gas combined cycle | TRUE | 7801 | Gulf Power Co | 643 | Lansing Smith | FL | Bay | 3A | Natural Gas Fired Combined Cycle | CT | G180 | S | X | N |  |  | 203.2 | 0.85 |  |  |  | N |  |  | OP | X | 4 | 2002 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage2002 | natural gas combined cycle | TRUE | 7801 | Gulf Power Co | 643 | Lansing Smith | FL | Bay | 3B | Natural Gas Fired Combined Cycle | CT | G180 | S | X | N |  |  | 203.2 | 0.85 |  |  |  | N |  |  | OP | X | 4 | 2002 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage2002 | natural gas combined cycle | TRUE | 7801 | Gulf Power Co | 643 | Lansing Smith | FL | Bay | 3S | Natural Gas Fired Combined Cycle | CA | G180 | S | Y | X |  |  | 213.3 | 0.85 | 660 | 646 | 360 | N |  |  | OP | X | 4 | 2002 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage1971 | petroleum | TRUE | 7801 | Gulf Power Co | 643 | Lansing Smith | FL | Bay | CT1 | Petroleum Liquids | GT |  | S | X | X |  |  | 41.8 | 0.9 | 32 | 40 | 32 | N |  |  | OP | X | 5 | 1971 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2017 | solar pv | TRUE | 18454 | Tampa Electric Co | 645 | Big Bend | FL | Hillsborough | 1 | Solar Photovoltaic | PV |  | S | X | X |  |  | 19.8 |  | 19.8 | 19.8 |  | N |  |  | OP | X | 2 | 2017 |  |  | N | Electric Utility | 1 | X | SUN | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage2009 | natural gas peaker | TRUE | 18454 | Tampa Electric Co | 645 | Big Bend | FL | Hillsborough | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 62 | 0.85 | 56 | 61 | 14 | N |  |  | OP | X | 8 | 2009 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2021 | natural gas peaker | TRUE | 18454 | Tampa Electric Co | 645 | Big Bend | FL | Hillsborough | GT5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 397.8 | 0.9 | 360 | 392 | 120 | N |  |  | OP | X | 12 | 2021 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 1H | [23 empty] | N | N
Vintage2021 | natural gas peaker | TRUE | 18454 | Tampa Electric Co | 645 | Big Bend | FL | Hillsborough | GT6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 397.8 | 0.9 | 360 | 392 | 120 | N |  |  | OP | X | 12 | 2021 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N
Vintage1970 | natural gas steam turbine | TRUE | 18454 | Tampa Electric Co | 645 | Big Bend | FL | Hillsborough | ST1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 445.5 | 0.9 | 385 | 395 | 185 | N |  |  | OP | X | 10 | 1970 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | 12H |  | Y |  |  |  | Y | [9 empty] | CA | NG | 445 | 12 | 2022 | N |  |  | N | N | N
Vintage1976 | natural gas steam turbine | TRUE | 18454 | Tampa Electric Co | 645 | Big Bend | FL | Hillsborough | ST3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 445.5 | 0.9 | 395 | 400 | 185 | N |  |  | OP | X | 5 | 1976 | 4 | 2023 | N | Electric Utility | 1 | X | NG | BIT |  |  |  |  | NG |  |  |  | N | N |  | 12H |  | Y |  |  |  | Y | [17 empty] | Y | Y | N
Vintage1985 | hard coal | TRUE | 18454 | Tampa Electric Co | 645 | Big Bend | FL | Hillsborough | ST4 | Conventional Steam Coal | ST |  | S | X | X |  |  | 486 | 0.9 | 437 | 442 | 157 | N |  |  | OP | X | 2 | 1985 |  |  | N | Electric Utility | 1 | X | BIT | NG |  |  |  |  | NG |  |  |  | N | N |  | 12H |  | Y |  |  |  | Y | [17 empty] | Y | Y | N
Vintage1987 | nuclear | TRUE | 7140 | Georgia Power Co | 649 | Vogtle | GA | Burke | 1 | Nuclear | ST |  | J | X | X |  |  | 1215 | 0.9 | 1150 | 1150 | 250 | N |  |  | OP | X | 5 | 1987 |  |  | N | Electric Utility | 1 | X | NUC | [9 empty] | N |  |  | OVER | [23 empty] | N | N
Vintage1989 | nuclear | TRUE | 7140 | Georgia Power Co | 649 | Vogtle | GA | Burke | 2 | Nuclear | ST |  | J | X | X |  |  | 1215 | 0.9 | 1152 | 1152 | 250 | N |  |  | OP | X | 5 | 1989 |  |  | N | Electric Utility | 1 | X | NUC | [9 empty] | N |  |  | OVER | [23 empty] | N | N
Vintage1972 | natural gas steam turbine | TRUE | 6909 | Gainesville Regional Utilities | 663 | Deerhaven Generating Station | FL | Alachua | 1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 75 | 0.85 | 75 | 75 | 21 | N |  |  | OP | X | 8 | 1972 | 12 | 2027 | N | Electric Utility | 1 | X | NG | RFO |  |  |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1981 | natural gas steam turbine | TRUE | 6909 | Gainesville Regional Utilities | 663 | Deerhaven Generating Station | FL | Alachua | 2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 250.7 | 0.85 | 232 | 232 | 65 | N |  |  | OP | X | 10 | 1981 | 12 | 2031 | N | Electric Utility | 1 | X | NG | BIT |  |  |  |  | NG | BIT |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y
Vintage1976 | natural gas peaker | TRUE | 6909 | Gainesville Regional Utilities | 663 | Deerhaven Generating Station | FL | Alachua | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 24.6 | 0.85 | 17.5 | 20 | 3 | N |  |  | SB | Y | 7 | 1976 | 10 | 2026 | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1976 | natural gas peaker | TRUE | 6909 | Gainesville Regional Utilities | 663 | Deerhaven Generating Station | FL | Alachua | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 24.6 | 0.85 | 17.5 | 20 | 3 | N |  |  | SB | Y | 8 | 1976 | 10 | 2026 | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1996 | natural gas peaker | TRUE | 6909 | Gainesville Regional Utilities | 663 | Deerhaven Generating Station | FL | Alachua | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 96.1 | 0.85 | 75 | 81 | 50 | N |  |  | OP | X | 1 | 1996 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2021 | natural gas combined cycle | TRUE | 6909 | Gainesville Regional Utilities | 664 | John R Kelly | FL | Alachua | 8.2 | Natural Gas Fired Combined Cycle | CA | G681 | S | N | X |  |  | 45.5 | 0.85 | 37.5 | 38 |  | N |  |  | OP | X | 7 | 2021 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage2001 | natural gas combined cycle | TRUE | 6909 | Gainesville Regional Utilities | 664 | John R Kelly | FL | Alachua | CT04 | Natural Gas Fired Combined Cycle | CT | G681 | S | X | N |  |  | 96.1 | 0.85 | 72 | 81 | 4 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1972 | petroleum | TRUE | 8795 | City of Homestead - (FL) | 665 | G W Ivey | FL | Miami Dade | 13 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 11 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1972 | petroleum | TRUE | 8795 | City of Homestead - (FL) | 665 | G W Ivey | FL | Miami Dade | 14 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 11 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1972 | petroleum | TRUE | 8795 | City of Homestead - (FL) | 665 | G W Ivey | FL | Miami Dade | 15 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 11 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1972 | petroleum | TRUE | 8795 | City of Homestead - (FL) | 665 | G W Ivey | FL | Miami Dade | 16 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 11 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1972 | petroleum | TRUE | 8795 | City of Homestead - (FL) | 665 | G W Ivey | FL | Miami Dade | 17 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 11 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1975 | petroleum | TRUE | 8795 | City of Homestead - (FL) | 665 | G W Ivey | FL | Miami Dade | 19 | Petroleum Liquids | IC |  | S | X | X |  |  | 8.8 | 0.8 | 8 | 8 | 3.5 | N |  |  | OP | X | 2 | 1975 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1970 | petroleum | TRUE | 8795 | City of Homestead - (FL) | 665 | G W Ivey | FL | Miami Dade | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 3 | 1970 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1981 | petroleum | TRUE | 8795 | City of Homestead - (FL) | 665 | G W Ivey | FL | Miami Dade | 20 | Petroleum Liquids | IC |  | S | X | X |  |  | 6.4 | 0.8 | 6 | 6 | 3 | N |  |  | OP | X | 5 | 1981 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1981 | petroleum | TRUE | 8795 | City of Homestead - (FL) | 665 | G W Ivey | FL | Miami Dade | 21 | Petroleum Liquids | IC |  | S | X | X |  |  | 6.4 | 0.8 | 6 | 6 | 3 | N |  |  | OP | X | 5 | 1981 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2013 | petroleum | TRUE | 8795 | City of Homestead - (FL) | 665 | G W Ivey | FL | Miami Dade | 22 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0 | N |  |  | SB | N | 1 | 2013 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1970 | petroleum | TRUE | 8795 | City of Homestead - (FL) | 665 | G W Ivey | FL | Miami Dade | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 3 | 1970 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 9617 | JEA | 666 | J D Kennedy | FL | Duval | GT37 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | FRCC | FRCC | 185 | 0.9 | 178.6 | 191.2 | 65 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2009 | natural gas peaker | TRUE | 9617 | JEA | 666 | J D Kennedy | FL | Duval | GT38 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | FRCC | FRCC | 185 | 0.85 | 178.6 | 191.2 | 65 | N |  |  | OP | X | 6 | 2009 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1966 | hard coal | TRUE | 9617 | JEA | 667 | Northside Generating Station | FL | Duval | 1 | Conventional Steam Coal | ST |  | S | X | X | FRCC | FRCC | 297.5 | 0.85 | 293 | 293 | 165 | N |  |  | OP | X | 3 | 1966 |  |  | N | Electric Utility | 1 | X | BIT | PC |  |  |  |  | NG |  |  |  | N | N |  | OVER | Y |  |  |  | Y | [15 empty] | N |  |  | Y | Y | N
Vintage1972 | hard coal | TRUE | 9617 | JEA | 667 | Northside Generating Station | FL | Duval | 2 | Conventional Steam Coal | ST |  | S | X | X | FRCC | FRCC | 297.5 | 0.85 | 293 | 293 | 165 | N |  |  | OP | X | 6 | 1972 |  |  | N | Electric Utility | 1 | X | BIT | PC |  |  |  |  | NG |  |  |  | N |  |  | OVER | Y |  |  |  | Y | [15 empty] | N |  |  | Y | Y | N
Vintage1975 | petroleum | TRUE | 9617 | JEA | 667 | Northside Generating Station | FL | Duval | 4 | Petroleum Liquids | GT |  | S | X | X | FRCC | FRCC | 62.1 | 0.9 | 53 | 61.6 | 15 | N |  |  | OP | X | 1 | 1975 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N | N | N
Vintage1974 | petroleum | TRUE | 9617 | JEA | 667 | Northside Generating Station | FL | Duval | 5 | Petroleum Liquids | GT |  | S | X | X | FRCC | FRCC | 62.1 | 0.9 | 53 | 61.6 | 15 | N |  |  | OP | X | 12 | 1974 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N | N | N
Vintage1974 | petroleum | TRUE | 9617 | JEA | 667 | Northside Generating Station | FL | Duval | 6 | Petroleum Liquids | GT |  | S | X | X | FRCC | FRCC | 62.1 | 0.9 | 53 | 61.6 | 15 | N |  |  | OP | X | 12 | 1974 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N | N
Vintage1975 | petroleum | TRUE | 9617 | JEA | 667 | Northside Generating Station | FL | Duval | GT3 | Petroleum Liquids | GT |  | S | X | X | FRCC | FRCC | 62.1 | 0.9 | 53 | 61.6 | 15 | N |  |  | OP | X | 1 | 1975 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N | N | N
Vintage1977 | natural gas steam turbine | TRUE | 9617 | JEA | 667 | Northside Generating Station | FL | Duval | ST3 | Natural Gas Steam Turbine | ST |  | S | X | X | FRCC | FRCC | 563.7 | 0.9 | 524 | 524 | 50 | N |  |  | OP | X | 6 | 1977 |  |  | N | Electric Utility | 1 | X | NG | RFO | LFG |  |  |  | NG |  |  |  | N | N |  | OVER | [20 empty] | N |  |  | Y | Y | Y
Vintage1976 | petroleum | TRUE | 10620 | City of Lake Worth Beach - (FL) | 673 | Tom G Smith | FL | Palm Beach | GT1 | Petroleum Liquids | GT |  | S | X | X |  |  | 30.8 | 0.85 | 26 | 31 | 8 | N |  |  | OP | X | 12 | 1976 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 12H |  |  |  |  | N | [18 empty] | N | N | N
Vintage1978 | natural gas combined cycle | TRUE | 10620 | City of Lake Worth Beach - (FL) | 673 | Tom G Smith | FL | Palm Beach | GT2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 21.4 | 0.9 | 21 | 23 | 16 | N |  |  | OP | X | 3 | 1978 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1965 | petroleum | TRUE | 10620 | City of Lake Worth Beach - (FL) | 673 | Tom G Smith | FL | Palm Beach | MU1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.85 | 2 | 2 | 1.8 | N |  |  | OP | X | 12 | 1965 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1965 | petroleum | TRUE | 10620 | City of Lake Worth Beach - (FL) | 673 | Tom G Smith | FL | Palm Beach | MU2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.85 | 2 | 2 | 1.6 | N |  |  | SB | N | 12 | 1965 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1965 | petroleum | TRUE | 10620 | City of Lake Worth Beach - (FL) | 673 | Tom G Smith | FL | Palm Beach | MU3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.85 | 2 | 2 | 1.6 | N |  |  | OP | X | 12 | 1965 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1965 | petroleum | TRUE | 10620 | City of Lake Worth Beach - (FL) | 673 | Tom G Smith | FL | Palm Beach | MU4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.85 | 2 | 2 | 1.6 | N |  |  | OP | X | 12 | 1965 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1965 | petroleum | TRUE | 10620 | City of Lake Worth Beach - (FL) | 673 | Tom G Smith | FL | Palm Beach | MU5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.85 | 2 | 2 | 1.6 | N |  |  | OP | X | 12 | 1965 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1967 | natural gas steam turbine | TRUE | 10620 | City of Lake Worth Beach - (FL) | 673 | Tom G Smith | FL | Palm Beach | S3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 26.5 | 0.85 | 26.5 | 26.5 | 8 | N |  |  | OP | X | 11 | 1967 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1978 | natural gas combined cycle | TRUE | 10620 | City of Lake Worth Beach - (FL) | 673 | Tom G Smith | FL | Palm Beach | S5 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X |  |  | 10 | 0.85 | 10 | 10 | 5 | N |  |  | OP | X | 3 | 1978 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage1925 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 674 | Pilot Butte | WY | Fremont | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.7 | 0 | N |  |  | OS | X | 1 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1929 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 674 | Pilot Butte | WY | Fremont | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0 | N |  |  | OS | X | 2 | 1929 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1962 | natural gas peaker | TRUE | 10623 | City of Lakeland - (FL) | 675 | Larsen Memorial | FL | Polk | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | N/A | N/A | 11.2 | 0.85 | 10 | 14 | 6 | N |  |  | OS | X | 11 | 1962 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | N | N
Vintage1962 | natural gas peaker | TRUE | 10623 | City of Lakeland - (FL) | 675 | Larsen Memorial | FL | Polk | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | N/A | N/A | 11.2 | 0.85 | 9 | 13 | 6 | N |  |  | OS | X | 12 | 1962 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | N | N
Vintage1956 | natural gas combined cycle | TRUE | 10623 | City of Lakeland - (FL) | 675 | Larsen Memorial | FL | Polk | 5 | Natural Gas Fired Combined Cycle | CA | 8CC | S | N | X | N/A | N/A | 25 | 0.85 | 28 | 28 | 12 | N |  |  | OP | X | 4 | 1956 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1992 | natural gas combined cycle | TRUE | 10623 | City of Lakeland - (FL) | 675 | Larsen Memorial | FL | Polk | 8 | Natural Gas Fired Combined Cycle | CT | 8CC | S | X | Y |  |  | 86.2 | 0.9 | 78 | 93 | 27 | N |  |  | OP | X | 7 | 1992 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas combined cycle | TRUE | 10623 | City of Lakeland - (FL) | 676 | C D McIntosh Jr | FL | Polk | 5CT | Natural Gas Fired Combined Cycle | CT | 5CC | S | X | N |  |  | 249 | 0.9 | 234 | 280 | 95 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage2002 | natural gas combined cycle | TRUE | 10623 | City of Lakeland - (FL) | 676 | C D McIntosh Jr | FL | Polk | 5ST | Natural Gas Fired Combined Cycle | CA | 5CC | S | N | X |  |  | 135 | 0.9 | 125 | 125 | 48 | N |  |  | OP | X | 10 | 2002 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage1973 | natural gas peaker | TRUE | 10623 | City of Lakeland - (FL) | 676 | C D McIntosh Jr | FL | Polk | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 26.6 | 0.9 | 17 | 19 | 3 | N |  |  | OP | X | 5 | 1973 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2020 | natural gas peaker | TRUE | 10623 | City of Lakeland - (FL) | 676 | C D McIntosh Jr | FL | Polk | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 130 | 0.85 | 117 | 122 | 85 | N |  |  | OP | X | 6 | 2020 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1970 | petroleum | TRUE | 10623 | City of Lakeland - (FL) | 676 | C D McIntosh Jr | FL | Polk | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 1 | N |  |  | OP | X | 1 | 1970 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1970 | petroleum | TRUE | 10623 | City of Lakeland - (FL) | 676 | C D McIntosh Jr | FL | Polk | IC2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 1 | N |  |  | OP | X | 1 | 1970 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1983 | hydro | TRUE | 12989 | Village of Morrisville - (VT) | 678 | W K Sanders | VT | Lamoille | 1 | Conventional Hydroelectric | HY |  | S | X | X | 4466 |  | 0.9 | 0.85 | 0.7 | 0.9 | 0.3 | N |  |  | OP | X | 7 | 1983 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H
Vintage1983 | hydro | TRUE | 12989 | Village of Morrisville - (VT) | 678 | W K Sanders | VT | Lamoille | 2 | Conventional Hydroelectric | HY |  | S | X | X | 4466 |  | 0.9 | 0.85 | 0.7 | 0.9 | 0.3 | N |  |  | OP | X | 7 | 1983 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H
Vintage1983 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 682 | Kerckhoff 2 | CA | Fresno | 1 | Conventional Hydroelectric | HY |  | S | X | X | KERCKHOF_7_B1 | KERCKHOF_7_B1 | 139.5 | 0.9 | 155 | 155 | 5 | N |  |  | OP | X | 5 | 1983 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1989 | natural gas peaker | TRUE | 14610 | Orlando Utilities Comm | 683 | Indian River Plant | FL | Brevard | A | Natural Gas Fired Combustion Turbine | GT |  | J | X | X |  |  | 41.4 | 0.85 | 37 | 48 | 22 | N |  |  | OP | X | 7 | 1989 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1989 | natural gas peaker | TRUE | 14610 | Orlando Utilities Comm | 683 | Indian River Plant | FL | Brevard | B | Natural Gas Fired Combustion Turbine | GT |  | J | X | X |  |  | 41.4 | 0.85 | 37 | 48 | 22 | N |  |  | OP | X | 7 | 1989 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1992 | natural gas peaker | TRUE | 14610 | Orlando Utilities Comm | 683 | Indian River Plant | FL | Brevard | C | Natural Gas Fired Combustion Turbine | GT |  | J | X | X |  |  | 130 | 0.85 | 108 | 127 | 40 | N |  |  | OP | X | 8 | 1992 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1992 | natural gas peaker | TRUE | 14610 | Orlando Utilities Comm | 683 | Indian River Plant | FL | Brevard | D | Natural Gas Fired Combustion Turbine | GT |  | J | X | X |  |  | 130 | 0.85 | 108 | 127 | 40 | N |  |  | OP | X | 8 | 1992 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1977 | natural gas combined cycle | TRUE | 18445 | City of Tallahassee - (FL) | 688 | Arvah B Hopkins | FL | Leon | 2 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | N/A | N/A | 259.2 | 0.85 | 141 | 145 | 120 | N |  |  | OP | X | 10 | 1977 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N
Vintage2008 | natural gas combined cycle | TRUE | 18445 | City of Tallahassee - (FL) | 688 | Arvah B Hopkins | FL | Leon | CT 2A | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | N/A | N/A | 198.9 | 0.85 | 159 | 185 | 70 | N |  |  | OP | X | 10 | 2008 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | NG | DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2005 | natural gas peaker | TRUE | 18445 | City of Tallahassee - (FL) | 688 | Arvah B Hopkins | FL | Leon | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | N/A | N/A | 60.5 | 0.85 | 46 | 48 | 12 | N |  |  | OP | X | 9 | 2005 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | NG | DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2005 | natural gas peaker | TRUE | 18445 | City of Tallahassee - (FL) | 688 | Arvah B Hopkins | FL | Leon | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | N/A | N/A | 60.5 | 0.85 | 46 | 48 | 12 | N |  |  | OP | X | 11 | 2005 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | NG | DFO |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage2019 | natural gas peaker | TRUE | 18445 | City of Tallahassee - (FL) | 688 | Arvah B Hopkins | FL | Leon | IC1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | N/A | N/A | 18.8 | 0.85 | 18.5 | 18.5 | 7.5 | N |  |  | OP | X | 1 | 2019 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 10M | [23 empty] | N | N | N
Vintage2019 | natural gas peaker | TRUE | 18445 | City of Tallahassee - (FL) | 688 | Arvah B Hopkins | FL | Leon | IC2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | N/A | N/A | 18.8 | 0.85 | 18.5 | 18.5 | 7.5 | N |  |  | OP | X | 1 | 2019 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 10M | [23 empty] | N | N | N
Vintage2019 | natural gas peaker | TRUE | 18445 | City of Tallahassee - (FL) | 688 | Arvah B Hopkins | FL | Leon | IC3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | N/A | N/A | 18.8 | 0.85 | 18.5 | 18.5 | 7.5 | N |  |  | OP | X | 1 | 2019 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 10M | [23 empty] | N | N | N
Vintage2019 | natural gas peaker | TRUE | 18445 | City of Tallahassee - (FL) | 688 | Arvah B Hopkins | FL | Leon | IC4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | N/A | N/A | 18.8 | 0.85 | 18.5 | 18.5 | 7.5 | N |  |  | OP | X | 1 | 2019 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 10M | [23 empty] | N | N | N
Vintage2020 | natural gas peaker | TRUE | 18445 | City of Tallahassee - (FL) | 688 | Arvah B Hopkins | FL | Leon | IC5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | N/A | N/A | 18.8 | 0.85 | 18.5 | 18.5 | 7.5 | N |  |  | OP | X | 4 | 2020 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 10M | [23 empty] | N | N | N
Vintage2000 | natural gas combined cycle | TRUE | 18445 | City of Tallahassee - (FL) | 689 | S O Purdom | FL | Wakulla | 8 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | N/A | N/A | 180 | 0.85 | 154 | 182 | 120 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | NG | DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2000 | natural gas combined cycle | TRUE | 18445 | City of Tallahassee - (FL) | 689 | S O Purdom | FL | Wakulla | 9 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X | N/A | N/A | 90.1 | 0.85 | 72 | 76 | 50 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N
Vintage2003 | hydro | TRUE | 27813 | USCE-Mobile District | 690 | J Woodruff | FL | Gadsden | 1A | Conventional Hydroelectric | HY |  | S | X | X |  |  | 14.5 | 0.95 | 14.5 | 14.5 | 5 | N |  |  | OP | X | 2 | 2003 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage2002 | hydro | TRUE | 27813 | USCE-Mobile District | 690 | J Woodruff | FL | Gadsden | 2A | Conventional Hydroelectric | HY |  | S | X | X |  |  | 14.5 | 0.95 | 14.5 | 14.5 | 5 | N |  |  | OP | X | 2 | 2002 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage2001 | hydro | TRUE | 27813 | USCE-Mobile District | 690 | J Woodruff | FL | Gadsden | 3A | Conventional Hydroelectric | HY |  | S | X | X |  |  | 14.5 | 0.95 | 14.5 | 14.5 | 5 | N |  |  | OP | X | 2 | 2001 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage2000 | onshore wind | TRUE | 62042 | SRIV Partnership LLC | 692 | Medicine Bow | WY | Carbon | 10 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 4.9 |  | 4.9 | 4.9 | 0 | N |  |  | OP | X | 7 | 2000 |  |  | N | IPP Non-CHP | 2 | X | WND | [9 empty] | N |  | 7
Vintage2000 | onshore wind | TRUE | 62042 | SRIV Partnership LLC | 692 | Medicine Bow | WY | Carbon | 11 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 1.3 |  | 1.3 | 1.3 | 0 | N |  |  | OP | X | 7 | 2000 |  |  | N | IPP Non-CHP | 2 | X | WND | [9 empty] | N |  | 2
Vintage1998 | petroleum | TRUE | 6443 | Florida Keys El Coop Assn, Inc | 696 | Marathon Generating Plant | FL | Monroe | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.5 | 1 | 3.5 | 3.5 | 3.5 | N |  |  | SB | Y | 1 | 1998 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2001 | petroleum | TRUE | 6443 | Florida Keys El Coop Assn, Inc | 696 | Marathon Generating Plant | FL | Monroe | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.5 | 1 | 3.5 | 3.5 | 3.5 | N |  |  | SB | Y | 1 | 2001 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1989 | petroleum | TRUE | 6443 | Florida Keys El Coop Assn, Inc | 696 | Marathon Generating Plant | FL | Monroe | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 1 | 2 | 2 | 2 | N |  |  | SB | Y | 5 | 1989 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N
Vintage1989 | petroleum | TRUE | 6443 | Florida Keys El Coop Assn, Inc | 696 | Marathon Generating Plant | FL | Monroe | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 1 | 2 | 2 | 2 | N |  |  | SB | Y | 5 | 1989 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N
Vintage1974 | petroleum | TRUE | 19150 | Trenton Municipal Utilities - (MO) | 698 | Trenton North | MO | Grundy | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2.7 | 2.7 | 0.7 | N |  |  | OP | X | 6 | 1974 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1974 | petroleum | TRUE | 19150 | Trenton Municipal Utilities - (MO) | 698 | Trenton North | MO | Grundy | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2.7 | 2.7 | 0.7 | N |  |  | OP | X | 6 | 1974 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1974 | petroleum | TRUE | 19150 | Trenton Municipal Utilities - (MO) | 698 | Trenton North | MO | Grundy | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2.7 | 2.7 | 0.7 | N |  |  | OP | X | 6 | 1974 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1974 | petroleum | TRUE | 19150 | Trenton Municipal Utilities - (MO) | 698 | Trenton North | MO | Grundy | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2.7 | 2.7 | 0.7 | N |  |  | OP | X | 6 | 1974 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1975 | petroleum | TRUE | 19150 | Trenton Municipal Utilities - (MO) | 698 | Trenton North | MO | Grundy | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2.7 | 2.7 | 0.7 | N |  |  | OP | X | 6 | 1975 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1926 | hydro | TRUE | 7140 | Georgia Power Co | 702 | Bartletts Ferry | AL | Lee | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.8 | 16.4 | 16.5 | 16.4 | N |  |  | OP | X | 12 | 1926 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1926 | hydro | TRUE | 7140 | Georgia Power Co | 702 | Bartletts Ferry | AL | Lee | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.8 | 16.4 | 16.5 | 16.4 | N |  |  | OP | X | 12 | 1926 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1928 | hydro | TRUE | 7140 | Georgia Power Co | 702 | Bartletts Ferry | AL | Lee | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.96 | 16.4 | 16.5 | 16.4 | N |  |  | OP | X | 12 | 1928 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1951 | hydro | TRUE | 7140 | Georgia Power Co | 702 | Bartletts Ferry | AL | Lee | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 20 | 0.8 | 21.9 | 22 | 21.9 | N |  |  | OP | X | 12 | 1951 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1985 | hydro | TRUE | 7140 | Georgia Power Co | 702 | Bartletts Ferry | AL | Lee | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 54 | 0.9 | 59 | 59.5 | 59 | N |  |  | OP | X | 10 | 1985 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1985 | hydro | TRUE | 7140 | Georgia Power Co | 702 | Bartletts Ferry | AL | Lee | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 54 | 0.9 | 59 | 59.5 | 59 | N |  |  | OP | X | 11 | 1985 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1971 | hard coal | TRUE | 7140 | Georgia Power Co | 703 | Bowen | GA | Bartow | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 805.8 | 0.85 | 714 | 714 | 450 | N |  |  | OP | X | 10 | 1971 |  |  | N | Electric Utility | 1 | X | BIT | DFO |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | N
Vintage1972 | hard coal | TRUE | 7140 | Georgia Power Co | 703 | Bowen | GA | Bartow | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 788.8 | 0.85 | 718 | 718 | 450 | N |  |  | OP | X | 9 | 1972 |  |  | N | Electric Utility | 1 | X | BIT | DFO |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | N
Vintage1974 | hard coal | TRUE | 7140 | Georgia Power Co | 703 | Bowen | GA | Bartow | 3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 952 | 0.85 | 883 | 883 | 550 | N |  |  | OP | X | 12 | 1974 |  |  | N | Electric Utility | 1 | X | BIT | DFO |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | N | N
Vintage1975 | hard coal | TRUE | 7140 | Georgia Power Co | 703 | Bowen | GA | Bartow | 4 | Conventional Steam Coal | ST |  | S | X | X |  |  | 952 | 0.85 | 885 | 885 | 550 | N |  |  | OP | X | 11 | 1975 |  |  | N | Electric Utility | 1 | X | BIT | DFO |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | N
Vintage1927 | hydro | TRUE | 7140 | Georgia Power Co | 704 | Burton Dam | GA | Rabun | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.9 | 4.8 | 4.4 | 4.4 | N |  |  | OP | X | 9 | 1927 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1927 | hydro | TRUE | 7140 | Georgia Power Co | 704 | Burton Dam | GA | Rabun | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.9 | 4.8 | 4.4 | 4.3 | N |  |  | OP | X | 9 | 1927 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1921 | hydro | TRUE | 7140 | Georgia Power Co | 706 | Flint River | GA | Dougherty | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 0.8 | 2.1 | 2 | 1.9 | N |  |  | OP | X | 12 | 1921 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1921 | hydro | TRUE | 7140 | Georgia Power Co | 706 | Flint River | GA | Dougherty | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 0.8 | 2.1 | 2 | 1.9 | N |  |  | OP | X | 12 | 1921 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1925 | hydro | TRUE | 7140 | Georgia Power Co | 706 | Flint River | GA | Dougherty | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 0.8 | 2.1 | 2 | 2 | N |  |  | OP | X | 12 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1915 | hydro | TRUE | 7140 | Georgia Power Co | 707 | Goat Rock | AL | Lee | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5 | 0.8 | 5 | 5.1 | 3.1 | N |  |  | OP | X | 12 | 1915 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1920 | hydro | TRUE | 7140 | Georgia Power Co | 707 | Goat Rock | AL | Lee | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5 | 0.94 | 5 | 5.1 | 5 | N |  |  | OP | X | 12 | 1920 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1955 | hydro | TRUE | 7140 | Georgia Power Co | 707 | Goat Rock | AL | Lee | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5 | 0.8 | 5 | 5.1 | 5 | N |  |  | OP | X | 12 | 1955 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage1956 | hydro | TRUE | 7140 | Georgia Power Co | 707 | Goat Rock | AL | Lee | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5 | 0.8 | 5 | 5.1 | 5 | N |  |  | OP | X | 2 | 1956 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H | [23 empty] | N
Vintage2005 | hydro | TRUE | 7140 | Georgia Power Co | 707 | Goat Rock | AL | Lee | 7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9.3 | 0.85 | 9.3 | 9.5 | 9.3 | N |  |  | OP | X | 6 | 2005 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 1H | [23 empty] | N
Vintage2005 | hydro | TRUE | 7140 | Georgia Power Co | 707 | Goat Rock | AL | Lee | 8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9.3 | 0.85 | 9.3 | 9.5 | 9.3 | N |  |  | OP | X | 6 | 2005 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 1H | [23 empty] | N
Vintage1971 | natural gas peaker | TRUE | 7140 | Georgia Power Co | 710 | Jack McDonough | GA | Cobb | 3A | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 41.8 | 0.9 | 32 | 40 | 32 | N |  |  | OP | X | 5 | 1971 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1971 | natural gas peaker | TRUE | 7140 | Georgia Power Co | 710 | Jack McDonough | GA | Cobb | 3B | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 41.8 | 0.9 | 32 | 40 | 32 | N |  |  | OP | X | 5 | 1971 |  |  | N | Electric Utility | 1 | X | NG | DFO | [11 empty] | 1H | [23 empty] | Y | N | Y
Vintage2011 | natural gas combined cycle | TRUE | 7140 | Georgia Power Co | 710 | Jack McDonough | GA | Cobb | 4 | Natural Gas Fired Combined Cycle | CA | G104 | S | Y | X |  |  | 369 | 0.9 | 360 | 360 | 209 | N |  |  | OP | X | 12 | 2011 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 12H | [23 empty] | N | N | N
Vintage2012 | natural gas combined cycle | TRUE | 7140 | Georgia Power Co | 710 | Jack McDonough | GA | Cobb | 5 | Natural Gas Fired Combined Cycle | CA | G105 | S | Y | X |  |  | 369 | 0.9 | 360 | 360 | 209 | N |  |  | OP | X | 4 | 2012 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 12H | [23 empty] | N | N | N
Vintage2012 | natural gas combined cycle | TRUE | 7140 | Georgia Power Co | 710 | Jack McDonough | GA | Cobb | 5ACT | Natural Gas Fired Combined Cycle | CT | G105 | S | X | N |  |  | 276.3 | 0.85 | 232.5 | 271 | 150 | N |  |  | OP | X | 4 | 2012 |  |  | N | Electric Utility | 1 | X | NG | DFO | [11 empty] | 12H | [23 empty] | Y | N | Y
Vintage2012 | natural gas combined cycle | TRUE | 7140 | Georgia Power Co | 710 | Jack McDonough | GA | Cobb | 5BCT | Natural Gas Fired Combined Cycle | CT | G105 | S | X | N |  |  | 276.3 | 0.85 | 232.5 | 271 | 150 | N |  |  | OP | X | 4 | 2012 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 12H | [23 empty] | N | N | N
Vintage2012 | natural gas combined cycle | TRUE | 7140 | Georgia Power Co | 710 | Jack McDonough | GA | Cobb | 6 | Natural Gas Fired Combined Cycle | CA | G106 | S | Y | X |  |  | 369 | 0.9 | 345 | 345 | 209 | N |  |  | OP | X | 10 | 2012 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 12H | [23 empty] | N | N | N
Vintage2012 | natural gas combined cycle | TRUE | 7140 | Georgia Power Co | 710 | Jack McDonough | GA | Cobb | 6ACT | Natural Gas Fired Combined Cycle | CT | G106 | S | X | N |  |  | 276.3 | 0.85 | 233 | 274.5 | 150 | N |  |  | OP | X | 10 | 2012 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 12H | [23 empty] | N | N | N
Vintage2012 | natural gas combined cycle | TRUE | 7140 | Georgia Power Co | 710 | Jack McDonough | GA | Cobb | 6BCT | Natural Gas Fired Combined Cycle | CT | G106 | S | X | N |  |  | 276.3 | 0.85 | 233 | 274.5 | 150 | N |  |  | OP | X | 10 | 2012 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 12H | [23 empty] | N | N | N
Vintage2011 | natural gas combined cycle | TRUE | 7140 | Georgia Power Co | 710 | Jack McDonough | GA | Cobb | CT4A | Natural Gas Fired Combined Cycle | CT | G104 | S | X | N |  |  | 276.3 | 0.85 | 237.5 | 276.5 | 150 | N |  |  | OP | X | 12 | 2011 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage2011 | natural gas combined cycle | TRUE | 7140 | Georgia Power Co | 710 | Jack McDonough | GA | Cobb | CT4B | Natural Gas Fired Combined Cycle | CT | G104 | S | X | N |  |  | 276.3 | 0.85 | 237.5 | 276.5 | 150 | N |  |  | OP | X | 12 | 2011 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 12H | [23 empty] | N | N | N
Vintage1911 | hydro | TRUE | 7140 | Georgia Power Co | 712 | Lloyd Shoals | GA | Jasper | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 3.8 | 3.8 | 3.5 | N |  |  | OP | X | 2 | 1911 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1911 | hydro | TRUE | 7140 | Georgia Power Co | 712 | Lloyd Shoals | GA | Jasper | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 3.8 | 3.8 | 3.5 | N |  |  | OP | X | 2 | 1911 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1911 | hydro | TRUE | 7140 | Georgia Power Co | 712 | Lloyd Shoals | GA | Jasper | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 3.8 | 3.8 | 3.5 | N |  |  | OP | X | 3 | 1911 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1911 | hydro | TRUE | 7140 | Georgia Power Co | 712 | Lloyd Shoals | GA | Jasper | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 3.8 | 3.8 | 3.5 | N |  |  | OP | X | 3 | 1911 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1916 | hydro | TRUE | 7140 | Georgia Power Co | 712 | Lloyd Shoals | GA | Jasper | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 3.8 | 3.8 | 3.5 | N |  |  | OP | X | 12 | 1916 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1917 | hydro | TRUE | 7140 | Georgia Power Co | 712 | Lloyd Shoals | GA | Jasper | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 3.8 | 3.8 | 3.5 | N |  |  | OP | X | 1 | 1917 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1986 | hydro | TRUE | 14328 | Pacific Gas & Electric Co. | 714 | Toadtown | CA | Butte | 1 | Conventional Hydroelectric | HY |  | S | X | X | TOADTWN_7_N002 | TOADTWN_7_N002 | 1.8 | 0.95 | 1.5 | 1.5 | 0 | N |  |  | OP | X | 4 | 1986 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1972 | petroleum | TRUE | 7140 | Georgia Power Co | 715 | McManus | GA | Glynn | 3A | Petroleum Liquids | GT |  | S | X | X |  |  | 55.4 | 0.9 | 46 | 57 | 3 | N |  |  | OP | X | 1 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1972 | petroleum | TRUE | 7140 | Georgia Power Co | 715 | McManus | GA | Glynn | 3B | Petroleum Liquids | GT |  | S | X | X |  |  | 55.4 | 0.9 | 46 | 57 | 3 | N |  |  | OP | X | 1 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1972 | petroleum | TRUE | 7140 | Georgia Power Co | 715 | McManus | GA | Glynn | 3C | Petroleum Liquids | GT |  | S | X | X |  |  | 55.4 | 0.9 | 46 | 57 | 3 | N |  |  | OP | X | 1 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1972 | petroleum | TRUE | 7140 | Georgia Power Co | 715 | McManus | GA | Glynn | 4A | Petroleum Liquids | GT |  | S | X | X |  |  | 65.3 | 0.9 | 46 | 57 | 3 | N |  |  | OP | X | 12 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1972 | petroleum | TRUE | 7140 | Georgia Power Co | 715 | McManus | GA | Glynn | 4B | Petroleum Liquids | GT |  | S | X | X |  |  | 65.3 | 0.9 | 46 | 57 | 3 | N |  |  | OP | X | 12 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1972 | petroleum | TRUE | 7140 | Georgia Power Co | 715 | McManus | GA | Glynn | 4C | Petroleum Liquids | GT |  | S | X | X |  |  | 65.3 | 0.9 | 46 | 57 | 3 | N |  |  | OP | X | 12 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1972 | petroleum | TRUE | 7140 | Georgia Power Co | 715 | McManus | GA | Glynn | 4D | Petroleum Liquids | GT |  | S | X | X |  |  | 65.3 | 0.9 | 46 | 57 | 3 | N |  |  | OP | X | 12 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1972 | petroleum | TRUE | 7140 | Georgia Power Co | 715 | McManus | GA | Glynn | 4E | Petroleum Liquids | GT |  | S | X | X |  |  | 65.3 | 0.9 | 46 | 57 | 3 | N |  |  | OP | X | 12 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1972 | petroleum | TRUE | 7140 | Georgia Power Co | 715 | McManus | GA | Glynn | 4F | Petroleum Liquids | GT |  | S | X | X |  |  | 65.3 | 0.9 | 46 | 57 | 3 | N |  |  | OP | X | 12 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1964 | petroleum | TRUE | 7140 | Georgia Power Co | 715 | McManus | GA | Glynn | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 12 | 1964 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1903 | hydro | TRUE | 7140 | Georgia Power Co | 717 | Morgan Falls | GA | Fulton | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 1.5 | 1.6 | 1.5 | N |  |  | OP | X | 12 | 1903 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1903 | hydro | TRUE | 7140 | Georgia Power Co | 717 | Morgan Falls | GA | Fulton | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 1.5 | 1.6 | 1.5 | N |  |  | OP | X | 12 | 1903 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1903 | hydro | TRUE | 7140 | Georgia Power Co | 717 | Morgan Falls | GA | Fulton | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 1.5 | 1.6 | 1.5 | N |  |  | OP | X | 12 | 1903 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1903 | hydro | TRUE | 7140 | Georgia Power Co | 717 | Morgan Falls | GA | Fulton | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 1.5 | 1.6 | 1.5 | N |  |  | OP | X | 12 | 1903 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1903 | hydro | TRUE | 7140 | Georgia Power Co | 717 | Morgan Falls | GA | Fulton | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 1.5 | 1.6 | 1.5 | N |  |  | OP | X | 12 | 1903 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1903 | hydro | TRUE | 7140 | Georgia Power Co | 717 | Morgan Falls | GA | Fulton | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 1.5 | 1.6 | 1.5 | N |  |  | OP | X | 12 | 1903 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1903 | hydro | TRUE | 7140 | Georgia Power Co | 717 | Morgan Falls | GA | Fulton | 7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 1.5 | 1.6 | 1.4 | N |  |  | OP | X | 12 | 1903 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1926 | hydro | TRUE | 7140 | Georgia Power Co | 718 | Nacoochee | GA | Rabun | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 3 | 3 | 3 | N |  |  | OP | X | 10 | 1926 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1926 | hydro | TRUE | 7140 | Georgia Power Co | 718 | Nacoochee | GA | Rabun | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 3 | 3 | 3 | N |  |  | OP | X | 12 | 1926 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1963 | hydro | TRUE | 7140 | Georgia Power Co | 719 | North Highlands | GA | Muscogee | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9.2 | 0.8 | 10.7 | 10.8 | 10.5 | N |  |  | OP | X | 2 | 1963 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1963 | hydro | TRUE | 7140 | Georgia Power Co | 719 | North Highlands | GA | Muscogee | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9.2 | 0.8 | 10.7 | 10.8 | 10.5 | N |  |  | OP | X | 3 | 1963 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1963 | hydro | TRUE | 7140 | Georgia Power Co | 719 | North Highlands | GA | Muscogee | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9.2 | 0.8 | 10.7 | 10.8 | 10.5 | N |  |  | OP | X | 1 | 1963 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1963 | hydro | TRUE | 7140 | Georgia Power Co | 719 | North Highlands | GA | Muscogee | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.8 | 2.3 | 2.3 | 2.3 | N |  |  | OP | X | 1 | 1963 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1959 | hydro | TRUE | 7140 | Georgia Power Co | 720 | Oliver Dam | GA | Muscogee | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18 | 0.8 | 17.7 | 17.5 | 17.5 | N |  |  | OP | X | 7 | 1959 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1959 | hydro | TRUE | 7140 | Georgia Power Co | 720 | Oliver Dam | GA | Muscogee | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18 | 0.8 | 17.7 | 17.5 | 17.5 | N |  |  | OP | X | 8 | 1959 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1959 | hydro | TRUE | 7140 | Georgia Power Co | 720 | Oliver Dam | GA | Muscogee | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18 | 0.8 | 17.7 | 17.5 | 17.5 | N |  |  | OP | X | 8 | 1959 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1959 | hydro | TRUE | 7140 | Georgia Power Co | 720 | Oliver Dam | GA | Muscogee | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6 | 0.8 | 5.9 | 5.8 | 5.7 | N |  |  | OP | X | 11 | 1959 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1953 | hydro | TRUE | 7140 | Georgia Power Co | 722 | Sinclair Dam | GA | Baldwin | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 22.5 | 0.8 | 21.9 | 21.9 | 21.9 | N |  |  | OP | X | 2 | 1953 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1953 | hydro | TRUE | 7140 | Georgia Power Co | 722 | Sinclair Dam | GA | Baldwin | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 22.5 | 0.8 | 21.9 | 21.9 | 21.9 | N |  |  | OP | X | 2 | 1953 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1913 | hydro | TRUE | 7140 | Georgia Power Co | 723 | Tallulah Falls | GA | Habersham | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 12 | 1 | 12.1 | 12.1 | 12.1 | N |  |  | OP | X | 9 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1913 | hydro | TRUE | 7140 | Georgia Power Co | 723 | Tallulah Falls | GA | Habersham | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 12 | 1 | 12.1 | 12.1 | 12.1 | N |  |  | OP | X | 10 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1914 | hydro | TRUE | 7140 | Georgia Power Co | 723 | Tallulah Falls | GA | Habersham | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 12 | 1 | 12.1 | 12.1 | 12.1 | N |  |  | OP | X | 9 | 1914 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1913 | hydro | TRUE | 7140 | Georgia Power Co | 723 | Tallulah Falls | GA | Habersham | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 12 | 1 | 12.2 | 12.2 | 12.2 | N |  |  | OP | X | 12 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1913 | hydro | TRUE | 7140 | Georgia Power Co | 723 | Tallulah Falls | GA | Habersham | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 12 | 1 | 12.2 | 12.2 | 12.2 | N |  |  | OP | X | 12 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1920 | hydro | TRUE | 7140 | Georgia Power Co | 723 | Tallulah Falls | GA | Habersham | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 12 | 1 | 12.2 | 12.2 | 12.2 | N |  |  | OP | X | 3 | 1920 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1925 | hydro | TRUE | 7140 | Georgia Power Co | 724 | Terrora | GA | Rabun | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8 | 0.8 | 8.3 | 8.3 | 8.3 | N |  |  | OP | X | 7 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1925 | hydro | TRUE | 7140 | Georgia Power Co | 724 | Terrora | GA | Rabun | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8 | 0.8 | 9.3 | 9.3 | 9.3 | Y | 1 | 2021 | OP | X | 3 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1923 | hydro | TRUE | 7140 | Georgia Power Co | 725 | Tugalo | GA | Habersham | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 11.2 | 0.9 | 13 | 13.1 | 13 | N |  |  | OP | X | 10 | 1923 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1923 | hydro | TRUE | 7140 | Georgia Power Co | 725 | Tugalo | GA | Habersham | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 11.2 | 0.9 | 13 | 13.1 | 13 | N |  |  | OP | X | 11 | 1923 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1924 | hydro | TRUE | 7140 | Georgia Power Co | 725 | Tugalo | GA | Habersham | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 11.2 | 0.9 | 13 | 13.1 | 13 | N |  |  | OP | X | 4 | 1924 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1924 | hydro | TRUE | 7140 | Georgia Power Co | 725 | Tugalo | GA | Habersham | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 11.2 | 0.9 | 13 | 13.1 | 13 | N |  |  | OP | X | 4 | 1924 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1974 | natural gas steam turbine | TRUE | 7140 | Georgia Power Co | 728 | Yates | GA | Coweta | 6 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 403.7 | 0.85 | 355.5 | 355.5 | 60 | N |  |  | OP | X | 7 | 1974 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N |  |  | OVER | [23 empty] | N | N | N
Vintage1974 | natural gas steam turbine | TRUE | 7140 | Georgia Power Co | 728 | Yates | GA | Coweta | 7 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 403.7 | 0.85 | 358.5 | 358.5 | 60 | N |  |  | OP | X | 4 | 1974 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N |  |  | OVER | [23 empty] | N | N | N
Vintage1925 | hydro | TRUE | 7140 | Georgia Power Co | 729 | Yonah | GA | Stephens | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7.5 | 0.9 | 9.5 | 9.6 | 9.5 | N |  |  | OP | X | 10 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1925 | hydro | TRUE | 7140 | Georgia Power Co | 729 | Yonah | GA | Stephens | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7.5 | 0.9 | 9.5 | 9.6 | 9.5 | N |  |  | OP | X | 11 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1925 | hydro | TRUE | 7140 | Georgia Power Co | 729 | Yonah | GA | Stephens | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7.5 | 0.9 | 9.5 | 9.6 | 9.5 | N |  |  | OP | X | 12 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H | [23 empty] | N
Vintage1970 | petroleum | TRUE | 7140 | Georgia Power Co | 732 | Boulevard | GA | Chatham | 1 | Petroleum Liquids | GT |  | S | X | X |  |  | 15.6 | 0.85 | 14 | 18.6 | 14 | N |  |  | OP | X | 9 | 1970 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1914 | hydro | TRUE | 17539 | Dominion Energy South Carolina, Inc | 736 | Stevens Creek | GA | Columbia | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 0.8 | 1.5 | 1.9 | 0.1 | N |  |  | OP | X | 6 | 1914 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1914 | hydro | TRUE | 17539 | Dominion Energy South Carolina, Inc | 736 | Stevens Creek | GA | Columbia | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 0.8 | 1.5 | 1.9 | 0.1 | N |  |  | OP | X | 6 | 1914 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1914 | hydro | TRUE | 17539 | Dominion Energy South Carolina, Inc | 736 | Stevens Creek | GA | Columbia | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 0.8 | 1.5 | 1.9 | 0.1 | N |  |  | OP | X | 6 | 1914 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 10M | [23 empty] | N
Vintage1914 | hydro | TRUE | 17539 | Dominion Energy South Carolina, Inc | 736 | Stevens Creek | GA | Columbia | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 0.8 | 1.5 | 1.9 | 0.1 | N |  |  | OP | X | 6 | 1914 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1914 | hydro | TRUE | 17539 | Dominion Energy South Carolina, Inc | 736 | Stevens Creek | GA | Columbia | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 0.8 | 1.5 | 1.9 | 0.1 | N |  |  | OP | X | 6 | 1914 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1925 | hydro | TRUE | 17539 | Dominion Energy South Carolina, Inc | 736 | Stevens Creek | GA | Columbia | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 0.8 | 1.5 | 1.9 | 0.1 | N |  |  | OP | X | 6 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1926 | hydro | TRUE | 17539 | Dominion Energy South Carolina, Inc | 736 | Stevens Creek | GA | Columbia | 7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 0.8 | 1.5 | 1.9 | 0.1 | N |  |  | OP | X | 6 | 1926 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1926 | hydro | TRUE | 17539 | Dominion Energy South Carolina, Inc | 736 | Stevens Creek | GA | Columbia | 8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 0.8 | 1.5 | 1.9 | 0.1 | N |  |  | OP | X | 6 | 1926 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 10M | [23 empty] | N
Vintage1994 | hydro | TRUE | 12397 | Metropolitan Water District of S CA | 745 | Etiwanda | CA | San Bernardino | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 23.9 | 0.95 | 23.9 | 23.9 | 2.5 | N |  |  | OP | X | 12 | 1994 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 12H
Vintage1987 | hydro | TRUE | 16612 | City & County of San Francisco | 751 | Moccasin Low Head Hydro Project | CA | Tuolumne | 1 | Conventional Hydroelectric | HY |  | S | X | X | INTKEP_2_UNITS-APND | INTKEP_2_UNITS | 2.9 | 0.8 | 2.9 | 2.9 | 0 | N |  |  | OP | X | 7 | 1987 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1930 | hydro | TRUE | 4538 | Crisp County Power Comm | 752 | Lake Blackshear Project | GA | Worth | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 2.4 | 2.4 | 0.9 | N |  |  | OP | X | 8 | 1930 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M | [23 empty] | N
Vintage1930 | hydro | TRUE | 4538 | Crisp County Power Comm | 752 | Lake Blackshear Project | GA | Worth | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5 | 0.8 | 4 | 4 | 1.4 | N |  |  | OP | X | 8 | 1930 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M | [23 empty] | N
Vintage1930 | hydro | TRUE | 4538 | Crisp County Power Comm | 752 | Lake Blackshear Project | GA | Worth | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.8 | 0.8 | 4.8 | 4.8 | 1.1 | N |  |  | OP | X | 5 | 1930 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M | [23 empty] | N
Vintage1930 | hydro | TRUE | 4538 | Crisp County Power Comm | 752 | Lake Blackshear Project | GA | Worth | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5 | 0.8 | 4 | 4 | 0.8 | N |  |  | OP | X | 5 | 1930 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M | [23 empty] | N
Vintage1957 | natural gas steam turbine | TRUE | 4538 | Crisp County Power Comm | 753 | Crisp Plant | GA | Worth | 1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 12.5 | 0.8 | 10 | 10 | 3 | N |  |  | OP | X | 6 | 1957 |  |  | N | Electric Utility | 1 | X | NG | BIT |  |  |  |  | NG |  |  |  | N | N |  | OVER |  | N |  |  | N | N | N | [16 empty] | N | N | N
Vintage1957 | natural gas peaker | TRUE | 4538 | Crisp County Power Comm | 753 | Crisp Plant | GA | Worth | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 5 | 0.8 | 4 | 4 | 1 | N |  |  | OP | X | 5 | 1957 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1962 | hydro | TRUE | 19375 | USCE-Savannah District | 754 | Hartwell Lake | GA | Hart | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 85 | 0.9 | 85 | 85 | 30 | N |  |  | OP | X | 4 | 1962 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M | [23 empty] | N
Vintage1962 | hydro | TRUE | 19375 | USCE-Savannah District | 754 | Hartwell Lake | GA | Hart | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 85 | 0.9 | 85 | 85 | 30 | N |  |  | OP | X | 4 | 1962 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M | [23 empty] | N
Vintage1962 | hydro | TRUE | 19375 | USCE-Savannah District | 754 | Hartwell Lake | GA | Hart | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 85 | 0.9 | 85 | 85 | 30 | N |  |  | OS | X | 4 | 1962 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M | [23 empty] | N
Vintage1962 | hydro | TRUE | 19375 | USCE-Savannah District | 754 | Hartwell Lake | GA | Hart | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 85 | 0.9 | 70 | 70 | 55 | N |  |  | OP | X | 4 | 1962 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M | [23 empty] | N
Vintage1983 | hydro | TRUE | 19375 | USCE-Savannah District | 754 | Hartwell Lake | GA | Hart | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 80 | 0.95 | 80 | 80 | 25 | N |  |  | OP | X | 11 | 1983 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1931 | hydro | TRUE | 18642 | Tennessee Valley Authority | 757 | Blue Ridge | GA | Fannin | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 22 | 0.8 | 16 | 13.4 | 7.2 | N |  |  | OP | X | 7 | 1931 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1994 | hydro | TRUE | 18642 | Tennessee Valley Authority | 757 | Blue Ridge | GA | Fannin | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 0.8 | 1.3 | 1.3 | 1 | N |  |  | OP | X | 9 | 1994 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1956 | hydro | TRUE | 18642 | Tennessee Valley Authority | 758 | Nottely | GA | Union | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.9 | 19.2 | 18.4 | 13.6 | N |  |  | OP | X | 1 | 1956 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1993 | hydro | TRUE | 18642 | Tennessee Valley Authority | 758 | Nottely | GA | Union | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | N |  |  | OP | X | 8 | 1993 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage2003 | hydro | TRUE | 27813 | USCE-Mobile District | 759 | Buford | GA | Forsyth | 1A | Conventional Hydroelectric | HY |  | S | X | X |  |  | 62 | 0.95 | 60 | 60 | 35 | N |  |  | OP | X | 12 | 2003 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage2004 | hydro | TRUE | 27813 | USCE-Mobile District | 759 | Buford | GA | Forsyth | 2A | Conventional Hydroelectric | HY |  | S | X | X |  |  | 62 | 0.95 | 60 | 60 | 35 | N |  |  | OP | X | 12 | 2004 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage2005 | hydro | TRUE | 27813 | USCE-Mobile District | 759 | Buford | GA | Forsyth | 3A | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7.2 | 0.95 | 6.8 | 6.6 | 6.6 | N |  |  | OP | X | 2 | 2005 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1950 | hydro | TRUE | 27813 | USCE-Mobile District | 760 | Allatoona | GA | Bartow | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 42.3 | 0.95 | 35 | 35 | 20 | N |  |  | OP | X | 1 | 1950 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage1950 | hydro | TRUE | 27813 | USCE-Mobile District | 760 | Allatoona | GA | Bartow | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 42.3 | 0.95 | 35 | 35 | 20 | N |  |  | OP | X | 3 | 1950 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage1950 | hydro | TRUE | 27813 | USCE-Mobile District | 760 | Allatoona | GA | Bartow | A | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.95 | 2 | 2 | 2 | N |  |  | OP | X | 2 | 1950 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage1963 | hydro | TRUE | 27813 | USCE-Mobile District | 761 | Walter F George | GA | Clay | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 42 | 0.95 | 42 | 42 | 40 | N |  |  | OP | X | 3 | 1963 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage1963 | hydro | TRUE | 27813 | USCE-Mobile District | 761 | Walter F George | GA | Clay | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 42 | 0.95 | 42 | 42 | 40 | N |  |  | OP | X | 5 | 1963 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage1963 | hydro | TRUE | 27813 | USCE-Mobile District | 761 | Walter F George | GA | Clay | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 42 | 0.95 | 42 | 42 | 40 | N |  |  | OP | X | 9 | 1963 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage1963 | hydro | TRUE | 27813 | USCE-Mobile District | 761 | Walter F George | GA | Clay | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 42 | 0.95 | 42 | 42 | 40 | N |  |  | OP | X | 11 | 1963 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage1977 | natural gas steam turbine | TRUE | 14077 | Oklahoma Municipal Power Authority | 762 | Ponca | OK | Kay | 2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 48 | 0.85 | 34 | 34 | 5 | N |  |  | OS | X | 10 | 1977 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1963 | petroleum | TRUE | 19547 | Hawaiian Electric Co Inc | 765 | Kahe | HI | Honolulu | K1 | Petroleum Liquids | ST |  | S | X | X |  |  | 81.6 | 0.8 | 77.9 | 77.9 | 20 | N |  |  | OP | X | 3 | 1963 |  |  | N | Electric Utility | 1 | X | RFO | [5 empty] | PG | [6 empty] | 12H | [23 empty] | N | N
Vintage1964 | petroleum | TRUE | 19547 | Hawaiian Electric Co Inc | 765 | Kahe | HI | Honolulu | K2 | Petroleum Liquids | ST |  | S | X | X |  |  | 81.6 | 0.8 | 78.1 | 78.1 | 30 | N |  |  | OP | X | 9 | 1964 |  |  | N | Electric Utility | 1 | X | RFO | [5 empty] | PG | [6 empty] | 12H | [23 empty] | N | N
Vintage1970 | petroleum | TRUE | 19547 | Hawaiian Electric Co Inc | 765 | Kahe | HI | Honolulu | K3 | Petroleum Liquids | ST |  | S | X | X |  |  | 85.8 | 0.8 | 82.1 | 82.1 | 20 | N |  |  | OP | X | 8 | 1970 |  |  | N | Electric Utility | 1 | X | RFO | [5 empty] | DFO | [6 empty] | 12H | [23 empty] | N | N | N
Vintage1972 | petroleum | TRUE | 19547 | Hawaiian Electric Co Inc | 765 | Kahe | HI | Honolulu | K4 | Petroleum Liquids | ST |  | S | X | X |  |  | 90.9 | 0.8 | 87.2 | 87.2 | 20 | N |  |  | OP | X | 6 | 1972 |  |  | N | Electric Utility | 1 | X | RFO | [5 empty] | DFO | [6 empty] | 12H | [23 empty] | N | N
Vintage1974 | petroleum | TRUE | 19547 | Hawaiian Electric Co Inc | 765 | Kahe | HI | Honolulu | K5 | Petroleum Liquids | ST |  | S | X | X |  |  | 134.9 | 0.8 | 128.1 | 128.1 | 55 | N |  |  | OP | X | 12 | 1974 |  |  | N | Electric Utility | 1 | X | RFO | [5 empty] | DFO | [6 empty] | 12H | [23 empty] | N
Vintage1981 | petroleum | TRUE | 19547 | Hawaiian Electric Co Inc | 765 | Kahe | HI | Honolulu | K6 | Petroleum Liquids | ST |  | S | X | X |  |  | 134.9 | 0.8 | 128.7 | 128.7 | 45 | N |  |  | OP | X | 3 | 1981 |  |  | N | Electric Utility | 1 | X | RFO | [5 empty] | DFO | [6 empty] | 12H | [23 empty] | N
Vintage1973 | petroleum | TRUE | 19547 | Hawaiian Electric Co Inc | 766 | Waiau | HI | Honolulu | W10 | Petroleum Liquids | GT |  | S | X | X |  |  | 51.3 | 0.8 | 51.2 | 51.2 | 6 | N |  |  | OP | X | 12 | 1973 |  |  | N | Electric Utility | 1 | X | DFO | [12 empty] | 12H | [23 empty] | N
Vintage1947 | petroleum | TRUE | 19547 | Hawaiian Electric Co Inc | 766 | Waiau | HI | Honolulu | W3 | Petroleum Liquids | ST |  | S | X | X |  |  | 50 | 0.8 | 47.2 | 47.2 | 20 | N |  |  | OP | X | 12 | 1947 |  |  | N | Electric Utility | 1 | X | RFO | [5 empty] | PG | [6 empty] | 12H | [23 empty] | N
Vintage1950 | petroleum | TRUE | 19547 | Hawaiian Electric Co Inc | 766 | Waiau | HI | Honolulu | W4 | Petroleum Liquids | ST |  | S | X | X |  |  | 50 | 0.8 | 47.7 | 47.7 | 20 | N |  |  | OP | X | 10 | 1950 |  |  | N | Electric Utility | 1 | X | RFO | [5 empty] | PG | [6 empty] | 12H | [23 empty] | N
Vintage1959 | petroleum | TRUE | 19547 | Hawaiian Electric Co Inc | 766 | Waiau | HI | Honolulu | W5 | Petroleum Liquids | ST |  | S | X | X |  |  | 54.4 | 0.8 | 51.9 | 51.9 | 23 | N |  |  | OP | X | 9 | 1959 |  |  | N | Electric Utility | 1 | X | RFO | [5 empty] | DFO | [6 empty] | 12H | [23 empty] | N
Vintage1961 | petroleum | TRUE | 19547 | Hawaiian Electric Co Inc | 766 | Waiau | HI | Honolulu | W6 | Petroleum Liquids | ST |  | S | X | X |  |  | 54.4 | 0.8 | 51.8 | 51.8 | 20 | N |  |  | OP | X | 6 | 1961 |  |  | N | Electric Utility | 1 | X | RFO | [5 empty] | DFO | [6 empty] | 12H | [23 empty] | N | N
Vintage1966 | petroleum | TRUE | 19547 | Hawaiian Electric Co Inc | 766 | Waiau | HI | Honolulu | W7 | Petroleum Liquids | ST |  | S | X | X |  |  | 81.6 | 0.8 | 77.8 | 77.8 | 20 | N |  |  | OP | X | 10 | 1966 |  |  | N | Electric Utility | 1 | X | RFO | [5 empty] | DFO | [6 empty] | 12H | [23 empty] | N | N
Vintage1968 | petroleum | TRUE | 19547 | Hawaiian Electric Co Inc | 766 | Waiau | HI | Honolulu | W8 | Petroleum Liquids | ST |  | S | X | X |  |  | 81.6 | 0.8 | 77.8 | 77.8 | 20 | N |  |  | OP | X | 11 | 1968 |  |  | N | Electric Utility | 1 | X | RFO | [5 empty] | DFO | [6 empty] | 12H | [23 empty] | N | N
Vintage1973 | petroleum | TRUE | 19547 | Hawaiian Electric Co Inc | 766 | Waiau | HI | Honolulu | W9 | Petroleum Liquids | GT |  | S | X | X |  |  | 51.3 | 0.8 | 51.2 | 51.2 | 6 | N |  |  | OP | X | 6 | 1973 |  |  | N | Electric Utility | 1 | X | DFO | [12 empty] | 12H | [23 empty] | N | N
Vintage1970 | petroleum | TRUE | 8287 | Hawaii Electric Light Co Inc | 768 | Waimea | HI | Hawaii | 12 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 12 | 1970 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1972 | petroleum | TRUE | 8287 | Hawaii Electric Light Co Inc | 768 | Waimea | HI | Hawaii | 13 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 5 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N
Vintage1972 | petroleum | TRUE | 8287 | Hawaii Electric Light Co Inc | 768 | Waimea | HI | Hawaii | 14 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 5 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1962 | petroleum | TRUE | 8287 | Hawaii Electric Light Co Inc | 769 | Kanoelehua | HI | Hawaii | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.9 | 2 | 2 | 2 | N |  |  | OP | X | 9 | 1962 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1972 | petroleum | TRUE | 8287 | Hawaii Electric Light Co Inc | 769 | Kanoelehua | HI | Hawaii | 15 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 8 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1972 | petroleum | TRUE | 8287 | Hawaii Electric Light Co Inc | 769 | Kanoelehua | HI | Hawaii | 16 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 8 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1973 | petroleum | TRUE | 8287 | Hawaii Electric Light Co Inc | 769 | Kanoelehua | HI | Hawaii | 17 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 12 | 1973 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1962 | petroleum | TRUE | 8287 | Hawaii Electric Light Co Inc | 769 | Kanoelehua | HI | Hawaii | CT1 | Petroleum Liquids | GT |  | S | X | X |  |  | 11.5 | 0.9 | 10.5 | 10.5 | 2.5 | N |  |  | OP | X | 1 | 1962 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1918 | hydro | TRUE | 8287 | Hawaii Electric Light Co Inc | 771 | Puueo | HI | Hawaii | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.9 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 12 | 1918 |  |  | N | Electric Utility | 1 | X | WAT | [10 empty] | N |  | 1H | [23 empty] | N
Vintage2005 | hydro | TRUE | 8287 | Hawaii Electric Light Co Inc | 771 | Puueo | HI | Hawaii | 2A | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.9 | 2.4 | 2.4 | 0.3 | N |  |  | OP | X | 10 | 2005 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1965 | petroleum | TRUE | 8287 | Hawaii Electric Light Co Inc | 772 | W H Hill | HI | Hawaii | 5 | Petroleum Liquids | ST |  | S | X | X |  |  | 14.1 | 0.9 | 14.1 | 14.1 | 5 | N |  |  | OP | X | 12 | 1965 |  |  | N | Electric Utility | 1 | X | RFO | DFO |  |  |  |  | PG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1974 | petroleum | TRUE | 8287 | Hawaii Electric Light Co Inc | 772 | W H Hill | HI | Hawaii | 6 | Petroleum Liquids | ST |  | S | X | X |  |  | 23 | 0.9 | 21.4 | 21.4 | 8 | N |  |  | OP | X | 12 | 1974 |  |  | N | Electric Utility | 1 | X | RFO | DFO |  |  |  |  | DFO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1921 | hydro | TRUE | 8287 | Hawaii Electric Light Co Inc | 774 | Waiau Hydro | HI | Hawaii | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.9 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 12 | 1921 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [15 empty] | HY | WAT | 1.5 | 12 | 2022 |  |  |  | N
Vintage1928 | hydro | TRUE | 8287 | Hawaii Electric Light Co Inc | 774 | Waiau Hydro | HI | Hawaii | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.9 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 12 | 1928 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1983 | hydro | TRUE | 14191 | South Feather Water and Power Agency | 776 | Sly Creek | CA | Butte | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 12.1 | 0.9 | 12.1 | 12.1 | 0 | N |  |  | OP | X | 7 | 1983 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1984 | hydro | TRUE | 3271 | Central Nebraska Pub P&I Dist | 785 | Kingsley | NE | Keith | 1 | Conventional Hydroelectric | HY |  | S | X | X | NPPDKINGSLEYUN1 | NPPDKINGSLEYUN1 | 50 | 0.95 | 41 | 41 | 5 | N |  |  | OP | X | 11 | 1984 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1984 | hydro | TRUE | 7601 | Green Mountain Power Corp | 788 | East Barnet | VT | Caledonia | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 0.8 | 1.9 | 1.9 | 0.2 | N |  |  | OP | X | 9 | 1984 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1984 | petroleum | TRUE | 40215 | Cordova Electric Coop, Inc | 789 | Orca | AK | Valdez Cordova | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 1.5 | N |  |  | OP | X | 10 | 1984 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N
Vintage1984 | petroleum | TRUE | 40215 | Cordova Electric Coop, Inc | 789 | Orca | AK | Valdez Cordova | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.4 | 0.8 | 2.4 | 2.4 | 1.4 | N |  |  | OP | X | 10 | 1984 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2000 | petroleum | TRUE | 40215 | Cordova Electric Coop, Inc | 789 | Orca | AK | Valdez Cordova | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.7 | N |  |  | OP | X | 3 | 2000 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2000 | petroleum | TRUE | 40215 | Cordova Electric Coop, Inc | 789 | Orca | AK | Valdez Cordova | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.7 | N |  |  | OP | X | 3 | 2000 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2009 | petroleum | TRUE | 40215 | Cordova Electric Coop, Inc | 789 | Orca | AK | Valdez Cordova | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.6 | 0.8 | 3.6 | 3.6 | 2.2 | N |  |  | OP | X | 7 | 2009 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1988 | hydro | TRUE | 9187 | City of Idaho Falls - (ID) | 790 | Gem State | ID | Bonneville | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 23.4 | 0.9 | 23.4 | 23.4 | 23.4 | N |  |  | OP | X | 11 | 1988 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1989 | hydro | TRUE | 7751 | Guadalupe Blanco River Authority | 791 | Canyon | TX | Comal | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.9 | 3 | 3 | 1 | N |  |  | OP | X | 1 | 1989 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1989 | hydro | TRUE | 7751 | Guadalupe Blanco River Authority | 791 | Canyon | TX | Comal | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.9 | 3 | 3 | 1 | N |  |  | OP | X | 1 | 1989 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1982 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 792 | Palaau Power Hybrid | HI | Maui | 15 | Petroleum Liquids | GT |  | S | X | X |  |  | 2.5 | 0.8 | 2 | 2 | 0.5 | N |  |  | SB | Y | 4 | 1982 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1996 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 792 | Palaau Power Hybrid | HI | Maui | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.2 | 0.8 | 2 | 2 | 0.3 | N |  |  | OP | X | 6 | 1996 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1996 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 792 | Palaau Power Hybrid | HI | Maui | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.2 | 0.8 | 2 | 2 | 0.3 | N |  |  | OP | X | 6 | 1996 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1996 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 792 | Palaau Power Hybrid | HI | Maui | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.2 | 0.8 | 2 | 2 | 0.3 | N |  |  | OP | X | 6 | 1996 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2017 | other | TRUE | 11843 | Maui Electric Co Ltd | 792 | Palaau Power Hybrid | HI | Maui | BAT1 | Batteries | BA |  | S | X | X |  |  | 2 |  | 2 | 2 | 0 | N |  |  | OP | X | 5 | 2017 |  |  | N | Electric Utility | 1 | X | MWH | [9 empty] | N |  |  | 10M
Vintage1985 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 792 | Palaau Power Hybrid | HI | Maui | CAT1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 0.3 | N |  |  | OP | X | 5 | 1985 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N | N | N
Vintage1985 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 792 | Palaau Power Hybrid | HI | Maui | CAT2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 0.3 | N |  |  | OP | X | 5 | 1985 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N | N | N
Vintage1985 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 792 | Palaau Power Hybrid | HI | Maui | CUM3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.9 | 0.9 | 0.3 | N |  |  | OP | X | 4 | 1985 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N | N | N
Vintage1985 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 792 | Palaau Power Hybrid | HI | Maui | CUM4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.9 | 0.9 | 0.3 | N |  |  | OP | X | 4 | 1985 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N | N | N
Vintage1985 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 792 | Palaau Power Hybrid | HI | Maui | CUM5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.9 | 0.9 | 0.3 | N |  |  | OP | X | 4 | 1985 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N | N | N
Vintage1991 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 792 | Palaau Power Hybrid | HI | Maui | CUM6 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.9 | 0.9 | 0.3 | N |  |  | OP | X | 12 | 1991 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N | N | N
Vintage1992 | hydro | TRUE | 6958 | City of Garland - (TX) | 794 | Lewisville | TX | Denton | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.8 | 0.9 | 2 | 2 | 0.5 | N |  |  | OP | X | 1 | 1992 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 1H
Vintage1990 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 805 | Charles E Monty | ME | Androscoggin | M-1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 14.2 | 0.9 | 14 | 14 | 0.2 | N |  |  | OP | X | 1 | 1990 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1990 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 805 | Charles E Monty | ME | Androscoggin | M2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 14.2 | 0.9 | 14 | 14 | 0.2 | N |  |  | OP | X | 1 | 1990 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 10M
Vintage1991 | hydro | TRUE | 15296 | New York Power Authority | 808 | Jarvis (Hinckley) | NY | Oneida | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.5 | 1 | 4.5 | 4.5 | 1 | N |  |  | OP | X | 7 | 1991 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1991 | hydro | TRUE | 15296 | New York Power Authority | 808 | Jarvis (Hinckley) | NY | Oneida | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.5 | 1 | 4.5 | 4.5 | 1 | N |  |  | OP | X | 7 | 1991 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1978 | hydro | TRUE | 9191 | Idaho Power Co | 809 | American Falls | ID | Power | 1 | Conventional Hydroelectric | HY |  | S | X | X | AFPR_1_TOT_GEN-APND | AFPR_1_TOT_GEN | 30.8 | 0.9 | 32 | 17.5 | 0 | N |  |  | OP | X | 7 | 1978 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [20 empty] | Y | 7 | 2023 | N
Vintage1978 | hydro | TRUE | 9191 | Idaho Power Co | 809 | American Falls | ID | Power | 2 | Conventional Hydroelectric | HY |  | S | X | X | AFPR_1_TOT_GEN-APND | AFPR_1_TOT_GEN | 30.8 | 0.9 | 31.5 | 15.1 | 0 | N |  |  | OP | X | 6 | 1978 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [20 empty] | Y | 1 | 2024 | N
Vintage1978 | hydro | TRUE | 9191 | Idaho Power Co | 809 | American Falls | ID | Power | 3 | Conventional Hydroelectric | HY |  | S | X | X | AFPR_1_TOT_GEN-APND | AFPR_1_TOT_GEN | 30.8 | 0.9 | 31.8 | 17.6 | 0 | N |  |  | OP | X | 3 | 1978 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [20 empty] | Y | 7 | 2024 | N
Vintage1949 | hydro | TRUE | 9191 | Idaho Power Co | 810 | Bliss | ID | Gooding | 1 | Conventional Hydroelectric | HY |  | S | X | X | BSPO_1_TOT_GEN-APNDBSPO_1_TOT_GEN-APND | BSPO_1_TOT_GEN | 25 | 0.87 | 32 | 25.2 | 0 | N |  |  | OP | X | 11 | 1949 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [20 empty] | Y | 1 | 2026 | N
Vintage1950 | hydro | TRUE | 9191 | Idaho Power Co | 810 | Bliss | ID | Gooding | 2 | Conventional Hydroelectric | HY |  | S | X | X | BSPO_1_TOT_GEN-APND | BSPO_1_TOT_GEN | 25 | 0.87 | 25.8 | 22.4 | 0 | N |  |  | OP | X | 1 | 1950 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [20 empty] | Y | 1 | 2027 | N
Vintage1950 | hydro | TRUE | 9191 | Idaho Power Co | 810 | Bliss | ID | Gooding | 3 | Conventional Hydroelectric | HY |  | S | X | X | BSPO_1_TOT_GEN-APND | BSPO_1_TOT_GEN | 25 | 0.87 | 22.4 | 22.5 | 0 | N |  |  | OP | X | 3 | 1950 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1959 | hydro | TRUE | 9191 | Idaho Power Co | 811 | Brownlee | ID | Washington | 1 | Conventional Hydroelectric | HY |  | S | X | X | BLPR_GNODE011 | BLPR_2_G011 | 112.5 | 0.9 | 114 | 116.1 | 0 | N |  |  | OP | X | 1 | 1959 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1958 | hydro | TRUE | 9191 | Idaho Power Co | 811 | Brownlee | ID | Washington | 2 | Conventional Hydroelectric | HY |  | S | X | X | BLPR_GNODE012 | BLPR_2_G012 | 112.5 | 0.9 | 104.6 | 109 | 0 | N |  |  | OP | X | 12 | 1958 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1958 | hydro | TRUE | 9191 | Idaho Power Co | 811 | Brownlee | ID | Washington | 3 | Conventional Hydroelectric | HY |  | S | X | X | BLPR_GNODE013 | BLPR_2_G013 | 112.5 | 0.9 | 104.2 | 107.9 | 0 | N |  |  | OP | X | 10 | 1958 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1958 | hydro | TRUE | 9191 | Idaho Power Co | 811 | Brownlee | ID | Washington | 4 | Conventional Hydroelectric | HY |  | S | X | X | BLPR_GNODE014 | BLPR_2_G014 | 112.5 | 0.9 | 108.8 | 119.3 | 0 | N |  |  | OP | X | 8 | 1958 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1980 | hydro | TRUE | 9191 | Idaho Power Co | 811 | Brownlee | ID | Washington | 5 | Conventional Hydroelectric | HY |  | S | X | X | BLPR_GNODE015 | BLPR_2_G015 | 225 | 0.9 | 241.7 | 233.2 | 0 | N |  |  | OP | X | 3 | 1980 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1952 | hydro | TRUE | 9191 | Idaho Power Co | 812 | C J Strike | ID | Owyhee | 1 | Conventional Hydroelectric | HY |  | S | X | X | SKPR_GNODE011 | SKPR_1_G011 | 27.6 | 0.92 | 31.2 | 31.2 | 0 | N |  |  | OP | X | 3 | 1952 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1952 | hydro | TRUE | 9191 | Idaho Power Co | 812 | C J Strike | ID | Owyhee | 2 | Conventional Hydroelectric | HY |  | S | X | X | SKPR_GNODE012 | SKPR_1_G012 | 27.6 | 0.92 | 30.3 | 30.2 | 0 | N |  |  | OP | X | 3 | 1952 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [20 empty] | Y | 1 | 2025 | N
Vintage1952 | hydro | TRUE | 9191 | Idaho Power Co | 812 | C J Strike | ID | Owyhee | 3 | Conventional Hydroelectric | HY |  | S | X | X | SKPR_GNODE013 | SKPR_1_G013 | 27.6 | 0.92 | 31.3 | 31.5 | 0 | N |  |  | OP | X | 3 | 1952 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1984 | hydro | TRUE | 9191 | Idaho Power Co | 813 | Cascade Dam | ID | Valley | 1 | Conventional Hydroelectric | HY |  | S | X | X | CDPO_6_TOT_GEN-APND | CDPO_6_TOT_GEN | 6.2 | 0.9 | 6.4 | 2.9 | 0 | N |  |  | OP | X | 5 | 1984 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1983 | hydro | TRUE | 9191 | Idaho Power Co | 813 | Cascade Dam | ID | Valley | 2 | Conventional Hydroelectric | HY |  | S | X | X | CDPO_6_TOT_GEN-APND | CDPO_6_TOT_GEN | 6.2 | 0.9 | 6.4 | 1.7 | 0 | N |  |  | OP | X | 12 | 1983 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1937 | hydro | TRUE | 9191 | Idaho Power Co | 814 | Clear Lake | ID | Gooding | 1 | Conventional Hydroelectric | HY |  | S | X | X | CLPR_GNODE001 | CLPR_7_G001 | 2.5 | 0.8 | 2.2 | 2.2 | 0 | N |  |  | OP | X | 12 | 1937 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1948 | hydro | TRUE | 9191 | Idaho Power Co | 815 | Lower Malad | ID | Gooding | 1 | Conventional Hydroelectric | HY |  | S | X | X | LMPR_GNODE001 | LMPR_1_G001 | 13.5 | 0.871 | 13.3 | 13.4 | 0 | N |  |  | OP | X | 10 | 1948 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1949 | hydro | TRUE | 9191 | Idaho Power Co | 816 | Lower Salmon | ID | Gooding | 1 | Conventional Hydroelectric | HY |  | S | X | X | LSPR_1_TOT_GEN-APND | LSPR_1_TOT_GEN | 15 | 0.86 | 13.6 | 14 | 0 | N |  |  | OA | X | 7 | 1949 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [20 empty] | Y | 6 | 2022 | N
Vintage1949 | hydro | TRUE | 9191 | Idaho Power Co | 816 | Lower Salmon | ID | Gooding | 2 | Conventional Hydroelectric | HY |  | S | X | X | LSPR_1_TOT_GEN-APND | LSPR_1_TOT_GEN | 15 | 0.86 | 14.4 | 12.9 | 0 | N |  |  | OP | X | 9 | 1949 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1949 | hydro | TRUE | 9191 | Idaho Power Co | 816 | Lower Salmon | ID | Gooding | 3 | Conventional Hydroelectric | HY |  | S | X | X | LSPR_1_TOT_GEN-APND | LSPR_1_TOT_GEN | 15 | 0.86 | 16.6 | 16.4 | 0 | N |  |  | OP | X | 2 | 1949 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [20 empty] | Y | 6 | 2022 | N
Vintage1949 | hydro | TRUE | 9191 | Idaho Power Co | 816 | Lower Salmon | ID | Gooding | 4 | Conventional Hydroelectric | HY |  | S | X | X | LSPR_1_TOT_GEN-APND | LSPR_1_TOT_GEN | 15 | 0.86 | 16.7 | 18.2 | 0 | N |  |  | OP | X | 3 | 1949 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1967 | petroleum | TRUE | 9191 | Idaho Power Co | 817 | Salmon Diesel | ID | Lemhi | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.7 | 2.7 | 0 | N |  |  | SB | Y | 12 | 1967 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1967 | petroleum | TRUE | 9191 | Idaho Power Co | 817 | Salmon Diesel | ID | Lemhi | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.7 | 2.7 | 0 | N |  |  | SB | Y | 12 | 1967 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1921 | hydro | TRUE | 9191 | Idaho Power Co | 818 | Shoshone Falls | ID | Jerome | 3 | Conventional Hydroelectric | HY |  | S | X | X | SFPR_GNODE003 | SFPR_7_G003 | 11.5 | 0.833 | 0.4 | 0.6 | 0 | N |  |  | OP | X | 8 | 1921 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage2020 | hydro | TRUE | 9191 | Idaho Power Co | 818 | Shoshone Falls | ID | Jerome | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.2 | 0.9 | 3 | 2.8 | 0 | N |  |  | OP | X | 9 | 2020 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1994 | hydro | TRUE | 9191 | Idaho Power Co | 819 | Swan Falls | ID | Ada | 1 | Conventional Hydroelectric | HY |  | S | X | X | SWPO_1_TOT_GEN-APND | SWPO_1_TOT_GEN | 12.5 | 0.95 | 14 | 13.3 | 0 | N |  |  | OP | X | 3 | 1994 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1994 | hydro | TRUE | 9191 | Idaho Power Co | 819 | Swan Falls | ID | Ada | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 12.5 | 0.95 | 13.9 | 13.3 | 0 | N |  |  | OP | X | 5 | 1994 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1920 | hydro | TRUE | 9191 | Idaho Power Co | 820 | Thousand Springs | ID | Gooding | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.8 | 0.8 | 5.7 | 6.4 | 0 | N |  |  | OP | X | 5 | 1920 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1935 | hydro | TRUE | 9191 | Idaho Power Co | 821 | Twin Falls (ID) | ID | Twin Falls | 1 | Conventional Hydroelectric | HY |  | S | X | X | TFPR_1_TOT_GEN-APND | TFPR_1_TOT_GEN | 8.4 | 0.9 | 10.1 | 9.6 | 0 | N |  |  | OP | X | 3 | 1935 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1995 | hydro | TRUE | 9191 | Idaho Power Co | 821 | Twin Falls (ID) | ID | Twin Falls | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 44.3 | 0.95 | 32.1 | 24.4 | 0 | N |  |  | OP | X | 7 | 1995 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1937 | hydro | TRUE | 9191 | Idaho Power Co | 822 | Upper Salmon A | ID | Twin Falls | 1 | Conventional Hydroelectric | HY |  | S | X | X | US12_1_TOT_A_GEN-APND | US12_1_TOT_A_GEN | 9 | 1 | 9.1 | 9.3 | 0 | N |  |  | OP | X | 9 | 1937 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [20 empty] | Y | 5 | 2029 | N
Vintage1937 | hydro | TRUE | 9191 | Idaho Power Co | 822 | Upper Salmon A | ID | Twin Falls | 2 | Conventional Hydroelectric | HY |  | S | X | X | S12_1_TOT_A_GEN-APND | US12_1_TOT_A_GEN | 9 | 1 | 8.2 | 8.3 | 0 | N |  |  | OP | X | 9 | 1937 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [20 empty] | Y | 5 | 2030 | N
Vintage1948 | hydro | TRUE | 9191 | Idaho Power Co | 823 | Upper Malad | ID | Gooding | 1 | Conventional Hydroelectric | HY |  | S | X | X | UMPR_GNODE001 | UMPR_7_G001 | 8.3 | 0.857 | 6.8 | 7.4 | 0 | N |  |  | OP | X | 6 | 1948 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1917 | hydro | TRUE | 14354 | PacifiCorp | 825 | Ashton | ID | Fremont | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.7 | 0.9 | 2.7 | 2.7 | 0 | N |  |  | OP | X | 7 | 1917 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1925 | hydro | TRUE | 14354 | PacifiCorp | 825 | Ashton | ID | Fremont | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.8 | 2.2 | 2.2 | 0 | N |  |  | OP | X | 7 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1925 | hydro | TRUE | 14354 | PacifiCorp | 825 | Ashton | ID | Fremont | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.8 | 2.2 | 2.2 | 0 | N |  |  | OP | X | 7 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1923 | hydro | TRUE | 14354 | PacifiCorp | 827 | Grace | ID | Caribou | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 11 | 0.9 | 11 | 11 | 0 | N |  |  | OP | X | 7 | 1923 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1923 | hydro | TRUE | 14354 | PacifiCorp | 827 | Grace | ID | Caribou | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 11 | 0.9 | 11 | 11 | 0 | N |  |  | OP | X | 7 | 1923 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1923 | hydro | TRUE | 14354 | PacifiCorp | 827 | Grace | ID | Caribou | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 11 | 0.9 | 11 | 11 | 0 | N |  |  | OP | X | 7 | 1923 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1915 | hydro | TRUE | 14354 | PacifiCorp | 829 | Oneida | ID | Franklin | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 0.9 | 9.3 | 9.3 | 0 | N |  |  | OP | X | 7 | 1915 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1916 | hydro | TRUE | 14354 | PacifiCorp | 829 | Oneida | ID | Franklin | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 0.9 | 9.3 | 9.3 | 0 | N |  |  | OP | X | 7 | 1916 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1920 | hydro | TRUE | 14354 | PacifiCorp | 829 | Oneida | ID | Franklin | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 0.9 | 9.3 | 9.3 | 0 | N |  |  | OP | X | 7 | 1920 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1924 | hydro | TRUE | 14354 | PacifiCorp | 831 | Soda | ID | Caribou | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7.6 | 0.855 | 7.6 | 7.6 | 0 | N |  |  | OP | X | 7 | 1924 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1924 | hydro | TRUE | 14354 | PacifiCorp | 831 | Soda | ID | Caribou | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7 | 0.855 | 7.6 | 7.6 | 0 | N |  |  | OP | X | 7 | 1924 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1953 | hydro | TRUE | 20169 | Avista Corp | 833 | Cabinet Gorge | ID | Bonner | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 59.4 | 0.9 | 44.3 | 66.5 | 18 | N |  |  | OP | X | 8 | 1953 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1953 | hydro | TRUE | 20169 | Avista Corp | 833 | Cabinet Gorge | ID | Bonner | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 73.2 | 0.9 | 73.9 | 79.8 | 30 | N |  |  | OP | X | 2 | 1953 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1952 | hydro | TRUE | 20169 | Avista Corp | 833 | Cabinet Gorge | ID | Bonner | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 73.2 | 0.9 | 73.4 | 80.2 | 30 | N |  |  | OP | X | 11 | 1952 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1952 | hydro | TRUE | 20169 | Avista Corp | 833 | Cabinet Gorge | ID | Bonner | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 59.4 | 0.9 | 63 | 68.3 | 20 | N |  |  | OP | X | 9 | 1952 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1907 | hydro | TRUE | 20169 | Avista Corp | 835 | Post Falls | ID | Kootenai | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 1 | 2.8 | 2.9 | 0.3 | N |  |  | OP | X | 12 | 1907 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1906 | hydro | TRUE | 20169 | Avista Corp | 835 | Post Falls | ID | Kootenai | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 1 | 2.8 | 2.9 | 0.3 | N |  |  | OP | X | 7 | 1906 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1906 | hydro | TRUE | 20169 | Avista Corp | 835 | Post Falls | ID | Kootenai | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 1 | 2.8 | 2.9 | 0.3 | N |  |  | OP | X | 8 | 1906 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1906 | hydro | TRUE | 20169 | Avista Corp | 835 | Post Falls | ID | Kootenai | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 1 | 2.8 | 2.9 | 0.3 | N |  |  | OP | X | 11 | 1906 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1908 | hydro | TRUE | 20169 | Avista Corp | 835 | Post Falls | ID | Kootenai | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 1 | 2.8 | 2.9 | 0.3 | N |  |  | OP | X | 8 | 1908 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1980 | hydro | TRUE | 20169 | Avista Corp | 835 | Post Falls | ID | Kootenai | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.5 | 0.8 | 3.5 | 3.5 | 0.3 | N |  |  | OS | X | 12 | 1980 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1985 | hydro | TRUE | 13402 | Nevada Irrigation District | 839 | Scott Flat | CA | Nevada | 7P | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.99 | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 2 | 1985 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1975 | hydro | TRUE | 19400 | USACE Northwestern Division | 840 | Dworshak | ID | Clearwater | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 103 | 0.95 | 103 | 90 | 90 | N |  |  | OA | X | 6 | 1975 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1975 | hydro | TRUE | 19400 | USACE Northwestern Division | 840 | Dworshak | ID | Clearwater | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 103 | 0.95 | 103 | 90 | 90 | N |  |  | OP | X | 9 | 1975 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1974 | hydro | TRUE | 19400 | USACE Northwestern Division | 840 | Dworshak | ID | Clearwater | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 259 | 0.95 | 259 | 220 | 220 | N |  |  | OP | X | 9 | 1974 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1982 | hydro | TRUE | 9187 | City of Idaho Falls - (ID) | 841 | City Power Plant | ID | Bonneville | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8 | 0.9 | 8 | 8 | 8 | N |  |  | OP | X | 7 | 1982 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1940 | hydro | TRUE | 9187 | City of Idaho Falls - (ID) | 843 | Lower No 2 | ID | Bonneville | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.9 | 3 | 3 | 3 | N |  |  | OP | X | 8 | 1940 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1982 | hydro | TRUE | 9187 | City of Idaho Falls - (ID) | 844 | Upper Power Plant | ID | Bonneville | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8 | 0.9 | 8 | 8 | 8 | N |  |  | OP | X | 9 | 1982 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1984 | hydro | TRUE | 13402 | Nevada Irrigation District | 846 | Combie South | CA | Nevada | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.99 | 0.5 | 0.5 | 0.5 | N |  |  | OP | X | 4 | 1984 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1984 | hydro | TRUE | 13402 | Nevada Irrigation District | 846 | Combie South | CA | Nevada | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.99 | 0.5 | 0.5 | 0.5 | N |  |  | OP | X | 4 | 1984 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1984 | hydro | TRUE | 13402 | Nevada Irrigation District | 846 | Combie South | CA | Nevada | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.99 | 0.5 | 0.5 | 0.5 | N |  |  | OP | X | 4 | 1984 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1957 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 850 | Palisades Dam | ID | Bonneville | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 44.1 | 0.95 | 44.1 | 44.1 | 0 | N |  |  | OP | X | 8 | 1957 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1957 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 850 | Palisades Dam | ID | Bonneville | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 44.1 | 0.95 | 44.1 | 44.1 | 0 | N |  |  | OP | X | 5 | 1957 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1957 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 850 | Palisades Dam | ID | Bonneville | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 44.1 | 0.95 | 44.1 | 44.1 | 0 | N |  |  | OP | X | 2 | 1957 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1958 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 850 | Palisades Dam | ID | Bonneville | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 44.1 | 0.95 | 44.1 | 44.1 | 0 | N |  |  | OP | X | 5 | 1958 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1955 | hydro | TRUE | 19400 | USACE Northwestern Division | 851 | Albeni Falls | ID | Bonner | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 14 | 0.9 | 14 | 14 | 14 | N |  |  | OP | X | 5 | 1955 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1955 | hydro | TRUE | 19400 | USACE Northwestern Division | 851 | Albeni Falls | ID | Bonner | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 14 | 0.9 | 14 | 14 | 14 | N |  |  | OP | X | 6 | 1955 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1955 | hydro | TRUE | 19400 | USACE Northwestern Division | 851 | Albeni Falls | ID | Bonner | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 14 | 0.9 | 14 | 14 | 14 | N |  |  | OP | X | 9 | 1955 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M
Vintage1968 | hard coal | TRUE | 49756 | Illinois Power Resources Generating LLC | 856 | E D Edwards | IL | Peoria | 2 | Conventional Steam Coal | ST |  | S | X | X | AMIL.EDWARDS2 | AMIL.EDWARDS2 | 280.5 | 0.85 | 245 | 255 | 140 | N |  |  | OP | X | 6 | 1968 | 12 | 2022 | N | IPP Non-CHP | 2 | X | SUB | DFO |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1972 | hard coal | TRUE | 49756 | Illinois Power Resources Generating LLC | 856 | E D Edwards | IL | Peoria | 3 | Conventional Steam Coal | ST |  | S | X | X | AMIL.EDWARDS3 | AMIL.EDWARDS3 | 363.8 | 0.85 | 315 | 330 | 175 | N |  |  | OP | X | 6 | 1972 | 12 | 2022 | N | IPP Non-CHP | 2 | X | SUB | DFO |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage2001 | natural gas combined cycle | TRUE | 59371 | Mainline Generation LLC | 862 | Grand Tower Energy Center LLC | IL | Jackson | 1 | Natural Gas Fired Combined Cycle | CT | CC01 | S | X | N | AMIL.CC.GDTWR1 | AMIL.CC.GDTWR1 | 223.2 | 0.9 | 161 | 182 | 110 | N |  |  | OS | X | 6 | 2001 |  |  | N | IPP Non-CHP | 2 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage2001 | natural gas combined cycle | TRUE | 59371 | Mainline Generation LLC | 862 | Grand Tower Energy Center LLC | IL | Jackson | 2 | Natural Gas Fired Combined Cycle | CT | CC02 | S | X | N | AMIL.CC.GDTWR2 | AMIL.CC.GDTWR2 | 223.2 | 0.9 | 159 | 178 | 110 | N |  |  | OS | X | 7 | 2001 |  |  | N | IPP Non-CHP | 2 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage1951 | natural gas combined cycle | TRUE | 59371 | Mainline Generation LLC | 862 | Grand Tower Energy Center LLC | IL | Jackson | 3 | Natural Gas Fired Combined Cycle | CA | CC01 | S | Y | X | AMIL.CC.GDTWR1 | AMIL.CC.GDTWR1 | 80.9 | 0.87 | 86 | 86 | 42 | N |  |  | OS | X | 3 | 1951 |  |  | N | IPP Non-CHP | 2 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage1958 | natural gas combined cycle | TRUE | 59371 | Mainline Generation LLC | 862 | Grand Tower Energy Center LLC | IL | Jackson | 4 | Natural Gas Fired Combined Cycle | CA | CC02 | S | Y | X | AMIL.CC.GDTWR2 | AMIL.CC.GDTWR2 | 113.6 | 0.85 | 105 | 105 | 58 | N |  |  | OS | X | 4 | 1958 |  |  | N | IPP Non-CHP | 2 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage1970 | nuclear | TRUE | 55951 | Exelon Nuclear | 869 | Dresden Generating Station | IL | Grundy | 2 | Nuclear | ST |  | S | X | X | 86101102 | 86101102 | 1009.3 | 0.945 | 902 | 943.9 | 150 | N |  |  | OP | X | 8 | 1970 |  |  | N | IPP Non-CHP | 2 | X | NUC | [9 empty] | N | N |  | OVER | [23 empty] | N
Vintage1971 | nuclear | TRUE | 55951 | Exelon Nuclear | 869 | Dresden Generating Station | IL | Grundy | 3 | Nuclear | ST |  | S | X | X | 86101103 | 86101103 | 1009.3 | 0.945 | 895 | 938.1 | 150 | N |  |  | OP | X | 10 | 1971 |  |  | N | IPP Non-CHP | 2 | X | NUC | [9 empty] | N | N |  | OVER | [23 empty] | N
Vintage1959 | natural gas steam turbine | TRUE | 12384 | Midwest Generations EME LLC | 874 | Joliet 9 | IL | Will | 6 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 360.4 | 0.85 | 314 | 314 | 95 | N |  |  | OP | X | 6 | 1959 |  |  | N | IPP Non-CHP | 2 | X | NG | [5 empty] | NG | [6 empty] | OVER |  | N |  |  | N | [18 empty] | N
Vintage1967 | hard coal | TRUE | 59918 | Dynegy Kincaid Generation | 876 | Kincaid Generation LLC | IL | Christian | 1 | Conventional Steam Coal | ST |  | S | X | X | PJM | PJM | 659.5 | 0.9 | 554 | 554 | 220 | N |  |  | OP | X | 6 | 1967 | 12 | 2027 | N | IPP Non-CHP | 2 | X | RC | SUB |  |  |  |  | NG |  |  |  | N | N |  | OVER |  | N |  | Y | Y | [18 empty] | N | N | N
Vintage1968 | hard coal | TRUE | 59918 | Dynegy Kincaid Generation | 876 | Kincaid Generation LLC | IL | Christian | 2 | Conventional Steam Coal | ST |  | S | X | X | PJM | PJM | 659.5 | 0.9 | 554 | 554 | 220 | N |  |  | OP | X | 6 | 1968 | 12 | 2027 | N | IPP Non-CHP | 2 | X | RC | SUB |  |  |  |  | NG |  |  |  | N | N |  | OVER |  | N |  | Y | Y | [18 empty] | N | N | N
Vintage1972 | hard coal | TRUE | 12384 | Midwest Generations EME LLC | 879 | Powerton | IL | Tazewell | 5 | Conventional Steam Coal | ST |  | S | X | X |  |  | 892.8 | 0.9 | 769 | 769 | 325 | N |  |  | OP | X | 9 | 1972 |  |  | N | IPP Non-CHP | 2 | X | SUB | NG | BIT |  |  |  | NG | [6 empty] | OVER |  | Y |  |  |  | Y | [17 empty] | N
Vintage1975 | hard coal | TRUE | 12384 | Midwest Generations EME LLC | 879 | Powerton | IL | Tazewell | 6 | Conventional Steam Coal | ST |  | S | X | X |  |  | 892.8 | 0.9 | 769 | 769 | 325 | N |  |  | OP | X | 12 | 1975 |  |  | N | IPP Non-CHP | 2 | X | SUB | NG | BIT |  |  |  | NG | [6 empty] | OVER |  | Y |  |  |  | Y | [17 empty] | N
Vintage1972 | nuclear | TRUE | 55951 | Exelon Nuclear | 880 | Quad Cities Generating Station | IL | Rock Island | 1 | Nuclear | ST |  | J | X | X | 86251101 | 86251101 | 1009.3 | 0.945 | 908 | 941.8 | 132 | N |  |  | OP | X | 12 | 1972 |  |  | N | IPP Non-CHP | 2 | X | NUC | [9 empty] | N | N |  | OVER | [23 empty] | N
Vintage1972 | nuclear | TRUE | 55951 | Exelon Nuclear | 880 | Quad Cities Generating Station | IL | Rock Island | 2 | Nuclear | ST |  | J | X | X | 86251102 | 86251102 | 1009.3 | 0.945 | 911 | 941.6 | 132 | N |  |  | OP | X | 12 | 1972 |  |  | N | IPP Non-CHP | 2 | X | NUC | [9 empty] | N | N |  | OVER | [23 empty] | N
Vintage1968 | petroleum | TRUE | 12384 | Midwest Generations EME LLC | 883 | Waukegan | IL | Lake | 311 | Petroleum Liquids | GT |  | S | X | X |  |  | 28 | 0.85 | 24.6 | 33.9 | 10 | N |  |  | SB | Y | 6 | 1968 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1968 | petroleum | TRUE | 12384 | Midwest Generations EME LLC | 883 | Waukegan | IL | Lake | 312 | Petroleum Liquids | GT |  | S | X | X |  |  | 28 | 0.85 | 28.5 | 37.4 | 10 | N |  |  | SB | Y | 6 | 1968 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1968 | petroleum | TRUE | 12384 | Midwest Generations EME LLC | 883 | Waukegan | IL | Lake | 321 | Petroleum Liquids | GT |  | S | X | X |  |  | 28 | 0.85 | 28 | 37.4 | 10 | N |  |  | SB | Y | 6 | 1968 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1968 | petroleum | TRUE | 12384 | Midwest Generations EME LLC | 883 | Waukegan | IL | Lake | 322 | Petroleum Liquids | GT |  | S | X | X |  |  | 28 | 0.85 | 26.7 | 35 | 10 | N |  |  | SB | Y | 6 | 1968 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1958 | hard coal | TRUE | 12384 | Midwest Generations EME LLC | 883 | Waukegan | IL | Lake | 7 | Conventional Steam Coal | ST |  | S | X | X |  |  | 326.4 | 0.85 | 328 | 328 | 130 | N |  |  | OP | X | 6 | 1958 | 6 | 2022 | N | IPP Non-CHP | 2 | X | SUB | NG |  |  |  |  | NG |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1962 | hard coal | TRUE | 12384 | Midwest Generations EME LLC | 883 | Waukegan | IL | Lake | 8 | Conventional Steam Coal | ST |  | S | X | X |  |  | 355.3 | 0.85 | 361 | 361 | 130 | N |  |  | OP | X | 7 | 1962 | 6 | 2022 | N | IPP Non-CHP | 2 | X | SUB | NG |  |  |  |  | NG |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1963 | hard coal | TRUE | 12384 | Midwest Generations EME LLC | 884 | Will County | IL | Will | 4 | Conventional Steam Coal | ST |  | S | X | X |  |  | 598.4 | 0.85 | 510 | 520 | 180 | N |  |  | OP | X | 6 | 1963 | 6 | 2022 | N | IPP Non-CHP | 2 | X | SUB | DFO |  |  |  |  | DFO |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1968 | petroleum | TRUE | 12384 | Midwest Generations EME LLC | 886 | Fisk Street | IL | Cook | 311 | Petroleum Liquids | GT |  | S | X | X |  |  | 32.5 | 0.85 | 25.4 | 34 | 10 | N |  |  | OP | X | 7 | 1968 |  |  | N | IPP Non-CHP | 2 | X | DFO | [12 empty] | 10M | [23 empty] | N
Vintage1968 | petroleum | TRUE | 12384 | Midwest Generations EME LLC | 886 | Fisk Street | IL | Cook | 312 | Petroleum Liquids | GT |  | S | X | X |  |  | 32.5 | 0.85 | 23.7 | 31.6 | 10 | N |  |  | OP | X | 7 | 1968 |  |  | N | IPP Non-CHP | 2 | X | DFO | [12 empty] | 10M | [23 empty] | N
Vintage1968 | petroleum | TRUE | 12384 | Midwest Generations EME LLC | 886 | Fisk Street | IL | Cook | 321 | Petroleum Liquids | GT |  | S | X | X |  |  | 32.5 | 0.85 | 25.4 | 34 | 10 | N |  |  | OP | X | 7 | 1968 |  |  | N | IPP Non-CHP | 2 | X | DFO | [12 empty] | 10M | [23 empty] | N
Vintage1968 | petroleum | TRUE | 12384 | Midwest Generations EME LLC | 886 | Fisk Street | IL | Cook | 322 | Petroleum Liquids | GT |  | S | X | X |  |  | 32.5 | 0.85 | 25.4 | 34 | 10 | N |  |  | OP | X | 7 | 1968 |  |  | N | IPP Non-CHP | 2 | X | DFO | [12 empty] | 10M | [23 empty] | N
Vintage1968 | petroleum | TRUE | 12384 | Midwest Generations EME LLC | 886 | Fisk Street | IL | Cook | 331 | Petroleum Liquids | GT |  | S | X | X |  |  | 32.5 | 0.85 | 23.7 | 31.6 | 10 | N |  |  | OP | X | 7 | 1968 |  |  | N | IPP Non-CHP | 2 | X | DFO | [12 empty] | 10M | [23 empty] | N
Vintage1968 | petroleum | TRUE | 12384 | Midwest Generations EME LLC | 886 | Fisk Street | IL | Cook | 332 | Petroleum Liquids | GT |  | S | X | X |  |  | 32.5 | 0.85 | 25.4 | 34 | 10 | N |  |  | OP | X | 7 | 1968 |  |  | N | IPP Non-CHP | 2 | X | DFO | [12 empty] | 10M | [23 empty] | N
Vintage1968 | petroleum | TRUE | 12384 | Midwest Generations EME LLC | 886 | Fisk Street | IL | Cook | 341 | Petroleum Liquids | GT |  | S | X | X |  |  | 32.5 | 0.85 | 25.4 | 34 | 10 | N |  |  | OS | X | 7 | 1968 |  |  | N | IPP Non-CHP | 2 | X | DFO | [12 empty] | 10M | [23 empty] | N
Vintage1968 | petroleum | TRUE | 12384 | Midwest Generations EME LLC | 886 | Fisk Street | IL | Cook | 342 | Petroleum Liquids | GT |  | S | X | X |  |  | 32.5 | 0.85 | 22.8 | 30.5 | 10 | N |  |  | OP | X | 7 | 1968 |  |  | N | IPP Non-CHP | 2 | X | DFO | [12 empty] | 10M | [23 empty] | N
Vintage1953 | hard coal | TRUE | 5748 | Electric Energy Inc | 887 | Joppa Steam | IL | Massac | 1 | Conventional Steam Coal | ST |  | J | X | X | GLBH | GLBH | 183.3 | 0.85 | 158 | 167 | 47 | N |  |  | OP | X | 8 | 1953 | 8 | 2022 | N | IPP Non-CHP | 2 | X | RC | NG | SUB |  |  |  | NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1953 | hard coal | TRUE | 5748 | Electric Energy Inc | 887 | Joppa Steam | IL | Massac | 2 | Conventional Steam Coal | ST |  | J | X | X | GLBH | GLBH | 183.3 | 0.85 | 158 | 167 | 47 | N |  |  | OP | X | 9 | 1953 | 8 | 2022 | N | IPP Non-CHP | 2 | X | RC | SUB |  |  |  |  | NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1954 | hard coal | TRUE | 5748 | Electric Energy Inc | 887 | Joppa Steam | IL | Massac | 3 | Conventional Steam Coal | ST |  | J | X | X | GLBH | GLBH | 183.3 | 0.85 | 158 | 167 | 47 | N |  |  | OP | X | 5 | 1954 | 8 | 2022 | N | IPP Non-CHP | 2 | X | RC | SUB |  |  |  |  | NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1954 | hard coal | TRUE | 5748 | Electric Energy Inc | 887 | Joppa Steam | IL | Massac | 4 | Conventional Steam Coal | ST |  | J | X | X | GLH.JOPPA4 | GLHJOPPA4 | 183.3 | 0.85 | 158 | 167 | 47 | N |  |  | OP | X | 8 | 1954 | 8 | 2022 | N | IPP Non-CHP | 2 | X | RC | NG | SUB |  |  |  | NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1955 | hard coal | TRUE | 5748 | Electric Energy Inc | 887 | Joppa Steam | IL | Massac | 5 | Conventional Steam Coal | ST |  | J | X | X | GLHJOPPA4 | GLHJOPPA4 | 183.3 | 0.85 | 158 | 167 | 47 | N |  |  | OP | X | 6 | 1955 | 8 | 2022 | N | IPP Non-CHP | 2 | X | RC | SUB |  |  |  |  | NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1955 | hard coal | TRUE | 5748 | Electric Energy Inc | 887 | Joppa Steam | IL | Massac | 6 | Conventional Steam Coal | ST |  | J | X | X | GLHJOPPA4 | GLHJOPPA4 | 183.3 | 0.85 | 158 | 167 | 47 | N |  |  | OP | X | 8 | 1955 | 8 | 2022 | N | IPP Non-CHP | 2 | X | RC | SUB |  |  |  |  | NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1970 | hard coal | TRUE | 5517 | Dynegy Midwest Generation Inc | 889 | Baldwin Energy Complex | IL | Randolph | 1 | Conventional Steam Coal | ST |  | S | X | X | AMIL.BALDW151 | AMIL.BALDW151 | 625.1 | 0.85 | 576 | 590 | 270 | N |  |  | OP | X | 7 | 1970 | 12 | 2025 | N | IPP Non-CHP | 2 | X | RC | SUB | OTH |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | N | N | N
Vintage1973 | hard coal | TRUE | 5517 | Dynegy Midwest Generation Inc | 889 | Baldwin Energy Complex | IL | Randolph | 2 | Conventional Steam Coal | ST |  | S | X | X | AMIL.BALDW152 | AMIL.BALDW152 | 634.5 | 0.9 | 581 | 595 | 400 | N |  |  | OP | X | 3 | 1973 | 12 | 2025 | N | IPP Non-CHP | 2 | X | RC | SUB | OTH |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | N | N | N
Vintage1970 | natural gas peaker | TRUE | 12341 | MidAmerican Energy Co | 899 | Moline | IL | Rock Island | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MEC.MOLCT14 | MEC.MOLCT14 | 18 | 0.85 | 16 | 20 | 2.5 | N |  |  | OP | X | 5 | 1970 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1970 | natural gas peaker | TRUE | 12341 | MidAmerican Energy Co | 899 | Moline | IL | Rock Island | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MEC.MOLCT14 | MEC.MOLCT14 | 18 | 0.85 | 16 | 20 | 2.5 | N |  |  | OP | X | 5 | 1970 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1970 | natural gas peaker | TRUE | 12341 | MidAmerican Energy Co | 899 | Moline | IL | Rock Island | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MEC.MOLCT14 | MEC.MOLCT14 | 18 | 0.85 | 16 | 20 | 2.5 | N |  |  | OP | X | 5 | 1970 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1970 | natural gas peaker | TRUE | 12341 | MidAmerican Energy Co | 899 | Moline | IL | Rock Island | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MEC.MOLCT14 | MEC.MOLCT14 | 18 | 0.85 | 16 | 20 | 2.5 | N |  |  | OP | X | 5 | 1970 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1942 | hydro | TRUE | 12341 | MidAmerican Energy Co | 899 | Moline | IL | Rock Island | HY1 | Conventional Hydroelectric | HY |  | S | X | X | MEC.MOLCT14 | MEC.MOLCT14 | 0.9 | 0.8 | 0.8 | 0.8 | 0.1 | N |  |  | OP | X | 1 | 1942 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 12H | [23 empty] | N
Vintage1942 | hydro | TRUE | 12341 | MidAmerican Energy Co | 899 | Moline | IL | Rock Island | HY2 | Conventional Hydroelectric | HY |  | S | X | X | MEC.MOLCT14 | MEC.MOLCT14 | 0.9 | 0.8 | 0.8 | 0.8 | 0.1 | N |  |  | OP | X | 1 | 1942 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 12H | [23 empty] | N
Vintage1942 | hydro | TRUE | 12341 | MidAmerican Energy Co | 899 | Moline | IL | Rock Island | HY3 | Conventional Hydroelectric | HY |  | S | X | X | MEC.MOLCT14 | MEC.MOLCT14 | 0.9 | 0.8 | 0.8 | 0.8 | 0.1 | N |  |  | OP | X | 1 | 1942 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 12H | [23 empty] | N
Vintage1942 | hydro | TRUE | 12341 | MidAmerican Energy Co | 899 | Moline | IL | Rock Island | HY4 | Conventional Hydroelectric | HY |  | S | X | X | MEC.MOLCT14 | MEC.MOLCT14 | 0.9 | 0.8 | 0.8 | 0.8 | 0.1 | N |  |  | OP | X | 1 | 1942 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 12H | [23 empty] | N
Vintage1985 | geothermal | TRUE | 56589 | Bottle Rock Power LLC | 902 | Bottle Rock Power | CA | Lake | 1 | Geothermal | ST |  | S | X | X |  |  | 55 | 0.9 | 9 | 9 | 1.8 | N |  |  | OS | X | 2 | 1985 |  |  | N | IPP Non-CHP | 2 | X | GEO | [5 empty] | OTH |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1929 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 903 | Rockton | IL | Winnebago | 1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.6 | 1 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 1 | 1929 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1929 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 903 | Rockton | IL | Winnebago | 2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.5 | 1 | 0.5 | 0.5 | 0.2 | N |  |  | OP | X | 1 | 1929 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1986 | hydro | TRUE | 3255 | California Dept. of Water Resources | 905 | Alamo | CA | Los Angeles | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 19.6 | 0.95 | 17 | 17 | 4 | N |  |  | OP | X | 7 | 1986 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 10M
Vintage2002 | natural gas peaker | TRUE | 19436 | Union Electric Co - (MO) | 913 | Venice | IL | Madison | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | AMMO.VENCTG2 | AMMO.VENCTG2 | 61 | 0.85 | 49 | 58 | 5 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage2005 | natural gas peaker | TRUE | 19436 | Union Electric Co - (MO) | 913 | Venice | IL | Madison | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | AMMO.VENCTG3 | AMMO.VENCTG3 | 200 | 0.85 | 169 | 192 | 119 | N |  |  | OP | X | 6 | 2005 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage2005 | natural gas peaker | TRUE | 19436 | Union Electric Co - (MO) | 913 | Venice | IL | Madison | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | AMMO.VENCTG4 | AMMO.VENCTG4 | 200 | 0.85 | 169 | 192 | 119 | N |  |  | OP | X | 6 | 2005 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage2005 | natural gas peaker | TRUE | 19436 | Union Electric Co - (MO) | 913 | Venice | IL | Madison | GT5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | AMMO.VENCTG5 | AMMO.VENCTG5 | 125 | 0.9 | 104 | 125 | 67 | N |  |  | OP | X | 10 | 2005 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1985 | hydro | TRUE | 14624 | PUD No 2 of Grant County | 917 | Quincy Chute | WA | Grant | 1 | Conventional Hydroelectric | HY |  | J | X | X |  |  | 9.4 | 0.95 | 9.4 | 9.4 | 4 | N |  |  | OP | X | 10 | 1985 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1984 | hydro | TRUE | 5932 | City of Ephraim - (UT) | 925 | Hydro Plant No 3 | UT | Sanpete | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.85 | 0.6 | 0.2 | 0.1 | N |  |  | OP | X | 9 | 1984 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M | [23 empty] | N
Vintage1984 | hydro | TRUE | 5932 | City of Ephraim - (UT) | 925 | Hydro Plant No 3 | UT | Sanpete | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.1 | 0.85 | 2 | 1.9 | 0.1 | N |  |  | OP | X | 9 | 1984 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M | [23 empty] | N
Vintage1982 | petroleum | TRUE | 2188 | City of Breese - (IL) | 934 | Breese | IL | Clinton | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 1 | N |  |  | SB | Y | 6 | 1982 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1992 | petroleum | TRUE | 2188 | City of Breese - (IL) | 934 | Breese | IL | Clinton | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 1 | N |  |  | SB | Y | 7 | 1992 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1997 | petroleum | TRUE | 2188 | City of Breese - (IL) | 934 | Breese | IL | Clinton | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 1 | N |  |  | SB | Y | 7 | 1997 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage2008 | petroleum | TRUE | 2188 | City of Breese - (IL) | 934 | Breese | IL | Clinton | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 1 | N |  |  | SB | Y | 2 | 2008 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage2014 | petroleum | TRUE | 2188 | City of Breese - (IL) | 934 | Breese | IL | Clinton | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 1 | N |  |  | SB | Y | 10 | 2014 |  |  | N | Electric Utility | 1 | X | DFO | [10 empty] | N |  | 1H | [23 empty] | N
Vintage1953 | petroleum | TRUE | 2188 | City of Breese - (IL) | 934 | Breese | IL | Clinton | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 1 | 1 | 0.9 | N |  |  | SB | Y | 12 | 1953 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1968 | petroleum | TRUE | 2188 | City of Breese - (IL) | 934 | Breese | IL | Clinton | IC3 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 1 | N |  |  | SB | Y | 7 | 1968 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1940 | petroleum | TRUE | 2634 | City of Bushnell - (IL) | 935 | Bushnell | IL | McDonough | 1 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 0.2 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | SB | Y | 6 | 1940 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1940 | petroleum | TRUE | 2634 | City of Bushnell - (IL) | 935 | Bushnell | IL | McDonough | 2 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 0.2 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | SB | Y | 6 | 1940 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1965 | petroleum | TRUE | 2634 | City of Bushnell - (IL) | 935 | Bushnell | IL | McDonough | 3 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 2.2 | 0.8 | 2.2 | 2.2 | 0.5 | N |  |  | SB | Y | 6 | 1965 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1965 | petroleum | TRUE | 2634 | City of Bushnell - (IL) | 935 | Bushnell | IL | McDonough | 4 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 2.2 | 0.8 | 2.2 | 2.2 | 0.5 | N |  |  | SB | Y | 6 | 1965 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1956 | petroleum | TRUE | 2634 | City of Bushnell - (IL) | 935 | Bushnell | IL | McDonough | 5 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 1 | 0.8 | 1 | 1 | 0.5 | N |  |  | SB | Y | 6 | 1956 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2000 | petroleum | TRUE | 2634 | City of Bushnell - (IL) | 935 | Bushnell | IL | McDonough | 6 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 2.5 | 0.8 | 2.5 | 2.5 | 1.5 | N |  |  | SB | Y | 9 | 2000 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2000 | petroleum | TRUE | 2634 | City of Bushnell - (IL) | 935 | Bushnell | IL | McDonough | 7 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 2.5 | 0.8 | 2.5 | 2.5 | 1.5 | N |  |  | SB | Y | 9 | 2000 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2003 | petroleum | TRUE | 3037 | City of Carlyle - (IL) | 936 | Carlyle | IL | Clinton | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 1.2 | N |  |  | OP | X | 10 | 2003 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2019 | petroleum | TRUE | 3037 | City of Carlyle - (IL) | 936 | Carlyle | IL | Clinton | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.8 | 0.8 | 2.8 | 2.8 | 1.2 | N |  |  | OP | X | 2 | 2019 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1964 | petroleum | TRUE | 3037 | City of Carlyle - (IL) | 936 | Carlyle | IL | Clinton | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1 | N |  |  | SB | Y | 8 | 1964 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1998 | petroleum | TRUE | 3037 | City of Carlyle - (IL) | 936 | Carlyle | IL | Clinton | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 1.2 | N |  |  | OP | X | 10 | 1998 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N
Vintage1999 | petroleum | TRUE | 3037 | City of Carlyle - (IL) | 936 | Carlyle | IL | Clinton | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 1.2 | N |  |  | OP | X | 9 | 1999 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N
Vintage1958 | petroleum | TRUE | 3040 | City of Carmi - (IL) | 937 | Carmi | IL | White | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.7 | 0.8 | 1.7 | 1.7 | 0.8 | N |  |  | OP | X | 12 | 1958 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1967 | petroleum | TRUE | 3040 | City of Carmi - (IL) | 937 | Carmi | IL | White | 12 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1 | 1 | 0.9 | N |  |  | OP | X | 12 | 1967 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1973 | petroleum | TRUE | 3040 | City of Carmi - (IL) | 937 | Carmi | IL | White | 13 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.4 | 0.8 | 4.3 | 4.3 | 2 | N |  |  | OP | X | 12 | 1973 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage2013 | petroleum | TRUE | 3040 | City of Carmi - (IL) | 937 | Carmi | IL | White | 14 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.4 | N |  |  | OP | X | 7 | 2013 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1948 | petroleum | TRUE | 3040 | City of Carmi - (IL) | 937 | Carmi | IL | White | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.5 | N |  |  | OP | X | 12 | 1948 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1951 | petroleum | TRUE | 3040 | City of Carmi - (IL) | 937 | Carmi | IL | White | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.4 | 0.8 | 1.2 | 1.2 | 0.5 | N |  |  | OP | X | 12 | 1951 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1958 | petroleum | TRUE | 3040 | City of Carmi - (IL) | 937 | Carmi | IL | White | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.7 | 0.8 | 1.7 | 1.7 | 0.5 | N |  |  | OP | X | 12 | 1958 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1967 | natural gas peaker | TRUE | 6192 | City of Farmer City - (IL) | 941 | Farmer City | IL | DeWitt | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 1.5 | 0.8 | 1.3 | 1.3 | 0.5 | N |  |  | OP | X | 7 | 1967 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1963 | petroleum | TRUE | 6192 | City of Farmer City - (IL) | 941 | Farmer City | IL | DeWitt | 2 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 1.1 | 0.8 | 0.9 | 0.9 | 0.5 | N |  |  | OP | X | 4 | 1963 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1951 | petroleum | TRUE | 6192 | City of Farmer City - (IL) | 941 | Farmer City | IL | DeWitt | 4 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 0.8 | 0.8 | 0.7 | 0.7 | 0.5 | N |  |  | OP | X | 4 | 1951 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1974 | natural gas peaker | TRUE | 6192 | City of Farmer City - (IL) | 941 | Farmer City | IL | DeWitt | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 3.5 | 0.8 | 2.8 | 2.8 | 0.5 | N |  |  | OP | X | 7 | 1974 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2012 | petroleum | TRUE | 6192 | City of Farmer City - (IL) | 941 | Farmer City | IL | DeWitt | 6 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 2.2 | 0.8 | 2 | 2 | 0.5 | N |  |  | OP | X | 8 | 2012 |  |  | N | Electric Utility | 1 | X | DFO | [10 empty] | N |  | 10M | [23 empty] | N
Vintage2012 | petroleum | TRUE | 6192 | City of Farmer City - (IL) | 941 | Farmer City | IL | DeWitt | 7 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 2.2 | 0.8 | 2 | 2 | 0.5 | N |  |  | OP | X | 8 | 2012 |  |  | N | Electric Utility | 1 | X | DFO | [10 empty] | N |  | 10M | [23 empty] | N
Vintage1948 | petroleum | TRUE | 6764 | Village of Freeburg - (IL) | 943 | Freeburg | IL | St Clair | 1 | Petroleum Liquids | IC |  | S | X | X | AMIL.IMEA1 | AMIL.IMEA1 | 0.4 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | SB | Y | 8 | 1948 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2007 | petroleum | TRUE | 6764 | Village of Freeburg - (IL) | 943 | Freeburg | IL | St Clair | 10 | Petroleum Liquids | IC |  | S | X | X | AMIL.IMEA1 | AMIL.IMEA1 | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | SB | Y | 9 | 2007 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2007 | petroleum | TRUE | 6764 | Village of Freeburg - (IL) | 943 | Freeburg | IL | St Clair | 11 | Petroleum Liquids | IC |  | S | X | X | AMIL.IMEA1 | AMIL.IMEA1 | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | SB | Y | 9 | 2007 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2007 | petroleum | TRUE | 6764 | Village of Freeburg - (IL) | 943 | Freeburg | IL | St Clair | 12 | Petroleum Liquids | IC |  | S | X | X | AMIL.IMEA1 | AMIL.IMEA1 | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | SB | Y | 9 | 2007 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1948 | petroleum | TRUE | 6764 | Village of Freeburg - (IL) | 943 | Freeburg | IL | St Clair | 2 | Petroleum Liquids | IC |  | S | X | X | AMIL.IMEA1 | AMIL.IMEA1 | 0.4 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | SB | Y | 8 | 1948 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1953 | petroleum | TRUE | 6764 | Village of Freeburg - (IL) | 943 | Freeburg | IL | St Clair | 3 | Petroleum Liquids | IC |  | S | X | X | AMIL.IMEA1 | AMIL.IMEA1 | 0.6 | 0.8 | 0.6 | 0.6 | 0.3 | N |  |  | SB | Y | 8 | 1953 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1959 | petroleum | TRUE | 6764 | Village of Freeburg - (IL) | 943 | Freeburg | IL | St Clair | 4 | Petroleum Liquids | IC |  | S | X | X | AMIL.IMEA1 | AMIL.IMEA1 | 1 | 0.8 | 1 | 1 | 0.5 | N |  |  | SB | Y | 8 | 1959 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1974 | petroleum | TRUE | 6764 | Village of Freeburg - (IL) | 943 | Freeburg | IL | St Clair | 6 | Petroleum Liquids | IC |  | S | X | X | AMIL.IMEA1 | AMIL.IMEA1 | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | SB | Y | 8 | 1974 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1986 | petroleum | TRUE | 6764 | Village of Freeburg - (IL) | 943 | Freeburg | IL | St Clair | 7 | Petroleum Liquids | IC |  | S | X | X | AMIL.IMEA1 | AMIL.IMEA1 | 2.6 | 0.8 | 2.6 | 2.6 | 1 | N |  |  | SB | Y | 7 | 1986 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1996 | petroleum | TRUE | 6764 | Village of Freeburg - (IL) | 943 | Freeburg | IL | St Clair | 8 | Petroleum Liquids | IC |  | S | X | X | AMIL.IMEA1 | AMIL.IMEA1 | 1.7 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | SB | Y | 1 | 1996 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1996 | petroleum | TRUE | 6764 | Village of Freeburg - (IL) | 943 | Freeburg | IL | St Clair | 9 | Petroleum Liquids | IC |  | S | X | X | AMIL.IMEA1 | AMIL.IMEA1 | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | SB | Y | 1 | 1996 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1974 | natural gas peaker | TRUE | 7095 | City of Geneseo - (IL) | 944 | Geneseo | IL | Henry | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 5.6 | 0.8 | 4.4 | 4.4 | 1.8 | N |  |  | OP | X | 3 | 1974 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [20 empty] | N |  |  | Y | Y | Y
Vintage2009 | onshore wind | TRUE | 7095 | City of Geneseo - (IL) | 944 | Geneseo | IL | Henry | 10 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 1.5 |  | 1.5 | 1.5 | 0 | N |  |  | OP | X | 9 | 2009 |  |  | N | Electric Utility | 1 | X | WND | [11 empty] | 1 | [21 empty] | N |  |  | N
Vintage2009 | onshore wind | TRUE | 7095 | City of Geneseo - (IL) | 944 | Geneseo | IL | Henry | 11 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 1.5 |  | 1.5 | 1.5 | 0 | N |  |  | OP | X | 10 | 2009 |  |  | N | Electric Utility | 1 | X | WND | [9 empty] | N |  | 1 | [21 empty] | N |  |  | N
Vintage2015 | solar pv | TRUE | 7095 | City of Geneseo - (IL) | 944 | Geneseo | IL | Henry | 12 | Solar Photovoltaic | PV |  | S | X | X |  |  | 1.2 |  | 0.9 | 0.9 |  | N |  |  | OP | X | 8 | 2015 |  |  | N | Electric Utility | 1 | X | SUN | [9 empty] | N | [26 empty] | N
Vintage1967 | natural gas peaker | TRUE | 7095 | City of Geneseo - (IL) | 944 | Geneseo | IL | Henry | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.5 | 0.8 | 2.8 | 2.8 | 1.5 | N |  |  | OP | X | 10 | 1967 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1966 | natural gas peaker | TRUE | 7095 | City of Geneseo - (IL) | 944 | Geneseo | IL | Henry | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.5 | 0.8 | 2.8 | 2.8 | 1.5 | N |  |  | OP | X | 6 | 1966 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1957 | natural gas peaker | TRUE | 7095 | City of Geneseo - (IL) | 944 | Geneseo | IL | Henry | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.3 | 1.3 | 1 | N |  |  | OP | X | 7 | 1957 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1990 | natural gas peaker | TRUE | 7095 | City of Geneseo - (IL) | 944 | Geneseo | IL | Henry | 5A | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 4.4 | 0.8 | 3.4 | 3.4 | 1.5 | N |  |  | OP | X | 8 | 1990 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2003 | natural gas peaker | TRUE | 7095 | City of Geneseo - (IL) | 944 | Geneseo | IL | Henry | 6A | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3 | 0.8 | 2.4 | 2.4 | 1.5 | N |  |  | OP | X | 5 | 2003 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1961 | natural gas peaker | TRUE | 7095 | City of Geneseo - (IL) | 944 | Geneseo | IL | Henry | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3 | 0.8 | 2.4 | 2.4 | 1 | N |  |  | OP | X | 6 | 1961 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1998 | petroleum | TRUE | 7095 | City of Geneseo - (IL) | 944 | Geneseo | IL | Henry | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.8 | 0.8 | 3.8 | 3.8 | 1 | N |  |  | OP | X | 5 | 1998 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N |  | N
Vintage1993 | petroleum | TRUE | 8573 | City of Highland | 946 | Highland | IL | Madison | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.8 | N |  |  | SB | Y | 7 | 1993 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1993 | petroleum | TRUE | 8573 | City of Highland | 946 | Highland | IL | Madison | IC2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.8 | N |  |  | SB | Y | 7 | 1993 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1993 | petroleum | TRUE | 8573 | City of Highland | 946 | Highland | IL | Madison | IC3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.8 | N |  |  | SB | Y | 7 | 1993 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1967 | petroleum | TRUE | 8573 | City of Highland | 946 | Highland | IL | Madison | IC5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1 | N |  |  | SB | Y | 3 | 1967 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1968 | petroleum | TRUE | 8573 | City of Highland | 946 | Highland | IL | Madison | IC6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1 | N |  |  | SB | Y | 1 | 1968 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1971 | petroleum | TRUE | 8573 | City of Highland | 946 | Highland | IL | Madison | IC7 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.4 | 0.8 | 4 | 4 | 2.2 | N |  |  | SB | Y | 8 | 1971 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1971 | petroleum | TRUE | 8573 | City of Highland | 946 | Highland | IL | Madison | IC8 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.4 | 0.8 | 4 | 4 | 2.2 | N |  |  | SB | Y | 8 | 1971 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1950 | petroleum | TRUE | 12167 | City of McLeansboro - (IL) | 948 | McLeansboro | IL | Hamilton | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.4 | 0.4 | 0.1 | N |  |  | SB | Y | 12 | 1950 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N | N | N
Vintage1979 | petroleum | TRUE | 12167 | City of McLeansboro - (IL) | 948 | McLeansboro | IL | Hamilton | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | SB | Y | 12 | 1979 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N | N | N
Vintage1979 | petroleum | TRUE | 12167 | City of McLeansboro - (IL) | 948 | McLeansboro | IL | Hamilton | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.4 | 0.8 | 2.2 | 2.2 | 0.5 | N |  |  | SB | Y | 12 | 1979 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N | N | N
Vintage1995 | petroleum | TRUE | 12167 | City of McLeansboro - (IL) | 948 | McLeansboro | IL | Hamilton | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1 | 1 | 0.5 | N |  |  | SB | Y | 1 | 1995 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1994 | petroleum | TRUE | 12167 | City of McLeansboro - (IL) | 948 | McLeansboro | IL | Hamilton | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1 | 1 | 0.5 | N |  |  | SB | Y | 12 | 1994 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2002 | petroleum | TRUE | 12167 | City of McLeansboro - (IL) | 948 | McLeansboro | IL | Hamilton | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.5 | N |  |  | SB | Y | 6 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2002 | petroleum | TRUE | 11736 | City of Marshall - (IL) | 949 | Marshall (IL) | IL | Clark | 10 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 4 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2002 | petroleum | TRUE | 11736 | City of Marshall - (IL) | 949 | Marshall (IL) | IL | Clark | 11 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 4 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2007 | petroleum | TRUE | 11736 | City of Marshall - (IL) | 949 | Marshall (IL) | IL | Clark | 12 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 1 | 2007 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage2007 | petroleum | TRUE | 11736 | City of Marshall - (IL) | 949 | Marshall (IL) | IL | Clark | 13 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 1 | 2007 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage2002 | petroleum | TRUE | 11736 | City of Marshall - (IL) | 949 | Marshall (IL) | IL | Clark | 5 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 2.5 | 0.8 | 2.5 | 2.5 | 1 | N |  |  | OP | X | 9 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N
Vintage2002 | petroleum | TRUE | 11736 | City of Marshall - (IL) | 949 | Marshall (IL) | IL | Clark | 6 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 4 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N
Vintage2002 | petroleum | TRUE | 11736 | City of Marshall - (IL) | 949 | Marshall (IL) | IL | Clark | 7 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 4 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N
Vintage2002 | petroleum | TRUE | 11736 | City of Marshall - (IL) | 949 | Marshall (IL) | IL | Clark | 8 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 4 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N
Vintage2002 | petroleum | TRUE | 11736 | City of Marshall - (IL) | 949 | Marshall (IL) | IL | Clark | 9 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 4 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N
Vintage2011 | petroleum | TRUE | 14840 | City of Peru - (IL) | 955 | Peru (IL) | IL | LaSalle | 11 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 2.7 | 0.8 | 2.7 | 2.7 | 0.2 | N |  |  | OP | X | 4 | 2011 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N |  | N
Vintage2011 | petroleum | TRUE | 14840 | City of Peru - (IL) | 955 | Peru (IL) | IL | LaSalle | 12 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 2.7 | 0.8 | 2.7 | 2.7 | 0.2 | N |  |  | OP | X | 4 | 2011 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N |  | N
Vintage2011 | petroleum | TRUE | 14840 | City of Peru - (IL) | 955 | Peru (IL) | IL | LaSalle | 13 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 2.7 | 0.8 | 2.7 | 2.7 | 0.2 | N |  |  | OP | X | 4 | 2011 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N |  | N
Vintage2011 | petroleum | TRUE | 14840 | City of Peru - (IL) | 955 | Peru (IL) | IL | LaSalle | 14 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 2.7 | 0.8 | 2.7 | 2.7 | 0.2 | N |  |  | OP | X | 4 | 2011 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N |  | N
Vintage2011 | petroleum | TRUE | 14840 | City of Peru - (IL) | 955 | Peru (IL) | IL | LaSalle | 15 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 2.7 | 0.8 | 2.7 | 2.7 | 0.2 | N |  |  | OP | X | 4 | 2011 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N |  | N
Vintage2011 | petroleum | TRUE | 14840 | City of Peru - (IL) | 955 | Peru (IL) | IL | LaSalle | 16 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 2.7 | 0.8 | 2.7 | 2.7 | 0.2 | N |  |  | OP | X | 9 | 2011 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2011 | petroleum | TRUE | 14840 | City of Peru - (IL) | 955 | Peru (IL) | IL | LaSalle | 17 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 2.7 | 0.8 | 2.7 | 2.7 | 0.2 | N |  |  | OP | X | 9 | 2011 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N |  | N
Vintage1968 | petroleum | TRUE | 14840 | City of Peru - (IL) | 955 | Peru (IL) | IL | LaSalle | GT1 | Petroleum Liquids | GT |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 10 | 0.8 | 8.6 | 8.6 | 1 | N |  |  | OP | X | 10 | 1968 |  |  | N | Electric Utility | 1 | X | JF | [9 empty] | N | N |  | 1H | [23 empty] | N |  | N
Vintage1996 | hydro | TRUE | 14840 | City of Peru - (IL) | 955 | Peru (IL) | IL | LaSalle | HC1 | Conventional Hydroelectric | HY |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 1.9 | 0.9 | 1.7 | 1.7 | 0.2 | N |  |  | OP | X | 9 | 1996 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1996 | hydro | TRUE | 14840 | City of Peru - (IL) | 955 | Peru (IL) | IL | LaSalle | HC2 | Conventional Hydroelectric | HY |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 1.9 | 0.9 | 1.7 | 1.7 | 0.2 | N |  |  | OP | X | 9 | 1996 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1996 | hydro | TRUE | 14840 | City of Peru - (IL) | 955 | Peru (IL) | IL | LaSalle | HC3 | Conventional Hydroelectric | HY |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 1.9 | 0.9 | 1.7 | 1.7 | 0.2 | N |  |  | OP | X | 9 | 1996 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1996 | hydro | TRUE | 14840 | City of Peru - (IL) | 955 | Peru (IL) | IL | LaSalle | HC4 | Conventional Hydroelectric | HY |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 1.9 | 0.9 | 1.7 | 1.7 | 0.2 | N |  |  | OP | X | 9 | 1996 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1953 | natural gas peaker | TRUE | 15388 | City of Princeton - (IL) | 957 | Princeton (IL) | IL | Bureau | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 2.3 | 0.8 | 2.3 | 2.3 | 0.5 | N |  |  | SB | Y | 7 | 1953 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1958 | natural gas peaker | TRUE | 15388 | City of Princeton - (IL) | 957 | Princeton (IL) | IL | Bureau | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 3 | 0.8 | 3 | 3 | 1 | N |  |  | SB | Y | 4 | 1958 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1965 | natural gas peaker | TRUE | 15388 | City of Princeton - (IL) | 957 | Princeton (IL) | IL | Bureau | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 3.4 | 0.8 | 3.4 | 3.4 | 1 | N |  |  | SB | Y | 8 | 1965 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1965 | natural gas peaker | TRUE | 15388 | City of Princeton - (IL) | 957 | Princeton (IL) | IL | Bureau | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 3.4 | 0.8 | 3.4 | 3.4 | 1 | N |  |  | SB | Y | 1 | 1965 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1971 | natural gas peaker | TRUE | 15388 | City of Princeton - (IL) | 957 | Princeton (IL) | IL | Bureau | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 4.4 | 0.8 | 4.4 | 4.4 | 1 | N |  |  | SB | Y | 7 | 1971 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1971 | natural gas peaker | TRUE | 15388 | City of Princeton - (IL) | 957 | Princeton (IL) | IL | Bureau | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 5.6 | 0.8 | 5.5 | 5.5 | 1 | N |  |  | SB | Y | 8 | 1971 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1976 | natural gas peaker | TRUE | 15388 | City of Princeton - (IL) | 957 | Princeton (IL) | IL | Bureau | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 7 | 0.8 | 7 | 7 | 1 | N |  |  | SB | Y | 9 | 1976 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1976 | natural gas peaker | TRUE | 15388 | City of Princeton - (IL) | 957 | Princeton (IL) | IL | Bureau | 8 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 8.8 | 0.8 | 8.7 | 8.7 | 1 | N |  |  | SB | Y | 9 | 1976 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2000 | petroleum | TRUE | 15686 | Village of Rantoul - (IL) | 958 | Rantoul | IL | Champaign | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.9 | 1.8 | 1.8 | 0.6 | N |  |  | OP | X | 8 | 2000 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N
Vintage2000 | petroleum | TRUE | 15686 | Village of Rantoul - (IL) | 958 | Rantoul | IL | Champaign | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.9 | 1.8 | 1.8 | 0.6 | N |  |  | OP | X | 8 | 2000 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N
Vintage2000 | petroleum | TRUE | 15686 | Village of Rantoul - (IL) | 958 | Rantoul | IL | Champaign | 12 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.9 | 1.8 | 1.8 | 0.6 | N |  |  | OP | X | 8 | 2000 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N
Vintage2000 | petroleum | TRUE | 15686 | Village of Rantoul - (IL) | 958 | Rantoul | IL | Champaign | 13 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.9 | 1.8 | 1.8 | 0.6 | N |  |  | OP | X | 8 | 2000 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N
Vintage2000 | petroleum | TRUE | 15686 | Village of Rantoul - (IL) | 958 | Rantoul | IL | Champaign | 14 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.9 | 1.8 | 1.8 | 0.6 | N |  |  | OP | X | 8 | 2000 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N
Vintage2001 | petroleum | TRUE | 15686 | Village of Rantoul - (IL) | 958 | Rantoul | IL | Champaign | 15 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.9 | 1.8 | 1.8 | 0.6 | N |  |  | OP | X | 1 | 2001 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N
Vintage2001 | petroleum | TRUE | 15686 | Village of Rantoul - (IL) | 958 | Rantoul | IL | Champaign | 16 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.9 | 1.8 | 1.8 | 0.6 | N |  |  | OP | X | 1 | 2001 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N
Vintage2000 | petroleum | TRUE | 15686 | Village of Rantoul - (IL) | 958 | Rantoul | IL | Champaign | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.9 | 1.8 | 1.8 | 0.6 | N |  |  | OP | X | 8 | 2000 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N
Vintage1968 | petroleum | TRUE | 15772 | City of Red Bud - (IL) | 959 | Red Bud | IL | Randolph | 1 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 2.4 | 0.8 | 2.2 | 2.2 | 1 | N |  |  | OP | X | 7 | 1968 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1959 | petroleum | TRUE | 15772 | City of Red Bud - (IL) | 959 | Red Bud | IL | Randolph | 2 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 1.1 | 0.8 | 0.9 | 1 | 0.5 | N |  |  | OP | X | 3 | 1959 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1964 | petroleum | TRUE | 15772 | City of Red Bud - (IL) | 959 | Red Bud | IL | Randolph | 3 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 2.4 | 0.8 | 2.2 | 2.2 | 1 | N |  |  | OP | X | 11 | 1964 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1973 | petroleum | TRUE | 15772 | City of Red Bud - (IL) | 959 | Red Bud | IL | Randolph | 4 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 3.5 | 0.8 | 3 | 3 | 1.5 | N |  |  | OP | X | 3 | 1973 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2002 | petroleum | TRUE | 15772 | City of Red Bud - (IL) | 959 | Red Bud | IL | Randolph | 7 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 2.8 | 0.8 | 3 | 3 | 1 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2002 | petroleum | TRUE | 15772 | City of Red Bud - (IL) | 959 | Red Bud | IL | Randolph | 8 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 2.8 | 0.8 | 3 | 3 | 1 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1940 | petroleum | TRUE | 16179 | Rochelle Municipal Utilities | 960 | North Ninth Street | IL | Ogle | 1 | Petroleum Liquids | IC |  | S | X | X | PJM/ComEd.ROCHELLE | PJM/ComEd.ROCHELLE | 0.3 | 0.8 | 0.6 | 0.6 | 0.5 | N |  |  | OP | X | 10 | 1940 |  |  | N | Electric Utility | 1 | X | DFO | [10 empty] | N |  | 1H | [23 empty] | N | N | N
Vintage1989 | natural gas peaker | TRUE | 16179 | Rochelle Municipal Utilities | 960 | North Ninth Street | IL | Ogle | 10 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PJM/ComEd.ROCHELLE | PJM/ComEd.ROCHELLE | 2.5 | 0.8 | 2 | 2 | 0.5 | N |  |  | OP | X | 5 | 1989 |  |  | N | Electric Utility | 1 | X | NG | DFO | [9 empty] | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1956 | natural gas peaker | TRUE | 16179 | Rochelle Municipal Utilities | 960 | North Ninth Street | IL | Ogle | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PJM/ComEd.ROCHELLE | PJM/ComEd.ROCHELLE | 2.5 | 0.8 | 2 | 2 | 0.5 | N |  |  | OP | X | 7 | 1956 |  |  | N | Electric Utility | 1 | X | NG | DFO | [9 empty] | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1946 | petroleum | TRUE | 16179 | Rochelle Municipal Utilities | 960 | North Ninth Street | IL | Ogle | 4 | Petroleum Liquids | IC |  | S | X | X | PJM/ComEd.ROCHELLE | PJM/ComEd.ROCHELLE | 1 | 0.8 | 0.7 | 0.7 | 0.5 | N |  |  | OP | X | 10 | 1946 |  |  | N | Electric Utility | 1 | X | DFO | [10 empty] | N |  | 1H | [23 empty] | N | N | N
Vintage1954 | natural gas peaker | TRUE | 16179 | Rochelle Municipal Utilities | 960 | North Ninth Street | IL | Ogle | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PJM/ComEd.ROCHELLE | PJM/ComEd.ROCHELLE | 2.5 | 0.8 | 2 | 2 | 0.5 | N |  |  | OP | X | 4 | 1954 |  |  | N | Electric Utility | 1 | X | NG | DFO | [9 empty] | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1967 | natural gas peaker | TRUE | 16179 | Rochelle Municipal Utilities | 960 | North Ninth Street | IL | Ogle | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PJM/ComEd.ROCHELLE | PJM/ComEd.ROCHELLE | 3.8 | 0.8 | 3.5 | 3.5 | 0.5 | N |  |  | OP | X | 2 | 1967 |  |  | N | Electric Utility | 1 | X | NG | DFO | [9 empty] | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1949 | petroleum | TRUE | 16179 | Rochelle Municipal Utilities | 960 | North Ninth Street | IL | Ogle | 8 | Petroleum Liquids | IC |  | S | X | X | PJM/ComEd.ROCHELLE | PJM/ComEd.ROCHELLE | 1 | 0.8 | 0.5 | 0.5 | 0.5 | N |  |  | OP | X | 6 | 1949 |  |  | N | Electric Utility | 1 | X | DFO | [10 empty] | N |  | 1H | [23 empty] | N |  | N
Vintage1989 | natural gas peaker | TRUE | 16179 | Rochelle Municipal Utilities | 960 | North Ninth Street | IL | Ogle | 9 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PJM/ComEd.ROCHELLE | PJM/ComEd.ROCHELLE | 3.5 | 0.8 | 3 | 3 | 0.5 | N |  |  | OP | X | 5 | 1989 |  |  | N | Electric Utility | 1 | X | NG | DFO | [9 empty] | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2014 | solar pv | TRUE | 16179 | Rochelle Municipal Utilities | 960 | North Ninth Street | IL | Ogle | SOL1 | Solar Photovoltaic | PV |  | S | X | X | PJM/ComEd.ROCHELLE | PJM/ComEd.ROCHELLE | 0.3 |  | 0.3 | 0.3 |  | N |  |  | OP | X | 11 | 2014 |  |  | N | Electric Utility | 1 | X | SUN | [10 empty] | N | [25 empty] | N
Vintage1967 | natural gas peaker | TRUE | 16179 | Rochelle Municipal Utilities | 961 | South Main Street | IL | Ogle | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.5 | 0.8 | 1.6 | 1.6 | 0.5 | N |  |  | SB | Y | 9 | 1967 |  |  | N | Electric Utility | 1 | X | NG | DFO | [11 empty] | 1H | [23 empty] | Y | Y | Y
Vintage2014 | petroleum | TRUE | 16179 | Rochelle Municipal Utilities | 961 | South Main Street | IL | Ogle | 13 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | SB | Y | 10 | 2014 |  |  | N | Electric Utility | 1 | X | DFO | [10 empty] | N |  | 10M | [23 empty] | N | N
Vintage2014 | petroleum | TRUE | 16179 | Rochelle Municipal Utilities | 961 | South Main Street | IL | Ogle | 14 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | SB | Y | 10 | 2014 |  |  | N | Electric Utility | 1 | X | DFO | [10 empty] | N |  | 10M | [23 empty] | N | N | N
Vintage2014 | petroleum | TRUE | 16179 | Rochelle Municipal Utilities | 961 | South Main Street | IL | Ogle | 15 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | SB | Y | 10 | 2014 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2016 | petroleum | TRUE | 16179 | Rochelle Municipal Utilities | 961 | South Main Street | IL | Ogle | 16 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 6 | 2016 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2016 | petroleum | TRUE | 16179 | Rochelle Municipal Utilities | 961 | South Main Street | IL | Ogle | 17 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 6 | 2016 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2016 | petroleum | TRUE | 16179 | Rochelle Municipal Utilities | 961 | South Main Street | IL | Ogle | 18 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 6 | 2016 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1967 | natural gas peaker | TRUE | 16179 | Rochelle Municipal Utilities | 961 | South Main Street | IL | Ogle | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2 | 2 | 0.5 | N |  |  | SB | Y | 9 | 1967 |  |  | N | Electric Utility | 1 | X | NG | DFO | [11 empty] | 1H | [23 empty] | Y | Y | Y
Vintage1978 | hard coal | TRUE | 17828 | City of Springfield - (IL) | 963 | Dallman | IL | Sangamon | 3 | Conventional Steam Coal | ST |  | S | X | X | CWLP.DALLMA83 | CWLP.DALLMA83 | 207.3 | 0.9 | 159 | 159 | 110 | N |  |  | OP | X | 6 | 1978 | 12 | 2023 | N | Electric Utility | 1 | X | BIT | [5 empty] | NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | N |  |  | N | N | N
Vintage2009 | hard coal | TRUE | 17828 | City of Springfield - (IL) | 963 | Dallman | IL | Sangamon | 4 | Conventional Steam Coal | ST |  | S | X | X | CWLP.DALLMA84 | CWLP.DALLMA84 | 230.1 | 0.85 | 196 | 196 | 95 | N |  |  | OP | X | 5 | 2009 |  |  | N | Electric Utility | 1 | X | BIT | [5 empty] | NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | N |  |  | N | N | N
Vintage2002 | petroleum | TRUE | 17828 | City of Springfield - (IL) | 964 | Lakeside | IL | Sangamon | D1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.7 | 1.7 | 1.7 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage2002 | petroleum | TRUE | 17828 | City of Springfield - (IL) | 964 | Lakeside | IL | Sangamon | D2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.7 | 1.7 | 1.7 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage2002 | petroleum | TRUE | 17828 | City of Springfield - (IL) | 964 | Lakeside | IL | Sangamon | D3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.7 | 1.7 | 1.7 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1970 | petroleum | TRUE | 17828 | City of Springfield - (IL) | 965 | Reynolds | IL | Sangamon | 1 | Petroleum Liquids | GT |  | S | X | X | CWLP.REYNOLS91 | CWLP.REYNOLS91 | 17.5 | 0.85 | 13.6 | 14.9 | 1 | N |  |  | OP | X | 11 | 1970 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1974 | petroleum | TRUE | 18277 | City of Sullivan - (IL) | 969 | Sullivan (IL) | IL | Moultrie | 1 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 4.3 | 0.8 | 4.3 | 4.3 | 1 | N |  |  | SB | Y | 12 | 1974 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1971 | petroleum | TRUE | 18277 | City of Sullivan - (IL) | 969 | Sullivan (IL) | IL | Moultrie | 10 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 2.4 | 0.8 | 2.2 | 2.4 | 0.5 | N |  |  | SB | Y | 6 | 1971 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1996 | petroleum | TRUE | 18277 | City of Sullivan - (IL) | 969 | Sullivan (IL) | IL | Moultrie | 11 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 2 | 0.8 | 2 | 2 | 0.5 | N |  |  | SB | Y | 2 | 1996 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1996 | petroleum | TRUE | 18277 | City of Sullivan - (IL) | 969 | Sullivan (IL) | IL | Moultrie | 12 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 1.1 | 0.8 | 1 | 1 | 0.5 | N |  |  | SB | Y | 2 | 1996 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2012 | petroleum | TRUE | 18277 | City of Sullivan - (IL) | 969 | Sullivan (IL) | IL | Moultrie | 13 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 2.3 | 0.8 | 2.3 | 2.3 | 0.5 | N |  |  | OP | X | 11 | 2012 |  |  | N | Electric Utility | 1 | X | DFO | [10 empty] | N |  | 10M | [23 empty] | N | N | N
Vintage2012 | petroleum | TRUE | 18277 | City of Sullivan - (IL) | 969 | Sullivan (IL) | IL | Moultrie | 14 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 2.3 | 0.8 | 2.3 | 2.3 | 0.5 | N |  |  | OP | X | 11 | 2012 |  |  | N | Electric Utility | 1 | X | DFO | [10 empty] | N |  | 10M | [23 empty] | N | N | N
Vintage2012 | petroleum | TRUE | 18277 | City of Sullivan - (IL) | 969 | Sullivan (IL) | IL | Moultrie | 15 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 2.3 | 0.8 | 2.3 | 2.3 | 0.5 | N |  |  | OP | X | 11 | 2012 |  |  | N | Electric Utility | 1 | X | DFO | [10 empty] | N |  | 10M | [23 empty] | N | N | N
Vintage1961 | petroleum | TRUE | 18277 | City of Sullivan - (IL) | 969 | Sullivan (IL) | IL | Moultrie | 2 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 2 | 0.8 | 2 | 2 | 0.5 | N |  |  | SB | Y | 11 | 1961 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1956 | petroleum | TRUE | 18277 | City of Sullivan - (IL) | 969 | Sullivan (IL) | IL | Moultrie | 3 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 1.5 | 0.8 | 1.3 | 1.5 | 0.5 | N |  |  | SB | Y | 11 | 1956 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1951 | petroleum | TRUE | 18277 | City of Sullivan - (IL) | 969 | Sullivan (IL) | IL | Moultrie | 4 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 1.1 | 0.8 | 0.9 | 1.1 | 0.5 | N |  |  | SB | Y | 5 | 1951 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1948 | petroleum | TRUE | 18277 | City of Sullivan - (IL) | 969 | Sullivan (IL) | IL | Moultrie | 5 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 1.1 | 0.8 | 1.1 | 1.1 | 0.5 | N |  |  | SB | Y | 9 | 1948 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1946 | petroleum | TRUE | 18277 | City of Sullivan - (IL) | 969 | Sullivan (IL) | IL | Moultrie | 6 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 0.6 | 0.8 | 0.6 | 0.6 | 0.3 | N |  |  | SB | Y | 6 | 1946 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1971 | petroleum | TRUE | 18277 | City of Sullivan - (IL) | 969 | Sullivan (IL) | IL | Moultrie | 9 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 2.4 | 0.8 | 2.2 | 2.4 | 0.5 | N |  |  | SB | Y | 6 | 1971 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1970 | petroleum | TRUE | 20180 | City of Waterloo - (IL) | 971 | Waterloo | IL | Monroe | 1 | Petroleum Liquids | IC |  | S | X | X | AMIL.IMEA1 | AMIL.IMEA1 | 3.1 | 0.8 | 2.7 | 2.7 | 1 | N |  |  | SB | Y | 5 | 1970 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1996 | petroleum | TRUE | 20180 | City of Waterloo - (IL) | 971 | Waterloo | IL | Monroe | 10 | Petroleum Liquids | IC |  | S | X | X | AMIL.IMEA1 | AMIL.IMEA1 | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 6 | 1996 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1996 | petroleum | TRUE | 20180 | City of Waterloo - (IL) | 971 | Waterloo | IL | Monroe | 11 | Petroleum Liquids | IC |  | S | X | X | AMIL.IMEA1 | AMIL.IMEA1 | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 6 | 1996 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage2002 | natural gas peaker | TRUE | 20180 | City of Waterloo - (IL) | 971 | Waterloo | IL | Monroe | 12 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | AMIL.IMEA1 | AMIL.IMEA1 | 6.6 | 0.8 | 6.6 | 7 | 4 | N |  |  | SB | Y | 5 | 2002 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2012 | natural gas peaker | TRUE | 20180 | City of Waterloo - (IL) | 971 | Waterloo | IL | Monroe | 13 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | AMIL.IMEA1 | AMIL.IMEA1 | 7 | 0.8 | 6.6 | 7 | 4 | N |  |  | SB | Y | 5 | 2012 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1954 | petroleum | TRUE | 20180 | City of Waterloo - (IL) | 971 | Waterloo | IL | Monroe | 2 | Petroleum Liquids | IC |  | S | X | X | AMIL.IMEA1 | AMIL.IMEA1 | 0.2 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | SB | Y | 6 | 1954 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1946 | petroleum | TRUE | 20180 | City of Waterloo - (IL) | 971 | Waterloo | IL | Monroe | 3 | Petroleum Liquids | IC |  | S | X | X | AMIL.IMEA1 | AMIL.IMEA1 | 0.2 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | SB | Y | 6 | 1946 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1963 | petroleum | TRUE | 20180 | City of Waterloo - (IL) | 971 | Waterloo | IL | Monroe | 4 | Petroleum Liquids | IC |  | S | X | X | AMIL.IMEA1 | AMIL.IMEA1 | 2 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | SB | Y | 5 | 1963 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1950 | petroleum | TRUE | 20180 | City of Waterloo - (IL) | 971 | Waterloo | IL | Monroe | 5 | Petroleum Liquids | IC |  | S | X | X | AMIL.IMEA1 | AMIL.IMEA1 | 0.5 | 0.8 | 0.4 | 0.4 | 0.3 | N |  |  | SB | Y | 6 | 1950 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1950 | petroleum | TRUE | 20180 | City of Waterloo - (IL) | 971 | Waterloo | IL | Monroe | 6 | Petroleum Liquids | IC |  | S | X | X | AMIL.IMEA1 | AMIL.IMEA1 | 0.5 | 0.8 | 0.5 | 0.5 | 0.3 | N |  |  | SB | Y | 6 | 1950 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1959 | petroleum | TRUE | 20180 | City of Waterloo - (IL) | 971 | Waterloo | IL | Monroe | 7 | Petroleum Liquids | IC |  | S | X | X | AMIL.IMEA1 | AMIL.IMEA1 | 1.7 | 0.8 | 1.5 | 1.5 | 0.5 | N |  |  | SB | Y | 6 | 1959 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1973 | petroleum | TRUE | 20180 | City of Waterloo - (IL) | 971 | Waterloo | IL | Monroe | 8 | Petroleum Liquids | IC |  | S | X | X | AMIL.IMEA1 | AMIL.IMEA1 | 3 | 0.8 | 2.4 | 2.4 | 1 | N |  |  | SB | Y | 4 | 1973 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N |  | N
Vintage1996 | petroleum | TRUE | 20180 | City of Waterloo - (IL) | 971 | Waterloo | IL | Monroe | 9 | Petroleum Liquids | IC |  | S | X | X | AMIL.IMEA1 | AMIL.IMEA1 | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 6 | 1996 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N |  | N
Vintage1953 | natural gas steam turbine | TRUE | 20824 | Village of Winnetka - (IL) | 972 | Winnetka | IL | Cook | 4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 9.4 | 0.8 | 9.4 | 9.4 | 2.4 | N |  |  | OP | X | 1 | 1953 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | NG |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | Y | Y | Y
Vintage1948 | natural gas steam turbine | TRUE | 20824 | Village of Winnetka - (IL) | 972 | Winnetka | IL | Cook | 6 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 6.3 | 0.8 | 6.3 | 6.3 | 2 | N |  |  | OP | X | 1 | 1948 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | NG |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | Y | Y | Y
Vintage1960 | natural gas steam turbine | TRUE | 20824 | Village of Winnetka - (IL) | 972 | Winnetka | IL | Cook | 7 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 12.5 | 0.8 | 12.5 | 12.5 | 3.1 | N |  |  | OP | X | 1 | 1960 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | NG |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | Y | Y | Y
Vintage1979 | petroleum | TRUE | 20824 | Village of Winnetka - (IL) | 972 | Winnetka | IL | Cook | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.6 | 0.8 | 2.6 | 2.6 | 1.8 | N |  |  | OP | X | 1 | 1979 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1979 | petroleum | TRUE | 20824 | Village of Winnetka - (IL) | 972 | Winnetka | IL | Cook | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.6 | 0.8 | 2.6 | 2.6 | 1.8 | N |  |  | OP | X | 1 | 1979 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1963 | hard coal | TRUE | 17632 | Southern Illinois Power Coop | 976 | Marion | IL | Williamson | 1 | Conventional Steam Coal | ST |  | S | X | X | SIPC.MARI69 | SIPCMARI69 | 33 | 0.85 | 40 | 40 | 30 | N |  |  | OP | X | 6 | 1963 |  |  | N | Electric Utility | 1 | X | BIT | DFO | PC |  |  |  | DFO |  |  |  | N | N |  | OVER | Y |  |  |  | Y | [18 empty] | N | N | N
Vintage1963 | hard coal | TRUE | 17632 | Southern Illinois Power Coop | 976 | Marion | IL | Williamson | 2 | Conventional Steam Coal | ST |  | S | X | X | SIPC.MARI69 | SIPCMARI69 | 33 | 0.85 | 40 | 40 | 30 | N |  |  | OP | X | 8 | 1963 |  |  | N | Electric Utility | 1 | X | BIT | DFO | PC |  |  |  | DFO |  |  |  | N | N |  | OVER | Y |  |  |  | Y | [18 empty] | N | N | N
Vintage1963 | hard coal | TRUE | 17632 | Southern Illinois Power Coop | 976 | Marion | IL | Williamson | 3 | Conventional Steam Coal | ST |  | S | X | X | SIPC.MARI69 | SIPCMARI69 | 33 | 0.85 | 40 | 40 | 30 | N |  |  | OP | X | 9 | 1963 |  |  | N | Electric Utility | 1 | X | BIT | DFO | PC |  |  |  | DFO |  |  |  | N | N |  | OVER | Y |  |  |  | Y | [18 empty] | N | N | N
Vintage2003 | natural gas peaker | TRUE | 17632 | Southern Illinois Power Coop | 976 | Marion | IL | Williamson | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SIPC.MARIOGEN5 | SIPC.MARIOGEN5 | 75 | 0.85 | 70 | 90 | 40 | N |  |  | SB | Y | 5 | 2003 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H |  | N |  |  | N | [18 empty] | Y | Y | Y
Vintage2003 | natural gas peaker | TRUE | 17632 | Southern Illinois Power Coop | 976 | Marion | IL | Williamson | 6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SIPC.MARIOGEN6 | SIPC.MARIOGEN6 | 75 | 0.85 | 70 | 90 | 40 | N |  |  | SB | Y | 5 | 2003 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H |  |  |  |  | N | [18 empty] | Y | Y | Y
Vintage1955 | hard coal | TRUE | 9269 | Indiana-Kentucky Electric Corp | 983 | Clifty Creek | IN | Jefferson | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 217.3 | 0.83 | 195.5 | 199.7 | 80 | N |  |  | OP | X | 2 | 1955 |  |  | N | Electric Utility | 1 | X | BIT | SUB |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1955 | hard coal | TRUE | 9269 | Indiana-Kentucky Electric Corp | 983 | Clifty Creek | IN | Jefferson | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 217.3 | 0.83 | 195.5 | 199.7 | 80 | N |  |  | OP | X | 5 | 1955 |  |  | N | Electric Utility | 1 | X | BIT | SUB |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1955 | hard coal | TRUE | 9269 | Indiana-Kentucky Electric Corp | 983 | Clifty Creek | IN | Jefferson | 3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 217.3 | 0.83 | 195.5 | 199.7 | 80 | N |  |  | OP | X | 7 | 1955 |  |  | N | Electric Utility | 1 | X | BIT | SUB |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1955 | hard coal | TRUE | 9269 | Indiana-Kentucky Electric Corp | 983 | Clifty Creek | IN | Jefferson | 4 | Conventional Steam Coal | ST |  | S | X | X |  |  | 217.3 | 0.83 | 195.5 | 199.7 | 80 | N |  |  | OP | X | 10 | 1955 |  |  | N | Electric Utility | 1 | X | BIT | SUB |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1955 | hard coal | TRUE | 9269 | Indiana-Kentucky Electric Corp | 983 | Clifty Creek | IN | Jefferson | 5 | Conventional Steam Coal | ST |  | S | X | X |  |  | 217.3 | 0.83 | 195.5 | 199.7 | 80 | N |  |  | OP | X | 11 | 1955 |  |  | N | Electric Utility | 1 | X | BIT | SUB |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1956 | hard coal | TRUE | 9269 | Indiana-Kentucky Electric Corp | 983 | Clifty Creek | IN | Jefferson | 6 | Conventional Steam Coal | ST |  | S | X | X |  |  | 217.3 | 0.83 | 195.5 | 199.7 | 80 | N |  |  | OP | X | 3 | 1956 |  |  | N | Electric Utility | 1 | X | BIT | SUB |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1913 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 986 | Elkhart | IN | Elkhart | 1 | Conventional Hydroelectric | HY |  | S | X | X | 32418411 | 34497125 | 1.4 | 0.8 | 0.6 | 1.1 | 0.5 | N |  |  | OP | X | 1 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H
Vintage1921 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 986 | Elkhart | IN | Elkhart | 2 | Conventional Hydroelectric | HY |  | S | X | X | 32418411 | 34497125 | 1 | 1 | 0.4 | 0.5 | 0.3 | N |  |  | OP | X | 1 | 1921 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H
Vintage1921 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 986 | Elkhart | IN | Elkhart | 3 | Conventional Hydroelectric | HY |  | S | X | X | 32418411 | 34497125 | 1 | 1 | 0.4 | 0.5 | 0.3 | N |  |  | OP | X | 1 | 1921 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H
Vintage1984 | hydro | TRUE | 14354 | PacifiCorp | 987 | Last Chance | ID | Caribou | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 1 | 0.2 | 0.2 | 0 | N |  |  | OP | X | 2 | 1984 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1984 | hydro | TRUE | 14354 | PacifiCorp | 987 | Last Chance | ID | Caribou | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 1 | 0.4 | 0.4 | 0 | N |  |  | OP | X | 2 | 1984 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1984 | hydro | TRUE | 14354 | PacifiCorp | 987 | Last Chance | ID | Caribou | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 1 | 0.8 | 0.8 | 0 | N |  |  | OP | X | 2 | 1984 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1989 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 989 | Twin Branch | IN | St Joseph | H1E | Conventional Hydroelectric | HY |  | S | X | X | 34886931 | 34497125 | 0.6 | 0.9 | 0.5 | 0.6 | 0.2 | N |  |  | OP | X | 5 | 1989 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H
Vintage1989 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 989 | Twin Branch | IN | St Joseph | H1W | Conventional Hydroelectric | HY |  | S | X | X | 34886931 | 34497125 | 0.6 | 0.9 | 0.5 | 0.6 | 0.2 | N |  |  | OP | X | 5 | 1989 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H
Vintage1989 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 989 | Twin Branch | IN | St Joseph | H2W | Conventional Hydroelectric | HY |  | S | X | X | 34886931 | 34497125 | 0.6 | 0.8 | 0.5 | 0.6 | 0.2 | N |  |  | OP | X | 5 | 1989 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H
Vintage1989 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 989 | Twin Branch | IN | St Joseph | H3W | Conventional Hydroelectric | HY |  | S | X | X | 34886931 | 34497125 | 0.6 | 1 | 0.5 | 0.6 | 0.2 | N |  |  | OP | X | 5 | 1989 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H
Vintage1989 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 989 | Twin Branch | IN | St Joseph | H4W | Conventional Hydroelectric | HY |  | S | X | X | 34886931 | 34497125 | 0.6 | 1 | 0.5 | 0.6 | 0.2 | N |  |  | OP | X | 5 | 1989 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H
Vintage1989 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 989 | Twin Branch | IN | St Joseph | H5W | Conventional Hydroelectric | HY |  | S | X | X | 34886931 | 34497125 | 0.6 | 1 | 0.5 | 0.6 | 0.2 | N |  |  | OP | X | 5 | 1989 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H
Vintage1989 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 989 | Twin Branch | IN | St Joseph | H6E | Conventional Hydroelectric | HY |  | S | X | X | 34886931 | 34497125 | 0.6 | 0.9 | 0.5 | 0.6 | 0.2 | N |  |  | OP | X | 5 | 1989 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H
Vintage1989 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 989 | Twin Branch | IN | St Joseph | H6W | Conventional Hydroelectric | HY |  | S | X | X | 34886931 | 34497125 | 0.6 | 0.9 | 0.5 | 0.6 | 0.2 | N |  |  | OP | X | 5 | 1989 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 1H
Vintage1958 | natural gas steam turbine | TRUE | 9273 | Indianapolis Power & Light Co | 990 | Harding Street | IN | Marion | 5 | Natural Gas Steam Turbine | ST |  | S | X | X | IPL.16STOU5O5 | IPL.16STOU5O5 | 100 | 0.85 | 101 | 101 | 30 | N |  |  | OP | X | 6 | 1958 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | N |  |  | N | [18 empty] | N |  | N
Vintage1961 | natural gas steam turbine | TRUE | 9273 | Indianapolis Power & Light Co | 990 | Harding Street | IN | Marion | 6 | Natural Gas Steam Turbine | ST |  | S | X | X | IPL.16STOU6O6 | IPL.16STOU6O6 | 100 | 0.85 | 99 | 99 | 30 | N |  |  | OP | X | 5 | 1961 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | N |  |  | N | [18 empty] | N |  | N
Vintage1973 | natural gas steam turbine | TRUE | 9273 | Indianapolis Power & Light Co | 990 | Harding Street | IN | Marion | 7 | Natural Gas Steam Turbine | ST |  | S | X | X | IPL.16STOU7O7 | IPL.16STOU7O7 | 463 | 0.85 | 418 | 418 | 130 | N |  |  | OP | X | 7 | 1973 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | N |  |  | N | [18 empty] | N |  | N
Vintage2016 | other | TRUE | 9273 | Indianapolis Power & Light Co | 990 | Harding Street | IN | Marion | BAT1 | Batteries | BA |  | S | X | X |  |  | 20 |  | 20 | 20 | 0.1 | N |  |  | OP | X | 6 | 2016 |  |  | N | Electric Utility | 1 | X | MWH | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1973 | petroleum | TRUE | 9273 | Indianapolis Power & Light Co | 990 | Harding Street | IN | Marion | GT1 | Petroleum Liquids | GT |  | S | X | X | IPL.16STOUTR1 | IPL.16STOUTR1 | 26 | 0.9 | 19.1 | 27.4 | 5 | N |  |  | OP | X | 5 | 1973 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1973 | petroleum | TRUE | 9273 | Indianapolis Power & Light Co | 990 | Harding Street | IN | Marion | GT2 | Petroleum Liquids | GT |  | S | X | X | IPL.16STOUTR1 | IPL.16STOUTR1 | 26 | 0.9 | 17.9 | 22.6 | 5 | N |  |  | OP | X | 5 | 1973 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1994 | natural gas peaker | TRUE | 9273 | Indianapolis Power & Light Co | 990 | Harding Street | IN | Marion | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | IPL.16STOC4C4 | IPL.16STOC4C4 | 83 | 0.8 | 67 | 67 | 45 | N |  |  | OP | X | 4 | 1994 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1995 | natural gas peaker | TRUE | 9273 | Indianapolis Power & Light Co | 990 | Harding Street | IN | Marion | GT5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | IPL.16STOC5C5 | IPL.16STOC5C5 | 83 | 0.8 | 67 | 67 | 45 | N |  |  | OP | X | 1 | 1995 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 9273 | Indianapolis Power & Light Co | 990 | Harding Street | IN | Marion | GT6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | IPL.16STOUCC6 | IPL.16STOUCC6 | 161 | 0.85 | 154 | 154 | 90 | N |  |  | OP | X | 5 | 2002 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1967 | petroleum | TRUE | 9273 | Indianapolis Power & Light Co | 990 | Harding Street | IN | Marion | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.1 | N |  |  | OP | X | 4 | 1967 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage2018 | natural gas combined cycle | TRUE | 9273 | Indianapolis Power & Light Co | 991 | Eagle Valley (IN) | IN | Morgan | GT1 | Natural Gas Fired Combined Cycle | CT | EGVS | S | X | Y |  |  | 207 | 0.85 | 207 | 207 | 110 | N |  |  | OP | X | 4 | 2018 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N | N
Vintage2018 | natural gas combined cycle | TRUE | 9273 | Indianapolis Power & Light Co | 991 | Eagle Valley (IN) | IN | Morgan | GT2 | Natural Gas Fired Combined Cycle | CT | EGVS | S | X | Y |  |  | 207 | 0.85 | 207 | 207 | 110 | N |  |  | OP | X | 4 | 2018 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N | N
Vintage2018 | natural gas combined cycle | TRUE | 9273 | Indianapolis Power & Light Co | 991 | Eagle Valley (IN) | IN | Morgan | STG1 | Natural Gas Fired Combined Cycle | CA | EGVS | S | Y | X |  |  | 230 | 0.85 | 230 | 230 | 75 | N |  |  | OP | X | 4 | 2018 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N | N
Vintage1938 | natural gas steam turbine | TRUE | 3599 | Citizens Thermal Energy | 992 | CC Perry K | IN | Marion | 6 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 5 | 1 | 3 | 5 | 1 | N |  |  | OP | X | 7 | 1938 |  |  | N | IPP CHP | 3 | X | NG | [5 empty] | NG |  |  |  | N | N |  | 12H |  | N | [21 empty] | N | N | N
Vintage2009 | natural gas steam turbine | TRUE | 3599 | Citizens Thermal Energy | 992 | CC Perry K | IN | Marion | 7 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 1.7 | 1 | 1.7 | 1.7 | 0.5 | N |  |  | OP | X | 6 | 2009 |  |  | Y | IPP CHP | 3 | T | NG | [5 empty] | NG |  |  |  | N | N |  | 12H |  | N |  |  | N | [18 empty] | N | N | N
Vintage2009 | natural gas steam turbine | TRUE | 3599 | Citizens Thermal Energy | 992 | CC Perry K | IN | Marion | 8 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 1.7 | 1 | 1.7 | 1.7 | 0.5 | N |  |  | OP | X | 6 | 2009 |  |  | Y | IPP CHP | 3 | T | NG | [5 empty] | NG |  |  |  | N | N |  | 12H |  | N |  |  | N | [18 empty] | N |  | N
Vintage1986 | hard coal | TRUE | 9273 | Indianapolis Power & Light Co | 994 | AES Petersburg | IN | Pike | 4 | Conventional Steam Coal | ST |  | S | X | X |  |  | 670.9 | 0.85 | 529.6 | 534.6 | 220 | N |  |  | OP | X | 4 | 1986 |  |  | N | Electric Utility | 1 | X | BIT | [5 empty] | DFO |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1967 | petroleum | TRUE | 9273 | Indianapolis Power & Light Co | 994 | AES Petersburg | IN | Pike | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 2.7 | N |  |  | OP | X | 8 | 1967 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1967 | petroleum | TRUE | 9273 | Indianapolis Power & Light Co | 994 | AES Petersburg | IN | Pike | IC2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 2.7 | N |  |  | OP | X | 8 | 1967 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1967 | petroleum | TRUE | 9273 | Indianapolis Power & Light Co | 994 | AES Petersburg | IN | Pike | IC3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 2.7 | N |  |  | OP | X | 8 | 1967 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1969 | hard coal | TRUE | 9273 | Indianapolis Power & Light Co | 994 | AES Petersburg | IN | Pike | ST2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 523.3 | 0.85 | 421.8 | 432.2 | 225 | N |  |  | OP | X | 12 | 1969 | 5 | 2023 | N | Electric Utility | 1 | X | BIT | [5 empty] | DFO |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1977 | hard coal | TRUE | 9273 | Indianapolis Power & Light Co | 994 | AES Petersburg | IN | Pike | ST3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 670.9 | 0.85 | 527.6 | 540.3 | 225 | N |  |  | OP | X | 11 | 1977 |  |  | N | Electric Utility | 1 | X | BIT | [5 empty] | DFO |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1974 | hard coal | TRUE | 13756 | Northern Indiana Pub Serv Co | 997 | Michigan City | IN | LaPorte | 12 | Conventional Steam Coal | ST |  | S | X | X | NIPS.MICHCP12 | NIPS.MICHCP12 | 540 | 0.9 | 455 | 455 | 310 | N |  |  | OP | X | 5 | 1974 | 5 | 2028 | N | Electric Utility | 1 | X | SUB | BIT | NG |  |  |  | NG |  |  |  | N | N |  | OVER |  |  |  | Y |  | Y | [17 empty] | Y | Y | N
Vintage1923 | hydro | TRUE | 13756 | Northern Indiana Pub Serv Co | 998 | Norway (IN) | IN | White | 1 | Conventional Hydroelectric | HY |  | S | X | X | NIPS.NORWAPNOR | NIPS.NORWAPNOR | 2 | 0.85 | 1.1 | 1.1 | 0.5 | N |  |  | OP | X | 6 | 1923 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H
Vintage1923 | hydro | TRUE | 13756 | Northern Indiana Pub Serv Co | 998 | Norway (IN) | IN | White | 2 | Conventional Hydroelectric | HY |  | S | X | X | NIPS.NORWAPNOR | NIPS.NORWAPNOR | 2 | 0.85 | 1.1 | 1.1 | 0.5 | N |  |  | OP | X | 6 | 1923 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H
Vintage1923 | hydro | TRUE | 13756 | Northern Indiana Pub Serv Co | 998 | Norway (IN) | IN | White | 3 | Conventional Hydroelectric | HY |  | S | X | X | NIPS.NORWAPNOR | NIPS.NORWAPNOR | 2 | 0.85 | 1.1 | 1.1 | 0.5 | N |  |  | OP | X | 6 | 1923 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H
Vintage1923 | hydro | TRUE | 13756 | Northern Indiana Pub Serv Co | 998 | Norway (IN) | IN | White | 4 | Conventional Hydroelectric | HY |  | S | X | X | NIPS.NORWAPNOR | NIPS.NORWAPNOR | 1.3 | 0.85 | 0.7 | 0.7 | 0.4 | N |  |  | OP | X | 6 | 1923 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H
Vintage1925 | hydro | TRUE | 13756 | Northern Indiana Pub Serv Co | 999 | Oakdale | IN | Carroll | 1 | Conventional Hydroelectric | HY |  | S | X | X | NIPS.OAKDAPOAK | NIPS.OAKDAPOAK | 4.3 | 0.85 | 2.9 | 2.9 | 1 | N |  |  | OP | X | 11 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H
Vintage1925 | hydro | TRUE | 13756 | Northern Indiana Pub Serv Co | 999 | Oakdale | IN | Carroll | 2 | Conventional Hydroelectric | HY |  | S | X | X | NIPS.OAKDAPOAK | NIPS.OAKDAPOAK | 3.2 | 0.85 | 2.2 | 2.2 | 0.8 | N |  |  | OP | X | 11 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H
Vintage1925 | hydro | TRUE | 13756 | Northern Indiana Pub Serv Co | 999 | Oakdale | IN | Carroll | 3 | Conventional Hydroelectric | HY |  | S | X | X | NIPS.OAKDAPOAK | NIPS.OAKDAPOAK | 4.3 | 0.85 | 0.9 | 0.9 | 0.4 | N |  |  | OP | X | 11 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H
Vintage1970 | hard coal | TRUE | 15470 | Duke Energy Indiana, LLC | 1001 | Cayuga | IN | Vermillion | 1 | Conventional Steam Coal | ST |  | S | X | X | CP/Comm Pricing | CP/Comm Pricing | 531 | 0.9 | 500 | 505 | 300 | N |  |  | OP | X | 10 | 1970 |  |  | N | Electric Utility | 1 | X | BIT | DFO |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N
Vintage1972 | hard coal | TRUE | 15470 | Duke Energy Indiana, LLC | 1001 | Cayuga | IN | Vermillion | 2 | Conventional Steam Coal | ST |  | S | X | X | CP/Comm Pricing | CP/Comm Pricing | 531 | 0.9 | 495 | 500 | 230 | N |  |  | OP | X | 6 | 1972 |  |  | N | Electric Utility | 1 | X | BIT | DFO |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N
Vintage1972 | petroleum | TRUE | 15470 | Duke Energy Indiana, LLC | 1001 | Cayuga | IN | Vermillion | 31 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.6 | 0.9 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 6 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H |  | N | [21 empty] | N | N
Vintage1972 | petroleum | TRUE | 15470 | Duke Energy Indiana, LLC | 1001 | Cayuga | IN | Vermillion | 32 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.6 | 0.9 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 6 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N
Vintage1972 | petroleum | TRUE | 15470 | Duke Energy Indiana, LLC | 1001 | Cayuga | IN | Vermillion | 33 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.6 | 0.9 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 6 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N
Vintage1972 | petroleum | TRUE | 15470 | Duke Energy Indiana, LLC | 1001 | Cayuga | IN | Vermillion | 34 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.6 | 0.9 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 6 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N
Vintage1993 | natural gas peaker | TRUE | 15470 | Duke Energy Indiana, LLC | 1001 | Cayuga | IN | Vermillion | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | CP/Comm Pricing | CP/Comm Pricing | 112.5 | 0.9 | 84 | 100 | 50 | N |  |  | OP | X | 6 | 1993 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2013 | hard coal | TRUE | 15470 | Duke Energy Indiana, LLC | 1004 | Edwardsport | IN | Knox | CT1 | Coal Integrated Gasification Combined Cycle | CT | 1 | S | X | N | CP/Comm Pricing | CP/Comm Pricing | 236.5 | 0.8 |  |  |  | N |  |  | OP | X | 6 | 2013 |  |  | N | Electric Utility | 1 | X | SGC | NG | [8 empty] | Y | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage2013 | hard coal | TRUE | 15470 | Duke Energy Indiana, LLC | 1004 | Edwardsport | IN | Knox | CT2 | Coal Integrated Gasification Combined Cycle | CT | 1 | S | X | N | CP/Comm Pricing | CP/Comm Pricing | 236.5 | 0.8 |  |  |  | N |  |  | OP | X | 6 | 2013 |  |  | N | Electric Utility | 1 | X | SGC | NG | [8 empty] | Y | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage2013 | hard coal | TRUE | 15470 | Duke Energy Indiana, LLC | 1004 | Edwardsport | IN | Knox | ST | Coal Integrated Gasification Combined Cycle | CA | 1 | S | N | X | CP/Comm Pricing | CP/Comm Pricing | 331.5 | 0.8 | 595 | 618 | 393 | N |  |  | OP | X | 6 | 2013 |  |  | N | Electric Utility | 1 | X | SGC | NG | [8 empty] | Y | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1967 | hydro | TRUE | 15470 | Duke Energy Indiana, LLC | 1005 | Markland | IN | Switzerland | 1 | Conventional Hydroelectric | HY |  | S | X | X | CP/Comm Pricing | CP/Comm Pricing | 25.9 | 0.8 | 17.9 | 17.9 | 15 | Y | 5 | 2021 | OP | X | 4 | 1967 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1967 | hydro | TRUE | 15470 | Duke Energy Indiana, LLC | 1005 | Markland | IN | Switzerland | 2 | Conventional Hydroelectric | HY |  | S | X | X | CP/Comm Pricing | CP/Comm Pricing | 25.9 | 0.8 | 17.9 | 17.9 | 17.9 | N |  |  | OP | X | 1 | 1967 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 10M | [23 empty] | N
Vintage1967 | hydro | TRUE | 15470 | Duke Energy Indiana, LLC | 1005 | Markland | IN | Switzerland | 3 | Conventional Hydroelectric | HY |  | S | X | X | CP/Comm Pricing | CP/Comm Pricing | 25.9 | 0.8 | 17.9 | 17.9 | 17.9 | N |  |  | OP | X | 2 | 1967 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1950 | natural gas combined cycle | TRUE | 15470 | Duke Energy Indiana, LLC | 1007 | Noblesville | IN | Hamilton | 1 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X | CP/Comm Pricing | CP/Comm Pricing | 50 | 0.8 | 42 | 43 | 42 | N |  |  | OP | X | 12 | 1950 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N
Vintage1950 | natural gas combined cycle | TRUE | 15470 | Duke Energy Indiana, LLC | 1007 | Noblesville | IN | Hamilton | 2 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X | CP/Comm Pricing | CP/Comm Pricing | 50 | 0.8 | 43 | 44 | 43 | N |  |  | OP | X | 9 | 1950 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N
Vintage2003 | natural gas combined cycle | TRUE | 15470 | Duke Energy Indiana, LLC | 1007 | Noblesville | IN | Hamilton | 3 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y | CP/Comm Pricing | CP/Comm Pricing | 61 | 0.8 | 60 | 74 | 60 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N
Vintage2003 | natural gas combined cycle | TRUE | 15470 | Duke Energy Indiana, LLC | 1007 | Noblesville | IN | Hamilton | 4 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y | CP/Comm Pricing | CP/Comm Pricing | 61 | 0.8 | 60 | 74 | 60 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N
Vintage2003 | natural gas combined cycle | TRUE | 15470 | Duke Energy Indiana, LLC | 1007 | Noblesville | IN | Hamilton | 5 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y | CP/Comm Pricing | CP/Comm Pricing | 61 | 0.8 | 59 | 75 | 59 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N
Vintage1966 | hard coal | TRUE | 17633 | Southern Indiana Gas & Elec Co | 1012 | F B Culley | IN | Warrick | 2 | Conventional Steam Coal | ST |  | S | X | X | SIGE.CULGN2 | SIGE.CULGN2 | 103.7 | 0.85 | 90 | 90 | 45 | N |  |  | OP | X | 12 | 1966 | 12 | 2025 | N | Electric Utility | 1 | X | BIT | NG |  |  |  |  | NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1973 | hard coal | TRUE | 17633 | Southern Indiana Gas & Elec Co | 1012 | F B Culley | IN | Warrick | 3 | Conventional Steam Coal | ST |  | S | X | X | SIGE.CULGN3 | SIGE.CULGN3 | 265.2 | 0.95 | 270 | 270 | 135 | N |  |  | OP | X | 6 | 1973 |  |  | N | Electric Utility | 1 | X | BIT | NG |  |  |  |  | NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1976 | natural gas combined cycle | TRUE | 6235 | Fayetteville Public Works Commission | 1016 | Butler-Warner Generation Plant | NC | Cumberland | 1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 28.8 | 0.9 | 20 | 25 | 1 | N |  |  | OP | X | 12 | 1976 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2019 | solar pv | TRUE | 6235 | Fayetteville Public Works Commission | 1016 | Butler-Warner Generation Plant | NC | Cumberland | 10 | Solar Photovoltaic | PV |  | S | X | X |  |  | 1 |  | 1 | 1 |  | N |  |  | OP | X | 6 | 2019 |  |  | N | Electric Utility | 1 | X | SUN | [9 empty] | N | N | [22 empty] | N |  |  | N
Vintage2019 | other | TRUE | 6235 | Fayetteville Public Works Commission | 1016 | Butler-Warner Generation Plant | NC | Cumberland | 11 | Batteries | BA |  | S | X | X |  |  | 0.5 |  | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 9 | 2019 |  |  | N | Electric Utility | 1 | X | MWH | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1976 | natural gas combined cycle | TRUE | 6235 | Fayetteville Public Works Commission | 1016 | Butler-Warner Generation Plant | NC | Cumberland | 2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 28.8 | 0.9 | 20 | 25 | 1 | N |  |  | OP | X | 12 | 1976 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1976 | natural gas combined cycle | TRUE | 6235 | Fayetteville Public Works Commission | 1016 | Butler-Warner Generation Plant | NC | Cumberland | 3 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 28.8 | 0.9 | 20 | 25 | 1 | N |  |  | OP | X | 7 | 1976 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1976 | natural gas peaker | TRUE | 6235 | Fayetteville Public Works Commission | 1016 | Butler-Warner Generation Plant | NC | Cumberland | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 28.8 | 0.9 | 20 | 25 | 1 | N |  |  | OP | X | 7 | 1976 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1977 | natural gas peaker | TRUE | 6235 | Fayetteville Public Works Commission | 1016 | Butler-Warner Generation Plant | NC | Cumberland | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 28.8 | 0.9 | 20 | 25 | 1 | N |  |  | OP | X | 7 | 1977 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1978 | natural gas combined cycle | TRUE | 6235 | Fayetteville Public Works Commission | 1016 | Butler-Warner Generation Plant | NC | Cumberland | 6 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 28.8 | 0.9 | 20 | 25 | 1 | N |  |  | OP | X | 6 | 1978 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1979 | natural gas combined cycle | TRUE | 6235 | Fayetteville Public Works Commission | 1016 | Butler-Warner Generation Plant | NC | Cumberland | 7 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 28.8 | 0.9 | 20 | 25 | 1 | N |  |  | OP | X | 6 | 1979 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1980 | natural gas combined cycle | TRUE | 6235 | Fayetteville Public Works Commission | 1016 | Butler-Warner Generation Plant | NC | Cumberland | 8 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 28.8 | 0.9 | 20 | 25 | 1 | N |  |  | OP | X | 5 | 1980 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1988 | natural gas combined cycle | TRUE | 6235 | Fayetteville Public Works Commission | 1016 | Butler-Warner Generation Plant | NC | Cumberland | 9 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X |  |  | 73 | 0.9 | 65 | 65 | 15 | N |  |  | OP | X | 12 | 1988 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage1989 | hydro | TRUE | 11588 | City of Manti - (UT) | 1020 | Manti Lower | UT | Sanpete | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.5 | 0.1 | 0.1 | N |  |  | OP | X | 1 | 1989 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1989 | hydro | TRUE | 11588 | City of Manti - (UT) | 1020 | Manti Lower | UT | Sanpete | HC1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.5 | 0.1 | 0.1 | N |  |  | OP | X | 1 | 1989 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1955 | hard coal | TRUE | 59774 | Crawfordsville Energy LLC | 1024 | Crawfordsville Power Plant | IN | Montgomery | 4 | Conventional Steam Coal | ST |  | S | X | X |  |  | 11.5 | 0.85 | 10.6 | 10.6 | 1.5 | N |  |  | OS | X | 1 | 1955 | 6 | 2023 | N | IPP Non-CHP | 2 | X | BIT | [5 empty] | NG |  |  |  | N | N |  | 12H |  |  | Y |  | Y | [18 empty] | N | N | N
Vintage1994 | petroleum | TRUE | 59774 | Crawfordsville Energy LLC | 1024 | Crawfordsville Power Plant | IN | Montgomery | D1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.9 | 0.9 | 0.8 | N |  |  | SB | N | 10 | 1994 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 1H |  |  |  | N | [19 empty] | N | N | N
Vintage2002 | petroleum | TRUE | 14839 | City of Peru - (IN) | 1037 | Peru (IN) | IN | Miami | D1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | SB | Y | 10 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | N | N | [21 empty] | N | N | N
Vintage1971 | petroleum | TRUE | 15860 | City of Rensselaer - (IN) | 1038 | Rensselaer City Light Plant | IN | Jasper | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.9 | 1.9 | 0.5 | N |  |  | OS | X | 1 | 1971 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1971 | petroleum | TRUE | 15860 | City of Rensselaer - (IN) | 1038 | Rensselaer City Light Plant | IN | Jasper | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.9 | 1.9 | 0.5 | N |  |  | OS | X | 1 | 1971 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1994 | natural gas peaker | TRUE | 15860 | City of Rensselaer - (IN) | 1038 | Rensselaer City Light Plant | IN | Jasper | 14 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 5 | 0.8 | 4.8 | 4.8 | 1 | N |  |  | OS | X | 7 | 1994 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2006 | natural gas peaker | TRUE | 15860 | City of Rensselaer - (IN) | 1038 | Rensselaer City Light Plant | IN | Jasper | 15 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 8.4 | 0.8 | 8.3 | 8.3 | 5.3 | N |  |  | OP | X | 9 | 2006 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1950 | petroleum | TRUE | 15860 | City of Rensselaer - (IN) | 1038 | Rensselaer City Light Plant | IN | Jasper | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.9 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | SB | Y | 1 | 1950 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1957 | petroleum | TRUE | 15860 | City of Rensselaer - (IN) | 1038 | Rensselaer City Light Plant | IN | Jasper | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.4 | 2.4 | 0.7 | N |  |  | SB | Y | 1 | 1957 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1955 | hard coal | TRUE | 15989 | City of Richmond - (IN) | 1040 | Whitewater Valley | IN | Wayne | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 33 | 0.85 | 34.7 | 34.7 | 13 | N |  |  | OP | X | 3 | 1955 |  |  | N | Electric Utility | 1 | X | BIT | [5 empty] | DFO |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1973 | hard coal | TRUE | 15989 | City of Richmond - (IN) | 1040 | Whitewater Valley | IN | Wayne | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 60.9 | 0.85 | 65 | 65 | 28 | N |  |  | OP | X | 8 | 1973 |  |  | N | Electric Utility | 1 | X | BIT | [5 empty] | DFO |  |  |  | N | N | 0 | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1977 | hard coal | TRUE | 9417 | Interstate Power and Light Co | 1047 | Lansing | IA | Allamakee | 4 | Conventional Steam Coal | ST |  | S | X | X | ALTW.LANSIN4 | ALTW.LANSIN4 | 274.5 | 0.9 | 235.3 | 238.3 | 100 | N |  |  | OP | X | 5 | 1977 | 12 | 2022 | N | Electric Utility | 1 | X | SUB | DFO |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | N |  |  | N | N | N
Vintage1924 | hydro | TRUE | 58149 | Renewable World Energies LLC | 1067 | Iowa Hydro LLC | IA | Jackson | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0 | N |  |  | OP | X | 1 | 1924 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1924 | hydro | TRUE | 58149 | Renewable World Energies LLC | 1067 | Iowa Hydro LLC | IA | Jackson | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0 | N |  |  | OP | X | 1 | 1924 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N |  | 0 | 10M | [23 empty] | N
Vintage1978 | natural gas peaker | TRUE | 9417 | Interstate Power and Light Co | 1068 | Marshalltown | IA | Marshall | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | ALTW.MTOWNCT1 | ALTW.MTOWNCT1 | 63 | 0.9 | 56 | 67.5 | 30 | N |  |  | OP | X | 6 | 1978 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1978 | natural gas peaker | TRUE | 9417 | Interstate Power and Light Co | 1068 | Marshalltown | IA | Marshall | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | ALTW.MTOWNCT2 | ALTW.MTOWNCT2 | 63 | 0.9 | 57.4 | 69.8 | 30 | N |  |  | OP | X | 6 | 1978 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1978 | natural gas peaker | TRUE | 9417 | Interstate Power and Light Co | 1068 | Marshalltown | IA | Marshall | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | ALTW.MTOWNCT3 | ALTW.MTOWNCT3 | 63 | 0.9 | 54.2 | 65.5 | 30 | N |  |  | OP | X | 7 | 1978 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1997 | hard coal | TRUE | 9417 | Interstate Power and Light Co | 1073 | Prairie Creek | IA | Linn | 1 | Conventional Steam Coal | ST |  | S | X | X | ALTW.PRARC1 | ALTW.PRARC1 | 14.6 | 0.9 | 4.2 | 4.2 | 1.5 | N |  |  | OP | X | 4 | 1997 |  |  | Y | Electric Utility | 1 | T | SUB | NG |  |  |  |  | NG |  |  |  | N | N |  | 12H |  |  |  | Y | Y | [15 empty] | Y | 12 | 2025 | Y | Y | N
Vintage1958 | hard coal | TRUE | 9417 | Interstate Power and Light Co | 1073 | Prairie Creek | IA | Linn | 3 | Conventional Steam Coal | ST |  | S | X | X | ALTW.PRARC3 | ALTW.PRARC3 | 50 | 0.85 | 29.3 | 32.2 | 9.2 | N |  |  | OP | X | 10 | 1958 |  |  | Y | Electric Utility | 1 | T | SUB | NG |  |  |  |  | NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [15 empty] | Y | 12 | 2025 | Y | Y | N
Vintage1967 | natural gas steam turbine | TRUE | 9417 | Interstate Power and Light Co | 1073 | Prairie Creek | IA | Linn | 4 | Natural Gas Steam Turbine | ST |  | S | X | X | ALTW.PRARC4 | ALTW.PRARC4 | 148.8 | 0.85 | 117.8 | 121.9 | 35 | N |  |  | OP | X | 4 | 1967 |  |  | Y | Electric Utility | 1 | T | NG | [5 empty] | NG |  |  |  | N | N |  | 12H |  | N |  |  | N | [15 empty] | N |  |  | N | N | N
Vintage1970 | natural gas peaker | TRUE | 12341 | MidAmerican Energy Co | 1079 | Coralville GT | IA | Johnson | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MEC.CORALV1 | MEC.CORALV1 | 18 | 0.85 | 16.7 | 20 | 2.5 | N |  |  | OP | X | 6 | 1970 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 1H | [23 empty] | N | N
Vintage1970 | natural gas peaker | TRUE | 12341 | MidAmerican Energy Co | 1079 | Coralville GT | IA | Johnson | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MEC.CORALV2 | MEC.CORALV2 | 18 | 0.85 | 17.2 | 20 | 2.5 | N |  |  | OP | X | 6 | 1970 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 10M | [23 empty] | N | N
Vintage1970 | natural gas peaker | TRUE | 12341 | MidAmerican Energy Co | 1079 | Coralville GT | IA | Johnson | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MEC.CORALV3 | MEC.CORALV3 | 18 | 0.85 | 16.8 | 20 | 2.5 | N |  |  | OP | X | 6 | 1970 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 10M | [23 empty] | N | N
Vintage1970 | natural gas peaker | TRUE | 12341 | MidAmerican Energy Co | 1079 | Coralville GT | IA | Johnson | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 18 | 0.85 | 16.5 | 20 | 2.5 | N |  |  | OP | X | 6 | 1970 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1978 | hard coal | TRUE | 12341 | MidAmerican Energy Co | 1082 | Walter Scott Jr Energy Center | IA | Pottawattamie | 3 | Conventional Steam Coal | ST |  | J | X | X | MEC.WSEC3 | MEC.WSEC3 | 725.8 | 0.9 | 705.2 | 705.2 | 250 | N |  |  | OP | X | 12 | 1978 |  |  | Y | Electric Utility | 1 | T | RC | [5 empty] | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N
Vintage2007 | hard coal | TRUE | 12341 | MidAmerican Energy Co | 1082 | Walter Scott Jr Energy Center | IA | Pottawattamie | 4 | Conventional Steam Coal | ST |  | J | X | X | MEC.WSEC4 | MEC.WSEC4 | 922.5 | 0.9 | 811.2 | 811.2 | 230 | N |  |  | OP | X | 6 | 2007 |  |  | N | Electric Utility | 1 | X | RC | [5 empty] | DFO |  |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | N | N | N
Vintage1966 | natural gas peaker | TRUE | 12341 | MidAmerican Energy Co | 1084 | River Hills | IA | Polk | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MEC.RHILLS14&58 | MEC.RHILLS14&58 | 16 | 0.85 | 14.9 | 16 | 2.5 | N |  |  | OP | X | 5 | 1966 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1966 | natural gas peaker | TRUE | 12341 | MidAmerican Energy Co | 1084 | River Hills | IA | Polk | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MEC.RHILLS14&58 | MEC.RHILLS14&58 | 16 | 0.85 | 14.9 | 16 | 2.5 | N |  |  | OP | X | 5 | 1966 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1966 | natural gas peaker | TRUE | 12341 | MidAmerican Energy Co | 1084 | River Hills | IA | Polk | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MEC.RHILLS14&58 | MEC.RHILLS14&58 | 16 | 0.85 | 14.9 | 16 | 2.5 | N |  |  | OP | X | 5 | 1966 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1966 | natural gas peaker | TRUE | 12341 | MidAmerican Energy Co | 1084 | River Hills | IA | Polk | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 16 | 0.85 | 14.9 | 16 | 2.5 | N |  |  | OP | X | 5 | 1966 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1967 | natural gas peaker | TRUE | 12341 | MidAmerican Energy Co | 1084 | River Hills | IA | Polk | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 16 | 0.85 | 14.5 | 16 | 2.5 | N |  |  | OP | X | 10 | 1967 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1967 | natural gas peaker | TRUE | 12341 | MidAmerican Energy Co | 1084 | River Hills | IA | Polk | 6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 16 | 0.85 | 14.5 | 16 | 2.5 | N |  |  | OP | X | 10 | 1967 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1968 | natural gas peaker | TRUE | 12341 | MidAmerican Energy Co | 1084 | River Hills | IA | Polk | 7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 16 | 0.85 | 14.5 | 16 | 2.5 | N |  |  | OP | X | 4 | 1968 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1968 | natural gas peaker | TRUE | 12341 | MidAmerican Energy Co | 1084 | River Hills | IA | Polk | 8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 16 | 0.85 | 14.5 | 16 | 2.5 | N |  |  | OP | X | 4 | 1968 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1975 | hard coal | TRUE | 12341 | MidAmerican Energy Co | 1091 | George Neal North | IA | Woodbury | 3 | Conventional Steam Coal | ST |  | J | X | X | MEC.NEALN3 | MEC.NEALN3 | 584.1 | 0.9 | 513.9 | 513.9 | 150 | N |  |  | OP | X | 5 | 1975 |  |  | N | Electric Utility | 1 | X | RC | NG |  |  |  |  | NG |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N | N
Vintage1969 | natural gas peaker | TRUE | 12341 | MidAmerican Energy Co | 1097 | Merl Parr | IA | Floyd | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MEC.CHASCS1 | MEC.CHASCDS1 | 18 | 0.9 | 16.3 | 18 | 6 | N |  |  | OP | X | 5 | 1969 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1969 | natural gas peaker | TRUE | 12341 | MidAmerican Energy Co | 1097 | Merl Parr | IA | Floyd | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MEC.CHASCS2 | MEC.CHASCS2 | 18 | 0.9 | 16.4 | 18 | 6 | N |  |  | OP | X | 5 | 1969 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1968 | hard coal | TRUE | 9417 | Interstate Power and Light Co | 1104 | Burlington (IA) | IA | Des Moines | 1 | Conventional Steam Coal | ST |  | S | X | X | ALTW.BRLGTN5 | ALTW.BRLGTN5 | 212 | 0.9 | 191.2 | 192.4 | 80 | N |  |  | OP | X | 6 | 1968 |  |  | N | Electric Utility | 1 | X | SUB | NG |  |  |  |  | NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | N |  |  | N | N | N
Vintage1994 | natural gas peaker | TRUE | 9417 | Interstate Power and Light Co | 1104 | Burlington (IA) | IA | Des Moines | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | ALTW.BRLGTN 1 | ALTW.BRLGTN 1 | 19.7 | 0.9 | 6.4 | 9.4 | 5 | N |  |  | OP | X | 5 | 1994 | 6 | 2026 | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1995 | natural gas peaker | TRUE | 9417 | Interstate Power and Light Co | 1104 | Burlington (IA) | IA | Des Moines | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | ALTW.BRLGTN 2 | ALTW.BRLGTN 2 | 19.7 | 0.9 | 11 | 14 | 5 | N |  |  | OP | X | 5 | 1995 | 6 | 2026 | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1996 | natural gas peaker | TRUE | 9417 | Interstate Power and Light Co | 1104 | Burlington (IA) | IA | Des Moines | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | ALTW.BRLGTN 3 | ALTW.BRLGTN 3 | 19.7 | 0.9 | 12.9 | 15.9 | 5 | N |  |  | OP | X | 4 | 1996 | 6 | 2026 | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1994 | natural gas peaker | TRUE | 9417 | Interstate Power and Light Co | 1104 | Burlington (IA) | IA | Des Moines | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | ALTW.BRLGTN 4 | ALTW.BRLGTN 4 | 19.7 | 0.9 | 5 | 5 | 5 | N |  |  | OP | X | 7 | 1994 | 6 | 2026 | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1913 | hydro | TRUE | 19436 | Union Electric Co - (MO) | 1109 | Keokuk | IA | Lee | 1 | Conventional Hydroelectric | HY |  | S | X | X | AMMO.KEOKUK1 | AMMO.KEOKUK1 | 7.6 | 0.8 | 10 | 10 | 0 | N |  |  | OP | X | 8 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H
Vintage1913 | hydro | TRUE | 19436 | Union Electric Co - (MO) | 1109 | Keokuk | IA | Lee | 10 | Conventional Hydroelectric | HY |  | S | X | X | AMMO.KEOKUK10 | AMMO.KEOKUK10 | 8.8 | 0.8 | 10 | 10 | 0 | N |  |  | OP | X | 8 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H
Vintage1913 | hydro | TRUE | 19436 | Union Electric Co - (MO) | 1109 | Keokuk | IA | Lee | 11 | Conventional Hydroelectric | HY |  | S | X | X | AMMO.KEOKUK11 | AMMO.KEOKUK11 | 8.8 | 0.8 | 10 | 10 | 0 | N |  |  | OP | X | 8 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H
Vintage1913 | hydro | TRUE | 19436 | Union Electric Co - (MO) | 1109 | Keokuk | IA | Lee | 12 | Conventional Hydroelectric | HY |  | S | X | X | AMMO.KEOKUK12 | AMMO.KEOKUK12 | 8.8 | 0.8 | 10 | 10 | 0 | N |  |  | OP | X | 8 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H
Vintage1913 | hydro | TRUE | 19436 | Union Electric Co - (MO) | 1109 | Keokuk | IA | Lee | 13 | Conventional Hydroelectric | HY |  | S | X | X | AMMO.KEOKUK13 | AMMO.KEOKUK13 | 8.8 | 0.8 | 10 | 10 | 0 | N |  |  | OP | X | 8 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H
Vintage1913 | hydro | TRUE | 19436 | Union Electric Co - (MO) | 1109 | Keokuk | IA | Lee | 14 | Conventional Hydroelectric | HY |  | S | X | X | AMMO.KEOKUK14 | AMMO.KEOKUK14 | 8.8 | 0.8 | 10 | 10 | 0 | N |  |  | OP | X | 8 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H
Vintage1913 | hydro | TRUE | 19436 | Union Electric Co - (MO) | 1109 | Keokuk | IA | Lee | 15 | Conventional Hydroelectric | HY |  | S | X | X | AMMO.KEOKUK15 | AMMO.KEOKUK15 | 8.8 | 0.8 | 8 | 8 | 0 | N |  |  | OP | X | 8 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H
Vintage1913 | hydro | TRUE | 19436 | Union Electric Co - (MO) | 1109 | Keokuk | IA | Lee | 2 | Conventional Hydroelectric | HY |  | S | X | X | AMMO.KEOKUK2 | AMMO.KEOKUK2 | 7.6 | 0.8 | 10 | 10 | 0 | N |  |  | OP | X | 8 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H
Vintage1913 | hydro | TRUE | 19436 | Union Electric Co - (MO) | 1109 | Keokuk | IA | Lee | 3 | Conventional Hydroelectric | HY |  | S | X | X | AMMO.KEOKUK3 | AMMO.KEOKUK3 | 7.6 | 0.8 | 10 | 10 | 0 | N |  |  | OP | X | 8 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H
Vintage1913 | hydro | TRUE | 19436 | Union Electric Co - (MO) | 1109 | Keokuk | IA | Lee | 4 | Conventional Hydroelectric | HY |  | S | X | X | AMMO.KEOKUK4 | AMMO.KEOKUK4 | 7.6 | 0.8 | 10 | 10 | 0 | N |  |  | OP | X | 8 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H
Vintage1913 | hydro | TRUE | 19436 | Union Electric Co - (MO) | 1109 | Keokuk | IA | Lee | 5 | Conventional Hydroelectric | HY |  | S | X | X | AMMO.KEOKUK5 | AMMO.KEOKUK5 | 7.6 | 0.8 | 8 | 8 | 0 | N |  |  | OP | X | 8 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H
Vintage1913 | hydro | TRUE | 19436 | Union Electric Co - (MO) | 1109 | Keokuk | IA | Lee | 6 | Conventional Hydroelectric | HY |  | S | X | X | AMMO.KEOKUK6 | AMMO.KEOKUK6 | 7.6 | 0.8 | 10 | 10 | 0 | N |  |  | OP | X | 8 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H
Vintage1913 | hydro | TRUE | 19436 | Union Electric Co - (MO) | 1109 | Keokuk | IA | Lee | 7 | Conventional Hydroelectric | HY |  | S | X | X | AMMO.KEOKUK7 | AMMO.KEOKUK7 | 8.8 | 0.8 | 10 | 10 | 0 | N |  |  | OP | X | 8 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H
Vintage1913 | hydro | TRUE | 19436 | Union Electric Co - (MO) | 1109 | Keokuk | IA | Lee | 8 | Conventional Hydroelectric | HY |  | S | X | X | AMMO.KEOKUK8 | AMMO.KEOKUK8 | 8.8 | 0.8 | 10 | 10 | 0 | N |  |  | OP | X | 8 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H
Vintage1913 | hydro | TRUE | 19436 | Union Electric Co - (MO) | 1109 | Keokuk | IA | Lee | 9 | Conventional Hydroelectric | HY |  | S | X | X | AMMO.KEOKUK9 | AMMO.KEOKUK9 | 8.8 | 0.8 | 10 | 10 | 0 | N |  |  | OP | X | 8 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 1H
Vintage1965 | petroleum | TRUE | 309 | City of Algona - (IA) | 1120 | Algona | IA | Kossuth | 6 | Petroleum Liquids | IC |  | S | X | X | WAUEALGONAMUNALGONA_1_UNIT_RA | WAUEALGONAMUNALGONA_1_UNIT_RA | 3.2 | 0.8 | 3.2 | 3.2 | 0.4 | N |  |  | OP | X | 12 | 1965 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1970 | petroleum | TRUE | 309 | City of Algona - (IA) | 1120 | Algona | IA | Kossuth | 7 | Petroleum Liquids | IC |  | S | X | X | WAUEALGONAMUNALGONA_1_UNIT_RA | WAUEALGONAMUNALGONA_1_UNIT_RA | 4.1 | 0.8 | 4.1 | 4.1 | 0.5 | N |  |  | OP | X | 9 | 1970 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1994 | petroleum | TRUE | 309 | City of Algona - (IA) | 1120 | Algona | IA | Kossuth | 8 | Petroleum Liquids | IC |  | S | X | X | WAUEALGONAMUNALGONA_1_UNIT_RA | WAUEALGONAMUNALGONA_1_UNIT_RA | 4.4 | 0.9 | 4.4 | 4.4 | 0.5 | N |  |  | OP | X | 11 | 1994 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1994 | petroleum | TRUE | 309 | City of Algona - (IA) | 1120 | Algona | IA | Kossuth | 9 | Petroleum Liquids | IC |  | S | X | X | WAUEALGONAMUNALGONA_1_UNIT_RA | WAUEALGONAMUNALGONA_1_UNIT_RA | 4.4 | 0.9 | 4.4 | 4.4 | 0.5 | N |  |  | OP | X | 11 | 1994 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2018 | petroleum | TRUE | 405 | City of Alta - (IA) | 1121 | Alta Municipal Utilities | IA | Buena Vista | 2A | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 1 | 2 | 2.1 | 0 | N |  |  | SB | Y | 11 | 2018 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2018 | petroleum | TRUE | 405 | City of Alta - (IA) | 1121 | Alta Municipal Utilities | IA | Buena Vista | 3A | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 1 | 2 | 2.1 | 0 | N |  |  | SB | Y | 11 | 2018 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1968 | natural gas steam turbine | TRUE | 554 | City of Ames - (IA) | 1122 | Ames Electric Services Power Plant | IA | Story | 7 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 37.5 | 0.85 | 31.8 | 31.8 | 15 | N |  |  | OP | X | 5 | 1968 |  |  | N | Electric Utility | 1 | X | NG | OBS |  |  |  |  | NG |  |  |  | N | N |  | 12H |  | N |  |  | N | [18 empty] | Y | Y | N
Vintage1982 | natural gas steam turbine | TRUE | 554 | City of Ames - (IA) | 1122 | Ames Electric Services Power Plant | IA | Story | 8 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 71.3 | 0.9 | 63.4 | 63.4 | 30 | N |  |  | OP | X | 6 | 1982 |  |  | N | Electric Utility | 1 | X | NG | OBS |  |  |  |  | NG |  |  |  | N | N |  | 12H |  | N |  |  | N | [18 empty] | Y | Y | N
Vintage1939 | petroleum | TRUE | 682 | City of Anita - (IA) | 1123 | Anita | IA | Cass | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.2 | 0.8 | 0.1 | 0.2 | 0 | N |  |  | OP | X | 10 | 1939 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1951 | petroleum | TRUE | 682 | City of Anita - (IA) | 1123 | Anita | IA | Cass | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.2 | 0.3 | 0 | N |  |  | OP | X | 3 | 1951 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2000 | petroleum | TRUE | 682 | City of Anita - (IA) | 1123 | Anita | IA | Cass | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2000 | petroleum | TRUE | 682 | City of Anita - (IA) | 1123 | Anita | IA | Cass | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2003 | petroleum | TRUE | 682 | City of Anita - (IA) | 1123 | Anita | IA | Cass | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0 | N |  |  | OP | X | 4 | 2003 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | natural gas peaker | TRUE | 965 | Atlantic Municipal Utilities | 1124 | Atlantic | IA | Cass | 6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | Behind the meter | Behind the meter | 10 | 0.8 | 9.8 | 10 | 2.5 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1954 | petroleum | TRUE | 1172 | Bancroft Municipal Utilities | 1125 | Bancroft | IA | Kossuth | 5 | Petroleum Liquids | IC |  | S | X | X | WAUEBNCRUNBANCROFT_RA |  | 0.6 | 0.9 | 0.5 | 0.5 | 0.1 | N |  |  | SB | Y | 1 | 1954 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2001 | petroleum | TRUE | 1172 | Bancroft Municipal Utilities | 1125 | Bancroft | IA | Kossuth | 6 | Petroleum Liquids | IC |  | S | X | X | WAUEBNCRUNBANCROFT-RA |  | 1.8 | 0.9 | 1.8 | 1.8 | 0.1 | N |  |  | OP | X | 3 | 2001 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2001 | petroleum | TRUE | 1172 | Bancroft Municipal Utilities | 1125 | Bancroft | IA | Kossuth | 7 | Petroleum Liquids | IC |  | S | X | X | WAUEBNCRUNBANCROFT-RA |  | 1.8 | 0.9 | 1.8 | 1.8 | 0.1 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2021 | petroleum | TRUE | 1515 | City of Bellevue - (IA) | 1126 | Bellevue | IA | Jackson | 1A | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.7 | 1.8 | 0.2 | N |  |  | SB | Y | 7 | 2021 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1992 | petroleum | TRUE | 1515 | City of Bellevue - (IA) | 1126 | Bellevue | IA | Jackson | 2 | Petroleum Liquids | IC |  | S | X | X | ALTW.ALTW | ALTW.ALTW | 1.6 | 0.8 | 1.6 | 1.6 | 0.2 | N |  |  | SB | Y | 5 | 1992 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2001 | petroleum | TRUE | 1515 | City of Bellevue - (IA) | 1126 | Bellevue | IA | Jackson | 3 | Petroleum Liquids | IC |  | S | X | X | ALTW.ALTW | ALTW.ALTW | 1.8 | 0.8 | 1.7 | 1.8 | 0.2 | N |  |  | SB | Y | 5 | 2001 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1963 | petroleum | TRUE | 1515 | City of Bellevue - (IA) | 1126 | Bellevue | IA | Jackson | 4 | Petroleum Liquids | IC |  | S | X | X | ALTW.ALTW | ALTW.ALTW | 0.7 | 0.8 | 0.6 | 0.6 | 0.2 | N |  |  | SB | Y | 7 | 1963 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1953 | petroleum | TRUE | 1515 | City of Bellevue - (IA) | 1126 | Bellevue | IA | Jackson | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.7 | 0.7 | 0.2 | N |  |  | SB | Y | 7 | 1953 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1971 | petroleum | TRUE | 1515 | City of Bellevue - (IA) | 1126 | Bellevue | IA | Jackson | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.8 | 2.4 | 2.4 | 0.5 | N |  |  | SB | Y | 7 | 1971 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1975 | natural gas peaker | TRUE | 1869 | City of Bloomfield - (IA) | 1127 | Bloomfield | IA | Davis | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.8 | 0.8 | 2.3 | 2.3 | 1.6 | N |  |  | SB | Y | 10 | 1975 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | N
Vintage1945 | petroleum | TRUE | 1869 | City of Bloomfield - (IA) | 1127 | Bloomfield | IA | Davis | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | SB | Y | 4 | 1945 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N | N | N
Vintage1964 | natural gas peaker | TRUE | 1869 | City of Bloomfield - (IA) | 1127 | Bloomfield | IA | Davis | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2.2 | 2.2 | 1.2 | N |  |  | SB | Y | 12 | 1964 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | N
Vintage1946 | petroleum | TRUE | 1869 | City of Bloomfield - (IA) | 1127 | Bloomfield | IA | Davis | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | SB | Y | 5 | 1946 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N | N | N
Vintage1951 | natural gas peaker | TRUE | 1869 | City of Bloomfield - (IA) | 1127 | Bloomfield | IA | Davis | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.8 | 0.8 | 0.5 | N |  |  | SB | Y | 6 | 1951 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | N
Vintage1958 | natural gas peaker | TRUE | 1869 | City of Bloomfield - (IA) | 1127 | Bloomfield | IA | Davis | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.2 | 1.2 | 0.6 | N |  |  | SB | Y | 7 | 1958 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y |  | N
Vintage2012 | petroleum | TRUE | 2287 | City of Brooklyn - (IA) | 1128 | Brooklyn | IA | Poweshiek | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.3 | 1 | 2 | 2 | 0.2 | N |  |  | OP | X | 9 | 2012 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1957 | petroleum | TRUE | 3137 | Cascade Municipal Utilities | 1129 | Cascade | IA | Dubuque | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.7 | 0.8 | 0.7 | 0.7 | 0.1 | N |  |  | SB | Y | 2 | 1957 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1971 | petroleum | TRUE | 3137 | Cascade Municipal Utilities | 1129 | Cascade | IA | Dubuque | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.9 | 2 | 0.3 | N |  |  | SB | Y | 12 | 1971 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [20 empty] | N |  |  | Y | Y | Y
Vintage1998 | petroleum | TRUE | 3137 | Cascade Municipal Utilities | 1129 | Cascade | IA | Dubuque | 3A | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | SB | Y | 1 | 1998 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1951 | petroleum | TRUE | 3137 | Cascade Municipal Utilities | 1129 | Cascade | IA | Dubuque | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.7 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | SB | Y | 4 | 1951 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N | 0 | 1H | [20 empty] | N |  |  | N | N | N
Vintage2020 | petroleum | TRUE | 3137 | Cascade Municipal Utilities | 1129 | Cascade | IA | Dubuque | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.9 | 1.9 | 0.5 | N |  |  | SB | Y | 1 | 2020 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N | 0 | 1H | [20 empty] | N |  |  | N | N | N
Vintage1968 | natural gas peaker | TRUE | 3203 | Cedar Falls Utilities | 1130 | Gas Turbine (IA) | IA | Black Hawk | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MEC.CFU | MEC.CFU | 19.6 | 0.85 | 17.6 | 17.6 | 5 | N |  |  | OP | X | 1 | 1968 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2000 | natural gas peaker | TRUE | 3203 | Cedar Falls Utilities | 1130 | Gas Turbine (IA) | IA | Black Hawk | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 23.8 | 0.85 | 22.7 | 22.7 | 10 | N |  |  | OP | X | 9 | 2000 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1963 | natural gas steam turbine | TRUE | 3203 | Cedar Falls Utilities | 1131 | Streeter Station | IA | Black Hawk | 6 | Natural Gas Steam Turbine | ST |  | S | X | X | MEC.CFU | MEC.CFU | 16.5 | 0.85 | 19.4 | 19.4 | 5 | N |  |  | OP | X | 9 | 1963 |  |  | N | Electric Utility | 1 | X | NG | BIT | WDS | OBS | AB |  | NG | BIT |  |  | N | N |  | 12H |  | N | Y |  | Y | [18 empty] | Y | Y | N
Vintage1973 | natural gas steam turbine | TRUE | 3203 | Cedar Falls Utilities | 1131 | Streeter Station | IA | Black Hawk | 7 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 35 | 0.9 | 36.2 | 36.2 | 6 | N |  |  | OP | X | 6 | 1973 |  |  | N | Electric Utility | 1 | X | NG | BIT |  |  |  |  | NG | BIT |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage2003 | petroleum | TRUE | 3900 | City of Coggon - (IA) | 1132 | Coggon | IA | Linn | IC5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 0.6 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1975 | petroleum | TRUE | 4375 | City of Corning - (IA) | 1134 | Corning | IA | Adams | 5 | Petroleum Liquids | IC |  | S | X | X | ALTW.ALTW | ALTW.ALTW | 2.8 | 0.9 | 2.8 | 2.8 | 0.1 | N |  |  | SB | Y | 6 | 1975 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage2006 | petroleum | TRUE | 4375 | City of Corning - (IA) | 1134 | Corning | IA | Adams | 6 | Petroleum Liquids | IC |  | S | X | X | ALTW.ALTW | ALTW.ALTW | 2 | 0.9 | 2 | 2 | 0.1 | N |  |  | SB | Y | 3 | 2006 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage2006 | petroleum | TRUE | 4375 | City of Corning - (IA) | 1134 | Corning | IA | Adams | 7 | Petroleum Liquids | IC |  | S | X | X | ALTW.ALTW | ALTW.ALTW | 2 | 0.9 | 2 | 2 | 0.1 | N |  |  | SB | Y | 3 | 2006 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage2000 | petroleum | TRUE | 4919 | City of Dayton - (IA) | 1135 | Dayton (IA) | IA | Webster | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 10 | 2000 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1946 | petroleum | TRUE | 5998 | City of Estherville - (IA) | 1137 | Estherville | IA | Emmet | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.1 | 1.1 | 1 | N |  |  | OP | X | 12 | 1946 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N | [25 empty] | N | N | N
Vintage1960 | natural gas peaker | TRUE | 5998 | City of Estherville - (IA) | 1137 | Estherville | IA | Emmet | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3 | 0.8 | 2.7 | 2.8 | 2 | N |  |  | OP | X | 6 | 1960 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N | [25 empty] | Y | N | Y
Vintage1969 | natural gas peaker | TRUE | 5998 | City of Estherville - (IA) | 1137 | Estherville | IA | Emmet | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 4 | 0.8 | 3.6 | 3.6 | 2 | N |  |  | OP | X | 6 | 1969 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N | [25 empty] | Y | N | Y
Vintage1969 | natural gas peaker | TRUE | 5998 | City of Estherville - (IA) | 1137 | Estherville | IA | Emmet | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 4 | 0.8 | 3.6 | 3.6 | 2 | N |  |  | OP | X | 1 | 1969 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N | [25 empty] | Y | N | Y
Vintage1960 | natural gas peaker | TRUE | 5998 | City of Estherville - (IA) | 1137 | Estherville | IA | Emmet | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3 | 0.8 | 2.7 | 2.8 | 2 | N |  |  | OP | X | 1 | 1960 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N | [25 empty] | Y | N | Y
Vintage1958 | petroleum | TRUE | 6579 | City of Forest City- (IA) | 1138 | Forest City Light Plant | IA | Winnebago | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.98 | 1.3 | 1.3 | 0.9 | N |  |  | OP | X | 1 | 1958 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1965 | petroleum | TRUE | 6579 | City of Forest City- (IA) | 1138 | Forest City Light Plant | IA | Winnebago | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.98 | 2.2 | 2.2 | 1.7 | N |  |  | OP | X | 1 | 1965 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1968 | petroleum | TRUE | 6579 | City of Forest City- (IA) | 1138 | Forest City Light Plant | IA | Winnebago | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.5 | 0.98 | 3.3 | 3.3 | 2.6 | N |  |  | OP | X | 1 | 1968 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1976 | petroleum | TRUE | 6579 | City of Forest City- (IA) | 1138 | Forest City Light Plant | IA | Winnebago | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 6.3 | 0.98 | 6.1 | 6.1 | 4.7 | N |  |  | OP | X | 1 | 1976 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1950 | petroleum | TRUE | 6579 | City of Forest City- (IA) | 1138 | Forest City Light Plant | IA | Winnebago | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.7 | 0.98 | 0.7 | 0.7 | 0.5 | N |  |  | OP | X | 1 | 1950 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2000 | petroleum | TRUE | 6579 | City of Forest City- (IA) | 1138 | Forest City Light Plant | IA | Winnebago | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 7.6 | 0.98 | 7.6 | 7.6 | 0.6 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2013 | petroleum | TRUE | 7424 | Gowrie Municipal Utilities | 1141 | Gowrie | IA | Webster | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.2 | 2.2 | 0.4 | N |  |  | OP | X | 1 | 2013 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N | 0 | 10M | [23 empty] | N | N | N
Vintage1957 | petroleum | TRUE | 7443 | City of Graettinger - (IA) | 1142 | Graettinger | IA | Palo Alto | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.5 | N |  |  | OP | X | 8 | 1957 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1990 | petroleum | TRUE | 7443 | City of Graettinger - (IA) | 1142 | Graettinger | IA | Palo Alto | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.8 | N |  |  | OP | X | 12 | 1990 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage2002 | petroleum | TRUE | 7443 | City of Graettinger - (IA) | 1142 | Graettinger | IA | Palo Alto | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.8 | N |  |  | OP | X | 2 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1994 | petroleum | TRUE | 7486 | City of Grand Junction - (IA) | 1143 | Grand Junction | IA | Greene | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.7 | 1 | 1.7 | 1.7 | 1 | N |  |  | OP | X | 12 | 1994 |  |  | N | Electric Utility | 1 | X | DFO | [12 empty] | 1H | [23 empty] | N | N | N
Vintage1963 | petroleum | TRUE | 7743 | Grundy Center Mun Light & Power | 1145 | Grundy Center City Light Plant | IA | Grundy | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.2 | 0.8 | 2.2 | 2.2 | 2.2 | N |  |  | OP | X | 11 | 1963 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1972 | petroleum | TRUE | 7743 | Grundy Center Mun Light & Power | 1145 | Grundy Center City Light Plant | IA | Grundy | IC2 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.5 | 0.8 | 3.5 | 3.5 | 3.5 | N |  |  | OP | X | 3 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1990 | petroleum | TRUE | 7743 | Grundy Center Mun Light & Power | 1145 | Grundy Center City Light Plant | IA | Grundy | IC3 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 3 | N |  |  | OP | X | 10 | 1990 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | petroleum | TRUE | 8122 | Harlan Municipal Utilities - (IA) | 1146 | Harlan | IA | Shelby | HMU1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.7 | 0.99 | 1.6 | 1.6 | 0.1 | N |  |  | SB | Y | 7 | 2001 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2001 | petroleum | TRUE | 8122 | Harlan Municipal Utilities - (IA) | 1146 | Harlan | IA | Shelby | HMU2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.7 | 0.99 | 1.6 | 1.6 | 0.1 | N |  |  | SB | Y | 7 | 2001 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1977 | petroleum | TRUE | 9275 | Indianola Municipal Utilities | 1150 | Indianola | IA | Warren | 7 | Petroleum Liquids | GT |  | S | X | X |  |  | 20.6 | 1 | 19.4 | 23 | 2.5 | N |  |  | OP | X | 1 | 1977 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2000 | petroleum | TRUE | 9275 | Indianola Municipal Utilities | 1150 | Indianola | IA | Warren | 8 | Petroleum Liquids | GT |  | S | X | X |  |  | 20.3 | 1 | 22.8 | 24 | 2.5 | N |  |  | OP | X | 1 | 2000 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2005 | petroleum | TRUE | 10608 | City of Lake Park - (IA) | 1153 | Lake Park | IA | Dickinson | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1.5 | N |  |  | OP | X | 4 | 2005 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N | N | N
Vintage2005 | petroleum | TRUE | 10608 | City of Lake Park - (IA) | 1153 | Lake Park | IA | Dickinson | G2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1.5 | N |  |  | OP | X | 5 | 2005 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1962 | petroleum | TRUE | 10606 | City of Lake Mills | 1154 | Lake Mills | IA | Winnebago | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 0.5 | N |  |  | OP | X | 11 | 1962 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1979 | petroleum | TRUE | 10606 | City of Lake Mills | 1154 | Lake Mills | IA | Winnebago | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 5.7 | 0.8 | 5.7 | 5.7 | 2 | N |  |  | OP | X | 3 | 1979 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1999 | petroleum | TRUE | 10606 | City of Lake Mills | 1154 | Lake Mills | IA | Winnebago | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 7.6 | 0.8 | 7.6 | 7.6 | 3 | N |  |  | OP | X | 6 | 1999 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1973 | petroleum | TRUE | 10650 | City of Lamoni - (IA) | 1155 | Lamoni Municipal Utilities | IA | Decatur | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.8 | 0.8 | 2.7 | 2.8 | 0 | N |  |  | OP | X | 6 | 1973 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1940 | petroleum | TRUE | 10650 | City of Lamoni - (IA) | 1155 | Lamoni Municipal Utilities | IA | Decatur | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0 | N |  |  | OP | X | 3 | 1940 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N | N | N
Vintage1941 | petroleum | TRUE | 10650 | City of Lamoni - (IA) | 1155 | Lamoni Municipal Utilities | IA | Decatur | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0 | N |  |  | OP | X | 8 | 1941 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N | N | N
Vintage1948 | petroleum | TRUE | 10650 | City of Lamoni - (IA) | 1155 | Lamoni Municipal Utilities | IA | Decatur | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0 | N |  |  | OP | X | 12 | 1948 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N | N | N
Vintage1955 | petroleum | TRUE | 10650 | City of Lamoni - (IA) | 1155 | Lamoni Municipal Utilities | IA | Decatur | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0 | N |  |  | OP | X | 1 | 1955 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1993 | petroleum | TRUE | 10650 | City of Lamoni - (IA) | 1155 | Lamoni Municipal Utilities | IA | Decatur | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0 | N |  |  | OP | X | 2 | 1993 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N | N | N
Vintage2011 | petroleum | TRUE | 10650 | City of Lamoni - (IA) | 1155 | Lamoni Municipal Utilities | IA | Decatur | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.3 | 2.3 | 0 | N |  |  | OP | X | 5 | 2011 |  |  | N | Electric Utility | 1 | X | DFO | [12 empty] | 10M | [23 empty] | N | N | N
Vintage2011 | petroleum | TRUE | 10650 | City of Lamoni - (IA) | 1155 | Lamoni Municipal Utilities | IA | Decatur | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.3 | 2.3 | 0 | N |  |  | OP | X | 5 | 2011 |  |  | N | Electric Utility | 1 | X | DFO | [12 empty] | 10M | [23 empty] | N | N | N
Vintage2000 | petroleum | TRUE | 10542 | La Porte City Utilities | 1156 | La Porte | IA | Black Hawk | 3A | Petroleum Liquids | IC |  | S | X | X | AMIL.VIN_ALA_P |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | SB | Y | 12 | 2000 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 10542 | La Porte City Utilities | 1156 | La Porte | IA | Black Hawk | 4A | Petroleum Liquids | IC |  | S | X | X | AMIL.VIN_ALA_P |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | SB | Y | 12 | 2000 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage2013 | petroleum | TRUE | 10542 | La Porte City Utilities | 1156 | La Porte | IA | Black Hawk | 6 | Petroleum Liquids | IC |  | S | X | X | AMIL.VIN ALA p |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | SB | Y | 7 | 2013 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1952 | petroleum | TRUE | 10769 | City of Laurens - (IA) | 1157 | Laurens | IA | Pocahontas | 3 | Petroleum Liquids | IC |  | S | X | X | WAUECLRMUNLAURENS_RA |  | 0.8 | 0.8 | 0.7 | 0.7 | 0.7 | N |  |  | SB | Y | 7 | 1952 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1951 | petroleum | TRUE | 10769 | City of Laurens - (IA) | 1157 | Laurens | IA | Pocahontas | 4 | Petroleum Liquids | IC |  | S | X | X | WAUECLRMUNLAURENS_RA |  | 0.8 | 0.8 | 0.7 | 0.7 | 0.7 | N |  |  | SB | Y | 7 | 1951 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2013 | petroleum | TRUE | 10769 | City of Laurens - (IA) | 1157 | Laurens | IA | Pocahontas | 5 | Petroleum Liquids | IC |  | S | X | X | WAUECLRMUNLAURENS_RA |  | 2.5 | 0.8 | 2.3 | 2.3 | 2.3 | N |  |  | SB | Y | 4 | 2013 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2013 | petroleum | TRUE | 10769 | City of Laurens - (IA) | 1157 | Laurens | IA | Pocahontas | 6 | Petroleum Liquids | IC |  | S | X | X | WAUECLRMUNLAURENS_RA |  | 2.5 | 0.8 | 2.3 | 2.3 | 2.3 | N |  |  | SB | Y | 4 | 2013 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2013 | petroleum | TRUE | 10769 | City of Laurens - (IA) | 1157 | Laurens | IA | Pocahontas | 7 | Petroleum Liquids | IC |  | S | X | X | WAUECLRMUNLAURENS_RA |  | 2.5 | 0.8 | 2.3 | 2.3 | 2.3 | N |  |  | SB | Y | 4 | 2013 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1948 | petroleum | TRUE | 10908 | City of Lenox - (IA) | 1158 | Lenox | IA | Taylor | 1 | Petroleum Liquids | IC |  | S | X | X | ALTW.ALTW | ALTW.ALTW | 0.3 | 0.8 | 0.3 | 0.3 | 0.1 | N |  |  | SB | Y | 9 | 1948 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1965 | petroleum | TRUE | 10908 | City of Lenox - (IA) | 1158 | Lenox | IA | Taylor | 2 | Petroleum Liquids | IC |  | S | X | X | ALTW.ALTW | ALTW.ALTW | 1.1 | 0.8 | 1.1 | 1.1 | 0.4 | N |  |  | SB | Y | 3 | 1965 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1966 | petroleum | TRUE | 10908 | City of Lenox - (IA) | 1158 | Lenox | IA | Taylor | 3 | Petroleum Liquids | IC |  | S | X | X | ALTW.ALTW | ALTW.ALTW | 0.9 | 0.8 | 0.9 | 0.9 | 0.4 | N |  |  | SB | Y | 3 | 1966 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage2001 | petroleum | TRUE | 10908 | City of Lenox - (IA) | 1158 | Lenox | IA | Taylor | 4 | Petroleum Liquids | IC |  | S | X | X | ALTW.ALTW | ALTW.ALTW | 1.8 | 0.8 | 1.7 | 1.8 | 1.3 | N |  |  | SB | Y | 10 | 2001 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage2016 | petroleum | TRUE | 10908 | City of Lenox - (IA) | 1158 | Lenox | IA | Taylor | 5 | Petroleum Liquids | IC |  | S | X | X | ALTW.ALTW | ALTW.ALTW | 2 | 0.8 | 1.8 | 1.8 | 1.3 | N |  |  | SB | Y | 2 | 2016 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1928 | petroleum | TRUE | 11581 | City of Manning | 1160 | Manning | IA | Carroll | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0.2 | N |  |  | SB | Y | 3 | 1928 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1928 | petroleum | TRUE | 11581 | City of Manning | 1160 | Manning | IA | Carroll | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0.2 | N |  |  | SB | Y | 3 | 1928 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1949 | petroleum | TRUE | 11581 | City of Manning | 1160 | Manning | IA | Carroll | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.2 | N |  |  | SB | Y | 7 | 1949 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage2012 | petroleum | TRUE | 11581 | City of Manning | 1160 | Manning | IA | Carroll | M1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.3 | 0.8 | 2.3 | 2.3 | 0.2 | N |  |  | OP | X | 4 | 2012 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N
Vintage2012 | petroleum | TRUE | 11581 | City of Manning | 1160 | Manning | IA | Carroll | M2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.3 | 0.8 | 2.3 | 2.3 | 0.2 | N |  |  | OP | X | 4 | 2012 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N
Vintage2012 | petroleum | TRUE | 11581 | City of Manning | 1160 | Manning | IA | Carroll | M3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.3 | 0.8 | 2.3 | 2.3 | 0.2 | N |  |  | OP | X | 4 | 2012 |  |  | N | Electric Utility | 1 | X | DFO | [10 empty] | N |  | 1H | [23 empty] | N | N
Vintage2004 | natural gas peaker | TRUE | 11611 | City of Maquoketa - (IA) | 1162 | Maquoketa 1 | IA | Jackson | 1A | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.1 | 0.95 | 2.8 | 3 | 1.5 | N |  |  | SB | Y | 6 | 2004 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2004 | natural gas peaker | TRUE | 11611 | City of Maquoketa - (IA) | 1162 | Maquoketa 1 | IA | Jackson | 2A | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.1 | 0.95 | 2.8 | 3 | 1.5 | N |  |  | SB | Y | 6 | 2004 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1969 | natural gas peaker | TRUE | 11611 | City of Maquoketa - (IA) | 1162 | Maquoketa 1 | IA | Jackson | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.1 | 0.95 | 1.8 | 1.9 | 1 | N |  |  | SB | Y | 10 | 1969 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1999 | petroleum | TRUE | 11611 | City of Maquoketa - (IA) | 1162 | Maquoketa 1 | IA | Jackson | 4A | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.95 | 1.7 | 1.7 | 0.9 | N |  |  | SB | Y | 7 | 1999 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N |  | N
Vintage1956 | natural gas peaker | TRUE | 11611 | City of Maquoketa - (IA) | 1162 | Maquoketa 1 | IA | Jackson | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.7 | 0.95 | 1.4 | 1.5 | 0.7 | N |  |  | SB | Y | 6 | 1956 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1962 | natural gas peaker | TRUE | 11611 | City of Maquoketa - (IA) | 1162 | Maquoketa 1 | IA | Jackson | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.5 | 0.95 | 2.1 | 2.2 | 1 | N |  |  | SB | Y | 11 | 1962 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1982 | natural gas peaker | TRUE | 11611 | City of Maquoketa - (IA) | 1162 | Maquoketa 1 | IA | Jackson | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 6.5 | 0.95 | 6 | 6.1 | 3 | N |  |  | SB | Y | 9 | 1982 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1996 | petroleum | TRUE | 11611 | City of Maquoketa - (IA) | 1162 | Maquoketa 1 | IA | Jackson | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.95 | 1.7 | 1.7 | 0.9 | N |  |  | SB | Y | 9 | 1996 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2000 | petroleum | TRUE | 11611 | City of Maquoketa - (IA) | 1162 | Maquoketa 1 | IA | Jackson | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.95 | 1.7 | 1.7 | 0.9 | N |  |  | SB | Y | 7 | 2000 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1977 | petroleum | TRUE | 12114 | City of McGregor- (IA) | 1163 | McGregor | IA | Clayton | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 0.6 | N |  |  | OP | X | 10 | 1977 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1941 | petroleum | TRUE | 12114 | City of McGregor- (IA) | 1163 | McGregor | IA | Clayton | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 12 | 1941 |  |  | N | Electric Utility | 1 | X | DFO | [10 empty] | N |  | 1H | [23 empty] | N | N | N
Vintage1954 | petroleum | TRUE | 12541 | City of Milford - (IA) | 1164 | Milford | IA | Dickinson | 1 | Petroleum Liquids | IC |  | S | X | X | WAUEMLFRDTCBUNMILFORD | WAUE.NMCA.MILFORD | 0.6 | 0.8 | 0.6 | 0.6 | 0.6 | N |  |  | OP | X | 1 | 1954 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H |  | N | [18 empty] | N |  |  | N | N | N
Vintage1949 | petroleum | TRUE | 12541 | City of Milford - (IA) | 1164 | Milford | IA | Dickinson | 4 | Petroleum Liquids | IC |  | S | X | X | WAUEMLFRDTCBUNMILFORD | WAUE.NMCA.MILFORD | 0.5 | 0.8 | 0.5 | 0.5 | 0.5 | N |  |  | OP | X | 1 | 1949 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1997 | petroleum | TRUE | 12541 | City of Milford - (IA) | 1164 | Milford | IA | Dickinson | 5 | Petroleum Liquids | IC |  | S | X | X | WAUEMLFDTCBUNMILFORD | WAUE.NMCA.MILFORD | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 5 | 1997 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1997 | petroleum | TRUE | 12541 | City of Milford - (IA) | 1164 | Milford | IA | Dickinson | 6 | Petroleum Liquids | IC |  | S | X | X | WAUEMLFRDTCBUNMILFORD | WAUE.NMCA.MILFORD | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 5 | 1997 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1997 | petroleum | TRUE | 12541 | City of Milford - (IA) | 1164 | Milford | IA | Dickinson | 7 | Petroleum Liquids | IC |  | S | X | X | WAUEMLFRDTCBUNMILFORD | WAUE.NMCA.MILFORD | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 5 | 1997 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1940 | petroleum | TRUE | 12839 | City of Montezuma - (IA) | 1165 | Montezuma | IA | Poweshiek | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.2 | 1 | 0.2 | 0.2 | 0.1 | N |  |  | SB | Y | 8 | 1940 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage2003 | petroleum | TRUE | 12839 | City of Montezuma - (IA) | 1165 | Montezuma | IA | Poweshiek | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.2 | 1 | 0.2 | 0.2 | 0.1 | N |  |  | SB | Y | 6 | 2003 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1947 | petroleum | TRUE | 12839 | City of Montezuma - (IA) | 1165 | Montezuma | IA | Poweshiek | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 1 | 0.5 | 0.5 | 0.4 | N |  |  | SB | Y | 8 | 1947 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1959 | petroleum | TRUE | 12839 | City of Montezuma - (IA) | 1165 | Montezuma | IA | Poweshiek | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 1 | 1 | 1.1 | 1 | N |  |  | SB | Y | 8 | 1959 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1967 | natural gas peaker | TRUE | 12839 | City of Montezuma - (IA) | 1165 | Montezuma | IA | Poweshiek | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.7 | 1 | 1.6 | 1.7 | 1.2 | N |  |  | SB | Y | 8 | 1967 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1974 | natural gas peaker | TRUE | 12839 | City of Montezuma - (IA) | 1165 | Montezuma | IA | Poweshiek | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 1.5 | N |  |  | SB | Y | 8 | 1974 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1998 | petroleum | TRUE | 12839 | City of Montezuma - (IA) | 1165 | Montezuma | IA | Poweshiek | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 1 | 1.8 | 1.8 | 1.4 | N |  |  | SB | Y | 6 | 1998 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 12839 | City of Montezuma - (IA) | 1165 | Montezuma | IA | Poweshiek | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 1 | 1.8 | 1.8 | 1.4 | N |  |  | SB | Y | 6 | 2000 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage2002 | petroleum | TRUE | 13038 | City of Mt Pleasant - (IA) | 1166 | Mt Pleasant | IA | Henry | 1 | Petroleum Liquids | IC |  | S | X | X | AMIL.HEN_AMT_P | AMIL.HEN_AMT_P | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | SB | Y | 2 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [5 empty] | DFO |  |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N | N | N
Vintage2002 | petroleum | TRUE | 13038 | City of Mt Pleasant - (IA) | 1166 | Mt Pleasant | IA | Henry | 10 | Petroleum Liquids | IC |  | S | X | X | AMIL.HEN_AMT_P | AMIL.HEN_AMT_P | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | SB | Y | 2 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [5 empty] | DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage2002 | petroleum | TRUE | 13038 | City of Mt Pleasant - (IA) | 1166 | Mt Pleasant | IA | Henry | 11 | Petroleum Liquids | IC |  | S | X | X | AMIL.HEN_AMT_P | AMIL.HEN_AMT_P | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | SB | Y | 2 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [5 empty] | DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage2002 | petroleum | TRUE | 13038 | City of Mt Pleasant - (IA) | 1166 | Mt Pleasant | IA | Henry | 12 | Petroleum Liquids | IC |  | S | X | X | AMIL.HEN_AMT_P | AMIL.HEN_AMT_P | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | SB | Y | 2 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [5 empty] | DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage2002 | petroleum | TRUE | 13038 | City of Mt Pleasant - (IA) | 1166 | Mt Pleasant | IA | Henry | 2 | Petroleum Liquids | IC |  | S | X | X | AMIL.HEN_AMT_P | AMIL.HEN_AMT_P | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | SB | Y | 2 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [5 empty] | DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage2002 | petroleum | TRUE | 13038 | City of Mt Pleasant - (IA) | 1166 | Mt Pleasant | IA | Henry | 3 | Petroleum Liquids | IC |  | S | X | X | AMIL.HEN_AMT_P | AMIL.HEN_AMT_P | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | SB | Y | 2 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [5 empty] | DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage2002 | petroleum | TRUE | 13038 | City of Mt Pleasant - (IA) | 1166 | Mt Pleasant | IA | Henry | 4A | Petroleum Liquids | IC |  | S | X | X | AMIL.HEN_AMT_P | AMIL.HEN_AMT_P | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | SB | Y | 2 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [5 empty] | DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage2002 | petroleum | TRUE | 13038 | City of Mt Pleasant - (IA) | 1166 | Mt Pleasant | IA | Henry | 5A | Petroleum Liquids | IC |  | S | X | X | AMIL.HEN_AMT_P | AMIL.HEN_AMT_P | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | SB | Y | 2 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [5 empty] | DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage2002 | petroleum | TRUE | 13038 | City of Mt Pleasant - (IA) | 1166 | Mt Pleasant | IA | Henry | 6 | Petroleum Liquids | IC |  | S | X | X | AMIL.HEN_AMT_P | AMIL.HEN_AMT_P | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | SB | Y | 2 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [5 empty] | DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage2002 | petroleum | TRUE | 13038 | City of Mt Pleasant - (IA) | 1166 | Mt Pleasant | IA | Henry | 7 | Petroleum Liquids | IC |  | S | X | X | AMIL.HEN_AMT_P | AMIL.HEN_AMT_P | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | SB | Y | 2 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [5 empty] | DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage2002 | petroleum | TRUE | 13038 | City of Mt Pleasant - (IA) | 1166 | Mt Pleasant | IA | Henry | 8 | Petroleum Liquids | IC |  | S | X | X | AMIL.HEN_AMT_P | AMIL.HEN_AMT_P | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | SB | Y | 2 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [5 empty] | DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage2002 | petroleum | TRUE | 13038 | City of Mt Pleasant - (IA) | 1166 | Mt Pleasant | IA | Henry | 9 | Petroleum Liquids | IC |  | S | X | X | AMIL.HEN_AMT_P | AMIL.HEN_AMT_P | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | SB | Y | 2 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [5 empty] | DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1958 | hard coal | TRUE | 13143 | Board of Water Electric & Communications | 1167 | Muscatine Plant #1 | IA | Muscatine | 7 | Conventional Steam Coal | ST |  | S | X | X | MPW.UNIT_7 | MPW.UNIT_9 | 25 | 0.85 | 20.1 | 20.1 | 6 | N |  |  | OP | X | 4 | 1958 |  |  | N | Electric Utility | 1 | X | SUB | NG |  |  |  |  | NG |  |  |  | N | N |  | OVER |  |  | Y |  | Y | [18 empty] | Y | Y | N
Vintage1969 | hard coal | TRUE | 13143 | Board of Water Electric & Communications | 1167 | Muscatine Plant #1 | IA | Muscatine | 8 | Conventional Steam Coal | ST |  | S | X | X | MPW.UNIT_8 | MPW.UNIT_9 | 75 | 0.85 | 25.1 | 25.1 | 20 | N |  |  | OP | X | 1 | 1969 |  |  | N | Electric Utility | 1 | X | SUB | NG |  |  |  |  | NG |  |  |  | N | N |  | OVER |  | N |  | Y | Y | [18 empty] | Y | Y | N
Vintage2000 | hard coal | TRUE | 13143 | Board of Water Electric & Communications | 1167 | Muscatine Plant #1 | IA | Muscatine | 8A | Conventional Steam Coal | ST |  | S | X | X | MPW.UNIT_8A | MPW.UNIT_9 | 18 | 0.85 | 14.5 | 14.5 | 10 | N |  |  | OP | X | 7 | 2000 |  |  | Y | Electric Utility | 1 | T | SUB | NG |  |  |  |  | NG |  |  |  | N | N |  | OVER |  | N |  | Y | Y | [18 empty] | Y | Y | N
Vintage1983 | hard coal | TRUE | 13143 | Board of Water Electric & Communications | 1167 | Muscatine Plant #1 | IA | Muscatine | 9 | Conventional Steam Coal | ST |  | S | X | X | MPW.UNIT_9 | MPW.UNIT_9 | 175.5 | 0.85 | 160.8 | 160.8 | 45 | N |  |  | OP | X | 4 | 1983 |  |  | N | Electric Utility | 1 | X | RC | SUB | DFO |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1967 | natural gas peaker | TRUE | 13444 | City of New Hampton - (IA) | 1168 | New Hampton | IA | Chickasaw | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.5 | 0.8 | 3.5 | 3.5 | 2 | N |  |  | SB | Y | 4 | 1967 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1973 | natural gas peaker | TRUE | 13444 | City of New Hampton - (IA) | 1168 | New Hampton | IA | Chickasaw | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 6.2 | 0.8 | 5 | 5 | 4 | N |  |  | SB | Y | 2 | 1973 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1973 | natural gas peaker | TRUE | 13444 | City of New Hampton - (IA) | 1168 | New Hampton | IA | Chickasaw | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 6.2 | 0.8 | 5 | 5 | 4 | N |  |  | SB | Y | 2 | 1973 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1999 | petroleum | TRUE | 13444 | City of New Hampton - (IA) | 1168 | New Hampton | IA | Chickasaw | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 5.3 | 0.8 | 5.3 | 5.3 | 3 | N |  |  | OP | X | 5 | 1999 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 13444 | City of New Hampton - (IA) | 1168 | New Hampton | IA | Chickasaw | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 5.3 | 0.8 | 5.3 | 5.3 | 3 | N |  |  | OP | X | 5 | 1999 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1951 | petroleum | TRUE | 13990 | City of Ogden - (IA) | 1169 | Ogden | IA | Boone | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.8 | 0.5 | 0.5 | 0.2 | N |  |  | SB | Y | 7 | 1951 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1958 | petroleum | TRUE | 13990 | City of Ogden - (IA) | 1169 | Ogden | IA | Boone | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.5 | N |  |  | SB | Y | 10 | 1958 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1971 | petroleum | TRUE | 13990 | City of Ogden - (IA) | 1169 | Ogden | IA | Boone | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 1.2 | N |  |  | SB | Y | 10 | 1971 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1963 | natural gas peaker | TRUE | 14201 | City of Osage - (IA) | 1172 | Osage (IA) | IA | Mitchell | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.2 | 0.8 | 3.1 | 3.1 | 1 | N |  |  | SB | Y | 9 | 1963 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | DFO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1973 | natural gas peaker | TRUE | 14201 | City of Osage - (IA) | 1172 | Osage (IA) | IA | Mitchell | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 6.2 | 0.8 | 6 | 6 | 1 | N |  |  | SB | Y | 10 | 1973 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | DFO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1996 | petroleum | TRUE | 14201 | City of Osage - (IA) | 1172 | Osage (IA) | IA | Mitchell | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.6 | 0.8 | 3.6 | 3.6 | 1 | N |  |  | SB | Y | 5 | 1996 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1998 | petroleum | TRUE | 14201 | City of Osage - (IA) | 1172 | Osage (IA) | IA | Mitchell | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.6 | 0.8 | 3.6 | 3.6 | 1 | N |  |  | SB | Y | 5 | 1998 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2016 | solar pv | TRUE | 14201 | City of Osage - (IA) | 1172 | Osage (IA) | IA | Mitchell | SO | Solar Photovoltaic | PV |  | S | X | X |  |  | 0.8 |  | 0.8 | 0.1 |  | N |  |  | OP | X | 11 | 2016 |  |  | N | Electric Utility | 1 | X | SUN | [9 empty] | N | [26 empty] | N
Vintage2009 | onshore wind | TRUE | 14201 | City of Osage - (IA) | 1172 | Osage (IA) | IA | Mitchell | W1 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 1.6 |  | 0.5 | 0.5 | 0.5 | N |  |  | OP | X | 12 | 2009 |  |  | N | Electric Utility | 1 | X | WND | [9 empty] | N |  | 1 | [24 empty] | N
Vintage1931 | hydro | TRUE | 14236 | Ottumwa City of | 1173 | Ottumwa City of | IA | Wapello | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.5 | N |  |  | OS | X | 8 | 1931 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 1H
Vintage1931 | hydro | TRUE | 14236 | Ottumwa City of | 1173 | Ottumwa City of | IA | Wapello | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 0.3 | N |  |  | OP | X | 8 | 1931 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 1H
Vintage1931 | hydro | TRUE | 14236 | Ottumwa City of | 1173 | Ottumwa City of | IA | Wapello | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.3 | N |  |  | OP | X | 8 | 1931 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  |  | 1H
Vintage1980 | natural gas peaker | TRUE | 15349 | City of Preston | 1176 | Preston (IA) | IA | Jackson | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | NA | NA | 1.8 | 0.9 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 12 | 1980 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage2020 | petroleum | TRUE | 15349 | City of Preston | 1176 | Preston (IA) | IA | Jackson | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 2 | 2 | 0.1 | N |  |  | OP | X | 1 | 2020 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | N
Vintage1972 | petroleum | TRUE | 15377 | City of Primghar - (IA) | 1177 | Primghar | IA | O'Brien | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.9 | 0.6 | 0.6 | 0.6 | N |  |  | OS | X | 1 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1992 | petroleum | TRUE | 15377 | City of Primghar - (IA) | 1177 | Primghar | IA | O'Brien | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.9 | 0.9 | 0.9 | 0.9 | N |  |  | OA | X | 5 | 1992 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1951 | petroleum | TRUE | 16211 | City of Rockford- (IA) | 1180 | Rockford | IA | Floyd | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.1 | N |  |  | SB | Y | 8 | 1951 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1961 | petroleum | TRUE | 16211 | City of Rockford- (IA) | 1180 | Rockford | IA | Floyd | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.9 | 0.9 | 0.1 | N |  |  | SB | Y | 8 | 1961 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 16211 | City of Rockford- (IA) | 1180 | Rockford | IA | Floyd | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.2 | N |  |  | SB | Y | 1 | 1999 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1968 | petroleum | TRUE | 16206 | Rock Rapids Municipal Utility | 1181 | Rock Rapids | IA | Lyon | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 1.8 | N |  |  | OP | X | 4 | 1968 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1971 | petroleum | TRUE | 17141 | City of Sibley - (IA) | 1184 | Sibley One | IA | Osceola | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 1 | 1.9 | 2.1 | 1 | N |  |  | OP | X | 9 | 1971 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 10M | [23 empty] | Y | N | N
Vintage1987 | petroleum | TRUE | 17141 | City of Sibley - (IA) | 1184 | Sibley One | IA | Osceola | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 1 | 1.1 | 1.2 | 1 | N |  |  | OP | X | 4 | 1987 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 10M | [23 empty] | N |  | N
Vintage2000 | petroleum | TRUE | 17141 | City of Sibley - (IA) | 1184 | Sibley One | IA | Osceola | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 1 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 10M | [23 empty] | N |  | N
Vintage1970 | other | TRUE | 17783 | City of Spencer - (IA) | 1186 | Spencer Gas Turbine | IA | Clay | GT1 | Petroleum Liquids | GT |  | S | X | X | WAUESPENCERUNSPENCER_RA |  | 23.8 | 0.8 | 17 | 20 | 10 | N |  |  | OP | X | 1 | 1970 |  |  | N | Electric Utility | 1 | X | KER | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1995 | petroleum | TRUE | 18014 | City of State Center - (IA) | 1187 | State Center | IA | Marshall | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 5 | 1995 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1995 | petroleum | TRUE | 18014 | City of State Center - (IA) | 1187 | State Center | IA | Marshall | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 5 | 1995 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1995 | petroleum | TRUE | 18014 | City of State Center - (IA) | 1187 | State Center | IA | Marshall | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 0.2 | N |  |  | OP | X | 5 | 1995 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1995 | petroleum | TRUE | 18014 | City of State Center - (IA) | 1187 | State Center | IA | Marshall | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 0.2 | N |  |  | OP | X | 5 | 1995 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1972 | natural gas peaker | TRUE | 18014 | City of State Center - (IA) | 1187 | State Center | IA | Marshall | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 8 | 1972 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1964 | petroleum | TRUE | 18177 | City of Story City - (IA) | 1188 | Story City | IA | Story | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 1 | N |  |  | OP | X | 1 | 1964 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | N
Vintage1972 | petroleum | TRUE | 18177 | City of Story City - (IA) | 1188 | Story City | IA | Story | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1 | N |  |  | OP | X | 1 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | N
Vintage2003 | petroleum | TRUE | 18177 | City of Story City - (IA) | 1188 | Story City | IA | Story | 4A | Petroleum Liquids | IC |  | S | X | X |  |  | 3.5 | 0.8 | 3.1 | 3.2 | 2 | N |  |  | OP | X | 5 | 2003 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | N
Vintage1993 | petroleum | TRUE | 18177 | City of Story City - (IA) | 1188 | Story City | IA | Story | 5A | Petroleum Liquids | IC |  | S | X | X |  |  | 3.1 | 0.8 | 3.1 | 3.1 | 2 | N |  |  | OP | X | 3 | 1993 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | N
Vintage1978 | petroleum | TRUE | 18177 | City of Story City - (IA) | 1188 | Story City | IA | Story | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1 | N |  |  | OP | X | 1 | 1978 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | N
Vintage1978 | petroleum | TRUE | 18177 | City of Story City - (IA) | 1188 | Story City | IA | Story | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1 | N |  |  | OP | X | 1 | 1978 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | N
Vintage1956 | petroleum | TRUE | 18231 | City of Stuart - (IA) | 1190 | Stuart (IA) | IA | Guthrie | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.9 | 0.6 | 0.6 | 0.3 | N |  |  | OP | X | 2 | 1956 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1968 | petroleum | TRUE | 18231 | City of Stuart - (IA) | 1190 | Stuart (IA) | IA | Guthrie | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.9 | 1.1 | 1.1 | 0.5 | N |  |  | OP | X | 6 | 1968 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1964 | petroleum | TRUE | 18231 | City of Stuart - (IA) | 1190 | Stuart (IA) | IA | Guthrie | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.9 | 1 | 1 | 0.5 | N |  |  | OP | X | 10 | 1964 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2021 | petroleum | TRUE | 18301 | City of Sumner - (IA) | 1191 | Sumner | IA | Bremer | G1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.9 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 2 | 2021 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage2021 | petroleum | TRUE | 18301 | City of Sumner - (IA) | 1191 | Sumner | IA | Bremer | G2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.9 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 2 | 2021 |  |  | N | Electric Utility | 1 | X | DFO | [12 empty] | 1H | [23 empty] | N
Vintage2021 | petroleum | TRUE | 18301 | City of Sumner - (IA) | 1191 | Sumner | IA | Bremer | G3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.9 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 2 | 2021 |  |  | N | Electric Utility | 1 | X | DFO | [12 empty] | 1H | [23 empty] | N
Vintage1963 | petroleum | TRUE | 19062 | City of Traer - (IA) | 1192 | Traer Main | IA | Tama | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1 | 1 | 0.9 | N |  |  | SB | Y | 1 | 1963 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N |  |  | 1H | [23 empty] | Y | Y | N
Vintage1963 | petroleum | TRUE | 19062 | City of Traer - (IA) | 1192 | Traer Main | IA | Tama | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1 | 1 | 0.9 | N |  |  | SB | Y | 1 | 1963 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N |  |  | 1H | [23 empty] | Y | Y | N
Vintage1970 | petroleum | TRUE | 19062 | City of Traer - (IA) | 1192 | Traer Main | IA | Tama | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.2 | 1.2 | 1.2 | N |  |  | SB | Y | 1 | 1970 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N |  |  | 1H | [23 empty] | Y | Y | N
Vintage2003 | petroleum | TRUE | 19843 | City of Villisca - (IA) | 1193 | Villisca Municipal Power Plant | IA | Montgomery | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.2 | N |  |  | SB | Y | 6 | 2003 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage2003 | petroleum | TRUE | 19843 | City of Villisca - (IA) | 1193 | Villisca Municipal Power Plant | IA | Montgomery | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.2 | N |  |  | SB | Y | 6 | 2003 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1955 | natural gas peaker | TRUE | 19865 | City of Vinton - (IA) | 1194 | Vinton | IA | Benton | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 0.6 | N |  |  | OP | X | 6 | 1955 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2009 | petroleum | TRUE | 19865 | City of Vinton - (IA) | 1194 | Vinton | IA | Benton | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 6 | 2009 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1946 | petroleum | TRUE | 19865 | City of Vinton - (IA) | 1194 | Vinton | IA | Benton | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OS | X | 6 | 1946 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1961 | natural gas peaker | TRUE | 19865 | City of Vinton - (IA) | 1194 | Vinton | IA | Benton | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 1.5 | N |  |  | OP | X | 6 | 1961 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1967 | natural gas peaker | TRUE | 19865 | City of Vinton - (IA) | 1194 | Vinton | IA | Benton | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.7 | 0.8 | 3.7 | 3.7 | 2 | N |  |  | OP | X | 6 | 1967 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1973 | natural gas peaker | TRUE | 19865 | City of Vinton - (IA) | 1194 | Vinton | IA | Benton | 8 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 5.6 | 0.8 | 5.6 | 5.6 | 3 | N |  |  | OP | X | 12 | 1973 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1992 | natural gas peaker | TRUE | 19865 | City of Vinton - (IA) | 1194 | Vinton | IA | Benton | 9 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 1.6 | N |  |  | OP | X | 9 | 1992 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1972 | petroleum | TRUE | 20259 | City of Webster City - (IA) | 1198 | Webster City | IA | Hamilton | 6 | Petroleum Liquids | GT |  | S | X | X |  |  | 21.3 | 0.85 | 20.7 | 25 | 5 | N |  |  | OP | X | 4 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | [5 empty] | OBG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1959 | petroleum | TRUE | 20364 | City of West Bend | 1199 | West Bend | IA | Palo Alto | 1 | Petroleum Liquids | IC |  | S | X | X | WAUEWBENDMUNUNWESTBEND_RA | WAUEWBENDMUNUNWESTBEND_RA | 1.1 | 0.9 | 1 | 1 | 0.5 | N |  |  | SB | Y | 8 | 1959 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1954 | petroleum | TRUE | 20364 | City of West Bend | 1199 | West Bend | IA | Palo Alto | 3 | Petroleum Liquids | IC |  | S | X | X | WAUEWBENDMUNUNWESTBEND_RA | WAUEWBENDMUNUNWESTBEND_RA | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | N |  |  | SB | Y | 12 | 1954 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1973 | petroleum | TRUE | 20364 | City of West Bend | 1199 | West Bend | IA | Palo Alto | 4 | Petroleum Liquids | IC |  | S | X | X | WAUEWBENDMUNUNWESTBEND_RA | WAUEWBENDMUNUNWESTBEND_RA | 2.2 | 0.9 | 2 | 2 | 0.5 | N |  |  | SB | Y | 11 | 1973 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage2013 | petroleum | TRUE | 20364 | City of West Bend | 1199 | West Bend | IA | Palo Alto | 5 | Petroleum Liquids | IC |  | S | X | X | WAUEWBENDMUNUNWESTBEND_RA | WAUEWBENDMUNUNWESTBEND_RA | 2.5 | 0.9 | 2.5 | 2.5 | 0.5 | N |  |  | SB | Y | 7 | 2013 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1974 | petroleum | TRUE | 20380 | City of West Liberty - (IA) | 1200 | West Liberty | IA | Muscatine | 2 | Petroleum Liquids | IC |  | S | X | X | AMIL.WLBRWEST | AMIL.WLBRWEST | 2.5 | 0.8 | 2.1 | 2.1 | 0.5 | N |  |  | SB | Y | 10 | 1974 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1982 | petroleum | TRUE | 20380 | City of West Liberty - (IA) | 1200 | West Liberty | IA | Muscatine | 3 | Petroleum Liquids | IC |  | S | X | X | AMIL.WLBRWEST | AMIL.WLBRWEST | 3 | 0.8 | 2.7 | 2.7 | 0.5 | N |  |  | SB | Y | 2 | 1982 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2004 | petroleum | TRUE | 20380 | City of West Liberty - (IA) | 1200 | West Liberty | IA | Muscatine | 5 | Petroleum Liquids | GT |  | S | X | X | AMIL.WLBRWEST | AMIL.WLBRWEST | 5.5 | 0.8 | 5 | 5.5 | 0.3 | N |  |  | SB | Y | 5 | 2004 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage2004 | petroleum | TRUE | 20380 | City of West Liberty - (IA) | 1200 | West Liberty | IA | Muscatine | 6 | Petroleum Liquids | GT |  | S | X | X | AMIL.WLBRWEST | AMIL.WLBRWEST | 5.5 | 0.8 | 5 | 5.5 | 0.3 | N |  |  | SB | Y | 5 | 2004 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1992 | petroleum | TRUE | 20789 | City of Wilton | 1202 | Wilton | IA | Muscatine | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 1 | 1.6 | 1.6 | 1.6 | N |  |  | OP | X | 1 | 1992 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1992 | petroleum | TRUE | 20789 | City of Wilton | 1202 | Wilton | IA | Muscatine | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 1 | 1.6 | 1.6 | 1.6 | N |  |  | OP | X | 1 | 1992 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1992 | petroleum | TRUE | 20789 | City of Wilton | 1202 | Wilton | IA | Muscatine | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 1 | 1.6 | 1.6 | 1.6 | N |  |  | OP | X | 1 | 1992 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N | N | N
Vintage2002 | petroleum | TRUE | 20789 | City of Wilton | 1202 | Wilton | IA | Muscatine | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.2 | 1 | 2.2 | 2.2 | 2.2 | N |  |  | OP | X | 5 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N | N | N
Vintage2002 | petroleum | TRUE | 20789 | City of Wilton | 1202 | Wilton | IA | Muscatine | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.2 | 1 | 2.2 | 2.2 | 2.2 | N |  |  | OP | X | 5 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N | N | N
Vintage1956 | petroleum | TRUE | 20835 | City of Winterset - (IA) | 1203 | Winterset | IA | Madison | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.5 | N |  |  | OP | X | 7 | 1956 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y |  | Y
Vintage1966 | petroleum | TRUE | 20835 | City of Winterset - (IA) | 1203 | Winterset | IA | Madison | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.7 | 0.8 | 1.7 | 1.7 | 0.5 | N |  |  | OP | X | 6 | 1966 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y |  | Y
Vintage1972 | petroleum | TRUE | 20835 | City of Winterset - (IA) | 1203 | Winterset | IA | Madison | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.4 | 0.8 | 4.4 | 4.4 | 1.5 | N |  |  | OP | X | 5 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y |  | Y
Vintage2002 | petroleum | TRUE | 20835 | City of Winterset - (IA) | 1203 | Winterset | IA | Madison | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.5 | N |  |  | OP | X | 4 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N |  | N
Vintage2002 | petroleum | TRUE | 20835 | City of Winterset - (IA) | 1203 | Winterset | IA | Madison | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.5 | N |  |  | OP | X | 4 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N |  | N
Vintage2002 | petroleum | TRUE | 20835 | City of Winterset - (IA) | 1203 | Winterset | IA | Madison | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.5 | N |  |  | OP | X | 4 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N |  | N
Vintage1973 | natural gas peaker | TRUE | 3258 | Central Iowa Power Cooperative | 1206 | Summit Lake | IA | Union | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | ALTW.CC.SLAK1 |  | 27 | 0.85 | 29.2 | 34.9 | 10 | N |  |  | OP | X | 7 | 1973 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1975 | natural gas peaker | TRUE | 3258 | Central Iowa Power Cooperative | 1206 | Summit Lake | IA | Union | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | ALTW.CC.SLAK2 |  | 35.3 | 0.9 | 27.4 | 32.8 | 10 | N |  |  | OP | X | 6 | 1975 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2021 | natural gas peaker | TRUE | 3258 | Central Iowa Power Cooperative | 1206 | Summit Lake | IA | Union | R1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 18.8 | 0.8 | 18.4 | 18.4 | 5 | N |  |  | OP | X | 4 | 2021 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage2021 | natural gas peaker | TRUE | 3258 | Central Iowa Power Cooperative | 1206 | Summit Lake | IA | Union | R2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 18.8 | 0.8 | 18.4 | 18.4 | 5 | N |  |  | OP | X | 4 | 2021 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage2021 | natural gas peaker | TRUE | 3258 | Central Iowa Power Cooperative | 1206 | Summit Lake | IA | Union | R3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 18.8 | 0.8 | 18.4 | 18.4 | 5 | N |  |  | OP | X | 4 | 2021 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1960 | natural gas steam turbine | TRUE | 4363 | Corn Belt Power Coop | 1217 | Earl F Wisdom | IA | Clay | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | WAUEWISDOMCBUNWISDOM_1_UNIT_RA | WAUE.BEPM.WISDOM1 | 37.5 | 0.85 | 37.5 | 38 | 12 | N |  |  | OP | X | 4 | 1960 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | NG |  |  |  | N | N | 0 | OVER |  | N |  |  | N | [18 empty] | Y | Y | Y
Vintage2004 | petroleum | TRUE | 4363 | Corn Belt Power Coop | 1217 | Earl F Wisdom | IA | Clay | 2 | Petroleum Liquids | GT |  | J | X | X | WAUEWISDOMCBUNWISDOM_2_BEPM_RA | WAUE.BEPM.WISDOM2 | 81.6 | 0.85 | 76 | 80 | 45 | N |  |  | OP | X | 4 | 2004 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N | 0 | 1H | [23 empty] | Y | N | Y
Vintage1965 | petroleum | TRUE | 12524 | Midwest Energy Inc | 1224 | Bird City | KS | Cheyenne | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.9 | 2 | 2 | 0.5 | N |  |  | OP | X | 1 | 1965 |  |  | N | Electric Utility | 1 | X | DFO | [5 empty] | DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1966 | petroleum | TRUE | 12524 | Midwest Energy Inc | 1224 | Bird City | KS | Cheyenne | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.9 | 2 | 2 | 0.5 | N |  |  | OS | X | 1 | 1966 |  |  | N | Electric Utility | 1 | X | DFO | [5 empty] | DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1970 | natural gas peaker | TRUE | 12524 | Midwest Energy Inc | 1225 | Colby | KS | Thomas | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | WR.MW.COLBY.MW | WR.MW.COLBY.MW | 16 | 0.85 | 13 | 13 | 5 | N |  |  | OP | X | 1 | 1970 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1963 | natural gas steam turbine | TRUE | 18315 | Sunflower Electric Power Corp | 1230 | Cimarron River | KS | Seward | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | MKECCIM_UN1 | MKECCIM_UN1 | 50 | 0.85 | 53.6 | 53.6 | 23 | N |  |  | OP | X | 10 | 1963 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1968 | natural gas peaker | TRUE | 18315 | Sunflower Electric Power Corp | 1230 | Cimarron River | KS | Seward | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MKECCIM_UN2 | MKECCIM_UN2 | 15 | 0.85 | 13.7 | 13.7 | 6 | N |  |  | SB | Y | 2 | 1968 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1969 | natural gas steam turbine | TRUE | 18315 | Sunflower Electric Power Corp | 1233 | Fort Dodge | KS | Ford | 4 | Natural Gas Steam Turbine | ST |  | S | X | X | MKECJUDLR_UN4 | MKECJUDLR_UN4 | 149 | 0.85 | 148.8 | 148.8 | 30 | N |  |  | OP | X | 6 | 1969 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1963 | natural gas steam turbine | TRUE | 18315 | Sunflower Electric Power Corp | 1235 | Great Bend - Sunflower | KS | Barton | 3 | Natural Gas Steam Turbine | ST |  | S | X | X | MKECMULGRN_UN3 | MKECMULGRN_UN3 | 81.6 | 0.85 | 99.7 | 99.7 | 23 | N |  |  | OP | X | 6 | 1963 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1988 | natural gas peaker | TRUE | 5860 | Empire District Electric Co | 1239 | Riverton | KS | Cherokee | 10 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | EDERIV1671UN10_ | EDERIV1671UN10_ | 16.3 | 1 | 13 | 16 | 4 | N |  |  | OP | X | 12 | 1988 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1988 | natural gas peaker | TRUE | 5860 | Empire District Electric Co | 1239 | Riverton | KS | Cherokee | 11 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | EDERIV1671UNI11_ | EDERIV1671UN11_ | 16.3 | 1 | 14 | 16 | 4 | N |  |  | OP | X | 11 | 1988 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2007 | natural gas combined cycle | TRUE | 5860 | Empire District Electric Co | 1239 | Riverton | KS | Cherokee | 12 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | EDERIV453UN12_1_ | EDERIV453UN12_1 | 148.8 | 1 | 149 | 180 | 98 | N |  |  | OP | X | 5 | 2007 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N |  | N
Vintage2016 | natural gas combined cycle | TRUE | 5860 | Empire District Electric Co | 1239 | Riverton | KS | Cherokee | 12-2 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | EDERIV453UN12_2 | EDERIV453UN12_2 | 118.8 | 0.85 | 117 | 117 |  | N |  |  | OP | X | 5 | 2016 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage1969 | petroleum | TRUE | 10005 | Evergy Kansas South, Inc | 1240 | Gordon Evans Energy Center | KS | Sedgwick | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.9 | 0.8 | 3 | 3 | 1 | N |  |  | SB | Y | 8 | 1969 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage2000 | natural gas peaker | TRUE | 10005 | Evergy Kansas South, Inc | 1240 | Gordon Evans Energy Center | KS | Sedgwick | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | WR.GEEC.GT.1 | WR.GEEC.GT.1 | 98.3 | 0.85 | 71.6 | 71.6 | 65 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 10005 | Evergy Kansas South, Inc | 1240 | Gordon Evans Energy Center | KS | Sedgwick | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | WR.GEEC.GT.2 | WR.GEEC.GT.2 | 98.3 | 0.85 | 71.7 | 71.7 | 65 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 10005 | Evergy Kansas South, Inc | 1240 | Gordon Evans Energy Center | KS | Sedgwick | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | WR.GEEC.GT.3 | WR.GEEC.GT.3 | 178.5 | 0.85 | 150.4 | 150.4 | 112 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1973 | hard coal | TRUE | 10000 | Evergy Metro | 1241 | La Cygne | KS | Linn | 1 | Conventional Steam Coal | ST |  | J | X | X | KCPLLACYGNEUNLAC1 | LACYGNEUNLAC1 | 873 | 0.9 | 757.8 | 757.8 | 404 | N |  |  | OP | X | 6 | 1973 |  |  | N | Electric Utility | 1 | X | SUB | BIT |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | N |  | Y | N | Y | [17 empty] | N | N | N
Vintage1977 | hard coal | TRUE | 10000 | Evergy Metro | 1241 | La Cygne | KS | Linn | 2 | Conventional Steam Coal | ST |  | J | X | X | KCPLLACYGNEUNLAC2 | LACYGNEUNLAC2 | 725.9 | 0.9 | 668.8 | 668.8 | 274 | N |  |  | OP | X | 5 | 1977 |  |  | N | Electric Utility | 1 | X | SUB | [5 empty] | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1974 | natural gas peaker | TRUE | 22500 | Evergy Kansas Central, Inc | 1248 | Hutchinson Energy Center | KS | Reno | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | WR.HEC.GT.1 | WR.HEC.GT.1 | 71 | 0.9 | 55.5 | 55.5 | 10 | N |  |  | OP | X | 5 | 1974 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1974 | natural gas peaker | TRUE | 22500 | Evergy Kansas Central, Inc | 1248 | Hutchinson Energy Center | KS | Reno | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | WR.HEC.GT.2 | WR.HEC.GT.2 | 71 | 0.9 | 55 | 55 | 10 | N |  |  | OP | X | 5 | 1974 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1974 | natural gas peaker | TRUE | 22500 | Evergy Kansas Central, Inc | 1248 | Hutchinson Energy Center | KS | Reno | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | WR.HEC.GT.3 | WR.HEC.GT.3 | 71 | 0.9 | 55.4 | 55.4 | 10 | N |  |  | OP | X | 5 | 1974 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1975 | petroleum | TRUE | 22500 | Evergy Kansas Central, Inc | 1248 | Hutchinson Energy Center | KS | Reno | GT4 | Petroleum Liquids | GT |  | S | X | X | WR.HEC.GT.4 | WR.HEC.GT.4 | 70 | 0.9 | 73.6 | 73.6 | 20 | N |  |  | OP | X | 6 | 1975 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 12H | [23 empty] | N
Vintage1983 | petroleum | TRUE | 22500 | Evergy Kansas Central, Inc | 1248 | Hutchinson Energy Center | KS | Reno | H1DG | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 3 | N |  |  | SB | Y | 1 | 1983 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1960 | hard coal | TRUE | 22500 | Evergy Kansas Central, Inc | 1250 | Lawrence Energy Center | KS | Douglas | 4 | Conventional Steam Coal | ST |  | S | X | X | WR.LEC.4 | WR.LEC.4 | 114 | 0.85 | 111.3 | 111.3 | 38 | N |  |  | OP | X | 3 | 1960 |  |  | N | Electric Utility | 1 | X | SUB | NG |  |  |  |  | NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1971 | hard coal | TRUE | 22500 | Evergy Kansas Central, Inc | 1250 | Lawrence Energy Center | KS | Douglas | 5 | Conventional Steam Coal | ST |  | S | X | X | WR.LEC.5 | WR.LEC.5 | 403 | 0.9 | 374 | 374 | 120 | N |  |  | OP | X | 5 | 1971 |  |  | N | Electric Utility | 1 | X | SUB | NG |  |  |  |  | NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1972 | petroleum | TRUE | 701 | City of Anthony - (KS) | 1258 | Anthony | KS | Harper | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.1 | 0.8 | 4.1 | 4.1 | 1 | N |  |  | OP | X | 8 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1976 | petroleum | TRUE | 701 | City of Anthony - (KS) | 1258 | Anthony | KS | Harper | IC2 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 1 | N |  |  | OP | X | 6 | 1976 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1981 | petroleum | TRUE | 701 | City of Anthony - (KS) | 1258 | Anthony | KS | Harper | IC3 | Petroleum Liquids | IC |  | S | X | X |  |  | 4 | 0.8 | 4 | 4 | 1 | N |  |  | OP | X | 7 | 1981 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1953 | natural gas peaker | TRUE | 911 | City of Ashland - (KS) | 1259 | Ashland | KS | Clark | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.6 | 0.9 | 0.6 | 0.6 | 0.2 | N |  |  | SB | Y | 9 | 1953 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1974 | natural gas peaker | TRUE | 911 | City of Ashland - (KS) | 1259 | Ashland | KS | Clark | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.9 | 0.9 | 0.7 | 0.7 | 0.3 | N |  |  | SB | Y | 9 | 1974 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1963 | petroleum | TRUE | 911 | City of Ashland - (KS) | 1259 | Ashland | KS | Clark | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.9 | 1.1 | 1.1 | 0.6 | N |  |  | SB | Y | 5 | 1963 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage2014 | petroleum | TRUE | 911 | City of Ashland - (KS) | 1259 | Ashland | KS | Clark | 4B | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.9 | 1.8 | 1.8 | 1 | N |  |  | SB | Y | 8 | 2014 |  |  | N | Electric Utility | 1 | X | DFO | [10 empty] | N |  | 1H | [23 empty] | N |  | N
Vintage1971 | petroleum | TRUE | 911 | City of Ashland - (KS) | 1259 | Ashland | KS | Clark | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.9 | 0.7 | 0.7 | 0.3 | N |  |  | SB | Y | 5 | 1971 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N |  | N
Vintage1954 | natural gas peaker | TRUE | 998 | City of Augusta - (KS) | 1261 | Augusta Electric Plant No 1 | KS | Butler | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.5 | N |  |  | SB | Y | 7 | 1954 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage1929 | petroleum | TRUE | 998 | City of Augusta - (KS) | 1261 | Augusta Electric Plant No 1 | KS | Butler | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.2 | N |  |  | SB | Y | 8 | 1929 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | OVER | [23 empty] | N |  | N
Vintage1949 | natural gas peaker | TRUE | 998 | City of Augusta - (KS) | 1261 | Augusta Electric Plant No 1 | KS | Butler | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.5 | N |  |  | SB | Y | 12 | 1949 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage1939 | petroleum | TRUE | 998 | City of Augusta - (KS) | 1261 | Augusta Electric Plant No 1 | KS | Butler | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.7 | 0.8 | 0.7 | 0.7 | 0.4 | N |  |  | SB | Y | 8 | 1939 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | OVER | [23 empty] | N
Vintage1956 | natural gas peaker | TRUE | 998 | City of Augusta - (KS) | 1261 | Augusta Electric Plant No 1 | KS | Butler | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.2 | 0.8 | 2.2 | 2.2 | 1.5 | N |  |  | SB | Y | 6 | 1956 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage1956 | natural gas peaker | TRUE | 998 | City of Augusta - (KS) | 1261 | Augusta Electric Plant No 1 | KS | Butler | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.2 | 0.8 | 2.2 | 2.2 | 1.5 | N |  |  | SB | Y | 7 | 1956 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage1964 | natural gas peaker | TRUE | 998 | City of Augusta - (KS) | 1261 | Augusta Electric Plant No 1 | KS | Butler | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.7 | N |  |  | SB | Y | 4 | 1964 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage2016 | petroleum | TRUE | 998 | City of Augusta - (KS) | 1261 | Augusta Electric Plant No 1 | KS | Butler | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.3 | N |  |  | SB | Y | 8 | 2016 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1970 | petroleum | TRUE | 1148 | City of Baldwin City- (KS) | 1262 | Baldwin City Plant No 1 | KS | Douglas | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.5 | 1.5 | 1 | N |  |  | OP | X | 5 | 1970 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1964 | petroleum | TRUE | 1148 | City of Baldwin City- (KS) | 1262 | Baldwin City Plant No 1 | KS | Douglas | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 0.7 | 0.7 | 0.5 | N |  |  | OP | X | 10 | 1964 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1964 | petroleum | TRUE | 1148 | City of Baldwin City- (KS) | 1262 | Baldwin City Plant No 1 | KS | Douglas | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 0.7 | 0.7 | 0.5 | N |  |  | OP | X | 10 | 1964 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1955 | natural gas peaker | TRUE | 1512 | City of Belleville - (KS) | 1263 | Belleville | KS | Republic | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.5 | N |  |  | OP | X | 1 | 1955 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H |  |  |  | N | [19 empty] | Y | Y | Y
Vintage1961 | natural gas peaker | TRUE | 1512 | City of Belleville - (KS) | 1263 | Belleville | KS | Republic | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.7 | 0.8 | 1.7 | 1.7 | 1 | N |  |  | OP | X | 1 | 1961 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H |  |  |  | N | [19 empty] | Y | Y | Y
Vintage1966 | natural gas peaker | TRUE | 1512 | City of Belleville - (KS) | 1263 | Belleville | KS | Republic | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.7 | 0.8 | 3.7 | 3.7 | 2 | N |  |  | OP | X | 1 | 1966 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H |  |  |  | N | [19 empty] | Y | Y | Y
Vintage1971 | natural gas peaker | TRUE | 1512 | City of Belleville - (KS) | 1263 | Belleville | KS | Republic | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 5.1 | 0.8 | 5.1 | 5.1 | 3 | N |  |  | OP | X | 1 | 1971 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H |  |  |  | N | [19 empty] | Y | Y | Y
Vintage2007 | petroleum | TRUE | 1512 | City of Belleville - (KS) | 1263 | Belleville | KS | Republic | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.8 | 0.8 | 2.8 | 2.8 | 1.6 | N |  |  | OP | X | 1 | 2007 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H |  |  |  | N | [19 empty] | N | N | N
Vintage1951 | petroleum | TRUE | 1525 | City of Beloit - (KS) | 1264 | Beloit | KS | Mitchell | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.1 | 1.1 | 0.5 | N |  |  | OP | X | 7 | 1951 |  |  | N | Electric Utility | 1 | X | DFO | NG |  |  |  |  | DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1951 | petroleum | TRUE | 1525 | City of Beloit - (KS) | 1264 | Beloit | KS | Mitchell | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.1 | 1.1 | 0.5 | N |  |  | OP | X | 7 | 1951 |  |  | N | Electric Utility | 1 | X | DFO | NG |  |  |  |  | DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1961 | petroleum | TRUE | 1525 | City of Beloit - (KS) | 1264 | Beloit | KS | Mitchell | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 6 | 1961 |  |  | N | Electric Utility | 1 | X | DFO | NG |  |  |  |  | DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1964 | petroleum | TRUE | 1525 | City of Beloit - (KS) | 1264 | Beloit | KS | Mitchell | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.5 | 0.8 | 3 | 3 | 2.2 | N |  |  | OP | X | 11 | 1964 |  |  | N | Electric Utility | 1 | X | DFO | NG |  |  |  |  | DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1950 | petroleum | TRUE | 1525 | City of Beloit - (KS) | 1264 | Beloit | KS | Mitchell | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.7 | 0.8 | 0.6 | 0.6 | 0.3 | N |  |  | OP | X | 5 | 1950 |  |  | N | Electric Utility | 1 | X | DFO | NG |  |  |  |  | DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1971 | petroleum | TRUE | 1525 | City of Beloit - (KS) | 1264 | Beloit | KS | Mitchell | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.1 | 0.8 | 3.5 | 3.5 | 2 | N |  |  | OP | X | 8 | 1971 |  |  | N | Electric Utility | 1 | X | DFO | NG |  |  |  |  | DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1980 | petroleum | TRUE | 1525 | City of Beloit - (KS) | 1264 | Beloit | KS | Mitchell | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 6 | 0.8 | 5.5 | 5.5 | 3 | N |  |  | OP | X | 8 | 1980 |  |  | N | Electric Utility | 1 | X | DFO | NG |  |  |  |  | DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1973 | natural gas peaker | TRUE | 2547 | City of Burlingame - (KS) | 1265 | Burlingame | KS | Osage | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.1 | 0.99 | 1 | 1.1 | 0.8 | N |  |  | OP | X | 8 | 1973 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1963 | natural gas peaker | TRUE | 2547 | City of Burlingame - (KS) | 1265 | Burlingame | KS | Osage | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.9 | 0.99 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 8 | 1963 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1969 | natural gas peaker | TRUE | 2547 | City of Burlingame - (KS) | 1265 | Burlingame | KS | Osage | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.1 | 0.99 | 1 | 1.1 | 0.8 | N |  |  | OP | X | 8 | 1969 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1980 | natural gas peaker | TRUE | 2547 | City of Burlingame - (KS) | 1265 | Burlingame | KS | Osage | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.9 | 0.99 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 1 | 1980 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage2003 | petroleum | TRUE | 2551 | City of Burlington - (KS) | 1266 | Burlington (KS) | KS | Coffey | 1A | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 1 | 2 | 2 | 0.7 | N |  |  | SB | Y | 7 | 2003 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N |  | N
Vintage1962 | petroleum | TRUE | 2551 | City of Burlington - (KS) | 1266 | Burlington (KS) | KS | Coffey | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 1 | 1.3 | 1.3 | 0.5 | N |  |  | SB | Y | 9 | 1962 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage2005 | petroleum | TRUE | 2551 | City of Burlington - (KS) | 1266 | Burlington (KS) | KS | Coffey | 4A | Petroleum Liquids | IC |  | S | X | X |  |  | 2.3 | 1 | 2.3 | 2.3 | 0.8 | N |  |  | SB | Y | 6 | 2005 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1955 | natural gas peaker | TRUE | 2551 | City of Burlington - (KS) | 1266 | Burlington (KS) | KS | Coffey | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1 | 1 | 1 | 1 | 0.5 | N |  |  | SB | Y | 7 | 1955 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1983 | natural gas peaker | TRUE | 2551 | City of Burlington - (KS) | 1266 | Burlington (KS) | KS | Coffey | IC6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 4.8 | 1 | 4.8 | 4.8 | 1 | N |  |  | SB | Y | 7 | 1983 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 3355 | City of Chanute | 1268 | Chanute 2 | KS | Neosho | 14 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 60 | 0.85 | 42 | 52 | 30 | N |  |  | OP | X | 2 | 2002 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 12H | [23 empty] | N
Vintage1965 | natural gas peaker | TRUE | 3355 | City of Chanute | 1268 | Chanute 2 | KS | Neosho | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1 | N |  |  | OP | X | 8 | 1965 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y |  | N
Vintage1965 | natural gas peaker | TRUE | 3355 | City of Chanute | 1268 | Chanute 2 | KS | Neosho | 8 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1 | N |  |  | OP | X | 8 | 1965 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y |  | N
Vintage1948 | natural gas steam turbine | TRUE | 3710 | City of Clay Center - (KS) | 1270 | Clay Center | KS | Clay | 5 | Natural Gas Steam Turbine | ST |  | S | X | X | SPP | SPP | 3 | 1 | 3 | 3 | 1 | N |  |  | OP | X | 1 | 1948 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | NG |  |  |  | N |  |  | 10M | [23 empty] | Y | Y | Y
Vintage1961 | natural gas steam turbine | TRUE | 3710 | City of Clay Center - (KS) | 1270 | Clay Center | KS | Clay | 6 | Natural Gas Steam Turbine | ST |  | S | X | X | SPP | SPP | 5 | 1 | 5 | 5 | 1 | N |  |  | OP | X | 1 | 1961 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | NG |  |  |  | N |  |  | 10M | [23 empty] | Y | Y | Y
Vintage1958 | natural gas peaker | TRUE | 3710 | City of Clay Center - (KS) | 1270 | Clay Center | KS | Clay | IC1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | SPP | SPP | 0.9 | 1 | 0.9 | 0.9 | 0.5 | N |  |  | OP | X | 1 | 1958 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 10M | [23 empty] | Y | Y | Y
Vintage1966 | natural gas peaker | TRUE | 3710 | City of Clay Center - (KS) | 1270 | Clay Center | KS | Clay | IC2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | SPP | SPP | 2.1 | 1 | 2 | 2 | 0.5 | N |  |  | OP | X | 1 | 1966 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 10M | [23 empty] | Y | Y | Y
Vintage1972 | natural gas peaker | TRUE | 3710 | City of Clay Center - (KS) | 1270 | Clay Center | KS | Clay | IC3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | SPP | SPP | 5.1 | 1 | 5 | 5 | 0.5 | N |  |  | OP | X | 1 | 1972 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 10M | [23 empty] | Y | Y | Y
Vintage1996 | natural gas peaker | TRUE | 3710 | City of Clay Center - (KS) | 1270 | Clay Center | KS | Clay | IC4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | SPP | SPP | 3.5 | 1 | 3.5 | 3.5 | 0.5 | N |  |  | OP | X | 4 | 1996 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1996 | natural gas peaker | TRUE | 3710 | City of Clay Center - (KS) | 1270 | Clay Center | KS | Clay | IC5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | SPP | SPP | 3.5 | 1 | 3.5 | 3.5 | 0.5 | N |  |  | OP | X | 6 | 1996 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage2005 | natural gas peaker | TRUE | 3710 | City of Clay Center - (KS) | 1270 | Clay Center | KS | Clay | IC6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | SPP | SPP | 6.8 | 1 | 6.8 | 6.8 | 0.5 | N |  |  | OP | X | 3 | 2005 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage2007 | petroleum | TRUE | 3892 | City of Coffeyville - (KS) | 1271 | Coffeyville | KS | Montgomery | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.5 | N |  |  | OP | X | 4 | 2007 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N | N | N
Vintage2007 | petroleum | TRUE | 3892 | City of Coffeyville - (KS) | 1271 | Coffeyville | KS | Montgomery | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.5 | N |  |  | OP | X | 4 | 2007 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N | N | N
Vintage1973 | natural gas steam turbine | TRUE | 3892 | City of Coffeyville - (KS) | 1271 | Coffeyville | KS | Montgomery | 7 | Natural Gas Steam Turbine | ST |  | S | X | X | GRDACOFFEYGRUN7 | GRDACOFFEYGRUN7 | 40 | 0.9 | 37 | 38.2 | 9 | N |  |  | OP | X | 6 | 1973 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N |  |  | 12H | [23 empty] | N | N
Vintage1958 | petroleum | TRUE | 3913 | City of Colby - (KS) | 1272 | Colby City of | KS | Thomas | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.7 | 0.8 | 1.2 | 1.2 | 1.2 | N |  |  | OP | X | 8 | 1958 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1958 | petroleum | TRUE | 3913 | City of Colby - (KS) | 1272 | Colby City of | KS | Thomas | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1 | 1 | 1 | N |  |  | OP | X | 5 | 1958 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1971 | petroleum | TRUE | 3913 | City of Colby - (KS) | 1272 | Colby City of | KS | Thomas | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.5 | 0.8 | 3.5 | 3.5 | 3.5 | N |  |  | OA | X | 10 | 1971 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1971 | petroleum | TRUE | 3913 | City of Colby - (KS) | 1272 | Colby City of | KS | Thomas | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.5 | 0.8 | 3.5 | 3.5 | 3.5 | N |  |  | OP | X | 6 | 1971 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1965 | petroleum | TRUE | 3913 | City of Colby - (KS) | 1272 | Colby City of | KS | Thomas | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 3 | 1965 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2019 | petroleum | TRUE | 3913 | City of Colby - (KS) | 1272 | Colby City of | KS | Thomas | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 2.5 | N |  |  | OP | X | 8 | 2019 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1965 | petroleum | TRUE | 5802 | City of Ellinwood - (KS) | 1274 | Ellinwood | KS | Barton | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.1 | 0.8 | 1.8 | 1.8 | 1.5 | N |  |  | OP | X | 8 | 1965 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1957 | petroleum | TRUE | 5802 | City of Ellinwood - (KS) | 1274 | Ellinwood | KS | Barton | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.4 | 0.8 | 1.3 | 1.3 | 0.8 | N |  |  | OP | X | 6 | 1957 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1948 | petroleum | TRUE | 5802 | City of Ellinwood - (KS) | 1274 | Ellinwood | KS | Barton | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | SB | Y | 6 | 1948 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1953 | petroleum | TRUE | 5802 | City of Ellinwood - (KS) | 1274 | Ellinwood | KS | Barton | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1 | 1 | 0.5 | N |  |  | OP | X | 7 | 1953 |  |  | N | Electric Utility | 1 | X | DFO | NG | [11 empty] | 1H | [23 empty] | Y | N | Y
Vintage1971 | petroleum | TRUE | 5802 | City of Ellinwood - (KS) | 1274 | Ellinwood | KS | Barton | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.3 | 0.8 | 2.7 | 2.7 | 2 | N |  |  | OP | X | 6 | 1971 |  |  | N | Electric Utility | 1 | X | DFO | NG | [11 empty] | 1H | [23 empty] | Y | N | Y
Vintage1958 | petroleum | TRUE | 5957 | City of Erie - (KS) | 1276 | Erie | KS | Neosho | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 0.9 | 0.9 | 0.5 | N |  |  | OP | X | 11 | 1958 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2005 | petroleum | TRUE | 5957 | City of Erie - (KS) | 1276 | Erie | KS | Neosho | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1 | 1 | 0.5 | N |  |  | OP | X | 4 | 2005 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2005 | petroleum | TRUE | 5957 | City of Erie - (KS) | 1276 | Erie | KS | Neosho | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1 | 1 | 0.5 | N |  |  | OP | X | 4 | 2005 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N | N | N
Vintage2005 | petroleum | TRUE | 5957 | City of Erie - (KS) | 1276 | Erie | KS | Neosho | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1 | 1 | 0.5 | N |  |  | OP | X | 4 | 2005 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N | N | N
Vintage1961 | petroleum | TRUE | 6965 | City of Garnett - (KS) | 1278 | Garnett Municipal | KS | Anderson | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 1 | 1.3 | 1.3 | 0.8 | N |  |  | OP | X | 1 | 1961 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1930 | petroleum | TRUE | 6965 | City of Garnett - (KS) | 1278 | Garnett Municipal | KS | Anderson | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 1 | 0.3 | 0.3 | 0.3 | N |  |  | OP | X | 1 | 1930 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1955 | petroleum | TRUE | 6965 | City of Garnett - (KS) | 1278 | Garnett Municipal | KS | Anderson | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 1 | 1.3 | 1.3 | 0.8 | N |  |  | OP | X | 1 | 1955 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1948 | petroleum | TRUE | 6965 | City of Garnett - (KS) | 1278 | Garnett Municipal | KS | Anderson | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 1 | 0.8 | 0.8 | 0.4 | N |  |  | OP | X | 1 | 1948 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N |  |  | 10M | [23 empty] | Y | N | N
Vintage2000 | petroleum | TRUE | 6965 | City of Garnett - (KS) | 1278 | Garnett Municipal | KS | Anderson | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 1 | 2.2 | 2.2 | 1.5 | N |  |  | OP | X | 11 | 2000 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N |  |  | 10M | [23 empty] | N | N | N
Vintage1981 | petroleum | TRUE | 6965 | City of Garnett - (KS) | 1278 | Garnett Municipal | KS | Anderson | IC5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.4 | 1 | 2.1 | 2.1 | 1 | N |  |  | OP | X | 1 | 1981 |  |  | N | Electric Utility | 1 | X | DFO | NG | [11 empty] | 10M | [23 empty] | N | N | N
Vintage1978 | petroleum | TRUE | 6965 | City of Garnett - (KS) | 1278 | Garnett Municipal | KS | Anderson | IC6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 1 | 2.2 | 2.2 | 1.5 | N |  |  | OP | X | 1 | 1978 |  |  | N | Electric Utility | 1 | X | DFO | NG | [11 empty] | 10M | [23 empty] | N | N | N
Vintage1955 | petroleum | TRUE | 7257 | City of Girard - (KS) | 1279 | Girard | KS | Crawford | 1 | Petroleum Liquids | IC |  | S | X | X | SPP | SPP | 1.4 | 0.8 | 1.1 | 1.1 | 1 | N |  |  | OP | X | 9 | 1955 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1962 | petroleum | TRUE | 7257 | City of Girard - (KS) | 1279 | Girard | KS | Crawford | 4 | Petroleum Liquids | IC |  | S | X | X | SPP | SPP | 2.2 | 0.8 | 1.8 | 1.8 | 1.2 | N |  |  | OP | X | 9 | 1962 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1997 | petroleum | TRUE | 7257 | City of Girard - (KS) | 1279 | Girard | KS | Crawford | 6 | Petroleum Liquids | IC |  | S | X | X | SPP | SPP | 3.5 | 0.8 | 3.2 | 3.3 | 3 | N |  |  | OP | X | 5 | 1997 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1997 | petroleum | TRUE | 7257 | City of Girard - (KS) | 1279 | Girard | KS | Crawford | 7 | Petroleum Liquids | IC |  | S | X | X | SPP | SPP | 3.7 | 0.8 | 3.4 | 3.4 | 3.2 | N |  |  | OP | X | 4 | 1997 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1971 | natural gas peaker | TRUE | 7374 | City of Goodland - (KS) | 1280 | Goodland | KS | Sherman | 10 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 2 | 1.5 | N |  |  | OP | X | 7 | 1971 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1978 | natural gas peaker | TRUE | 7374 | City of Goodland - (KS) | 1280 | Goodland | KS | Sherman | 11 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 4.3 | 0.8 | 3.5 | 3.8 | 3.2 | N |  |  | OP | X | 9 | 1978 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1995 | natural gas peaker | TRUE | 7374 | City of Goodland - (KS) | 1280 | Goodland | KS | Sherman | 12 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1 | 0.8 | 0.8 | 0.9 | 0.6 | N |  |  | OP | X | 5 | 1995 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1999 | natural gas peaker | TRUE | 7374 | City of Goodland - (KS) | 1280 | Goodland | KS | Sherman | 13 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.1 | 1.3 | 1 | N |  |  | OP | X | 5 | 1999 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1939 | petroleum | TRUE | 7374 | City of Goodland - (KS) | 1280 | Goodland | KS | Sherman | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.7 | 0.8 | 0.7 | 0.7 | 0.5 | N |  |  | OP | X | 3 | 1939 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1962 | natural gas peaker | TRUE | 7374 | City of Goodland - (KS) | 1280 | Goodland | KS | Sherman | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.2 | 0.8 | 1.8 | 2.1 | 1.7 | N |  |  | OP | X | 7 | 1962 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1966 | natural gas peaker | TRUE | 7374 | City of Goodland - (KS) | 1280 | Goodland | KS | Sherman | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.2 | 0.8 | 1.8 | 2.1 | 1.7 | N |  |  | OP | X | 2 | 1966 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1975 | natural gas peaker | TRUE | 7374 | City of Goodland - (KS) | 1280 | Goodland | KS | Sherman | 8 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 5 | 0.8 | 4.6 | 4.8 | 3.5 | N |  |  | OP | X | 5 | 1975 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage2001 | petroleum | TRUE | 8490 | City of Herington - (KS) | 1283 | Herington | KS | Dickinson | 4B | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.5 | 1.5 | 0.5 | N |  |  | SB | Y | 7 | 2001 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1962 | petroleum | TRUE | 8599 | City of Hill City | 1285 | Hill City | KS | Graham | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.1 | 1.2 | 0.9 | N |  |  | OP | X | 3 | 1962 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1962 | petroleum | TRUE | 8599 | City of Hill City | 1285 | Hill City | KS | Graham | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.1 | 1.2 | 0.9 | N |  |  | OP | X | 3 | 1962 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1952 | petroleum | TRUE | 8599 | City of Hill City | 1285 | Hill City | KS | Graham | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.4 | N |  |  | OP | X | 5 | 1952 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1967 | petroleum | TRUE | 8599 | City of Hill City | 1285 | Hill City | KS | Graham | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1 | 1 | 0.8 | N |  |  | OP | X | 8 | 1967 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1974 | petroleum | TRUE | 8599 | City of Hill City | 1285 | Hill City | KS | Graham | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.2 | 1.2 | 0.9 | N |  |  | OP | X | 10 | 1974 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1974 | petroleum | TRUE | 8599 | City of Hill City | 1285 | Hill City | KS | Graham | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.2 | 1.2 | 0.9 | N |  |  | OP | X | 12 | 1974 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1996 | petroleum | TRUE | 8703 | City of Hoisington - (KS) | 1286 | Hoisington | KS | Barton | 2A | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1.1 | 1.1 | 0.7 | N |  |  | OP | X | 9 | 1996 |  |  | N | Electric Utility | 1 | X | DFO | [12 empty] | 1H | [23 empty] | N |  | N
Vintage1961 | natural gas peaker | TRUE | 8703 | City of Hoisington - (KS) | 1286 | Hoisington | KS | Barton | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1.8 | N |  |  | OP | X | 8 | 1961 |  |  | N | Electric Utility | 1 | X | NG | DFO | [11 empty] | 1H | [23 empty] | Y | Y | Y
Vintage1966 | natural gas peaker | TRUE | 8703 | City of Hoisington - (KS) | 1286 | Hoisington | KS | Barton | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 4 | 0.8 | 4 | 4 | 2.9 | N |  |  | OP | X | 8 | 1966 |  |  | N | Electric Utility | 1 | X | NG | DFO | [11 empty] | 1H | [23 empty] | Y | Y | Y
Vintage1970 | petroleum | TRUE | 8770 | City of Holton - (KS) | 1287 | Holton | KS | Jackson | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 2 | 1 | N |  |  | OP | X | 8 | 1970 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1994 | petroleum | TRUE | 8770 | City of Holton - (KS) | 1287 | Holton | KS | Jackson | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.4 | 0.8 | 2.2 | 2.4 | 1.7 | N |  |  | OP | X | 1 | 1994 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | N
Vintage2001 | natural gas peaker | TRUE | 8770 | City of Holton - (KS) | 1287 | Holton | KS | Jackson | 12 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.1 | 0.8 | 3 | 3.1 | 2.5 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | N
Vintage2001 | natural gas peaker | TRUE | 8770 | City of Holton - (KS) | 1287 | Holton | KS | Jackson | 13 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.1 | 0.8 | 3 | 3.1 | 2.5 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y |  | N
Vintage1958 | petroleum | TRUE | 8770 | City of Holton - (KS) | 1287 | Holton | KS | Jackson | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.4 | 1.7 | 0.9 | N |  |  | OP | X | 2 | 1958 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y |  | N
Vintage1963 | petroleum | TRUE | 8770 | City of Holton - (KS) | 1287 | Holton | KS | Jackson | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.8 | 0.8 | 2.4 | 2.6 | 1.2 | N |  |  | OP | X | 5 | 1963 |  |  | N | Electric Utility | 1 | X | DFO | NG | [9 empty] | N |  | 1H | [23 empty] | Y | N | N
Vintage1969 | petroleum | TRUE | 8770 | City of Holton - (KS) | 1287 | Holton | KS | Jackson | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.3 | 0.8 | 3.8 | 4 | 2.6 | N |  |  | OP | X | 6 | 1969 |  |  | N | Electric Utility | 1 | X | DFO | NG | [9 empty] | N |  | 1H | [23 empty] | Y | N | N
Vintage1970 | petroleum | TRUE | 8770 | City of Holton - (KS) | 1287 | Holton | KS | Jackson | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 2 | 1 | N |  |  | OP | X | 8 | 1970 |  |  | N | Electric Utility | 1 | X | DFO | NG | [9 empty] | N |  | 1H | [23 empty] | Y | N | N
Vintage1998 | natural gas peaker | TRUE | 9418 | City of Iola - (KS) | 1291 | Iola | KS | Allen | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 5 | 1 | 5 | 5 | 2.5 | N |  |  | OP | X | 8 | 1998 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1981 | petroleum | TRUE | 9418 | City of Iola - (KS) | 1291 | Iola | KS | Allen | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 1 | 2.9 | 2.9 | 2 | N |  |  | OP | X | 6 | 1981 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2020 | petroleum | TRUE | 9418 | City of Iola - (KS) | 1291 | Iola | KS | Allen | 14 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 1 | 2 | 2 | 1 | N |  |  | OP | X | 2 | 2020 |  |  | N | Electric Utility | 1 | X | DFO | [10 empty] | N |  | 10M | [23 empty] | N
Vintage2020 | petroleum | TRUE | 9418 | City of Iola - (KS) | 1291 | Iola | KS | Allen | 15 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 1 | 2 | 2 | 1 | N |  |  | OP | X | 2 | 2020 |  |  | N | Electric Utility | 1 | X | DFO | [10 empty] | N |  | 10M | [23 empty] | N
Vintage2021 | petroleum | TRUE | 9418 | City of Iola - (KS) | 1291 | Iola | KS | Allen | 16 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 1 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 8 | 2021 |  |  | N | Electric Utility | 1 | X | DFO | [10 empty] | N |  | 10M | [23 empty] | N | N | N
Vintage2000 | natural gas peaker | TRUE | 9418 | City of Iola - (KS) | 1291 | Iola | KS | Allen | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 5 | 1 | 5 | 5 | 2.5 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1969 | petroleum | TRUE | 9418 | City of Iola - (KS) | 1291 | Iola | KS | Allen | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 1 | 2.9 | 2.9 | 2 | N |  |  | OP | X | 5 | 1969 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1971 | petroleum | TRUE | 9418 | City of Iola - (KS) | 1291 | Iola | KS | Allen | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 1 | 2.9 | 2.9 | 2 | N |  |  | OP | X | 5 | 1971 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1976 | petroleum | TRUE | 9418 | City of Iola - (KS) | 1291 | Iola | KS | Allen | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 1 | 2.9 | 2.9 | 2 | N |  |  | OP | X | 2 | 1976 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1977 | petroleum | TRUE | 9418 | City of Iola - (KS) | 1291 | Iola | KS | Allen | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 1 | 2.9 | 2.9 | 2 | N |  |  | OP | X | 6 | 1977 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2015 | petroleum | TRUE | 9732 | City of Jetmore | 1292 | Jetmore | KS | Hodgeman | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 1 | N |  |  | SB | Y | 11 | 2015 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N | 0 | 1H |  |  |  | N | [16 empty] | N |  |  | N | N | N
Vintage1955 | natural gas steam turbine | TRUE | 9996 | City of Kansas City - (KS) | 1294 | Kaw | KS | Wyandotte | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | kacy | kacy | 50.1 | 0.97 | 41.9 | 41.9 | 30 | N |  |  | OS | X | 6 | 1955 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N |  |  | OVER |  | N |  |  | N | [18 empty] | N | N | N
Vintage1957 | natural gas steam turbine | TRUE | 9996 | City of Kansas City - (KS) | 1294 | Kaw | KS | Wyandotte | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | kacy | kacy | 50.1 | 0.97 | 41.9 | 41.9 | 30 | N |  |  | OS | X | 4 | 1957 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N |  |  | OVER |  | N |  |  | N | [18 empty] | N | N | N
Vintage1962 | natural gas steam turbine | TRUE | 9996 | City of Kansas City - (KS) | 1294 | Kaw | KS | Wyandotte | 3 | Natural Gas Steam Turbine | ST |  | S | X | X | kacy | kacy | 65.5 | 0.97 | 56.5 | 56.5 | 30 | N |  |  | OS | X | 5 | 1962 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N |  |  | OVER |  | N |  |  | N | [18 empty] | N | N | N
Vintage1974 | petroleum | TRUE | 9996 | City of Kansas City - (KS) | 1295 | Quindaro | KS | Wyandotte | GT2 | Petroleum Liquids | GT |  | S | X | X | kacy | kacy | 65.7 | 0.97 | 56 | 56 | 20 | N |  |  | OP | X | 7 | 1974 |  |  | N | Electric Utility | 1 | X | DFO | [5 empty] | DFO |  |  |  | N | N |  | 1H |  |  |  |  | N | [15 empty] | N |  |  | N | N | N
Vintage1977 | petroleum | TRUE | 9996 | City of Kansas City - (KS) | 1295 | Quindaro | KS | Wyandotte | GT3 | Petroleum Liquids | GT |  | S | X | X | kacy | kacy | 65.7 | 0.97 | 46 | 46 | 20 | N |  |  | OP | X | 8 | 1977 |  |  | N | Electric Utility | 1 | X | DFO | [5 empty] | DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1965 | natural gas steam turbine | TRUE | 9996 | City of Kansas City - (KS) | 1295 | Quindaro | KS | Wyandotte | ST1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 81.6 | 0.97 | 72 | 72 | 35 | N |  |  | OS | X | 5 | 1965 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER |  | N | [21 empty] | N | N | N
Vintage1971 | natural gas steam turbine | TRUE | 9996 | City of Kansas City - (KS) | 1295 | Quindaro | KS | Wyandotte | ST2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 157.5 | 0.97 | 85 | 85 | 55 | N |  |  | OS | X | 12 | 1971 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER |  | N | [21 empty] | N | N | N
Vintage1962 | natural gas peaker | TRUE | 10321 | City of Kingman - (KS) | 1296 | Kingman Municipal Power and Light Plant | KS | Kingman | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.2 | 0.8 | 1.9 | 2 | 1 | N |  |  | SB | Y | 4 | 1962 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1977 | natural gas peaker | TRUE | 10321 | City of Kingman - (KS) | 1296 | Kingman Municipal Power and Light Plant | KS | Kingman | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.2 | 0.8 | 1.9 | 2 | 1.2 | N |  |  | OP | X | 6 | 1977 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1969 | natural gas peaker | TRUE | 10321 | City of Kingman - (KS) | 1296 | Kingman Municipal Power and Light Plant | KS | Kingman | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.5 | 0.8 | 3.4 | 3.4 | 2.5 | N |  |  | OP | X | 9 | 1969 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1979 | natural gas peaker | TRUE | 10321 | City of Kingman - (KS) | 1296 | Kingman Municipal Power and Light Plant | KS | Kingman | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.4 | 0.8 | 2.1 | 2.1 | 1.2 | N |  |  | OP | X | 11 | 1979 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1984 | natural gas peaker | TRUE | 10321 | City of Kingman - (KS) | 1296 | Kingman Municipal Power and Light Plant | KS | Kingman | 8 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.4 | 2.4 | 1.6 | N |  |  | OP | X | 6 | 1984 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1993 | natural gas peaker | TRUE | 10321 | City of Kingman - (KS) | 1296 | Kingman Municipal Power and Light Plant | KS | Kingman | 9 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 6.3 | 0.8 | 6.3 | 6.3 | 4 | N |  |  | OP | X | 12 | 1993 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1962 | petroleum | TRUE | 10559 | City of La Crosse - (KS) | 1297 | La Crosse | KS | Rush | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.5 | N |  |  | OP | X | 11 | 1962 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1964 | petroleum | TRUE | 10559 | City of La Crosse - (KS) | 1297 | La Crosse | KS | Rush | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.5 | N |  |  | OP | X | 12 | 1964 |  |  | N | Electric Utility | 1 | X | DFO | NG | [11 empty] | 1H | [23 empty] | Y | N | Y
Vintage1969 | petroleum | TRUE | 10559 | City of La Crosse - (KS) | 1297 | La Crosse | KS | Rush | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.5 | N |  |  | OP | X | 1 | 1969 |  |  | N | Electric Utility | 1 | X | DFO | NG | [11 empty] | 1H | [23 empty] | Y |  | Y
Vintage1975 | petroleum | TRUE | 10559 | City of La Crosse - (KS) | 1297 | La Crosse | KS | Rush | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 12 | 1975 |  |  | N | Electric Utility | 1 | X | DFO | NG | [11 empty] | 1H | [23 empty] | Y |  | Y
Vintage2004 | petroleum | TRUE | 10713 | City of Larned - (KS) | 1299 | Larned | KS | Pawnee | CAT | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 1 | 2 | 2 | 0.2 | N |  |  | OP | X | 4 | 2004 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage2004 | petroleum | TRUE | 10713 | City of Larned - (KS) | 1299 | Larned | KS | Pawnee | CAT1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 1 | 2 | 2 | 0.2 | N |  |  | OP | X | 4 | 2004 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage2004 | petroleum | TRUE | 10713 | City of Larned - (KS) | 1299 | Larned | KS | Pawnee | CAT2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 1 | 2 | 2 | 0.2 | N |  |  | OP | X | 4 | 2004 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage2004 | petroleum | TRUE | 10713 | City of Larned - (KS) | 1299 | Larned | KS | Pawnee | CAT3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 1 | 2 | 2 | 0.2 | N |  |  | OP | X | 4 | 2004 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N
Vintage2004 | petroleum | TRUE | 10713 | City of Larned - (KS) | 1299 | Larned | KS | Pawnee | CAT4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 1 | 2 | 2 | 0.2 | N |  |  | OP | X | 4 | 2004 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N
Vintage1976 | petroleum | TRUE | 10713 | City of Larned - (KS) | 1299 | Larned | KS | Pawnee | IC5 | Petroleum Liquids | IC |  | S | X | X |  |  | 6.4 | 1 | 6 | 6 | 0.5 | N |  |  | OP | X | 12 | 1976 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1964 | petroleum | TRUE | 11017 | City of Lincoln Center - (KS) | 1300 | Lincoln | KS | Lincoln | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.1 | 1.1 | 0.7 | N |  |  | SB | Y | 8 | 1964 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1964 | petroleum | TRUE | 11017 | City of Lincoln Center - (KS) | 1300 | Lincoln | KS | Lincoln | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.1 | 1.1 | 0.7 | N |  |  | SB | Y | 8 | 1964 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1958 | petroleum | TRUE | 11017 | City of Lincoln Center - (KS) | 1300 | Lincoln | KS | Lincoln | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.7 | 0.8 | 0.6 | 0.6 | 0.4 | N |  |  | SB | Y | 1 | 1958 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1974 | petroleum | TRUE | 11017 | City of Lincoln Center - (KS) | 1300 | Lincoln | KS | Lincoln | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.5 | 0.8 | 3 | 3 | 1.5 | N |  |  | SB | Y | 8 | 1974 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2017 | petroleum | TRUE | 11017 | City of Lincoln Center - (KS) | 1300 | Lincoln | KS | Lincoln | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | SB | Y | 8 | 2017 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1973 | natural gas peaker | TRUE | 12208 | City of McPherson - (KS) | 1305 | McPherson 2 | KS | McPherson | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 72.4 | 0.9 | 50.5 | 60 | 22 | N |  |  | OP | X | 6 | 1973 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1976 | petroleum | TRUE | 12208 | City of McPherson - (KS) | 1305 | McPherson 2 | KS | McPherson | GT2 | Petroleum Liquids | GT |  | S | X | X |  |  | 71.2 | 0.9 | 51.8 | 60 | 22 | N |  |  | OP | X | 6 | 1976 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1979 | natural gas peaker | TRUE | 12208 | City of McPherson - (KS) | 1305 | McPherson 2 | KS | McPherson | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 71.2 | 0.9 | 51.7 | 60 | 22 | N |  |  | OP | X | 6 | 1979 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1951 | natural gas peaker | TRUE | 12242 | City of Meade - (KS) | 1306 | Meade | KS | Meade | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.9 | 0.9 | 0.8 | 0.8 | 0.4 | N |  |  | OP | X | 1 | 1951 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1957 | natural gas peaker | TRUE | 12242 | City of Meade - (KS) | 1306 | Meade | KS | Meade | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.1 | 0.9 | 1.1 | 1.1 | 0.6 | N |  |  | OP | X | 1 | 1957 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1961 | natural gas peaker | TRUE | 12242 | City of Meade - (KS) | 1306 | Meade | KS | Meade | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.4 | 0.9 | 1.3 | 1.4 | 0.8 | N |  |  | OP | X | 1 | 1961 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1965 | petroleum | TRUE | 12242 | City of Meade - (KS) | 1306 | Meade | KS | Meade | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.1 | 0.9 | 1.5 | 1.7 | 1.2 | N |  |  | OP | X | 1 | 1965 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1972 | natural gas peaker | TRUE | 12242 | City of Meade - (KS) | 1306 | Meade | KS | Meade | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.7 | 0.9 | 1.9 | 2 | 1.2 | N |  |  | OP | X | 1 | 1972 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1961 | natural gas peaker | TRUE | 21533 | City of Minneapolis - (KS) | 1307 | Minneapolis City of | KS | Ottawa | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.2 | 1.2 | 0.6 | N |  |  | OP | X | 12 | 1961 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1955 | natural gas peaker | TRUE | 21533 | City of Minneapolis - (KS) | 1307 | Minneapolis City of | KS | Ottawa | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.7 | 0.8 | 0.5 | 0.5 | 0.3 | N |  |  | OP | X | 4 | 1955 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1966 | natural gas peaker | TRUE | 21533 | City of Minneapolis - (KS) | 1307 | Minneapolis City of | KS | Ottawa | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.1 | 0.8 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 9 | 1966 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1972 | natural gas peaker | TRUE | 21533 | City of Minneapolis - (KS) | 1307 | Minneapolis City of | KS | Ottawa | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3 | 0.8 | 2.7 | 2.7 | 1.5 | N |  |  | OP | X | 2 | 1972 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1989 | petroleum | TRUE | 21533 | City of Minneapolis - (KS) | 1307 | Minneapolis City of | KS | Ottawa | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 5 | 1989 |  |  | N | Electric Utility | 1 | X | DFO | [12 empty] | 10M | [23 empty] | N | N | N
Vintage1956 | petroleum | TRUE | 13948 | City of Oberlin - (KS) | 1312 | Oberlin (KS) | KS | Decatur | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.9 | 0.9 | 0.9 | 0.6 | N |  |  | SB | Y | 1 | 1956 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N | 0 | 12H | [23 empty] | Y | Y | Y
Vintage1954 | petroleum | TRUE | 13948 | City of Oberlin - (KS) | 1312 | Oberlin (KS) | KS | Decatur | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.9 | 0.6 | 0.6 | 0.4 | N |  |  | SB | Y | 1 | 1954 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1967 | petroleum | TRUE | 13948 | City of Oberlin - (KS) | 1312 | Oberlin (KS) | KS | Decatur | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.9 | 1.2 | 1.2 | 0.8 | N |  |  | SB | Y | 10 | 1967 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1973 | petroleum | TRUE | 13948 | City of Oberlin - (KS) | 1312 | Oberlin (KS) | KS | Decatur | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.9 | 1.3 | 1.3 | 1 | N |  |  | SB | Y | 8 | 1973 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1963 | petroleum | TRUE | 13948 | City of Oberlin - (KS) | 1312 | Oberlin (KS) | KS | Decatur | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.9 | 1.2 | 1.2 | 0.8 | N |  |  | SB | Y | 8 | 1963 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1955 | natural gas peaker | TRUE | 14199 | City of Osage City - (KS) | 1313 | Osage City | KS | Osage | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | WROSAGE-3LD2 | WROSAGE-3LD2 | 1.1 | 0.8 | 0.9 | 0.9 | 0.5 | N |  |  | OP | X | 9 | 1955 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1960 | natural gas peaker | TRUE | 14199 | City of Osage City - (KS) | 1313 | Osage City | KS | Osage | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | WROSAGE-3LD2 | WROSAGE-3LD2 | 1.2 | 0.8 | 1.1 | 1.1 | 0.5 | N |  |  | OP | X | 9 | 1960 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1967 | natural gas peaker | TRUE | 14199 | City of Osage City - (KS) | 1313 | Osage City | KS | Osage | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | WROSAGE-3LD2 | WROSAGE-3LD2 | 2 | 0.8 | 1.9 | 1.9 | 1.1 | N |  |  | OP | X | 9 | 1967 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1970 | natural gas peaker | TRUE | 14199 | City of Osage City - (KS) | 1313 | Osage City | KS | Osage | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | WROSAGE-3LD2 | WROSAGE-3LD2 | 2 | 0.8 | 1.9 | 1.9 | 1.1 | N |  |  | OP | X | 9 | 1970 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1984 | natural gas peaker | TRUE | 14199 | City of Osage City - (KS) | 1313 | Osage City | KS | Osage | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | WROSAGE-3LD2 | WROSAGE-3LD2 | 1.7 | 0.8 | 1.5 | 1.5 | 1 | N |  |  | OP | X | 6 | 1984 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage2011 | natural gas peaker | TRUE | 14199 | City of Osage City - (KS) | 1313 | Osage City | KS | Osage | IC3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | WROSAGE-3LD2 | WROSAG-3LD2 | 2 | 0.8 | 1.9 | 1.9 | 1.1 | N |  |  | OP | X | 5 | 2011 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1983 | natural gas peaker | TRUE | 14199 | City of Osage City - (KS) | 1313 | Osage City | KS | Osage | IC6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | WROSAGE-3LD2 | WROSAGE-3LD2 | 1.1 | 0.8 | 0.9 | 0.9 | 0.6 | N |  |  | OP | X | 7 | 1983 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1957 | petroleum | TRUE | 14203 | City of Osawatomie - (KS) | 1314 | Osawatomie City of | KS | Miami | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.3 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | SB | Y | 2 | 1957 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1950 | petroleum | TRUE | 14203 | City of Osawatomie - (KS) | 1314 | Osawatomie City of | KS | Miami | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1 | 1 | 0.2 | N |  |  | SB | Y | 10 | 1950 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1966 | petroleum | TRUE | 14203 | City of Osawatomie - (KS) | 1314 | Osawatomie City of | KS | Miami | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.1 | 0.8 | 2.8 | 2.8 | 1.3 | N |  |  | SB | Y | 5 | 1966 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N |  |  | 10M | [23 empty] | Y | Y | Y
Vintage1967 | petroleum | TRUE | 14214 | City of Osborne - (KS) | 1315 | Osborne | KS | Osborne | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.3 | 0.8 | 1.4 | 1.6 | 0.5 | N |  |  | SB | Y | 6 | 1967 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1963 | petroleum | TRUE | 14214 | City of Osborne - (KS) | 1315 | Osborne | KS | Osborne | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.2 | 1.4 | 0.5 | N |  |  | SB | Y | 6 | 1963 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1957 | petroleum | TRUE | 14214 | City of Osborne - (KS) | 1315 | Osborne | KS | Osborne | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 0.6 | 0.7 | 0.5 | N |  |  | SB | Y | 6 | 1957 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1992 | natural gas peaker | TRUE | 14214 | City of Osborne - (KS) | 1315 | Osborne | KS | Osborne | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | SB | Y | 4 | 1992 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1992 | natural gas peaker | TRUE | 14214 | City of Osborne - (KS) | 1315 | Osborne | KS | Osborne | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | SB | Y | 4 | 1992 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1994 | natural gas peaker | TRUE | 14214 | City of Osborne - (KS) | 1315 | Osborne | KS | Osborne | 8 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.7 | 0.8 | 0.6 | 0.6 | 0.2 | N |  |  | SB | Y | 9 | 1994 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1962 | natural gas peaker | TRUE | 14229 | City of Ottawa - (KS) | 1316 | Ottawa | KS | Franklin | IC3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | KMEA_EMP1_OTTA3 | KMEA_EMP1_OTTA3 | 3.7 | 0.8 | 3.2 | 3.2 | 2 | N |  |  | OP | X | 5 | 1962 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1958 | natural gas peaker | TRUE | 14229 | City of Ottawa - (KS) | 1316 | Ottawa | KS | Franklin | IC4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | KMEA_EMP1_OTTA4 | KMEA_EMP1_OTTA4 | 3.5 | 0.8 | 3 | 3 | 2 | N |  |  | OP | X | 12 | 1958 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1981 | natural gas peaker | TRUE | 14229 | City of Ottawa - (KS) | 1316 | Ottawa | KS | Franklin | IC6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | KMEA_EMP1_OTTA6 | KMEA_EMP1_OTTA6 | 6 | 0.8 | 5.9 | 5.9 | 3 | N |  |  | OP | X | 5 | 1981 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1981 | natural gas peaker | TRUE | 14229 | City of Ottawa - (KS) | 1316 | Ottawa | KS | Franklin | IC7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | KMEA_EMP1_OTTA7 | KMEA_EMP1_OTTA7 | 6 | 0.8 | 5.9 | 5.9 | 3 | N |  |  | OP | X | 5 | 1981 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1965 | natural gas steam turbine | TRUE | 15321 | City of Pratt- (KS) | 1317 | Pratt | KS | Pratt | 5 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 14 | 0.85 | 13 | 13 | 5 | N |  |  | OP | X | 1 | 1965 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1958 | petroleum | TRUE | 15321 | City of Pratt- (KS) | 1317 | Pratt | KS | Pratt | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.5 | N |  |  | OP | X | 1 | 1958 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1994 | natural gas peaker | TRUE | 16440 | City of Russell - (KS) | 1319 | Russell Downtown | KS | Russell | 11 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.6 | 0.8 | 3.2 | 3.2 | 3 | N |  |  | OP | X | 11 | 1994 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1994 | natural gas peaker | TRUE | 16440 | City of Russell - (KS) | 1319 | Russell Downtown | KS | Russell | 12 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.6 | 0.8 | 3.2 | 3.2 | 3 | N |  |  | OP | X | 11 | 1994 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1971 | natural gas peaker | TRUE | 16440 | City of Russell - (KS) | 1319 | Russell Downtown | KS | Russell | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.5 | 0.8 | 3 | 3 | 3 | N |  |  | OP | X | 2 | 1971 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1978 | petroleum | TRUE | 16440 | City of Russell - (KS) | 1319 | Russell Downtown | KS | Russell | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 1.8 | N |  |  | OP | X | 8 | 1978 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N |  | N
Vintage1981 | petroleum | TRUE | 16440 | City of Russell - (KS) | 1319 | Russell Downtown | KS | Russell | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 1.8 | N |  |  | OP | X | 8 | 1981 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N |  | N
Vintage1992 | petroleum | TRUE | 16518 | City of Sabetha - (KS) | 1320 | Sabetha Power Plant | KS | Nemaha | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.8 | 2.7 | 2.7 | 1.5 | N |  |  | OP | X | 9 | 1992 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 16518 | City of Sabetha - (KS) | 1320 | Sabetha Power Plant | KS | Nemaha | 12 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 4.4 | 0.8 | 4.1 | 4.1 | 2.5 | N |  |  | OP | X | 1 | 2001 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1957 | petroleum | TRUE | 16518 | City of Sabetha - (KS) | 1320 | Sabetha Power Plant | KS | Nemaha | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.2 | 1.2 | 1 | N |  |  | OP | X | 8 | 1957 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1947 | petroleum | TRUE | 16518 | City of Sabetha - (KS) | 1320 | Sabetha Power Plant | KS | Nemaha | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 1 | 0.6 | 0.6 | 0.5 | N |  |  | OP | X | 8 | 1947 |  |  | N | Electric Utility | 1 | X | DFO | NG | [11 empty] | 1H | [23 empty] | Y | N | Y
Vintage1950 | petroleum | TRUE | 16518 | City of Sabetha - (KS) | 1320 | Sabetha Power Plant | KS | Nemaha | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 1 | 0.7 | 0.7 | 0.2 | N |  |  | OP | X | 8 | 1950 |  |  | N | Electric Utility | 1 | X | DFO | NG | [11 empty] | 1H | [23 empty] | Y |  | Y
Vintage1961 | petroleum | TRUE | 16518 | City of Sabetha - (KS) | 1320 | Sabetha Power Plant | KS | Nemaha | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.4 | 0.8 | 1.2 | 1.2 | 0.8 | N |  |  | OP | X | 8 | 1961 |  |  | N | Electric Utility | 1 | X | DFO | NG | [11 empty] | 1H | [23 empty] | Y |  | Y
Vintage1967 | petroleum | TRUE | 16518 | City of Sabetha - (KS) | 1320 | Sabetha Power Plant | KS | Nemaha | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.4 | 0.8 | 1.2 | 1.2 | 0.8 | N |  |  | OP | X | 8 | 1967 |  |  | N | Electric Utility | 1 | X | DFO | NG | [11 empty] | 1H | [23 empty] | Y | N | Y
Vintage1970 | petroleum | TRUE | 16518 | City of Sabetha - (KS) | 1320 | Sabetha Power Plant | KS | Nemaha | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.2 | 0.8 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 8 | 1970 |  |  | N | Electric Utility | 1 | X | DFO | NG | [11 empty] | 1H | [23 empty] | Y | N | Y
Vintage1978 | petroleum | TRUE | 16518 | City of Sabetha - (KS) | 1320 | Sabetha Power Plant | KS | Nemaha | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.1 | 2.1 | 0.8 | N |  |  | OP | X | 8 | 1978 |  |  | N | Electric Utility | 1 | X | DFO | NG | [11 empty] | 1H | [23 empty] | Y | N | Y
Vintage1990 | petroleum | TRUE | 16518 | City of Sabetha - (KS) | 1320 | Sabetha Power Plant | KS | Nemaha | IC10 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.1 | 2.1 | 1.5 | N |  |  | OP | X | 7 | 1990 |  |  | N | Electric Utility | 1 | X | DFO | NG | [11 empty] | 1H | [23 empty] | Y | N | Y
Vintage1985 | petroleum | TRUE | 16518 | City of Sabetha - (KS) | 1320 | Sabetha Power Plant | KS | Nemaha | IC9 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1 | 1 | 0.8 | N |  |  | OP | X | 6 | 1985 |  |  | N | Electric Utility | 1 | X | DFO | NG | [11 empty] | 1H | [23 empty] | Y |  | Y
Vintage1964 | petroleum | TRUE | 17872 | City of St Francis - (KS) | 1321 | St Francis | KS | Cheyenne | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.4 | N |  |  | OP | X | 8 | 1964 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1972 | petroleum | TRUE | 17872 | City of St Francis - (KS) | 1321 | St Francis | KS | Cheyenne | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2.7 | 2.7 | 0.4 | N |  |  | OP | X | 10 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1953 | petroleum | TRUE | 17872 | City of St Francis - (KS) | 1321 | St Francis | KS | Cheyenne | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.9 | 0.9 | 0.4 | N |  |  | OP | X | 8 | 1953 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2002 | petroleum | TRUE | 17879 | City of St. John - (KS) | 1322 | St John | KS | Stafford | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 0.8 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N
Vintage1965 | petroleum | TRUE | 17879 | City of St. John - (KS) | 1322 | St John | KS | Stafford | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.7 | 0.8 | 1.7 | 1.7 | 0.8 | N |  |  | OP | X | 9 | 1965 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1982 | petroleum | TRUE | 17879 | City of St. John - (KS) | 1322 | St John | KS | Stafford | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1.3 | N |  |  | OP | X | 12 | 1982 |  |  | N | Electric Utility | 1 | X | DFO | [10 empty] | N |  | 10M | [23 empty] | N |  | N
Vintage1970 | natural gas peaker | TRUE | 16988 | City of Sharon Springs - (KS) | 1324 | Sharon Spring | KS | Wallace | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.7 | N |  |  | OP | X | 11 | 1970 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1964 | natural gas peaker | TRUE | 16988 | City of Sharon Springs - (KS) | 1324 | Sharon Spring | KS | Wallace | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.7 | N |  |  | OP | X | 8 | 1964 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1958 | natural gas peaker | TRUE | 16988 | City of Sharon Springs - (KS) | 1324 | Sharon Spring | KS | Wallace | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 7 | 1958 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1951 | natural gas peaker | TRUE | 16988 | City of Sharon Springs - (KS) | 1324 | Sharon Spring | KS | Wallace | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.4 | N |  |  | OP | X | 8 | 1951 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1973 | petroleum | TRUE | 17924 | City of Stafford - (KS) | 1325 | Stafford | KS | Stafford | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.4 | 0.97 | 1.4 | 1.4 | 0.9 | N |  |  | OP | X | 7 | 1973 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | N
Vintage1983 | petroleum | TRUE | 17924 | City of Stafford - (KS) | 1325 | Stafford | KS | Stafford | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.97 | 1.1 | 1.1 | 0.9 | N |  |  | OP | X | 5 | 1983 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | N
Vintage1962 | petroleum | TRUE | 18086 | City of Sterling - (KS) | 1326 | Sterling | KS | Rice | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.3 | 1.3 | 0.9 | N |  |  | OP | X | 8 | 1962 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1950 | petroleum | TRUE | 18086 | City of Sterling - (KS) | 1326 | Sterling | KS | Rice | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 8 | 1950 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1972 | petroleum | TRUE | 18086 | City of Sterling - (KS) | 1326 | Sterling | KS | Rice | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.8 | 2.2 | 2.2 | 1 | N |  |  | OP | X | 11 | 1972 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1955 | petroleum | TRUE | 18086 | City of Sterling - (KS) | 1326 | Sterling | KS | Rice | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 7 | 1955 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage2002 | petroleum | TRUE | 18086 | City of Sterling - (KS) | 1326 | Sterling | KS | Rice | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.4 | 0.8 | 1.2 | 1.2 | 0.9 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage2002 | petroleum | TRUE | 18086 | City of Sterling - (KS) | 1326 | Sterling | KS | Rice | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.4 | 0.8 | 1.2 | 1.2 | 0.9 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage2002 | petroleum | TRUE | 18086 | City of Sterling - (KS) | 1326 | Sterling | KS | Rice | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.4 | 0.8 | 1.2 | 1.2 | 0.9 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1967 | petroleum | TRUE | 18137 | City of Stockton - (KS) | 1327 | Stockton | KS | Rooks | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 0.9 | 0.9 | 0.6 | N |  |  | OP | X | 7 | 1967 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1962 | petroleum | TRUE | 18137 | City of Stockton - (KS) | 1327 | Stockton | KS | Rooks | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 0.9 | 0.9 | 0.6 | N |  |  | OP | X | 5 | 1962 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1971 | petroleum | TRUE | 18137 | City of Stockton - (KS) | 1327 | Stockton | KS | Rooks | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.7 | 1.7 | 1.5 | N |  |  | OP | X | 7 | 1971 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1955 | petroleum | TRUE | 18137 | City of Stockton - (KS) | 1327 | Stockton | KS | Rooks | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1 | 1 | 0.8 | N |  |  | OP | X | 7 | 1955 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1963 | natural gas peaker | TRUE | 20069 | City of Wamego - (KS) | 1328 | Wamego | KS | Pottawatomie | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.92 | 1.3 | 1.3 | 0.9 | N |  |  | OP | X | 9 | 1963 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage2016 | natural gas peaker | TRUE | 20069 | City of Wamego - (KS) | 1328 | Wamego | KS | Pottawatomie | 10 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.2 | 0.92 | 3.2 | 3.2 | 1.7 | N |  |  | OP | X | 3 | 2016 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1972 | natural gas peaker | TRUE | 20069 | City of Wamego - (KS) | 1328 | Wamego | KS | Pottawatomie | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.92 | 1.3 | 1.3 | 0.9 | N |  |  | OP | X | 6 | 1972 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1956 | natural gas peaker | TRUE | 20069 | City of Wamego - (KS) | 1328 | Wamego | KS | Pottawatomie | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.1 | 0.92 | 1.1 | 1.1 | 0.5 | N |  |  | OP | X | 8 | 1956 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1967 | natural gas peaker | TRUE | 20069 | City of Wamego - (KS) | 1328 | Wamego | KS | Pottawatomie | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2 | 0.92 | 2 | 2 | 1.5 | N |  |  | OP | X | 1 | 1967 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1979 | natural gas peaker | TRUE | 20069 | City of Wamego - (KS) | 1328 | Wamego | KS | Pottawatomie | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.4 | 0.92 | 2.4 | 2.4 | 1.5 | N |  |  | OP | X | 8 | 1979 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1996 | natural gas peaker | TRUE | 20069 | City of Wamego - (KS) | 1328 | Wamego | KS | Pottawatomie | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.92 | 1.3 | 1.3 | 0.9 | N |  |  | OP | X | 6 | 1996 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1996 | natural gas peaker | TRUE | 20069 | City of Wamego - (KS) | 1328 | Wamego | KS | Pottawatomie | 8 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.92 | 1.3 | 1.3 | 0.9 | N |  |  | OP | X | 6 | 1996 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1996 | natural gas peaker | TRUE | 20069 | City of Wamego - (KS) | 1328 | Wamego | KS | Pottawatomie | 9 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.92 | 1.3 | 1.3 | 0.9 | N |  |  | OP | X | 6 | 1996 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1963 | petroleum | TRUE | 20141 | City of Washington - (KS) | 1329 | Washington | KS | Washington | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1 | 1 | 0.8 | N |  |  | OP | X | 8 | 1963 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1958 | petroleum | TRUE | 20141 | City of Washington - (KS) | 1329 | Washington | KS | Washington | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 0.8 | 0.8 | 0.4 | N |  |  | OP | X | 4 | 1958 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1978 | petroleum | TRUE | 20141 | City of Washington - (KS) | 1329 | Washington | KS | Washington | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.7 | 0.8 | 0.4 | N |  |  | OP | X | 6 | 1978 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1953 | petroleum | TRUE | 20141 | City of Washington - (KS) | 1329 | Washington | KS | Washington | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.4 | 0.5 | 0.3 | N |  |  | OP | X | 11 | 1953 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1967 | petroleum | TRUE | 20141 | City of Washington - (KS) | 1329 | Washington | KS | Washington | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.3 | 1.4 | 0.7 | N |  |  | OP | X | 4 | 1967 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1976 | petroleum | TRUE | 20141 | City of Washington - (KS) | 1329 | Washington | KS | Washington | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 0.9 | 1 | 0.8 | N |  |  | OP | X | 1 | 1976 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1986 | petroleum | TRUE | 20141 | City of Washington - (KS) | 1329 | Washington | KS | Washington | IC4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.6 | 0.8 | 2.3 | 2.4 | 1.8 | N |  |  | OP | X | 12 | 1986 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage1972 | natural gas steam turbine | TRUE | 20315 | City of Wellington - (KS) | 1330 | Wellington 1 | KS | Sumner | 4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 20 | 0.85 | 19.5 | 19.5 | 4 | N |  |  | OP | X | 8 | 1972 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage2004 | petroleum | TRUE | 20315 | City of Wellington - (KS) | 1330 | Wellington 1 | KS | Sumner | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1.6 | N |  |  | OP | X | 2 | 2004 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage2004 | petroleum | TRUE | 20315 | City of Wellington - (KS) | 1330 | Wellington 1 | KS | Sumner | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1.6 | N |  |  | OP | X | 2 | 2004 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1962 | natural gas peaker | TRUE | 20813 | City of Winfield - (KS) | 1332 | West 14th Street | KS | Cowley | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 11 | 0.9 | 11.1 | 11.2 | 3 | N |  |  | OP | X | 8 | 1962 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1973 | natural gas steam turbine | TRUE | 18315 | Sunflower Electric Power Corp | 1336 | Garden City | KS | Finney | S2 | Natural Gas Steam Turbine | ST |  | S | X | X | SECIGRDNCT1UN2 | SECIGRDNCT1UN2 | 97.9 | 0.85 | 97.6 | 97.6 | 23 | N |  |  | OP | X | 4 | 1973 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1968 | natural gas peaker | TRUE | 18315 | Sunflower Electric Power Corp | 1336 | Garden City | KS | Finney | S3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SECIGRDNCT1UN3 | SECIGRDNCT1UN3 | 16 | 0.85 | 12.8 | 12.8 | 10 | N |  |  | SB | Y | 6 | 1968 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1976 | natural gas peaker | TRUE | 18315 | Sunflower Electric Power Corp | 1336 | Garden City | KS | Finney | S4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SECIGRDNCT1UN4 | SECIGRDNCT1UN4 | 71.2 | 0.9 | 57.1 | 57.1 | 20 | N |  |  | OP | X | 5 | 1976 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1979 | natural gas peaker | TRUE | 18315 | Sunflower Electric Power Corp | 1336 | Garden City | KS | Finney | S5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SECIGRDNCT1UN5 | SECIGRDNCT1UN5 | 71.2 | 0.9 | 53.8 | 53.8 | 20 | N |  |  | OP | X | 7 | 1979 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1963 | natural gas steam turbine | TRUE | 22053 | Kentucky Power Co | 1353 | Big Sandy | KY | Lawrence | 1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 280.5 | 0.85 | 260 | 260 | 100 | N |  |  | OP | X | 1 | 1963 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | 12H |  | N | [21 empty] | N | N | N
Vintage1925 | hydro | TRUE | 10171 | Kentucky Utilities Co | 1354 | Dix Dam | KY | Mercer | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9.4 | 0.8 | 10.5 | 10.5 | 2 | N |  |  | OP | X | 11 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 10M | [23 empty] | N
Vintage1925 | hydro | TRUE | 10171 | Kentucky Utilities Co | 1354 | Dix Dam | KY | Mercer | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9.4 | 0.8 | 10.5 | 10.5 | 2 | N |  |  | OP | X | 11 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 10M | [23 empty] | N
Vintage1925 | hydro | TRUE | 10171 | Kentucky Utilities Co | 1354 | Dix Dam | KY | Mercer | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9.4 | 0.8 | 10.5 | 10.5 | 2 | N |  |  | OP | X | 11 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 10M | [23 empty] | N
Vintage1995 | natural gas peaker | TRUE | 10171 | Kentucky Utilities Co | 1355 | E W Brown | KY | Mercer | 10 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 126 | 0.85 | 121 | 138 | 50 | N |  |  | OP | X | 12 | 1995 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1996 | natural gas peaker | TRUE | 10171 | Kentucky Utilities Co | 1355 | E W Brown | KY | Mercer | 11 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 126 | 0.85 | 121 | 128 | 50 | N |  |  | OP | X | 5 | 1996 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1971 | hard coal | TRUE | 10171 | Kentucky Utilities Co | 1355 | E W Brown | KY | Mercer | 3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 464 | 0.9 | 412 | 416 | 155 | N |  |  | OP | X | 7 | 1971 |  |  | N | Electric Utility | 1 | X | BIT | [5 empty] | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage2001 | natural gas peaker | TRUE | 10171 | Kentucky Utilities Co | 1355 | E W Brown | KY | Mercer | 5 | Natural Gas Fired Combustion Turbine | GT |  | J | X | X |  |  | 123 | 0.85 | 130 | 130 | 50 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1999 | natural gas peaker | TRUE | 10171 | Kentucky Utilities Co | 1355 | E W Brown | KY | Mercer | 6 | Natural Gas Fired Combustion Turbine | GT |  | J | X | X |  |  | 176.8 | 0.85 | 146 | 171 | 90 | N |  |  | OP | X | 8 | 1999 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1999 | natural gas peaker | TRUE | 10171 | Kentucky Utilities Co | 1355 | E W Brown | KY | Mercer | 7 | Natural Gas Fired Combustion Turbine | GT |  | J | X | X |  |  | 176.8 | 0.85 | 146 | 171 | 105 | N |  |  | OP | X | 8 | 1999 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1995 | natural gas peaker | TRUE | 10171 | Kentucky Utilities Co | 1355 | E W Brown | KY | Mercer | 8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 126 | 0.85 | 121 | 128 | 50 | N |  |  | OP | X | 2 | 1995 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1994 | natural gas peaker | TRUE | 10171 | Kentucky Utilities Co | 1355 | E W Brown | KY | Mercer | 9 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 126 | 0.85 | 121 | 138 | 50 | N |  |  | OP | X | 8 | 1994 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2016 | solar pv | TRUE | 10171 | Kentucky Utilities Co | 1355 | E W Brown | KY | Mercer | SOLAR | Solar Photovoltaic | PV |  | J | X | X |  |  | 13 |  | 10 | 10 |  | N |  |  | OP | X | 5 | 2016 |  |  | N | Electric Utility | 1 | X | SUN | [9 empty] | N | N
Vintage1974 | hard coal | TRUE | 10171 | Kentucky Utilities Co | 1356 | Ghent | KY | Carroll | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 556.9 | 0.9 | 474 | 476 | 218 | N |  |  | OP | X | 2 | 1974 |  |  | N | Electric Utility | 1 | X | RC | BIT |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1977 | hard coal | TRUE | 10171 | Kentucky Utilities Co | 1356 | Ghent | KY | Carroll | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 556.3 | 0.9 | 495 | 477 | 225 | N |  |  | OP | X | 4 | 1977 |  |  | N | Electric Utility | 1 | X | RC | BIT |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1981 | hard coal | TRUE | 10171 | Kentucky Utilities Co | 1356 | Ghent | KY | Carroll | 3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 556.5 | 0.9 | 485 | 478 | 210 | N |  |  | OP | X | 5 | 1981 |  |  | N | Electric Utility | 1 | X | RC | BIT |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1984 | hard coal | TRUE | 10171 | Kentucky Utilities Co | 1356 | Ghent | KY | Carroll | 4 | Conventional Steam Coal | ST |  | S | X | X |  |  | 556.2 | 0.9 | 465 | 487 | 215 | N |  |  | OP | X | 8 | 1984 |  |  | N | Electric Utility | 1 | X | RC | BIT |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1970 | natural gas peaker | TRUE | 10171 | Kentucky Utilities Co | 1358 | Haefling | KY | Fayette | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 20.7 | 0.85 | 12 | 14 | 2 | N |  |  | OP | X | 10 | 1970 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1970 | natural gas peaker | TRUE | 10171 | Kentucky Utilities Co | 1358 | Haefling | KY | Fayette | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 20.7 | 0.85 | 12 | 14 | 2 | N |  |  | OP | X | 10 | 1970 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2008 | hydro | TRUE | 54775 | Lock 7 Hydro Partners LLC | 1359 | Mother Ann Lee | KY | Mercer | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.8 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 12 | 2008 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N |  | 0 | 10M | [23 empty] | N
Vintage2007 | hydro | TRUE | 54775 | Lock 7 Hydro Partners LLC | 1359 | Mother Ann Lee | KY | Mercer | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.8 | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 7 | 2007 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N |  | 0 | 10M | [23 empty] | N
Vintage2007 | hydro | TRUE | 54775 | Lock 7 Hydro Partners LLC | 1359 | Mother Ann Lee | KY | Mercer | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.8 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 3 | 2007 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N |  | 0 | 10M | [23 empty] | N
Vintage2015 | natural gas combined cycle | TRUE | 11249 | Louisville Gas & Electric Co | 1363 | Cane Run | KY | Jefferson | 7A | Natural Gas Fired Combined Cycle | CT | 7ABS | J | X | N |  |  | 260 | 1 | 213 | 226 | 95 | N |  |  | OP | X | 6 | 2015 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage2015 | natural gas combined cycle | TRUE | 11249 | Louisville Gas & Electric Co | 1363 | Cane Run | KY | Jefferson | 7B | Natural Gas Fired Combined Cycle | CT | 7ABS | J | X | N |  |  | 260 | 1 | 213 | 226 | 95 | N |  |  | OP | X | 6 | 2015 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage2015 | natural gas combined cycle | TRUE | 11249 | Louisville Gas & Electric Co | 1363 | Cane Run | KY | Jefferson | 7S | Natural Gas Fired Combined Cycle | CA | 7ABS | J | N | X |  |  | 287 | 1 | 237 | 231 | 38 | N |  |  | OP | X | 6 | 2015 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage1972 | hard coal | TRUE | 11249 | Louisville Gas & Electric Co | 1364 | Mill Creek (KY) | KY | Jefferson | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 355.5 | 0.9 | 300 | 300 | 115 | N |  |  | OP | X | 8 | 1972 |  |  | N | Electric Utility | 1 | X | RC | BIT |  |  |  |  | NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1974 | hard coal | TRUE | 11249 | Louisville Gas & Electric Co | 1364 | Mill Creek (KY) | KY | Jefferson | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 355.5 | 0.9 | 297 | 297 | 115 | N |  |  | OP | X | 7 | 1974 |  |  | N | Electric Utility | 1 | X | RC | BIT |  |  |  |  | NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1978 | hard coal | TRUE | 11249 | Louisville Gas & Electric Co | 1364 | Mill Creek (KY) | KY | Jefferson | 3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 462.6 | 0.9 | 391 | 394 | 170 | N |  |  | OP | X | 8 | 1978 |  |  | N | Electric Utility | 1 | X | RC | BIT |  |  |  |  | NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1982 | hard coal | TRUE | 11249 | Louisville Gas & Electric Co | 1364 | Mill Creek (KY) | KY | Jefferson | 4 | Conventional Steam Coal | ST |  | S | X | X |  |  | 543.6 | 0.9 | 477 | 486 | 175 | N |  |  | OP | X | 9 | 1982 |  |  | N | Electric Utility | 1 | X | RC | BIT |  |  |  |  | NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1928 | hydro | TRUE | 11249 | Louisville Gas & Electric Co | 1365 | Ohio Falls | KY | Jefferson | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 13.7 | 0.93 | 12.6 | 12.6 | 2 | N |  |  | OP | X | 1 | 1928 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1928 | hydro | TRUE | 11249 | Louisville Gas & Electric Co | 1365 | Ohio Falls | KY | Jefferson | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 13.7 | 0.93 | 12.6 | 12.6 | 2 | N |  |  | OP | X | 1 | 1928 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1928 | hydro | TRUE | 11249 | Louisville Gas & Electric Co | 1365 | Ohio Falls | KY | Jefferson | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 13.7 | 0.93 | 12.6 | 12.6 | 2 | N |  |  | OP | X | 1 | 1928 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1928 | hydro | TRUE | 11249 | Louisville Gas & Electric Co | 1365 | Ohio Falls | KY | Jefferson | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 13.7 | 0.93 | 12.6 | 12.6 | 2 | N |  |  | OP | X | 1 | 1928 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H
Vintage1928 | hydro | TRUE | 11249 | Louisville Gas & Electric Co | 1365 | Ohio Falls | KY | Jefferson | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 13.7 | 0.93 | 12.6 | 12.6 | 2 | N |  |  | OP | X | 1 | 1928 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1928 | hydro | TRUE | 11249 | Louisville Gas & Electric Co | 1365 | Ohio Falls | KY | Jefferson | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 13.7 | 0.93 | 12.6 | 12.6 | 2 | N |  |  | OP | X | 1 | 1928 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1928 | hydro | TRUE | 11249 | Louisville Gas & Electric Co | 1365 | Ohio Falls | KY | Jefferson | 7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 13.7 | 0.93 | 12.6 | 12.6 | 2 | N |  |  | OP | X | 1 | 1928 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1928 | hydro | TRUE | 11249 | Louisville Gas & Electric Co | 1365 | Ohio Falls | KY | Jefferson | 8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 13.7 | 0.8 | 12.6 | 12.6 | 2 | N |  |  | OP | X | 1 | 1928 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1968 | natural gas peaker | TRUE | 11249 | Louisville Gas & Electric Co | 1366 | Paddys Run | KY | Jefferson | 12 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 32.6 | 0.85 | 23 | 28 | 23 | N |  |  | OP | X | 7 | 1968 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage2001 | natural gas peaker | TRUE | 11249 | Louisville Gas & Electric Co | 1366 | Paddys Run | KY | Jefferson | 13 | Natural Gas Fired Combustion Turbine | GT |  | J | X | X |  |  | 178 | 0.85 | 147 | 175 | 81 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1966 | hydro | TRUE | 19462 | USCE-Nashville District | 1371 | Barkley | KY | Lyon | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 32.5 | 0.9 | 37 | 37 | 32.5 | N |  |  | OP | X | 1 | 1966 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 10M | [23 empty] | N
Vintage1966 | hydro | TRUE | 19462 | USCE-Nashville District | 1371 | Barkley | KY | Lyon | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 32.5 | 0.9 | 37 | 37 | 32.5 | N |  |  | OP | X | 2 | 1966 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 10M | [23 empty] | N
Vintage1966 | hydro | TRUE | 19462 | USCE-Nashville District | 1371 | Barkley | KY | Lyon | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 32.5 | 0.9 | 37 | 37 | 32.5 | N |  |  | OP | X | 3 | 1966 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 10M | [23 empty] | N
Vintage1966 | hydro | TRUE | 19462 | USCE-Nashville District | 1371 | Barkley | KY | Lyon | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 32.5 | 0.9 | 37 | 37 | 32.5 | N |  |  | OP | X | 3 | 1966 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 10M | [23 empty] | N
Vintage1952 | petroleum | TRUE | 14459 | City of Paris - (KY) | 1376 | Paris (KY) | KY | Bourbon | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.4 | 1.4 | 0.2 | N |  |  | OP | X | 12 | 1952 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N | N
Vintage1954 | petroleum | TRUE | 14459 | City of Paris - (KY) | 1376 | Paris (KY) | KY | Bourbon | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.4 | 1.4 | 0.2 | N |  |  | OP | X | 12 | 1954 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N | N
Vintage1934 | petroleum | TRUE | 14459 | City of Paris - (KY) | 1376 | Paris (KY) | KY | Bourbon | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.7 | 0.8 | 0.8 | 0.8 | 0.2 | N |  |  | OP | X | 12 | 1934 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N | N
Vintage1947 | petroleum | TRUE | 14459 | City of Paris - (KY) | 1376 | Paris (KY) | KY | Bourbon | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 1.1 | 1.1 | 0.2 | N |  |  | OP | X | 12 | 1947 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1949 | petroleum | TRUE | 14459 | City of Paris - (KY) | 1376 | Paris (KY) | KY | Bourbon | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.2 | 1.2 | 0.2 | N |  |  | OP | X | 12 | 1949 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N | N
Vintage1974 | petroleum | TRUE | 14459 | City of Paris - (KY) | 1376 | Paris (KY) | KY | Bourbon | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.1 | 0.8 | 3 | 3 | 0.2 | N |  |  | OP | X | 12 | 1974 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N | N
Vintage1974 | petroleum | TRUE | 14459 | City of Paris - (KY) | 1376 | Paris (KY) | KY | Bourbon | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.1 | 0.8 | 3 | 3 | 0.2 | N |  |  | OP | X | 12 | 1974 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N | N
Vintage1945 | hydro | TRUE | 18642 | Tennessee Valley Authority | 1377 | Kentucky Dam | KY | Marshall | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 44.6 | 0.92 | 44 | 37 | 18.9 | N |  |  | OP | X | 4 | 1945 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1944 | hydro | TRUE | 18642 | Tennessee Valley Authority | 1377 | Kentucky Dam | KY | Marshall | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 42.4 | 0.92 | 45.4 | 37 | 18.9 | N |  |  | OP | X | 11 | 1944 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1944 | hydro | TRUE | 18642 | Tennessee Valley Authority | 1377 | Kentucky Dam | KY | Marshall | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 42.4 | 0.92 | 44.9 | 37.2 | 18.9 | N |  |  | OP | X | 9 | 1944 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1945 | hydro | TRUE | 18642 | Tennessee Valley Authority | 1377 | Kentucky Dam | KY | Marshall | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 44.6 | 0.92 | 43.1 | 35.4 | 18.9 | N |  |  | OP | X | 12 | 1945 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1948 | hydro | TRUE | 18642 | Tennessee Valley Authority | 1377 | Kentucky Dam | KY | Marshall | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 44.6 | 0.92 | 45.1 | 36.5 | 18.9 | N |  |  | OP | X | 1 | 1948 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage2017 | natural gas combined cycle | TRUE | 18642 | Tennessee Valley Authority | 1378 | Paradise | KY | Muhlenberg | CTG1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 231 | 0.85 | 211 | 231 | 150 | N |  |  | OP | X | 4 | 2017 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 1H | [23 empty] | N | N | N
Vintage2017 | natural gas combined cycle | TRUE | 18642 | Tennessee Valley Authority | 1378 | Paradise | KY | Muhlenberg | CTG2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 231 | 0.85 | 211 | 231 | 150 | N |  |  | OP | X | 4 | 2017 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 1H | [23 empty] | N | N | N
Vintage2017 | natural gas combined cycle | TRUE | 18642 | Tennessee Valley Authority | 1378 | Paradise | KY | Muhlenberg | CTG3 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 231 | 0.85 | 211 | 231 | 150 | N |  |  | OP | X | 4 | 2017 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 1H | [23 empty] | N | N | N
Vintage2017 | natural gas combined cycle | TRUE | 18642 | Tennessee Valley Authority | 1378 | Paradise | KY | Muhlenberg | STG1 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 467 | 0.85 | 467 | 467 | 70 | N |  |  | OP | X | 4 | 2017 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 12H | [23 empty] | N | N | N
Vintage1953 | hard coal | TRUE | 18642 | Tennessee Valley Authority | 1379 | Shawnee | KY | McCracken | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 175 | 0.9 | 134 | 138 | 51 | N |  |  | OP | X | 4 | 1953 | 12 | 2033 | N | Electric Utility | 1 | X | SUB | DFO |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1953 | hard coal | TRUE | 18642 | Tennessee Valley Authority | 1379 | Shawnee | KY | McCracken | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 175 | 0.9 | 134 | 138 | 51 | N |  |  | OP | X | 6 | 1953 | 12 | 2033 | N | Electric Utility | 1 | X | SUB | DFO |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1953 | hard coal | TRUE | 18642 | Tennessee Valley Authority | 1379 | Shawnee | KY | McCracken | 3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 175 | 0.9 | 134 | 138 | 51 | N |  |  | OP | X | 10 | 1953 |  |  | N | Electric Utility | 1 | X | SUB | DFO |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1954 | hard coal | TRUE | 18642 | Tennessee Valley Authority | 1379 | Shawnee | KY | McCracken | 4 | Conventional Steam Coal | ST |  | S | X | X |  |  | 175 | 0.9 | 134 | 138 | 51 | N |  |  | OP | X | 1 | 1954 | 12 | 2033 | N | Electric Utility | 1 | X | SUB | DFO |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1954 | hard coal | TRUE | 18642 | Tennessee Valley Authority | 1379 | Shawnee | KY | McCracken | 5 | Conventional Steam Coal | ST |  | S | X | X |  |  | 175 | 0.9 | 134 | 138 | 51 | N |  |  | OP | X | 10 | 1954 | 12 | 2033 | N | Electric Utility | 1 | X | SUB | DFO |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1954 | hard coal | TRUE | 18642 | Tennessee Valley Authority | 1379 | Shawnee | KY | McCracken | 6 | Conventional Steam Coal | ST |  | S | X | X |  |  | 175 | 0.9 | 134 | 138 | 51 | N |  |  | OP | X | 11 | 1954 | 12 | 2033 | N | Electric Utility | 1 | X | SUB | DFO |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1954 | hard coal | TRUE | 18642 | Tennessee Valley Authority | 1379 | Shawnee | KY | McCracken | 7 | Conventional Steam Coal | ST |  | S | X | X |  |  | 175 | 0.9 | 134 | 138 | 51 | N |  |  | OP | X | 12 | 1954 | 12 | 2033 | N | Electric Utility | 1 | X | SUB | DFO |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1955 | hard coal | TRUE | 18642 | Tennessee Valley Authority | 1379 | Shawnee | KY | McCracken | 8 | Conventional Steam Coal | ST |  | S | X | X |  |  | 175 | 0.9 | 134 | 138 | 51 | N |  |  | OP | X | 3 | 1955 | 12 | 2033 | N | Electric Utility | 1 | X | SUB | DFO |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1955 | hard coal | TRUE | 18642 | Tennessee Valley Authority | 1379 | Shawnee | KY | McCracken | 9 | Conventional Steam Coal | ST |  | S | X | X |  |  | 175 | 0.9 | 134 | 138 | 51 | N |  |  | OP | X | 7 | 1955 | 12 | 2033 | N | Electric Utility | 1 | X | SUB | DFO |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1952 | hydro | TRUE | 19462 | USCE-Nashville District | 1380 | Wolf Creek | KY | Russell | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 45 | 0.9 | 52 | 52 | 45 | N |  |  | OP | X | 8 | 1952 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 10M | [23 empty] | N
Vintage1952 | hydro | TRUE | 19462 | USCE-Nashville District | 1380 | Wolf Creek | KY | Russell | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 45 | 0.9 | 52 | 52 | 45 | N |  |  | OP | X | 7 | 1952 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 10M | [23 empty] | N
Vintage1952 | hydro | TRUE | 19462 | USCE-Nashville District | 1380 | Wolf Creek | KY | Russell | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 45 | 0.9 | 40 | 40 | 40 | N |  |  | OP | X | 3 | 1952 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 10M | [23 empty] | N
Vintage1951 | hydro | TRUE | 19462 | USCE-Nashville District | 1380 | Wolf Creek | KY | Russell | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 45 | 0.9 | 52 | 52 | 45 | N |  |  | OP | X | 12 | 1951 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 10M | [23 empty] | N
Vintage1951 | hydro | TRUE | 19462 | USCE-Nashville District | 1380 | Wolf Creek | KY | Russell | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 45 | 0.9 | 52 | 52 | 45 | N |  |  | OP | X | 10 | 1951 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 10M | [23 empty] | N
Vintage1951 | hydro | TRUE | 19462 | USCE-Nashville District | 1380 | Wolf Creek | KY | Russell | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 45 | 0.9 | 52 | 52 | 45 | N |  |  | OP | X | 10 | 1951 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 10M | [23 empty] | N
Vintage1976 | natural gas peaker | TRUE | 1692 | Big Rivers Electric Corp | 1383 | Robert A Reid | KY | Webster | GEN2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | BREC.REIDCT | BREC.REIDCT | 98.8 | 0.9 | 58 | 65 | 20 | N |  |  | OP | X | 3 | 1976 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1965 | hard coal | TRUE | 5580 | East Kentucky Power Coop, Inc | 1384 | Cooper | KY | Pulaski | 1 | Conventional Steam Coal | ST |  | S | X | X | 1123180704 | 88100101 | 113.6 | 0.928 | 116 | 116 | 30 | N |  |  | OP | X | 2 | 1965 |  |  | N | Electric Utility | 1 | X | BIT | WDS |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1969 | hard coal | TRUE | 5580 | East Kentucky Power Coop, Inc | 1384 | Cooper | KY | Pulaski | 2 | Conventional Steam Coal | ST |  | S | X | X | 123180705 | 88100102 | 230.4 | 0.938 | 225 | 225 | 100 | N |  |  | OP | X | 10 | 1969 |  |  | N | Electric Utility | 1 | X | BIT | [5 empty] | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1951 | other | FALSE | 11241 | Entergy Louisiana LLC | 1391 | Louisiana 1 | LA | East Baton Rouge | 1A | Other Gases | ST |  | S | X | X |  |  | 23 | 0.85 | 18 | 18 | 2 | N |  |  | OP | X | 10 | 1951 |  |  | Y | Industrial CHP | 7 | B | OG | NG | DFO |  |  |  | NG | OG |  |  | N |  |  | 12H | [23 empty] | Y |  | N
Vintage1954 | other | FALSE | 11241 | Entergy Louisiana LLC | 1391 | Louisiana 1 | LA | East Baton Rouge | 2A | Other Gases | ST |  | S | X | X |  |  | 62.5 | 0.85 | 55 | 55 | 20 | N |  |  | OP | X | 12 | 1954 |  |  | Y | Industrial CHP | 7 | T | OG | NG | DFO |  |  |  | NG | OG |  |  | N |  |  | OVER | [23 empty] | Y |  | N
Vintage1954 | other | FALSE | 11241 | Entergy Louisiana LLC | 1391 | Louisiana 1 | LA | East Baton Rouge | 3A | Other Gases | ST |  | S | X | X |  |  | 63 | 0.85 | 55 | 55 | 20 | N |  |  | OP | X | 9 | 1954 |  |  | Y | Industrial CHP | 7 | T | OG | NG | DFO |  |  |  | NG | OG |  |  | N |  |  | OVER | [23 empty] | Y |  | N
Vintage1987 | natural gas peaker | FALSE | 11241 | Entergy Louisiana LLC | 1391 | Louisiana 1 | LA | East Baton Rouge | 4A | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 129.1 | 0.9 | 100 | 100 | 30 | N |  |  | OP | X | 8 | 1987 |  |  | Y | Industrial CHP | 7 | T | NG | OG | DFO | [7 empty] | N |  |  | 12H | [23 empty] | N |  | N
Vintage1999 | natural gas peaker | FALSE | 11241 | Entergy Louisiana LLC | 1391 | Louisiana 1 | LA | East Baton Rouge | 5A | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 173.3 | 0.85 | 154.4 | 164.4 | 16 | N |  |  | OP | X | 1 | 1999 |  |  | Y | Industrial CHP | 7 | T | NG | OG | DFO | [7 empty] | N |  |  | 12H | [23 empty] | N |  | N
Vintage1950 | natural gas steam turbine | TRUE | 11241 | Entergy Louisiana LLC | 1392 | Louisiana 2 | LA | East Baton Rouge | 10 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 50 | 0.85 | 40 | 40 | 5 | N |  |  | OS | X | 1 | 1950 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N |  |  | 12H | [23 empty] | N
Vintage1950 | natural gas steam turbine | TRUE | 11241 | Entergy Louisiana LLC | 1392 | Louisiana 2 | LA | East Baton Rouge | 11 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 50 | 0.85 | 40 | 40 | 5 | N |  |  | OS | X | 11 | 1950 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N |  |  | 12H | [23 empty] | N
Vintage1953 | natural gas steam turbine | TRUE | 11241 | Entergy Louisiana LLC | 1392 | Louisiana 2 | LA | East Baton Rouge | 12 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 75 | 0.85 | 58 | 58 | 10 | N |  |  | OS | X | 5 | 1953 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N |  |  | 12H | [23 empty] | N
Vintage1959 | petroleum | TRUE | 11241 | Entergy Louisiana LLC | 1393 | R S Nelson | LA | Calcasieu | 1 | Petroleum Coke | ST |  | J | X | X | EES.NELSON1 | EES.NELSON1 | 113.6 | 0.85 | 97.2 | 109 | 80 | N |  |  | OP | X | 2 | 1959 |  |  | Y | Electric Utility | 1 | T | PC | [5 empty] | NG |  |  |  | N | N |  | OVER | Y | N |  |  | Y | [18 empty] | N
Vintage1959 | petroleum | TRUE | 11241 | Entergy Louisiana LLC | 1393 | R S Nelson | LA | Calcasieu | 2 | Petroleum Coke | ST |  | J | X | X | EES.NELSON2 | EES.NELSON2 | 113.6 | 0.85 | 93.2 | 108 | 80 | N |  |  | OP | X | 5 | 1959 |  |  | Y | Electric Utility | 1 | T | PC | [5 empty] | NG |  |  |  | N |  |  | OVER | Y | N |  |  | Y | [18 empty] | N
Vintage1970 | natural gas steam turbine | TRUE | 11241 | Entergy Louisiana LLC | 1393 | R S Nelson | LA | Calcasieu | 4 | Natural Gas Steam Turbine | ST |  | S | X | X | EES.NELSON4 | EES.NELSON4 | 591.8 | 0.87 | 424.7 | 434.3 | 163 | N |  |  | OP | X | 7 | 1970 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N |  |  | OVER |  | N | [21 empty] | N | N | N
Vintage1982 | hard coal | TRUE | 11241 | Entergy Louisiana LLC | 1393 | R S Nelson | LA | Calcasieu | 6 | Conventional Steam Coal | ST |  | J | X | X | EES.NELSON6 | EES.NELSON6 | 614.6 | 0.87 | 524 | 524 | 150 | N |  |  | OP | X | 5 | 1982 |  |  | N | Electric Utility | 1 | X | SUB | [5 empty] | DFO |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1961 | natural gas combined cycle | TRUE | 3265 | Cleco Power LLC | 1396 | Coughlin Power Station | LA | Evangeline | 6 | Natural Gas Fired Combined Cycle | CA | CC6 | S | Y | X | CLEC.CPS6ST |  | 113.6 | 0.85 | 103.1 |  | 50 | N |  |  | OP | X | 4 | 1961 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N |  |  | 12H | [23 empty] | N |  | N
Vintage1966 | natural gas combined cycle | TRUE | 3265 | Cleco Power LLC | 1396 | Coughlin Power Station | LA | Evangeline | 7 | Natural Gas Fired Combined Cycle | CA | CC7 | S | Y | X | CLEC.CPS7ST |  | 243.1 | 0.85 | 181.6 |  | 50 | N |  |  | OP | X | 2 | 1966 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 12H | [23 empty] | N |  | N
Vintage2000 | natural gas combined cycle | TRUE | 3265 | Cleco Power LLC | 1396 | Coughlin Power Station | LA | Evangeline | U6CT | Natural Gas Fired Combined Cycle | CT | CC6 | S | X | Y | CLEC.CPS6 |  | 188.7 | 0.85 | 155.5 |  | 120 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 12H | [23 empty] | N | N | N
Vintage2000 | natural gas combined cycle | TRUE | 3265 | Cleco Power LLC | 1396 | Coughlin Power Station | LA | Evangeline | U72 | Natural Gas Fired Combined Cycle | CT | CC7 | S | X | Y | CLEC.CPS72 |  | 188.7 | 0.85 | 148.5 |  | 120 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 12H | [23 empty] | N | N | N
Vintage2000 | natural gas combined cycle | TRUE | 3265 | Cleco Power LLC | 1396 | Coughlin Power Station | LA | Evangeline | U7CT | Natural Gas Fired Combined Cycle | CT | CC7 | S | X | Y | CLEC.CPS71 |  | 188.7 | 0.85 | 147.6 |  | 120 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | X | NG | [12 empty] | 12H | [23 empty] | N | N | N
Vintage1971 | natural gas steam turbine | TRUE | 3265 | Cleco Power LLC | 1400 | Teche | LA | St Mary | 3 | Natural Gas Steam Turbine | ST |  | S | X | X | CLEC.TPS3 |  | 348.5 | 0.85 | 336.2 | 328 | 65 | N |  |  | OP | X | 3 | 1971 |  |  | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | NG |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage2011 | natural gas peaker | TRUE | 3265 | Cleco Power LLC | 1400 | Teche | LA | St Mary | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | CLEC.TPS4 |  | 42.2 | 0.85 | 33.1 | 34 | 30 | N |  |  | OP | X | 3 | 2011 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage1966 | natural gas steam turbine | TRUE | 11241 | Entergy Louisiana LLC | 1402 | Little Gypsy | LA | St Charles | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | EES.L_GYPSY2 | EES.L_GYPSY2 | 420.7 | 0.85 | 412.5 | 416.8 | 24 | N |  |  | OP | X | 4 | 1966 | 6 | 2026 | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | NG |  |  |  | N |  |  | 12H | [23 empty] | Y | Y | Y
Vintage1969 | natural gas steam turbine | TRUE | 11241 | Entergy Louisiana LLC | 1402 | Little Gypsy | LA | St Charles | 3 | Natural Gas Steam Turbine | ST |  | S | X | X | EES.L_GYPSY3 | EES.L_GYPSY3 | 582.2 | 0.85 | 513.5 | 522.1 | 150 | N |  |  | OP | X | 3 | 1969 | 6 | 2029 | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | NG |  |  |  | N |  |  | OVER | [23 empty] | Y | N | N
Vintage1973 | natural gas steam turbine | TRUE | 11241 | Entergy Louisiana LLC | 1403 | Nine Mile Point | LA | Jefferson | 5 | Natural Gas Steam Turbine | ST |  | S | X | X | EES.NINEMILE5 | EES.NINEMILE5 | 895.1 | 0.9 | 742.1 | 749.7 | 190 | N |  |  | OP | X | 6 | 1973 | 6 | 2033 | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | NG |  |  |  | N |  |  | OVER | [23 empty] | Y | Y | Y
Vintage1971 | natural gas steam turbine | TRUE | 11241 | Entergy Louisiana LLC | 1403 | Nine Mile Point | LA | Jefferson | 6(4) | Natural Gas Steam Turbine | ST |  | S | X | X | EES.NINEMILE4 | EES.NINEMILE4 | 895.1 | 0.9 | 738 | 755.6 | 190 | N |  |  | OP | X | 5 | 1971 | 6 | 2031 | N | Electric Utility | 1 | X | NG | DFO |  |  |  |  | NG |  |  |  | N |  |  | OVER | [23 empty] | Y | Y | Y
Vintage2014 | natural gas combined cycle | TRUE | 11241 | Entergy Louisiana LLC | 1403 | Nine Mile Point | LA | Jefferson | 6A | Natural Gas Fired Combined Cycle | CT | PB01 | S | X | N |  |  | 194.7 | 0.85 | 168 | 180 | 17 | N |  |  | OP | X | 12 | 2014 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 10M | [23 empty] | Y | N | Y
Vintage2014 | natural gas combined cycle | TRUE | 11241 | Entergy Louisiana LLC | 1403 | Nine Mile Point | LA | Jefferson | 6B | Natural Gas Fired Combined Cycle | CT | PB01 | S | X | N |  |  | 194.7 | 0.85 | 168 | 180 | 17 | N |  |  | OP | X | 12 | 2014 |  |  | N | Electric Utility | 1 | X | NG | DFO | [11 empty] | 10M | [23 empty] | Y |  | Y
Vintage2014 | natural gas combined cycle | TRUE | 11241 | Entergy Louisiana LLC | 1403 | Nine Mile Point | LA | Jefferson | 6C | Natural Gas Fired Combined Cycle | CA | PB01 | S | Y | X |  |  | 260.1 | 0.85 | 554.9 | 597.3 | 50 | N |  |  | OP | X | 12 | 2014 |  |  | N | Electric Utility | 1 | X | NG | DFO | [11 empty] | 12H | [23 empty] | N |  | N
Vintage1973 | natural gas peaker | TRUE | 11241 | Entergy Louisiana LLC | 1404 | Sterlington | LA | Ouachita | 7A | Natural Gas Fired Combustion Turbine | GT | PB01 | S | X | X | EES.STERL7 | EES.STERL7 | 59.3 | 0.9 | 47 | 53.2 | 5 | N |  |  | OP | X | 4 | 1973 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1960 | natural gas steam turbine | TRUE | 17698 | Southwestern Electric Power Co | 1416 | Arsenal Hill | LA | Caddo | 5 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 125 | 0.85 | 110 | 110 | 35 | N |  |  | OP | X | 3 | 1960 | 12 | 2025 | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N |  |  | OVER | [23 empty] | N | N | N
Vintage1957 | natural gas steam turbine | TRUE | 17698 | Southwestern Electric Power Co | 1417 | Lieberman | LA | Caddo | 3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 114 | 0.85 | 100 | 100 | 35 | N |  |  | OP | X | 6 | 1957 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1959 | natural gas steam turbine | TRUE | 17698 | Southwestern Electric Power Co | 1417 | Lieberman | LA | Caddo | 4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 114 | 0.85 | 108 | 108 | 35 | N |  |  | OP | X | 5 | 1959 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1967 | natural gas steam turbine | TRUE | 8884 | Terrebonne Parish Consol Gov't | 1439 | Houma | LA | Terrebonne | 14 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 12.6 | 0.85 | 10 | 10 | 3.9 | N |  |  | OP | X | 8 | 1967 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N |  |  | 12H | [23 empty] | N | N | N
Vintage1972 | natural gas steam turbine | TRUE | 8884 | Terrebonne Parish Consol Gov't | 1439 | Houma | LA | Terrebonne | 15 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 25.5 | 0.85 | 23.5 | 23.5 | 8 | N |  |  | OP | X | 8 | 1972 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N |  |  | 12H | [23 empty] | N | N | N
Vintage1977 | natural gas steam turbine | TRUE | 8884 | Terrebonne Parish Consol Gov't | 1439 | Houma | LA | Terrebonne | 16 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 40.8 | 0.85 | 34 | 34 | 9 | N |  |  | OP | X | 1 | 1977 |  |  | N | Electric Utility | 1 | X | NG | [5 empty] | NG |  |  |  | N |  |  | 12H | [23 empty] | N | N | N
Vintage1965 | petroleum | TRUE | 13483 | City of New Roads - (LA) | 1453 | New Roads | LA | Pointe Coupee | 1 | Petroleum Liquids | IC |  | S | X | X | NA | NA | 2.3 | 0.9 | 1.8 | 1.8 | 0.3 | N |  |  | OP | X | 6 | 1965 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1953 | petroleum | TRUE | 13483 | City of New Roads - (LA) | 1453 | New Roads | LA | Pointe Coupee | 2 | Petroleum Liquids | IC |  | S | X | X | NA | NA | 0.6 | 0.9 | 0.6 | 0.6 | 0.3 | N |  |  | OP | X | 6 | 1953 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1957 | petroleum | TRUE | 13483 | City of New Roads - (LA) | 1453 | New Roads | LA | Pointe Coupee | 3 | Petroleum Liquids | IC |  | S | X | X | NA | NA | 1.1 | 0.9 | 0.7 | 0.7 | 0.3 | N |  |  | OP | X | 6 | 1957 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1957 | petroleum | TRUE | 13483 | City of New Roads - (LA) | 1453 | New Roads | LA | Pointe Coupee | 4 | Petroleum Liquids | IC |  | S | X | X | NA | NA | 1.7 | 0.9 | 1.2 | 1.2 | 0.3 | N |  |  | OP | X | 6 | 1957 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1951 | petroleum | TRUE | 13483 | City of New Roads - (LA) | 1453 | New Roads | LA | Pointe Coupee | 5 | Petroleum Liquids | IC |  | S | X | X | NA | NA | 1.7 | 0.9 | 1.2 | 1.2 | 0.3 | N |  |  | OP | X | 6 | 1951 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1971 | petroleum | TRUE | 13483 | City of New Roads - (LA) | 1453 | New Roads | LA | Pointe Coupee | 6 | Petroleum Liquids | IC |  | S | X | X | NA | NA | 2 | 0.9 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 6 | 1971 |  |  | N | Electric Utility | 1 | X | DFO | NG | [8 empty] | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1969 | petroleum | TRUE | 26253 | Louisiana Energy & Power Authority | 1456 | Rayne | LA | Acadia | 8 | Petroleum Liquids | IC |  | W | X | X | NA | NA | 4.1 | 0.9 | 3.4 | 3.4 | 0.2 | N |  |  | OS | X | 1 | 1969 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N
Vintage1969 | petroleum | TRUE | 26253 | Louisiana Energy & Power Authority | 1456 | Rayne | LA | Acadia | 9 | Petroleum Liquids | IC |  | W | X | X | NA | NA | 4.1 | 0.9 | 3.6 | 3.6 | 0.2 | N |  |  | OS | X | 6 | 1969 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N
Vintage1972 | natural gas steam turbine | TRUE | 11252 | Louisiana Generating LLC | 1464 | Big Cajun 1 | LA | Pointe Coupee | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | LAGN.BCI_1 | LAGN.BCI_1 | 113.6 | 0.85 | 110 | 110 | 35 | N |  |  | OP | X | 6 | 1972 |  |  | N | IPP Non-CHP | 2 | X | NG | [5 empty] | NG |  |  |  | N | N |  | 12H |  |  |  |  | N | [18 empty] | N | N | N
Vintage1972 | natural gas steam turbine | TRUE | 11252 | Louisiana Generating LLC | 1464 | Big Cajun 1 | LA | Pointe Coupee | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | LAGN.BCI_2 | LAGN.BCI_2 | 113.6 | 0.85 | 110 | 110 | 35 | N |  |  | OP | X | 6 | 1972 |  |  | N | IPP Non-CHP | 2 | X | NG | [5 empty] | NG |  |  |  | N | N |  | 12H |  |  |  |  | N | [18 empty] | N | N | N
Vintage2001 | natural gas peaker | TRUE | 11252 | Louisiana Generating LLC | 1464 | Big Cajun 1 | LA | Pointe Coupee | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | LAGN.BC1T_3 | LAGN.BC1T_3 | 132.8 | 0.9 | 105 | 115 | 70 | N |  |  | OP | X | 5 | 2001 |  |  | N | IPP Non-CHP | 2 | X | NG | [9 empty] | N | N |  | 1H |  |  |  |  | N | [18 empty] | N | N | N
Vintage2001 | natural gas peaker | TRUE | 11252 | Louisiana Generating LLC | 1464 | Big Cajun 1 | LA | Pointe Coupee | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | LAGN.BC1T_4 | LAGN.BC1T_4 | 132.8 | 0.9 | 105 | 115 | 70 | N |  |  | OP | X | 6 | 2001 |  |  | N | IPP Non-CHP | 2 | X | NG | [9 empty] | N | N |  | 1H |  |  |  |  | N | [18 empty] | N | N | N
Vintage1924 | hydro | TRUE | 59178 | Brookfield Black Bear Hydro, LLC | 1469 | Ellsworth Hydro Station | ME | Hancock | EL01 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 0.8 | 2.6 | 2.5 | 1 | N |  |  | OP | X | 7 | 1924 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 12H
Vintage1938 | hydro | TRUE | 59178 | Brookfield Black Bear Hydro, LLC | 1469 | Ellsworth Hydro Station | ME | Hancock | EL02 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.8 | 2.1 | 2 | 0.5 | N |  |  | OP | X | 7 | 1938 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 12H
Vintage1938 | hydro | TRUE | 59178 | Brookfield Black Bear Hydro, LLC | 1469 | Ellsworth Hydro Station | ME | Hancock | EL03 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.8 | 2.1 | 2 | 0.5 | N |  |  | OP | X | 7 | 1938 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 12H
Vintage1924 | hydro | TRUE | 59178 | Brookfield Black Bear Hydro, LLC | 1469 | Ellsworth Hydro Station | ME | Hancock | EL04 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 2.5 | 2.4 | 1 | N |  |  | OP | X | 7 | 1924 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 12H
Vintage2011 | hydro | TRUE | 59178 | Brookfield Black Bear Hydro, LLC | 1475 | Milford Hydro Station | ME | Penobscot | MF01 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.9 | 0.7 | 0.7 | 0.2 | N |  |  | OP | X | 11 | 2011 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N |  | 1H
Vintage2011 | hydro | TRUE | 59178 | Brookfield Black Bear Hydro, LLC | 1475 | Milford Hydro Station | ME | Penobscot | MF02 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.9 | 0.7 | 0.7 | 0.2 | N |  |  | OP | X | 11 | 2011 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N |  | 1H
Vintage1956 | hydro | TRUE | 59178 | Brookfield Black Bear Hydro, LLC | 1475 | Milford Hydro Station | ME | Penobscot | MF03 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 1.2 | N |  |  | OP | X | 7 | 1956 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 1H
Vintage1946 | hydro | TRUE | 59178 | Brookfield Black Bear Hydro, LLC | 1475 | Milford Hydro Station | ME | Penobscot | MF04 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.8 | N |  |  | OP | X | 7 | 1946 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 1H
Vintage1941 | hydro | TRUE | 59178 | Brookfield Black Bear Hydro, LLC | 1475 | Milford Hydro Station | ME | Penobscot | MF05 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.7 | N |  |  | OP | X | 7 | 1941 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 1H
Vintage1942 | hydro | TRUE | 59178 | Brookfield Black Bear Hydro, LLC | 1475 | Milford Hydro Station | ME | Penobscot | MF06 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.7 | N |  |  | OP | X | 7 | 1942 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 1H
Vintage1913 | hydro | TRUE | 59178 | Brookfield Black Bear Hydro, LLC | 1478 | Stillwater Hydro Station | ME | Penobscot | SW01 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.5 | 0.5 | 0.2 | N |  |  | OP | X | 1 | 1913 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 1H
Vintage1913 | hydro | TRUE | 59178 | Brookfield Black Bear Hydro, LLC | 1478 | Stillwater Hydro Station | ME | Penobscot | SW02 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.5 | 0.5 | 0.2 | N |  |  | OP | X | 1 | 1913 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 1H
Vintage1916 | hydro | TRUE | 59178 | Brookfield Black Bear Hydro, LLC | 1478 | Stillwater Hydro Station | ME | Penobscot | SW03 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.5 | 0.5 | 0.2 | N |  |  | OP | X | 1 | 1916 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 1H
Vintage1929 | hydro | TRUE | 59178 | Brookfield Black Bear Hydro, LLC | 1478 | Stillwater Hydro Station | ME | Penobscot | SW04 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 1 | 1929 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 1H
Vintage1910 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1482 | Bonny Eagle | ME | York | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.9 | 1.5 | 1.5 | 0.1 | N |  |  | OP | X | 1 | 1910 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1910 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1482 | Bonny Eagle | ME | York | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.9 | 1.5 | 1.5 | 0.1 | N |  |  | OP | X | 1 | 1910 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1910 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1482 | Bonny Eagle | ME | York | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.9 | 1.5 | 1.5 | 0.1 | N |  |  | OP | X | 1 | 1910 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1910 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1482 | Bonny Eagle | ME | York | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.9 | 1.5 | 1.5 | 0.1 | N |  |  | OP | X | 1 | 1910 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1910 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1482 | Bonny Eagle | ME | York | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.9 | 1.5 | 1.5 | 0.1 | N |  |  | OP | X | 1 | 1910 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1910 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1482 | Bonny Eagle | ME | York | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.9 | 1.5 | 1.5 | 0.1 | N |  |  | OP | X | 1 | 1910 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1982 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1483 | Brunswick Hydro | ME | Cumberland | B1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 12.6 | 0.9 | 13 | 13 | 0.1 | N |  |  | OP | X | 3 | 1982 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1983 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1483 | Brunswick Hydro | ME | Cumberland | B2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.5 | 0.9 | 3.5 | 3.5 | 0.1 | N |  |  | OP | X | 4 | 1983 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1983 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1483 | Brunswick Hydro | ME | Cumberland | B3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.5 | 0.9 | 3.5 | 3.5 | 0.1 | N |  |  | OP | X | 4 | 1983 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1970 | petroleum | TRUE | 14876 | FPL Energy Cape LLC | 1484 | Cape Gas Turbine | ME | Cumberland | GT4 | Petroleum Liquids | GT |  | S | X | X |  |  | 17.5 | 0.85 | 16 | 20 | 2 | N |  |  | OP | X | 1 | 1970 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1970 | petroleum | TRUE | 14876 | FPL Energy Cape LLC | 1484 | Cape Gas Turbine | ME | Cumberland | GT5 | Petroleum Liquids | GT |  | S | X | X |  |  | 17.5 | 0.85 | 16 | 20 | 2 | N |  |  | OP | X | 1 | 1970 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1937 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1486 | Cataract Hydro | ME | York | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.6 | 0.8 | 8 | 8 | 0.5 | N |  |  | OP | X | 1 | 1937 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1903 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1488 | Deer Rips | ME | Androscoggin | DR1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 1 | 1903 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1903 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1488 | Deer Rips | ME | Androscoggin | DR2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 1 | 1903 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1906 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1488 | Deer Rips | ME | Androscoggin | DR3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.9 | 0.8 | 0.8 | 0.8 | 0.1 | N |  |  | OP | X | 1 | 1906 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1911 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1488 | Deer Rips | ME | Androscoggin | DR4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 1 | 1911 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1913 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1488 | Deer Rips | ME | Androscoggin | DR5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 1 | 1913 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1919 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1488 | Deer Rips | ME | Androscoggin | DR6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 0.8 | 1.7 | 1.7 | 0.1 | N |  |  | OP | X | 1 | 1919 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1924 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1488 | Deer Rips | ME | Androscoggin | DR7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.8 | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 1 | 1924 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1926 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1491 | Gulf Island | ME | Androscoggin | GI1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.4 | 0.8 | 7.2 | 7.2 | 0.5 | N |  |  | OP | X | 1 | 1926 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1926 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1491 | Gulf Island | ME | Androscoggin | GI2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.4 | 0.8 | 8.1 | 8.1 | 0.5 | N |  |  | OP | X | 1 | 1926 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1926 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1491 | Gulf Island | ME | Androscoggin | GI3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.4 | 0.8 | 7.9 | 7.9 | 0.5 | N |  |  | OP | X | 1 | 1926 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1954 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1492 | Harris Hydro | ME | Somerset | HA1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.9 | 16.8 | 16.8 | 2 | N |  |  | OP | X | 1 | 1954 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1954 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1492 | Harris Hydro | ME | Somerset | HA2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 30 | 0.9 | 35 | 34.9 | 15 | N |  |  | OP | X | 1 | 1954 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1955 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1492 | Harris Hydro | ME | Somerset | HA3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 30 | 0.9 | 34.2 | 34.2 | 15 | N |  |  | OP | X | 1 | 1955 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1955 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1492 | Harris Hydro | ME | Somerset | HA4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.4 | 0.9 | 1.4 | 1.4 | 0.1 | N |  |  | OP | X | 1 | 1955 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1917 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1493 | Hiram | ME | Cumberland | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.9 | 3.1 | 3.1 | 0.1 | N |  |  | OP | X | 1 | 1917 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1985 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1493 | Hiram | ME | Cumberland | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8.1 | 0.9 | 8.5 | 8.5 | 0.1 | N |  |  | OP | X | 1 | 1985 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1924 | hydro | TRUE | 56854 | Messalonskee Stream Hydro LLC | 1497 | Messalonskee 2 (Oakland) | ME | Kennebec | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.8 | 0.8 | 2.8 | 2.8 | 0.3 | N |  |  | OP | X | 1 | 1924 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1918 | hydro | TRUE | 56854 | Messalonskee Stream Hydro LLC | 1498 | Messalonskee 3 | ME | Kennebec | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.3 | N |  |  | OP | X | 1 | 1918 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1935 | hydro | TRUE | 56854 | Messalonskee Stream Hydro LLC | 1500 | Messalonskee 5 | ME | Kennebec | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.3 | N |  |  | OP | X | 1 | 1935 |  |  | N | IPP Non-CHP | 2 | X | WAT | [12 empty] | 1H | [23 empty] | N
Vintage1925 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1501 | North Gorham | ME | Cumberland | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.1 | 0.9 | 1 | 1 | 0.1 | N |  |  | OP | X | 1 | 1925 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1925 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1501 | North Gorham | ME | Cumberland | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.1 | 0.9 | 1 | 1 | 0.1 | N |  |  | OP | X | 1 | 1925 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1913 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1504 | Shawmut | ME | Somerset | SH1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.9 | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 1 | 1913 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage1913 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1504 | Shawmut | ME | Somerset | SH2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.9 | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 1 | 1913 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage1913 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1504 | Shawmut | ME | Somerset | SH3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.9 | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 1 | 1913 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage1913 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1504 | Shawmut | ME | Somerset | SH4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.9 | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 1 | 1913 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage1913 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1504 | Shawmut | ME | Somerset | SH5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.9 | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 1 | 1913 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage1921 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1504 | Shawmut | ME | Somerset | SH6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 1 | 1921 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage1982 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1504 | Shawmut | ME | Somerset | SH7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 0.9 | 1.9 | 1.9 | 0.1 | N |  |  | OP | X | 1 | 1982 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1982 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1504 | Shawmut | ME | Somerset | SH8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 0.9 | 1.9 | 1.9 | 0.1 | N |  |  | OP | X | 1 | 1982 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1948 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1505 | Skelton | ME | York | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8.4 | 0.9 | 10.8 | 10.8 | 0.5 | N |  |  | OP | X | 1 | 1948 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1948 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1505 | Skelton | ME | York | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8.4 | 0.9 | 10.8 | 10.8 | 0.5 | N |  |  | OP | X | 1 | 1948 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1957 | petroleum | TRUE | 31719 | FPL Energy Wyman LLC | 1507 | William F Wyman Hybrid | ME | Cumberland | 1 | Petroleum Liquids | ST |  | S | X | X |  |  | 50 | 0.85 | 50.1 | 49.5 | 10 | N |  |  | OP | X | 1 | 1957 |  |  | N | IPP Non-CHP | 2 | X | RFO | [5 empty] | DFO |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1958 | petroleum | TRUE | 31719 | FPL Energy Wyman LLC | 1507 | William F Wyman Hybrid | ME | Cumberland | 2 | Petroleum Liquids | ST |  | S | X | X |  |  | 50 | 0.85 | 47.8 | 52.8 | 10 | N |  |  | OP | X | 1 | 1958 |  |  | N | IPP Non-CHP | 2 | X | RFO | [5 empty] | DFO |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1965 | petroleum | TRUE | 31719 | FPL Energy Wyman LLC | 1507 | William F Wyman Hybrid | ME | Cumberland | 3 | Petroleum Liquids | ST |  | S | X | X |  |  | 113.6 | 0.85 | 110.9 | 113.8 | 30 | N |  |  | OP | X | 1 | 1965 |  |  | N | IPP Non-CHP | 2 | X | RFO | [5 empty] | DFO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1978 | petroleum | TRUE | 31719 | FPL Energy Wyman LLC | 1507 | William F Wyman Hybrid | ME | Cumberland | 4 | Petroleum Liquids | ST |  | J | X | X |  |  | 632.4 | 0.93 | 602.1 | 605.8 | 60 | N |  |  | OP | X | 1 | 1978 |  |  | N | IPP Non-CHP | 2 | X | RFO | [5 empty] | DFO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2016 | other | TRUE | 31719 | FPL Energy Wyman LLC | 1507 | William F Wyman Hybrid | ME | Cumberland | BESS | Batteries | BA |  | S | X | X |  |  | 16.7 |  | 16.2 | 16.2 | 0 | N |  |  | OP | X | 12 | 2016 |  |  | N | IPP Non-CHP | 2 | X | MWH | [12 empty] | 10M | [23 empty] | N |  | N
Vintage1982 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1508 | West Buxton | ME | York | WB1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.9 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 1 | 1982 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1982 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1508 | West Buxton | ME | York | WB2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.9 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 1 | 1982 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1920 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1508 | West Buxton | ME | York | WB3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.1 | 0.9 | 1.1 | 1.1 | 0.1 | N |  |  | OP | X | 1 | 1920 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1907 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1508 | West Buxton | ME | York | WB4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.9 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 1 | 1907 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1904 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1508 | West Buxton | ME | York | WB5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.9 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 1 | 1904 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1927 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1508 | West Buxton | ME | York | WB6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4 | 0.9 | 4 | 4 | 0.1 | N |  |  | OP | X | 1 | 1927 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage1921 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1509 | Weston Hydro | ME | Somerset | WE1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.8 | 3.3 | 3.3 | 0.1 | N |  |  | OP | X | 1 | 1921 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1920 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1509 | Weston Hydro | ME | Somerset | WE2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.8 | 3.3 | 3.3 | 0.1 | N |  |  | OP | X | 1 | 1920 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1921 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1509 | Weston Hydro | ME | Somerset | WE3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.8 | 3.3 | 3.3 | 0.1 | N |  |  | OP | X | 1 | 1921 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1923 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1509 | Weston Hydro | ME | Somerset | WE4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.8 | 3.3 | 3.3 | 0.1 | N |  |  | OP | X | 1 | 1923 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1939 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1510 | Williams Hydro | ME | Somerset | WI1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7 | 0.9 | 8.2 | 8.2 | 0.1 | N |  |  | OP | X | 1 | 1939 |  |  | N | IPP Non-CHP | 2 | X | WAT | [12 empty] | 10M
Vintage1950 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1510 | Williams Hydro | ME | Somerset | WI2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6 | 0.9 | 6.7 | 6.7 | 0.1 | N |  |  | OP | X | 1 | 1950 |  |  | N | IPP Non-CHP | 2 | X | WAT | [12 empty] | 10M
Vintage1930 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1511 | Wyman Hydro | ME | Somerset | WY1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 24 | 0.9 | 29.4 | 29.4 | 8 | N |  |  | OP | X | 1 | 1930 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1931 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1511 | Wyman Hydro | ME | Somerset | WY2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 24 | 1 | 29.9 | 29.9 | 23 | N |  |  | OP | X | 1 | 1931 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1940 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 1511 | Wyman Hydro | ME | Somerset | WY3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 24 | 0.9 | 29.2 | 29.2 | 8 | N |  |  | OP | X | 1 | 1940 |  |  | N | IPP Non-CHP | 2 | X | WAT | [11 empty] | 0 | 10M
Vintage1941 | hydro | TRUE | 14597 | Algonquin Northern Maine | 1516 | Squa Pan Hydro Station | ME | Aroostook | SP1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 0.8 | 1.4 | 1.4 | 1 | N |  |  | SB | Y | 12 | 1941 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1956 | petroleum | TRUE | 60422 | H.A. Wagner LLC | 1554 | Herbert A Wagner | MD | Anne Arundel | 1 | Petroleum Liquids | ST |  | S | X | X | 50689 | 50689 | 132.8 | 0.85 | 126 | 126 | 40 | N |  |  | OP | X | 2 | 1956 |  |  | N | IPP Non-CHP | 2 | X | RFO | NG |  |  |  |  | NG |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | Y | N | Y
Vintage1966 | hard coal | TRUE | 60422 | H.A. Wagner LLC | 1554 | Herbert A Wagner | MD | Anne Arundel | 3 | Conventional Steam Coal | ST |  | S | X | X | 50691 | 50691 | 359 | 0.9 | 305 | 305 | 105 | N |  |  | OP | X | 8 | 1966 |  |  | N | IPP Non-CHP | 2 | X | RC | BIT |  |  |  |  | NG |  |  |  | N | N |  | OVER |  | Y |  |  | N | Y | [14 empty] | N |  |  | N |  | N
Vintage1972 | petroleum | TRUE | 60422 | H.A. Wagner LLC | 1554 | Herbert A Wagner | MD | Anne Arundel | 4 | Petroleum Liquids | ST |  | S | X | X | 50692 | 50692 | 414.7 | 0.9 | 397 | 397 | 60 | N |  |  | OP | X | 8 | 1972 |  |  | N | IPP Non-CHP | 2 | X | RFO | [5 empty] | NG |  |  |  | N | N |  | OVER | [20 empty] | N |  |  | N |  | N
Vintage1967 | petroleum | TRUE | 60422 | H.A. Wagner LLC | 1554 | Herbert A Wagner | MD | Anne Arundel | GT1 | Petroleum Liquids | GT |  | S | X | X | 50688 | 50688 | 16 | 0.85 | 12.9 | 12.9 | 2 | N |  |  | OP | X | 8 | 1967 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N |  | N
Vintage1972 | petroleum | TRUE | 4161 | Constellation Power Source Gen | 1556 | Perryman | MD | Harford | GT1 | Petroleum Liquids | GT |  | S | X | X | PERRYMAN13 KVCT 1 | PERRYMAN13 KVCT 1 | 53.1 | 0.85 | 52 | 52 | 5 | N |  |  | OP | X | 1 | 1972 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1972 | petroleum | TRUE | 4161 | Constellation Power Source Gen | 1556 | Perryman | MD | Harford | GT3 | Petroleum Liquids | GT |  | S | X | X | PERRYMAN13 KVCT 3 | PERRYMAN13 KVCT 3 | 53.1 | 0.85 | 51 | 51 | 5 | N |  |  | OP | X | 4 | 1972 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1972 | petroleum | TRUE | 4161 | Constellation Power Source Gen | 1556 | Perryman | MD | Harford | GT4 | Petroleum Liquids | GT |  | S | X | X | PERRYMAN13 KVCT 4 | PERRYMAN13 KVCT 4 | 53.1 | 0.85 | 52 | 52 | 5 | N |  |  | OP | X | 4 | 1972 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1995 | natural gas peaker | TRUE | 4161 | Constellation Power Source Gen | 1556 | Perryman | MD | Harford | GT5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | PERRYMAN33 KVCT 51 | PERRYMAN33 KVCT 51 | 192 | 0.9 | 139 | 149 | 110 | N |  |  | OP | X | 6 | 1995 |  |  | N | IPP Non-CHP | 2 | X | NG | DFO | [8 empty] | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage2015 | natural gas peaker | TRUE | 4161 | Constellation Power Source Gen | 1556 | Perryman | MD | Harford | GT6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | PERRYMN613.8 KV PERYMAN6 | PERRYMN613.8 KV PERYMAN6 | 141 | 0.85 | 109.8 | 120 | 60 | N |  |  | OP | X | 6 | 2015 |  |  | N | IPP Non-CHP | 2 | X | NG | DFO | [9 empty] | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1970 | petroleum | TRUE | 4161 | Constellation Power Source Gen | 1557 | Philadelphia | MD | Baltimore City | GT1 | Petroleum Liquids | GT |  | S | X | X | PHILADRD4 KVCT 1 | PHILADRD4 KVCT 1 | 20.7 | 0.85 | 15.3 | 16 | 3 | N |  |  | OP | X | 8 | 1970 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1970 | petroleum | TRUE | 4161 | Constellation Power Source Gen | 1557 | Philadelphia | MD | Baltimore City | GT2 | Petroleum Liquids | GT |  | S | X | X | PHILADRD4 KVCT 2 | PHILADRD4 KVCT 2 | 20.7 | 0.85 | 16 | 16 | 3 | N |  |  | OP | X | 8 | 1970 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1970 | petroleum | TRUE | 4161 | Constellation Power Source Gen | 1557 | Philadelphia | MD | Baltimore City | GT3 | Petroleum Liquids | GT |  | S | X | X | PHILADRD4 KVCT 3 | PHILADRD4 KVCT 3 | 20.7 | 0.85 | 14.8 | 16 | 3 | N |  |  | OP | X | 9 | 1970 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1970 | petroleum | TRUE | 4161 | Constellation Power Source Gen | 1557 | Philadelphia | MD | Baltimore City | GT4 | Petroleum Liquids | GT |  | S | X | X | PHILADRD4 KVCT 4 | PHILADRD4 KVCT 4 | 20.7 | 0.85 | 14.8 | 16 | 3 | N |  |  | OP | X | 9 | 1970 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1968 | petroleum | TRUE | 56609 | Calpine Mid-Atlantic Generation LLC | 1563 | Crisfield | MD | Somerset | CRIS | Petroleum Liquids | IC |  | S | X | X | 50881 | 50881 | 2.9 | 0.8 | 2.6 | 2.6 | 2 | N |  |  | SB | Y | 5 | 1968 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N
Vintage1968 | petroleum | TRUE | 56609 | Calpine Mid-Atlantic Generation LLC | 1563 | Crisfield | MD | Somerset | CRS2 | Petroleum Liquids | IC |  | S | X | X | 50882 | 50882 | 2.9 | 0.8 | 2.6 | 2.6 | 2 | N |  |  | SB | Y | 5 | 1968 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N
Vintage1968 | petroleum | TRUE | 56609 | Calpine Mid-Atlantic Generation LLC | 1563 | Crisfield | MD | Somerset | CRS3 | Petroleum Liquids | IC |  | S | X | X | 50883 | 50883 | 2.9 | 0.8 | 2.6 | 2.6 | 2 | N |  |  | SB | Y | 5 | 1968 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N
Vintage1968 | petroleum | TRUE | 56609 | Calpine Mid-Atlantic Generation LLC | 1563 | Crisfield | MD | Somerset | CRS4 | Petroleum Liquids | IC |  | S | X | X | 50884 | 50884 | 2.9 | 0.8 | 2.6 | 2.6 | 2 | N |  |  | SB | Y | 5 | 1968 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N | N
Vintage1968 | petroleum | TRUE | 19830 | NRG Vienna Operations Inc | 1564 | Vienna Operations | MD | Dorchester | 10 | Petroleum Liquids | GT |  | W | X | X |  |  | 18.6 | 0.85 | 14.3 | 14.3 | 14 | N |  |  | OP | X | 1 | 1968 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1972 | petroleum | TRUE | 19830 | NRG Vienna Operations Inc | 1564 | Vienna Operations | MD | Dorchester | 8 | Petroleum Liquids | ST |  | W | X | X |  |  | 162 | 0.9 | 153 | 153 | 55 | N |  |  | OP | X | 1 | 1972 |  |  | N | IPP Non-CHP | 2 | X | RFO | DFO |  |  |  |  | DFO |  |  |  | N | N |  | OVER |  |  |  |  | N | [15 empty] | N |  |  | N | N | N
Vintage1925 | hydro | TRUE | 54679 | BP Piney & Deep Creek LLC | 1567 | Deep Creek | MD | Garrett | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 0.8 | 9 | 9 | 5 | N |  |  | OP | X | 7 | 1925 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1925 | hydro | TRUE | 54679 | BP Piney & Deep Creek LLC | 1567 | Deep Creek | MD | Garrett | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 0.8 | 9 | 9 | 5 | N |  |  | OP | X | 7 | 1925 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N |  |  | 10M
Vintage1975 | natural gas steam turbine | TRUE | 12653 | Lanyard Power Holdings, LLC | 1571 | Chalk Point Power | MD | Prince Georges | 3 | Natural Gas Steam Turbine | ST |  | W | X | X | 50817 | CHALKPT 24 KV CHLKG3 | 659 | 0.9 | 595 | 614 | 582 | N |  |  | OP | X | 5 | 1975 |  |  | N | IPP Non-CHP | 2 | X | NG | DFO |  |  |  |  | NG | DFO |  |  | N |  |  | OVER | [23 empty] | N | N | N
Vintage1981 | natural gas steam turbine | TRUE | 12653 | Lanyard Power Holdings, LLC | 1571 | Chalk Point Power | MD | Prince Georges | 4 | Natural Gas Steam Turbine | ST |  | W | X | X | 50818 | CHALKPT 24 KV CHLKG4 | 659 | 0.9 | 585.3 | 598.2 | 582 | N |  |  | OP | X | 12 | 1981 |  |  | N | IPP Non-CHP | 2 | X | NG | DFO |  |  |  |  | NG | DFO |  |  | N |  |  | OVER | [23 empty] | N | N | N
Vintage1974 | petroleum | TRUE | 12653 | Lanyard Power Holdings, LLC | 1571 | Chalk Point Power | MD | Prince Georges | GT2 | Petroleum Liquids | GT |  | W | X | X | 50810 | CHALKPT 13 KV CT2 | 35 | 0.9 | 24 | 26 | 5 | N |  |  | OP | X | 6 | 1974 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N |  |  | 1H | [23 empty] | N
Vintage1991 | natural gas peaker | TRUE | 12653 | Lanyard Power Holdings, LLC | 1571 | Chalk Point Power | MD | Prince Georges | GT3 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X | 50811 | CHALKPT 13 KV CT3 | 103 | 0.85 | 86 | 100 | 33 | N |  |  | OP | X | 6 | 1991 |  |  | N | IPP Non-CHP | 2 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1991 | natural gas peaker | TRUE | 12653 | Lanyard Power Holdings, LLC | 1571 | Chalk Point Power | MD | Prince Georges | GT4 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X | 50812 | CHALKPT 13 KV CT4 | 103 | 0.85 | 86 | 100 | 33 | N |  |  | OP | X | 6 | 1991 |  |  | N | IPP Non-CHP | 2 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1991 | natural gas peaker | TRUE | 12653 | Lanyard Power Holdings, LLC | 1571 | Chalk Point Power | MD | Prince Georges | GT5 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X | 50813 | CHALKPT 13 KV CT5 | 125 | 0.9 | 109 | 123 | 65 | N |  |  | OP | X | 6 | 1991 |  |  | N | IPP Non-CHP | 2 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1991 | natural gas peaker | TRUE | 12653 | Lanyard Power Holdings, LLC | 1571 | Chalk Point Power | MD | Prince Georges | GT6 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X | 50814 | CHALKPT 13 KV CT6 | 125 | 0.9 | 109 | 126 | 65 | N |  |  | OP | X | 6 | 1991 |  |  | N | IPP Non-CHP | 2 | X | NG | DFO | [8 empty] | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1967 | petroleum | TRUE | 12653 | Lanyard Power Holdings, LLC | 1572 | Dickerson Power | MD | Montgomery | GT1 | Petroleum Liquids | GT |  | W | X | X | 50819 | DICKERSH 13 KV HCT1 | 19 | 0.85 | 18 | 18 | 18 | N |  |  | OP | X | 3 | 1967 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N | N | N
Vintage1992 | natural gas peaker | TRUE | 12653 | Lanyard Power Holdings, LLC | 1572 | Dickerson Power | MD | Montgomery | GT2 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X | 50823 | DICKERSH 13 KV HCT2 | 163 | 0.9 | 147 | 167 | 40 | N |  |  | OP | X | 6 | 1992 |  |  | N | IPP Non-CHP | 2 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1992 | natural gas peaker | TRUE | 12653 | Lanyard Power Holdings, LLC | 1572 | Dickerson Power | MD | Montgomery | GT3 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X | 50824 | DICKERSHO4 KV STADC1 | 163 | 0.9 | 147 | 167 | 40 | N |  |  | OP | X | 6 | 1992 |  |  | N | IPP Non-CHP | 2 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1973 | petroleum | TRUE | 12653 | Lanyard Power Holdings, LLC | 1573 | Morgantown Generating Plant | MD | Charles | 3 | Petroleum Liquids | GT |  | S | X | X | 50828 | MORGANTO 13KV CT3 | 65 | 0.9 | 54 | 59 | 20 | N |  |  | OP | X | 6 | 1973 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1973 | petroleum | TRUE | 12653 | Lanyard Power Holdings, LLC | 1573 | Morgantown Generating Plant | MD | Charles | 4 | Petroleum Liquids | GT |  | S | X | X | 50829 | MORGANTO 13KV CT4 | 65 | 0.9 | 54 | 59 | 20 | N |  |  | OP | X | 6 | 1973 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1973 | petroleum | TRUE | 12653 | Lanyard Power Holdings, LLC | 1573 | Morgantown Generating Plant | MD | Charles | 5 | Petroleum Liquids | GT |  | S | X | X | 50830 | MORGANTO 13KV CT5 | 65 | 0.9 | 54 | 59 | 20 | N |  |  | OP | X | 5 | 1973 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1973 | petroleum | TRUE | 12653 | Lanyard Power Holdings, LLC | 1573 | Morgantown Generating Plant | MD | Charles | 6 | Petroleum Liquids | GT |  | S | X | X | 50831 | MORGANTO 13KV CT6 | 65 | 0.9 | 54 | 59 | 20 | N |  |  | OP | X | 5 | 1973 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1970 | petroleum | TRUE | 12653 | Lanyard Power Holdings, LLC | 1573 | Morgantown Generating Plant | MD | Charles | GT1 | Petroleum Liquids | GT |  | S | X | X | 50832 | MORGANTO13KV UNITC1 | 18 | 0.8 | 13 | 17 | 7 | N |  |  | OP | X | 12 | 1970 | 9 | 2022 | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1971 | petroleum | TRUE | 12653 | Lanyard Power Holdings, LLC | 1573 | Morgantown Generating Plant | MD | Charles | GT2 | Petroleum Liquids | GT |  | S | X | X | 50833 | MORGANTO13KV UNITC2 | 18 | 0.8 | 13 | 17 | 7 | N |  |  | OP | X | 2 | 1971 | 9 | 2022 | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1970 | hard coal | TRUE | 12653 | Lanyard Power Holdings, LLC | 1573 | Morgantown Generating Plant | MD | Charles | ST1 | Conventional Steam Coal | ST |  | S | X | X |  | MORGANTO23 KV UNIT01 | 626 | 0.9 | 596 | 596 | 197 | N |  |  | OP | X | 6 | 1970 | 6 | 2022 | N | IPP Non-CHP | 2 | X | BIT | [5 empty] | DFO |  |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [14 empty] | N |  |  | N | N | N
Vintage1971 | hard coal | TRUE | 12653 | Lanyard Power Holdings, LLC | 1573 | Morgantown Generating Plant | MD | Charles | ST2 | Conventional Steam Coal | ST |  | S | X | X |  | MORGANTO23 KV UNIT02 | 626 | 0.9 | 609 | 609 | 203 | N |  |  | OP | X | 6 | 1971 | 6 | 2022 | N | IPP Non-CHP | 2 | X | BIT | [5 empty] | DFO |  |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [14 empty] | N |  |  | N | N | N
Vintage1928 | hydro | TRUE | 6035 | Exelon Power | 1574 | Conowingo | MD | Harford | 1 | Conventional Hydroelectric | HY |  | S | X | X | CONOWING13 KV GEN1 | CONOWING13 KV GEN1 | 45 | 0.9 | 48 | 48 | 5 | N |  |  | OP | X | 3 | 1928 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1964 | hydro | TRUE | 6035 | Exelon Power | 1574 | Conowingo | MD | Harford | 10 | Conventional Hydroelectric | HY |  | S | X | X | CONOWING13 KV G10 | CONOWING13 KV G10 | 55.6 | 0.9 | 65 | 65 | 30 | N |  |  | OP | X | 5 | 1964 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1964 | hydro | TRUE | 6035 | Exelon Power | 1574 | Conowingo | MD | Harford | 11 | Conventional Hydroelectric | HY |  | S | X | X | CONOWING13 KV G11 | CONOWING13 KV G11 | 55.6 | 0.9 | 65 | 65 | 30 | N |  |  | OP | X | 5 | 1964 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1928 | hydro | TRUE | 6035 | Exelon Power | 1574 | Conowingo | MD | Harford | 2 | Conventional Hydroelectric | HY |  | S | X | X | CONOWING13 KV GEN2 | CONOWING13 KV GEN2 | 36 | 0.9 | 36 | 36 | 5 | N |  |  | OP | X | 3 | 1928 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1928 | hydro | TRUE | 6035 | Exelon Power | 1574 | Conowingo | MD | Harford | 3 | Conventional Hydroelectric | HY |  | S | X | X | CONOWING13 KV GEN3 | CONOWING13 KV GEN3 | 48 | 0.9 | 48 | 48 | 5 | N |  |  | OP | X | 3 | 1928 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1928 | hydro | TRUE | 6035 | Exelon Power | 1574 | Conowingo | MD | Harford | 4 | Conventional Hydroelectric | HY |  | S | X | X | CONOWING13 KV GEN4 | CONOWING13 KV GEN4 | 47.7 | 0.9 | 48 | 48 | 5 | N |  |  | OP | X | 4 | 1928 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1928 | hydro | TRUE | 6035 | Exelon Power | 1574 | Conowingo | MD | Harford | 5 | Conventional Hydroelectric | HY |  | S | X | X | CONOWING13 KV GEN5 | CONOWING13 KV GEN5 | 36 | 0.9 | 36 | 36 | 5 | N |  |  | OP | X | 6 | 1928 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1928 | hydro | TRUE | 6035 | Exelon Power | 1574 | Conowingo | MD | Harford | 6 | Conventional Hydroelectric | HY |  | S | X | X | CONOWING13 KV GEN6 | CONOWING13 KV GEN6 | 47.7 | 0.9 | 48 | 48 | 5 | N |  |  | OP | X | 7 | 1928 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1928 | hydro | TRUE | 6035 | Exelon Power | 1574 | Conowingo | MD | Harford | 7 | Conventional Hydroelectric | HY |  | S | X | X | CONOWING13 KV UNIT07 | CONOWING13 KV UNIT07 | 48 | 0.9 | 48 | 48 | 5 | N |  |  | OP | X | 6 | 1928 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1964 | hydro | TRUE | 6035 | Exelon Power | 1574 | Conowingo | MD | Harford | 8 | Conventional Hydroelectric | HY |  | S | X | X | CONOWING13 KV GEN8 | CONOWING13 KV GEN8 | 55.6 | 0.9 | 65 | 65 | 30 | N |  |  | OP | X | 3 | 1964 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1964 | hydro | TRUE | 6035 | Exelon Power | 1574 | Conowingo | MD | Harford | 9 | Conventional Hydroelectric | HY |  | S | X | X | CONOWING13 KV GEN9 | CONOWING13 KV GEN9 | 55.6 | 0.9 | 65 | 65 | 30 | N |  |  | OP | X | 3 | 1964 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1966 | petroleum | TRUE | 5625 | Easton Utilities Comm | 1580 | Easton | MD | Talbot | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.5 | 0.8 | 3.5 | 3.5 | 0 | N |  |  | OP | X | 5 | 1966 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1995 | petroleum | TRUE | 5625 | Easton Utilities Comm | 1580 | Easton | MD | Talbot | 101 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0 | N |  |  | OP | X | 12 | 1995 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1995 | petroleum | TRUE | 5625 | Easton Utilities Comm | 1580 | Easton | MD | Talbot | 102 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0 | N |  |  | OP | X | 12 | 1995 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1968 | petroleum | TRUE | 5625 | Easton Utilities Comm | 1580 | Easton | MD | Talbot | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.8 | 0.8 | 3.6 | 3.6 | 0 | N |  |  | OP | X | 6 | 1968 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1970 | petroleum | TRUE | 5625 | Easton Utilities Comm | 1580 | Easton | MD | Talbot | 12 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.1 | 0.8 | 4.1 | 4.1 | 0 | N |  |  | OP | X | 7 | 1970 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1973 | petroleum | TRUE | 5625 | Easton Utilities Comm | 1580 | Easton | MD | Talbot | 13 | Petroleum Liquids | IC |  | S | X | X |  |  | 5.6 | 0.8 | 5.6 | 5.6 | 0 | N |  |  | OP | X | 7 | 1973 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1973 | petroleum | TRUE | 5625 | Easton Utilities Comm | 1580 | Easton | MD | Talbot | 14 | Petroleum Liquids | IC |  | S | X | X |  |  | 5.6 | 0.8 | 5.6 | 5.6 | 0 | N |  |  | OP | X | 7 | 1973 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1954 | petroleum | TRUE | 5625 | Easton Utilities Comm | 1580 | Easton | MD | Talbot | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2 | 2 | 0 | N |  |  | OP | X | 11 | 1954 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1957 | petroleum | TRUE | 5625 | Easton Utilities Comm | 1580 | Easton | MD | Talbot | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2 | 2 | 0 | N |  |  | OP | X | 5 | 1957 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1961 | petroleum | TRUE | 5625 | Easton Utilities Comm | 1580 | Easton | MD | Talbot | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.8 | 2.5 | 2.5 | 0 | N |  |  | OP | X | 12 | 1961 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1970 | petroleum | TRUE | 6035 | Exelon Power | 1586 | Exelon Framingham LLC | MA | Norfolk | GT1 | Petroleum Liquids | GT |  | S | X | X | UN.FRAMNGHM13.8FMJ1 | UN.FRAMNGHM13.8FMJ1 | 14.2 | 0.85 | 10.1 | 14.2 | 5 | N |  |  | OP | X | 3 | 1970 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1969 | petroleum | TRUE | 6035 | Exelon Power | 1586 | Exelon Framingham LLC | MA | Norfolk | GT2 | Petroleum Liquids | GT |  | S | X | X | UN.FRAMNGHM13.8FMJ2 | UN.FRAMNGHM13.8FMJ2 | 14.2 | 0.85 | 10 | 14.7 | 5 | N |  |  | OP | X | 9 | 1969 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1969 | petroleum | TRUE | 6035 | Exelon Power | 1586 | Exelon Framingham LLC | MA | Norfolk | GT3 | Petroleum Liquids | GT |  | S | X | X | UN.FRAMNGHM13.8FMJ3 | UN.FRAMNGHM13.8FMJ3 | 14.2 | 0.85 | 11.3 | 15.3 | 5 | N |  |  | OP | X | 9 | 1969 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage2003 | natural gas combined cycle | TRUE | 49965 | Constellation Mystic Power LLC | 1588 | Mystic Generating Station | MA | Middlesex | GT81 | Natural Gas Fired Combined Cycle | CT | G941 | S | X | N | UN MYSTIC 18 1MYS8 | UN MYSTIC 18 1MYS8 | 278.6 | 0.85 | 228.8 | 268.4 | 140 | N |  |  | OP | X | 4 | 2003 | 6 | 2024 | N | IPP Non-CHP | 2 | X | NG | [9 empty] | N | N | 0 | 12H | [20 empty] | N |  |  | N | N | N
Vintage2003 | natural gas combined cycle | TRUE | 49965 | Constellation Mystic Power LLC | 1588 | Mystic Generating Station | MA | Middlesex | GT82 | Natural Gas Fired Combined Cycle | CT | G941 | S | X | N | UN MYSTIC 18 1NYS8 | UN MYSTIC 18 1MYS8 | 278.6 | 0.85 | 230 | 271 | 140 | N |  |  | OP | X | 4 | 2003 | 6 | 2024 | N | IPP Non-CHP | 2 | X | NG | [9 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N
Vintage2003 | natural gas combined cycle | TRUE | 49965 | Constellation Mystic Power LLC | 1588 | Mystic Generating Station | MA | Middlesex | GT93 | Natural Gas Fired Combined Cycle | CT | G942 | S | X | N | UN MYSTIC 18 1MYS9 | UN MYSTIC 18 1MYS9 | 278.6 | 0.85 | 229.9 | 275.8 | 140 | N |  |  | OP | X | 6 | 2003 | 6 | 2024 | N | IPP Non-CHP | 2 | X | NG | [9 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N
Vintage2003 | natural gas combined cycle | TRUE | 49965 | Constellation Mystic Power LLC | 1588 | Mystic Generating Station | MA | Middlesex | GT94 | Natural Gas Fired Combined Cycle | CT | G942 | S | X | N | UN MYSTIC 18 1MYS9 | UN MYSTIC 18 1MYS9 | 278.6 | 0.85 | 229.6 | 275.4 | 140 | N |  |  | OP | X | 6 | 2003 | 6 | 2024 | N | IPP Non-CHP | 2 | X | NG | [9 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N
Vintage2003 | natural gas combined cycle | TRUE | 49965 | Constellation Mystic Power LLC | 1588 | Mystic Generating Station | MA | Middlesex | ST85 | Natural Gas Fired Combined Cycle | CA | G941 | S | Y | X | UN MYSTIC 18 1MYS8 | UN MYSTIC 18 1MYS8 | 315 | 0.85 | 244.6 | 301.2 | 75 | N |  |  | OP | X | 4 | 2003 | 6 | 2024 | N | IPP Non-CHP | 2 | X | NG | [9 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N
Vintage2003 | natural gas combined cycle | TRUE | 49965 | Constellation Mystic Power LLC | 1588 | Mystic Generating Station | MA | Middlesex | ST96 | Natural Gas Fired Combined Cycle | CA | G942 | S | Y | X | UN MYSTIC 18 1MYS9 | UN MYSTIC 18 1MYS9 | 315 | 0.85 | 250.7 | 300.8 | 75 | N |  |  | OP | X | 6 | 2003 | 6 | 2024 | N | IPP Non-CHP | 2 | X | NG | [9 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N
Vintage1970 | petroleum | TRUE | 6035 | Exelon Power | 1592 | Exelon Medway LLC | MA | Norfolk | GT1 | Petroleum Liquids | GT |  | S | X | X | UN.W_MEDWAY13.8WMJ1 | UN.W_MEDWAY13.8WMJ1 | 45 | 0.85 | 42 | 64 | 20 | N |  |  | OP | X | 7 | 1970 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1971 | petroleum | TRUE | 6035 | Exelon Power | 1592 | Exelon Medway LLC | MA | Norfolk | GT2 | Petroleum Liquids | GT |  | S | X | X | UN.W_MEDWAY13.8WMJ2 | UN.W_MEDWAY13.8WMJ2 | 45 | 0.85 | 39.8 | 61.6 | 20 | N |  |  | OP | X | 3 | 1971 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1970 | petroleum | TRUE | 6035 | Exelon Power | 1592 | Exelon Medway LLC | MA | Norfolk | GT3 | Petroleum Liquids | GT |  | S | X | X | UN.MEDWAYJ313.8WMJ3 | UN.MEDWAYJ313.8WMJ3 | 45 | 0.85 | 42 | 62.4 | 20 | N |  |  | OP | X | 7 | 1970 |  |  | N | IPP Non-CHP | 2 | X | DFO | [9 empty] | N | N | 0 | 1H | [20 empty] | N |  |  | N
Vintage1958 | natural gas combined cycle | TRUE | 59528 | Kendall Green Energy, LLC | 1595 | Kendall Square Station | MA | Middlesex | 3 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | 10349 | 10349 | 27.2 | 0.8 | 22.9 | 22.9 | 14 | N |  |  | OP | X | 8 | 1958 |  |  | Y | IPP CHP | 3 | T | NG | [9 empty] | N | N |  | 12H | [23 empty] | N
Vintage2002 | natural gas combined cycle | TRUE | 59528 | Kendall Green Energy, LLC | 1595 | Kendall Square Station | MA | Middlesex | GEN4 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | 1672 | 1672 | 186.2 | 0.85 | 183.1 | 187.4 | 90 | N |  |  | OP | X | 12 | 2002 |  |  | Y | IPP CHP | 3 | T | NG | DFO | [8 empty] | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1970 | petroleum | TRUE | 59528 | Kendall Green Energy, LLC | 1595 | Kendall Square Station | MA | Middlesex | JET1 | Petroleum Liquids | GT |  | S | X | X | 452 | 452 | 21.3 | 0.85 | 18 | 23 | 14 | N |  |  | OP | X | 9 | 1970 |  |  | N | IPP CHP | 3 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1969 | petroleum | TRUE | 64488 | Vineyard Reliability LLC | 1597 | Oak Bluffs Diesel Generating Facility | MA | Dukes | UN1 | Petroleum Liquids | IC |  | S | X | X | 1030 | 1030 | 2.7 | 0.8 | 2.8 | 2.8 | 2 | N |  |  | OP | X | 1 | 1969 |  |  | N | IPP Non-CHP | 2 | X | DFO | [10 empty] | N |  | 1H | [23 empty] | N
Vintage1969 | petroleum | TRUE | 64488 | Vineyard Reliability LLC | 1597 | Oak Bluffs Diesel Generating Facility | MA | Dukes | UN2 | Petroleum Liquids | IC |  | S | X | X | 1030 | 1030 | 2.7 | 0.8 | 2.8 | 2.8 | 2 | N |  |  | OP | X | 1 | 1969 |  |  | N | IPP Non-CHP | 2 | X | DFO | [10 empty] | N |  | 1H | [23 empty] | N
Vintage1972 | petroleum | TRUE | 64488 | Vineyard Reliability LLC | 1597 | Oak Bluffs Diesel Generating Facility | MA | Dukes | UN3 | Petroleum Liquids | IC |  | S | X | X | 1030 | 1030 | 2.7 | 0.8 | 2.8 | 2.8 | 2 | N |  |  | OP | X | 1 | 1972 |  |  | N | IPP Non-CHP | 2 | X | DFO | [10 empty] | N |  | 1H | [23 empty] | N
Vintage1968 | petroleum | TRUE | 61708 | NRG Canal 3 Development LLC | 1599 | Canal | MA | Barnstable | 1 | Petroleum Liquids | ST |  | W | X | X | 365 | UN.CANAL 18.0CAN1 | 585 | 0.925 | 560 | 567 | 200 | N |  |  | OP | X | 6 | 1968 |  |  | N | IPP Non-CHP | 2 | X | RFO | DFO |  |  |  |  | DFO |  |  |  | N | N |  | OVER | [23 empty] | N
Vintage1976 | petroleum | TRUE | 61708 | NRG Canal 3 Development LLC | 1599 | Canal | MA | Barnstable | 2 | Petroleum Liquids | ST |  | W | X | X | 366 | UN.CANAL 18.0CAN2 | 580 | 0.95 | 558.8 | 562 | 170 | N |  |  | OP | X | 1 | 1976 |  |  | N | IPP Non-CHP | 2 | X | RFO | NG | DFO |  |  |  | NG | DFO |  |  | N | N |  | OVER | [23 empty] | Y | Y | Y
Vintage2019 | natural gas peaker | TRUE | 61708 | NRG Canal 3 Development LLC | 1599 | Canal | MA | Barnstable | 3 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X | 38310 | UN.CANAL 25 CAN3 | 330 | 0.85 | 330 | 367.7 | 103 | N |  |  | OP | X | 6 | 2019 |  |  | N | IPP Non-CHP | 2 | X | NG | DFO |  |  |  |  | NG |  |  |  | N | N | 0 | 1H | [23 empty] | Y | N | Y
Vintage1921 | hydro | TRUE | 8776 | City of Holyoke Gas and Electric Dept. | 1603 | Boatlock | MA | Hampden | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.9 | 0.7 | 0.7 | 0.3 | N |  |  | OP | X | 1 | 1921 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 10M
Vintage1924 | hydro | TRUE | 8776 | City of Holyoke Gas and Electric Dept. | 1603 | Boatlock | MA | Hampden | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.8 | 1.5 | 1.5 | 0.8 | N |  |  | OP | X | 1 | 1924 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 10M
Vintage1924 | hydro | TRUE | 8776 | City of Holyoke Gas and Electric Dept. | 1603 | Boatlock | MA | Hampden | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 0.8 | N |  |  | OP | X | 1 | 1924 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N | N | 0 | 10M
Vintage1935 | hydro | TRUE | 8776 | City of Holyoke Gas and Electric Dept. | 1604 | Chemical | MA | Hampden | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 1 | 1935 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage1935 | hydro | TRUE | 8776 | City of Holyoke Gas and Electric Dept. | 1604 | Chemical | MA | Hampden | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 1 | 1935 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage1952 | hydro | TRUE | 8776 | City of Holyoke Gas and Electric Dept. | 1605 | Hadley Falls | MA | Hampden | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 17.6 | 0.8 | 18.1 | 18.1 | 5 | N |  |  | OP | X | 1 | 1952 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage1983 | hydro | TRUE | 8776 | City of Holyoke Gas and Electric Dept. | 1605 | Hadley Falls | MA | Hampden | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15.8 | 0.9 | 15 | 15 | 10 | N |  |  | OP | X | 11 | 1983 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage1906 | hydro | TRUE | 8776 | City of Holyoke Gas and Electric Dept. | 1607 | Riverside Holyoke | MA | Hampden | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.4 | N |  |  | OP | X | 1 | 1906 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage1906 | hydro | TRUE | 8776 | City of Holyoke Gas and Electric Dept. | 1607 | Riverside Holyoke | MA | Hampden | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.4 | N |  |  | OP | X | 1 | 1906 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage1922 | hydro | TRUE | 8776 | City of Holyoke Gas and Electric Dept. | 1607 | Riverside Holyoke | MA | Hampden | 7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.9 | N |  |  | OP | X | 1 | 1922 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage1931 | hydro | TRUE | 8776 | City of Holyoke Gas and Electric Dept. | 1607 | Riverside Holyoke | MA | Hampden | 8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4 | 0.8 | 4 | 4 | 2.7 | N |  |  | OP | X | 1 | 1931 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage2019 | petroleum | TRUE | 13206 | Nantucket Electric Co | 1615 | Nantucket Hybrid | MA | Nantucket | 18 | Petroleum Liquids | GT |  | W | X | X |  |  | 15.4 | 0.8 | 13.5 | 15.4 | 7.3 | N |  |  | OP | X | 8 | 2019 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N |  | N
Vintage2019 | petroleum | TRUE | 13206 | Nantucket Electric Co | 1615 | Nantucket Hybrid | MA | Nantucket | 19 | Petroleum Liquids | IC |  | W | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.1 | N |  |  | OP | X | 8 | 2019 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N |  | N
Vintage2019 | other | TRUE | 13206 | Nantucket Electric Co | 1615 | Nantucket Hybrid | MA | Nantucket | 20 | Batteries | BA |  | W | X | X |  |  | 6 |  | 6 | 6 | 0.1 | N |  |  | OP | X | 7 | 2019 |  |  | N | Electric Utility | 1 | X | MWH | [9 empty] | N | N |  | 10M | [23 empty] | N |  | N
Vintage1974 | hydro | TRUE | 61122 | Great River Hydro, LLC | 1620 | Deerfield 5 | MA | Berkshire | GEN1 | Conventional Hydroelectric | HY |  | S | X | X | 393 |  | 17.5 | 0.9 | 13.9 | 13.9 | 6.5 | N |  |  | OP | X | 10 | 1974 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 10M | [23 empty] | N
Vintage1915 | hydro | TRUE | 58185 | FirstLight Power Resources, Inc. - MA | 1629 | Cabot | MA | Franklin | 1 | Conventional Hydroelectric | HY |  | S | X | X | N.MONTAGUE13.8 CABT | N.MONTAGUE13.8 CABT | 10.3 | 0.8 | 10.3 | 10.3 | 3 | N |  |  | OP | X | 1 | 1915 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1915 | hydro | TRUE | 58185 | FirstLight Power Resources, Inc. - MA | 1629 | Cabot | MA | Franklin | 2 | Conventional Hydroelectric | HY |  | S | X | X | N.MONTAGUE13.8 CABT | N.MONTAGUE13.8 CABT | 10.3 | 0.8 | 10.3 | 10.3 | 3 | N |  |  | OP | X | 1 | 1915 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1916 | hydro | TRUE | 58185 | FirstLight Power Resources, Inc. - MA | 1629 | Cabot | MA | Franklin | 3 | Conventional Hydroelectric | HY |  | S | X | X | N.MONTAGUE13.8 CABT | N.MONTAGUE13.8 CABT | 10.3 | 0.8 | 10.3 | 10.3 | 3 | N |  |  | OP | X | 1 | 1916 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1916 | hydro | TRUE | 58185 | FirstLight Power Resources, Inc. - MA | 1629 | Cabot | MA | Franklin | 4 | Conventional Hydroelectric | HY |  | S | X | X | N.MONTAGUE13.8 CABT | N.MONTAGUE13.8 CABT | 10.3 | 0.8 | 10.3 | 10.3 | 3 | N |  |  | OP | X | 1 | 1916 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1917 | hydro | TRUE | 58185 | FirstLight Power Resources, Inc. - MA | 1629 | Cabot | MA | Franklin | 5 | Conventional Hydroelectric | HY |  | S | X | X | N.MONTAGUE13.8 CABT | N.MONTAGUE13.8 CABT | 10.3 | 0.8 | 10.3 | 10.3 | 9 | N |  |  | OP | X | 1 | 1917 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1917 | hydro | TRUE | 58185 | FirstLight Power Resources, Inc. - MA | 1629 | Cabot | MA | Franklin | 6 | Conventional Hydroelectric | HY |  | S | X | X | MONTAGUE13.8 CABT | MONTAGUE13.8 CABT | 10.3 | 0.8 | 10.3 | 10.3 | 9 | N |  |  | OP | X | 1 | 1917 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 1H | [23 empty] | N
Vintage1930 | hydro | TRUE | 8776 | City of Holyoke Gas and Electric Dept. | 1630 | Cobble Mountain | MA | Hampden | 1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 13 | 0.8 | 12.9 | 13 | 3 | N |  |  | OP | X | 1 | 1930 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1930 | hydro | TRUE | 8776 | City of Holyoke Gas and Electric Dept. | 1630 | Cobble Mountain | MA | Hampden | 2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 7 | 0.8 | 6.8 | 6.9 | 1 | N |  |  | OP | X | 1 | 1930 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1930 | hydro | TRUE | 8776 | City of Holyoke Gas and Electric Dept. | 1630 | Cobble Mountain | MA | Hampden | 3 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 13 | 0.8 | 12.9 | 13 | 3 | N |  |  | OP | X | 1 | 1930 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1969 | other | TRUE | 56401 | NAEA Energy Massachusetts LLC | 1631 | Doreen | MA | Berkshire | DORE | Petroleum Liquids | GT |  | S | X | X |  |  | 21.1 | 0.85 | 16.1 | 20.7 | 15 | N |  |  | OP | X | 7 | 1969 |  |  | N | IPP Non-CHP | 2 | X | KER | [9 empty] | N | N |  | 10M | [23 empty] | N | N | N
Vintage1964 | hydro | TRUE | 61350 | Central Rivers Power MA, LLC | 1634 | Gardners Falls | MA | Franklin | GF2 | Conventional Hydroelectric | HY |  | S | X | X | 851 |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.4 | N |  |  | OA | X | 1 | 1964 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 1H
Vintage1914 | hydro | TRUE | 61350 | Central Rivers Power MA, LLC | 1634 | Gardners Falls | MA | Franklin | GF3 | Conventional Hydroelectric | HY |  | S | X | X | 851 |  | 0.9 | 0.8 | 0.9 | 0.9 | 0.8 | N |  |  | OP | X | 1 | 1914 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 1H
Vintage1914 | hydro | TRUE | 61350 | Central Rivers Power MA, LLC | 1634 | Gardners Falls | MA | Franklin | GF4 | Conventional Hydroelectric | HY |  | S | X | X | 851 |  | 0.9 | 0.8 | 0.9 | 0.9 | 0.8 | N |  |  | OP | X | 1 | 1914 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 1H
Vintage1925 | hydro | TRUE | 61350 | Central Rivers Power MA, LLC | 1634 | Gardners Falls | MA | Franklin | GF5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 1 | N |  |  | OP | X | 1 | 1925 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 1H
Vintage1918 | hydro | TRUE | 61350 | Central Rivers Power MA, LLC | 1637 | Putts Bridge | MA | Hampden | PB2 | Conventional Hydroelectric | HY |  | S | X | X | 873 |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.5 | N |  |  | OP | X | 1 | 1918 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 1H
Vintage1918 | hydro | TRUE | 61350 | Central Rivers Power MA, LLC | 1637 | Putts Bridge | MA | Hampden | PB3 | Conventional Hydroelectric | HY |  | S | X | X | 873 |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.5 | N |  |  | OA | X | 1 | 1918 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 1H
Vintage1934 | hydro | TRUE | 61350 | Central Rivers Power MA, LLC | 1638 | Redbridge | MA | Hampden | RB3 | Conventional Hydroelectric | HY |  | S | X | X | 874 |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 1 | 1934 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 1H
Vintage1926 | hydro | TRUE | 61350 | Central Rivers Power MA, LLC | 1638 | Redbridge | MA | Hampden | RB4 | Conventional Hydroelectric | HY |  | S | X | X | 874 |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 1 | 1926 |  |  | N | IPP Non-CHP | 2 | X | WAT | [9 empty] | N | N | 0 | 1H
Vintage2002 | natural gas peaker | TRUE | 56401 | NAEA Energy Massachusetts LLC | 1642 | Essential Power Massachusetts LLC | MA | Hampden | GT-1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 60 | 0.85 | 33.3 | 48 | 25 | N |  |  | OP | X | 4 | 2002 |  |  | N | IPP Non-CHP | 2 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 56401 | NAEA Energy Massachusetts LLC | 1642 | Essential Power Massachusetts LLC | MA | Hampden | GT-2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 60 | 0.85 | 33.4 | 48 | 25 | N |  |  | OP | X | 4 | 2002 |  |  | N | IPP Non-CHP | 2 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1968 | other | TRUE | 56401 | NAEA Energy Massachusetts LLC | 1642 | Essential Power Massachusetts LLC | MA | Hampden | WS10 | Petroleum Liquids | GT |  | S | X | X |  |  | 17 | 0.85 | 17.1 | 21.9 | 15 | N |  |  | OP | X | 1 | 1968 |  |  | N | IPP Non-CHP | 2 | X | KER | [9 empty] | N | N |  | 10M | [23 empty] | N | N
Vintage1969 | other | TRUE | 56401 | NAEA Energy Massachusetts LLC | 1643 | Woodland Road | MA | Berkshire | WOOD | Petroleum Liquids | GT |  | S | X | X |  |  | 20.4 | 0.85 | 16.5 | 21 | 15 | N |  |  | OP | X | 1 | 1969 |  |  | N | IPP Non-CHP | 2 | X | KER | [9 empty] | N |  |  | 10M | [23 empty] | N | N | N
Vintage1977 | natural gas combined cycle | TRUE | 2144 | Town of Braintree - (MA) | 1660 | Potter Station 2 | MA | Norfolk | CC2 | Natural Gas Fired Combined Cycle | CT | POT2 | J | X | N | 540 | 540 | 76 | 0.9 | 62.6 | 77.6 | 37 | N |  |  | OS | X | 4 | 1977 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1977 | natural gas combined cycle | TRUE | 2144 | Town of Braintree - (MA) | 1660 | Potter Station 2 | MA | Norfolk | CC3 | Natural Gas Fired Combined Cycle | CA | POT2 | J | N | X | 540 | 540 | 25 | 0.9 | 15.5 | 18.5 | 8 | N |  |  | OS | X | 4 | 1977 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 12H | [23 empty] | N | N | N
Vintage2009 | natural gas peaker | TRUE | 2144 | Town of Braintree - (MA) | 1660 | Potter Station 2 | MA | Norfolk | WAT1 | Natural Gas Fired Combustion Turbine | GT |  | J | X | X | 15484 | 15484 | 58 | 0.85 | 52.6 | 57.4 | 28 | N |  |  | OP | X | 7 | 2009 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M |  |  |  |  | N | [18 empty] | Y | Y | Y
Vintage2009 | natural gas peaker | TRUE | 2144 | Town of Braintree - (MA) | 1660 | Potter Station 2 | MA | Norfolk | WAT2 | Natural Gas Fired Combustion Turbine | GT |  | J | X | X | 15485 | 15485 | 58 | 0.85 | 52.6 | 57.4 | 28 | N |  |  | OP | X | 7 | 2009 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1986 | natural gas peaker | TRUE | 9442 | Town of Ipswich - (MA) | 1670 | High Street Station | MA | Essex | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.3 | 0.7 | N |  |  | OP | X | 8 | 1986 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1984 | natural gas peaker | TRUE | 9442 | Town of Ipswich - (MA) | 1670 | High Street Station | MA | Essex | 10 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.3 | 0.7 | N |  |  | OP | X | 4 | 1984 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1982 | natural gas peaker | TRUE | 9442 | Town of Ipswich - (MA) | 1670 | High Street Station | MA | Essex | 11 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.1 | 0.7 | N |  |  | OP | X | 9 | 1982 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1983 | natural gas peaker | TRUE | 9442 | Town of Ipswich - (MA) | 1670 | High Street Station | MA | Essex | 12 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.3 | 0.7 | N |  |  | OP | X | 8 | 1983 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1954 | natural gas peaker | TRUE | 9442 | Town of Ipswich - (MA) | 1670 | High Street Station | MA | Essex | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 0.7 | N |  |  | OP | X | 8 | 1954 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1951 | natural gas peaker | TRUE | 9442 | Town of Ipswich - (MA) | 1670 | High Street Station | MA | Essex | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.2 | 1.2 | 0.7 | N |  |  | OP | X | 7 | 1951 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1956 | petroleum | TRUE | 9442 | Town of Ipswich - (MA) | 1670 | High Street Station | MA | Essex | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.4 | 0.7 | N |  |  | OP | X | 9 | 1956 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1960 | petroleum | TRUE | 9442 | Town of Ipswich - (MA) | 1670 | High Street Station | MA | Essex | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.7 | N |  |  | SB | Y | 8 | 1960 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1961 | natural gas peaker | TRUE | 9442 | Town of Ipswich - (MA) | 1670 | High Street Station | MA | Essex | 9 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 0.7 | N |  |  | OP | X | 10 | 1961 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1971 | natural gas peaker | TRUE | 14605 | City of Peabody - (MA) | 1678 | Waters River | MA | Essex | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | UN.WATER_RV23 W_J1 | UN.WATER_RV23 W_J1 | 21.3 | 0.85 | 16 | 22 | 15 | N |  |  | OP | X | 12 | 1971 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1990 | natural gas peaker | TRUE | 14605 | City of Peabody - (MA) | 1678 | Waters River | MA | Essex | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | UN.WATER_RV115 W_J2 | UN.WATER_RV115 W_J2 | 43.6 | 0.95 | 30 | 44 | 20 | N |  |  | OP | X | 11 | 1990 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1976 | natural gas combined cycle | TRUE | 18488 | City of Taunton | 1682 | Cleary Flood Hybrid | MA | Bristol | 9A | Natural Gas Fired Combined Cycle | CT | CC1 | J | X | N | Taunton Node | un.Cleary 115 CLE9C | 23 | 0.9 | 18 | 21.4 | 3 | N |  |  | OP | X | 10 | 1976 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage2020 | other | TRUE | 18488 | City of Taunton | 1682 | Cleary Flood Hybrid | MA | Bristol | BS1 | Batteries | BA |  | S | X | X |  |  | 3 |  | 2.9 | 3 | 0.1 | N |  |  | OP | X | 3 | 2020 |  |  | N | Electric Utility | 1 | X | MWH | [12 empty] | 10M
Vintage1975 | natural gas combined cycle | TRUE | 18488 | City of Taunton | 1682 | Cleary Flood Hybrid | MA | Bristol | CA9 | Natural Gas Fired Combined Cycle | CA | CC1 | J | Y | X | Taunton Node | un.Cleary 115 CLE9C | 95 | 0.9 | 85 | 87 | 70 | N |  |  | OP | X | 12 | 1975 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1924 | hydro | TRUE | 4254 | Consumers Energy Co | 1693 | Alcona | MI | Alcona | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4 | 0.9 | 1.4 | 1.5 | 0 | N |  |  | OP | X | 1 | 1924 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage1924 | hydro | TRUE | 4254 | Consumers Energy Co | 1693 | Alcona | MI | Alcona | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4 | 0.9 | 1.4 | 1.5 | 0 | N |  |  | OP | X | 1 | 1924 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage1935 | hydro | TRUE | 4254 | Consumers Energy Co | 1694 | Allegan Dam | MI | Allegan | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.3 | 0.3 | 0 | N |  |  | OP | X | 1 | 1935 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage1935 | hydro | TRUE | 4254 | Consumers Energy Co | 1694 | Allegan Dam | MI | Allegan | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.9 | 0.8 | 0.5 | 0.6 | 0 | N |  |  | OP | X | 1 | 1935 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage1945 | hydro | TRUE | 4254 | Consumers Energy Co | 1694 | Allegan Dam | MI | Allegan | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.8 | 0.6 | 0.7 | 0 | N |  |  | OP | X | 1 | 1945 |  |  | N | Electric Utility | 1 | X | WAT | [9 empty] | N |  | 0 | 10M
Vintage1918 | hydro | TRUE | 4254 | Consumers Energy Co | 1698 | C W Tippy | MI | Manistee | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.7 | 0.95 | 2.1 | 2.2 | 0 | N |  |  | OP | X | 1 | 1918 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1918 | hydro | TRUE | 4254 | Consumers Energy Co | 1698 | C W Tippy | MI | Manistee | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.7 | 0.95 | 2.1 | 2.2 | 0 | N |  |  | OP | X | 1 | 1918 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1918 | hydro | TRUE | 4254 | Consumers Energy Co | 1698 | C W Tippy | MI | Manistee | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.7 | 0.95 | 2.1 | 2.2 | 0 | N |  |  | OP | X | 1 | 1918 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1911 | hydro | TRUE | 4254 | Consumers Energy Co | 1700 | Cooke | MI | Iosco | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.9 | 1.5 | 1.5 | 0 | N |  |  | OP | X | 1 | 1911 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1911 | hydro | TRUE | 4254 | Consumers Energy Co | 1700 | Cooke | MI | Iosco | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.9 | 3 | 2.9 | 0 | N |  |  | OP | X | 1 | 1911 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1911 | hydro | TRUE | 4254 | Consumers Energy Co | 1700 | Cooke | MI | Iosco | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.9 | 2.9 | 2.7 | 0 | N |  |  | OP | X | 1 | 1911 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1907 | hydro | TRUE | 4254 | Consumers Energy Co | 1701 | Croton | MI | Newaygo | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.8 | 1.2 | 1.6 | 0 | N |  |  | OP | X | 1 | 1907 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1907 | hydro | TRUE | 4254 | Consumers Energy Co | 1701 | Croton | MI | Newaygo | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.8 | 1.2 | 1.6 | 0 | N |  |  | OP | X | 1 | 1907 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1915 | hydro | TRUE | 4254 | Consumers Energy Co | 1701 | Croton | MI | Newaygo | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.4 | 1 | 0.5 | 0.7 | 0 | N |  |  | OP | X | 1 | 1915 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1912 | hydro | TRUE | 4254 | Consumers Energy Co | 1701 | Croton | MI | Newaygo | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 0.9 | 0.6 | 0.8 | 0 | N |  |  | OP | X | 1 | 1912 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1959 | hard coal | TRUE | 4254 | Consumers Energy Co | 1702 | Dan E Karn | MI | Bay | 1A | Conventional Steam Coal | ST | G381 | S | X | X |  |  | 136 | 0.85 | 127.5 | 127.5 | 70 | N |  |  | OP | X | 11 | 1959 | 5 | 2023 | N | Electric Utility | 1 | X | SUB | BIT |  |  |  |  | DFO |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y
Vintage1959 | hard coal | TRUE | 4254 | Consumers Energy Co | 1702 | Dan E Karn | MI | Bay | 1B | Conventional Steam Coal | ST | G381 | S | X | X |  |  | 136 | 0.85 | 127.5 | 127.5 | 70 | N |  |  | OP | X | 11 | 1959 | 5 | 2023 | N | Electric Utility | 1 | X | SUB | BIT |  |  |  |  | DFO |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y
Vintage1961 | hard coal | TRUE | 4254 | Consumers Energy Co | 1702 | Dan E Karn | MI | Bay | 2A | Conventional Steam Coal | ST | G382 | S | X | X |  |  | 136 | 0.85 | 117.1 | 116 | 65 | N |  |  | OP | X | 3 | 1961 | 5 | 2023 | N | Electric Utility | 1 | X | SUB | BIT |  |  |  |  | DFO |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y
Vintage1961 | hard coal | TRUE | 4254 | Consumers Energy Co | 1702 | Dan E Karn | MI | Bay | 2B | Conventional Steam Coal | ST | G382 | S | X | X |  |  | 136 | 0.85 | 117.1 | 116 | 65 | N |  |  | OP | X | 3 | 1961 | 5 | 2023 | N | Electric Utility | 1 | X | SUB | BIT |  |  |  |  | DFO |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y
Vintage1975 | natural gas steam turbine | TRUE | 4254 | Consumers Energy Co | 1702 | Dan E Karn | MI | Bay | 3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 692.5 | 0.85 | 604.5 | 574 | 60 | N |  |  | OP | X | 1 | 1975 |  |  | N | Electric Utility | 1 | X | NG | RFO | DFO |  |  |  | RFO | [6 empty] | 12H | [23 empty] | Y | Y | Y
Vintage1977 | natural gas steam turbine | TRUE | 4254 | Consumers Energy Co | 1702 | Dan E Karn | MI | Bay | 4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 709.8 | 0.85 | 608.4 | 379 | 60 | N |  |  | OP | X | 9 | 1977 |  |  | N | Electric Utility | 1 | X | NG | RFO | DFO |  |  |  | RFO | [6 empty] | 12H | [23 empty] | Y | Y | Y
Vintage1912 | hydro | TRUE | 4254 | Consumers Energy Co | 1704 | Five Channels | MI | Iosco | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.8 | 3.1 | 3.1 | 0 | N |  |  | OP | X | 1 | 1912 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1912 | hydro | TRUE | 4254 | Consumers Energy Co | 1704 | Five Channels | MI | Iosco | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.9 | 3.1 | 2.9 | 0 | N |  |  | OP | X | 1 | 1912 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1918 | hydro | TRUE | 4254 | Consumers Energy Co | 1705 | Foote | MI | Iosco | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.9 | 1 | 1.1 | 0 | N |  |  | OP | X | 1 | 1918 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1918 | hydro | TRUE | 4254 | Consumers Energy Co | 1705 | Foote | MI | Iosco | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.9 | 1 | 1.1 | 0 | N |  |  | OP | X | 1 | 1918 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1918 | hydro | TRUE | 4254 | Consumers Energy Co | 1705 | Foote | MI | Iosco | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.9 | 1 | 1.1 | 0 | N |  |  | OP | X | 1 | 1918 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1931 | hydro | TRUE | 4254 | Consumers Energy Co | 1707 | Hardy | MI | Newaygo | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 0.8 | 10.7 | 10.3 | 0 | N |  |  | OP | X | 6 | 1931 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1931 | hydro | TRUE | 4254 | Consumers Energy Co | 1707 | Hardy | MI | Newaygo | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 0.8 | 10.7 | 10.4 | 0 | N |  |  | OP | X | 6 | 1931 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1931 | hydro | TRUE | 4254 | Consumers Energy Co | 1707 | Hardy | MI | Newaygo | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 11.5 | 0.8 | 11.5 | 11.5 | 0 | N |  |  | OP | X | 6 | 1931 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1925 | hydro | TRUE | 4254 | Consumers Energy Co | 1708 | Hodenpyl | MI | Wexford | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8.5 | 0.96 | 2.1 | 2.4 | 0 | N |  |  | OP | X | 7 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1925 | hydro | TRUE | 4254 | Consumers Energy Co | 1708 | Hodenpyl | MI | Wexford | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8.5 | 0.96 | 2.1 | 2.4 | 0 | N |  |  | OP | X | 8 | 1925 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1962 | hard coal | TRUE | 4254 | Consumers Energy Co | 1710 | J H Campbell | MI | Ottawa | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 265.2 | 0.85 | 260 | 260 | 100 | N |  |  | OP | X | 10 | 1962 | 5 | 2025 | N | Electric Utility | 1 | X | SUB | [5 empty] | DFO |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1967 | hard coal | TRUE | 4254 | Consumers Energy Co | 1710 | J H Campbell | MI | Ottawa | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 378.8 | 0.77 | 328 | 295 | 100 | N |  |  | OP | X | 7 | 1967 | 5 | 2025 | N | Electric Utility | 1 | X | SUB | BIT |  |  |  |  | DFO |  |  |  | N |  |  | OVER |  | Y |  |  |  | Y | [17 empty] | N
Vintage1980 | hard coal | TRUE | 4254 | Consumers Energy Co | 1710 | J H Campbell | MI | Ottawa | 3 | Conventional Steam Coal | ST |  | J | X | X |  |  | 916.8 | 0.86 | 841.4 | 848 | 350 | N |  |  | OP | X | 9 | 1980 | 5 | 2025 | N | Electric Utility | 1 | X | SUB | [5 empty] | DFO |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1913 | hydro | TRUE | 4254 | Consumers Energy Co | 1712 | Loud | MI | Iosco | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.9 | 2.2 | 2.2 | 0 | N |  |  | OP | X | 1 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1913 | hydro | TRUE | 4254 | Consumers Energy Co | 1712 | Loud | MI | Iosco | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.9 | 2.2 | 2.2 | 0 | N |  |  | OP | X | 1 | 1913 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1973 | other | TRUE | 4254 | Consumers Energy Co | 1713 | Ludington | MI | Mason | 1 | Hydroelectric Pumped Storage | PS |  | J | X | X |  |  | 329.8 | 0.85 | 362.7 | 361 | 240 | N |  |  | OP | X | 1 | 1973 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1973 | other | TRUE | 4254 | Consumers Energy Co | 1713 | Ludington | MI | Mason | 2 | Hydroelectric Pumped Storage | PS |  | J | X | X |  |  | 329.8 | 0.85 | 362.6 | 361 | 240 | N |  |  | OP | X | 3 | 1973 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1973 | other | TRUE | 4254 | Consumers Energy Co | 1713 | Ludington | MI | Mason | 3 | Hydroelectric Pumped Storage | PS |  | J | X | X |  |  | 329.8 | 0.85 | 331 | 310 | 240 | N |  |  | OA | X | 4 | 1973 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M | [7 empty] | 49 | 32 | 5 | 2022
Vintage1973 | other | TRUE | 4254 | Consumers Energy Co | 1713 | Ludington | MI | Mason | 4 | Hydroelectric Pumped Storage | PS |  | J | X | X |  |  | 329.8 | 0.85 | 362.1 | 361 | 240 | N |  |  | OP | X | 6 | 1973 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1973 | other | TRUE | 4254 | Consumers Energy Co | 1713 | Ludington | MI | Mason | 5 | Hydroelectric Pumped Storage | PS |  | J | X | X |  |  | 329.8 | 0.85 | 362.7 | 361 | 240 | N |  |  | OP | X | 8 | 1973 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1973 | other | TRUE | 4254 | Consumers Energy Co | 1713 | Ludington | MI | Mason | 6 | Hydroelectric Pumped Storage | PS |  | J | X | X |  |  | 329.8 | 0.85 | 362.7 | 361 | 240 | N |  |  | OP | X | 10 | 1973 |  |  | N | Electric Utility | 1 | X | WAT | [12 empty] | 10M
Vintage1916 | hydro | TRUE | 4254 | Consumers Energy Co | 1714 | Mio | MI | Oscoda | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 0.9 | 0.8 | 0.8 | 0 | N |  |  | OP | X | 1 | 1916 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1916 | hydro | TRUE | 4254 | Consumers Energy Co | 1714 | Mio | MI | Oscoda | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 0.9 | 0.8 | 0.8 | 0 | N |  |  | OP | X | 1 | 1916 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1972 | nuclear | TRUE | 56192 | Entergy Nuclear Palisades LLC | 1715 | Palisades | MI | Van Buren | 1 | Nuclear | ST |  | S | X | X | CONS.PALISA2A1 | CONS.PALISA2A1 | 811.8 | 0.8 | 795.8 | 815.2 | 0 | N |  |  | OP | X | 3 | 1972 | 6 | 2022 | N | IPP Non-CHP | 2 | X | NUC | [9 empty] | N | N |  | 12H | [23 empty] | N
Vintage1922 | hydro | TRUE | 4254 | Consumers Energy Co | 1716 | Rogers | MI | Mecosta | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.7 | 0.9 | 0.6 | 0.8 | 0 | N |  |  | OP | X | 1 | 1922 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1922 | hydro | TRUE | 4254 | Consumers Energy Co | 1716 | Rogers | MI | Mecosta | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.7 | 0.9 | 0.6 | 0.8 | 0 | N |  |  | OP | X | 1 | 1922 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1922 | hydro | TRUE | 4254 | Consumers Energy Co | 1716 | Rogers | MI | Mecosta | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.7 | 0.9 | 0.6 | 0.8 | 0 | N |  |  | OP | X | 1 | 1922 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1922 | hydro | TRUE | 4254 | Consumers Energy Co | 1716 | Rogers | MI | Mecosta | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.7 | 0.9 | 0.6 | 0.8 | 0 | N |  |  | OP | X | 1 | 1922 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1907 | hydro | TRUE | 4254 | Consumers Energy Co | 1722 | Webber | MI | Ionia | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.3 | 1 | 0.9 | 1.3 | 0 | N |  |  | OP | X | 1 | 1907 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1949 | hydro | TRUE | 4254 | Consumers Energy Co | 1722 | Webber | MI | Ionia | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.8 | 0.3 | 0.4 | 0 | N |  |  | OP | X | 1 | 1949 |  |  | N | Electric Utility | 1 | X | WAT | [11 empty] | 0 | 10M
Vintage1969 | petroleum | TRUE | 5109 | DTE Electric Company | 1725 | Colfax | MI | Livingston | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2 | 2 | 0.6 | N |  |  | OP | X | 11 | 1969 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N |  | N
Vintage1969 | petroleum | TRUE | 5109 | DTE Electric Company | 1725 | Colfax | MI | Livingston | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 12 | 1969 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N |  | N
Vintage1969 | petroleum | TRUE | 5109 | DTE Electric Company | 1725 | Colfax | MI | Livingston | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 11 | 1969 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N |  | N
Vintage1969 | petroleum | TRUE | 5109 | DTE Electric Company | 1725 | Colfax | MI | Livingston | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 12 | 1969 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1969 | petroleum | TRUE | 5109 | DTE Electric Company | 1725 | Colfax | MI | Livingston | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 11 | 1969 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage2000 | natural gas peaker | TRUE | 5109 | DTE Electric Company | 1728 | Delray | MI | Wayne | 11-1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 71.1 | 0.97 | 64 | 80 | 35 | N |  |  | OP | X | 2 | 2000 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage2000 | natural gas peaker | TRUE | 5109 | DTE Electric Company | 1728 | Delray | MI | Wayne | 12-1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 71.1 | 0.85 | 63 | 79 | 35 | N |  |  | OP | X | 2 | 2000 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1988 | nuclear | TRUE | 5109 | DTE Electric Company | 1729 | Fermi | MI | Monroe | 2 | Nuclear | ST |  | S | X | X |  |  | 1217 | 0.9 | 1141 | 1161 | 690 | N |  |  | OP | X | 1 | 1988 |  |  | N | Electric Utility | 1 | X | NUC | [9 empty] | N | N |  | OVER | [23 empty] | N
Vintage1966 | petroleum | TRUE | 5109 | DTE Electric Company | 1729 | Fermi | MI | Monroe | 3 | Petroleum Liquids | GT |  | S | X | X |  |  | 16 | 0.85 | 13 | 19 | 4 | N |  |  | OP | X | 4 | 1966 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1966 | petroleum | TRUE | 5109 | DTE Electric Company | 1729 | Fermi | MI | Monroe | 4 | Petroleum Liquids | GT |  | S | X | X |  |  | 16 | 0.85 | 12 | 18 | 4 | N |  |  | OP | X | 4 | 1966 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1966 | petroleum | TRUE | 5109 | DTE Electric Company | 1729 | Fermi | MI | Monroe | GT1 | Petroleum Liquids | GT |  | S | X | X |  |  | 16 | 0.85 | 13 | 19 | 4 | N |  |  | OP | X | 4 | 1966 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1966 | petroleum | TRUE | 5109 | DTE Electric Company | 1729 | Fermi | MI | Monroe | GT2 | Petroleum Liquids | GT |  | S | X | X |  |  | 16 | 0.85 | 13 | 19 | 4 | N |  |  | OP | X | 4 | 1966 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1967 | natural gas peaker | TRUE | 5109 | DTE Electric Company | 1730 | Hancock | MI | Oakland | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 19 | 0.85 | 11 | 18 | 3 | N |  |  | OP | X | 9 | 1967 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1967 | natural gas peaker | TRUE | 5109 | DTE Electric Company | 1730 | Hancock | MI | Oakland | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 19 | 0.85 | 17 | 22 | 3 | N |  |  | OP | X | 11 | 1967 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1970 | natural gas peaker | TRUE | 5109 | DTE Electric Company | 1730 | Hancock | MI | Oakland | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 41.8 | 0.9 | 32 | 42 | 4 | N |  |  | OP | X | 5 | 1970 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1966 | natural gas peaker | TRUE | 5109 | DTE Electric Company | 1730 | Hancock | MI | Oakland | 6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 41.8 | 0.9 | 33 | 42 | 4 | N |  |  | OP | X | 4 | 1966 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1971 | hard coal | TRUE | 5109 | DTE Electric Company | 1733 | Monroe (MI) | MI | Monroe | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 817.2 | 0.9 | 758 | 758 | 280 | N |  |  | OP | X | 6 | 1971 |  |  | N | Electric Utility | 1 | X | RC | PC | DFO | BIT | SUB |  | DFO |  |  |  | N | N |  | 12H |  | Y |  |  |  | Y | [17 empty] | Y | Y | N
Vintage1973 | hard coal | TRUE | 5109 | DTE Electric Company | 1733 | Monroe (MI) | MI | Monroe | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 822.6 | 0.95 | 773 | 783 | 280 | N |  |  | OP | X | 3 | 1973 |  |  | N | Electric Utility | 1 | X | RC | PC | DFO | BIT | SUB |  | DFO |  |  |  | N | N |  | 12H |  | Y |  |  |  | Y | [17 empty] | Y | Y | N
Vintage1973 | hard coal | TRUE | 5109 | DTE Electric Company | 1733 | Monroe (MI) | MI | Monroe | 3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 822.6 | 0.9 | 773 | 783 | 280 | N |  |  | OP | X | 5 | 1973 |  |  | N | Electric Utility | 1 | X | RC | PC | DFO | BIT | SUB |  | DFO |  |  |  | N | N |  | 12H |  | Y |  |  |  | Y | [17 empty] | Y | Y | N
Vintage1974 | hard coal | TRUE | 5109 | DTE Electric Company | 1733 | Monroe (MI) | MI | Monroe | 4 | Conventional Steam Coal | ST |  | S | X | X |  |  | 817.2 | 0.95 | 762 | 762 | 280 | N |  |  | OP | X | 5 | 1974 |  |  | N | Electric Utility | 1 | X | RC | PC | DFO | BIT | SUB |  | DFO |  |  |  | N | N |  | 12H |  | Y |  |  |  | Y | [17 empty] | Y | Y | N
Vintage1969 | petroleum | TRUE | 5109 | DTE Electric Company | 1733 | Monroe (MI) | MI | Monroe | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2 | 2 | 0.6 | N |  |  | OP | X | 11 | 1969 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1969 | petroleum | TRUE | 5109 | DTE Electric Company | 1733 | Monroe (MI) | MI | Monroe | IC2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 12 | 1969 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1969 | petroleum | TRUE | 5109 | DTE Electric Company | 1733 | Monroe (MI) | MI | Monroe | IC3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 11 | 1969 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1969 | petroleum | TRUE | 5109 | DTE Electric Company | 1733 | Monroe (MI) | MI | Monroe | IC4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 12 | 1969 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1969 | petroleum | TRUE | 5109 | DTE Electric Company | 1733 | Monroe (MI) | MI | Monroe | IC5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 11 | 1969 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1967 | natural gas peaker | TRUE | 5109 | DTE Electric Company | 1734 | Northeast (MI) | MI | Macomb | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 16 | 0.85 | 15 | 20 | 7 | N |  |  | OP | X | 9 | 1967 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1966 | natural gas peaker | TRUE | 5109 | DTE Electric Company | 1734 | Northeast (MI) | MI | Macomb | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 16 | 0.85 | 15 | 20 | 6.5 | N |  |  | OP | X | 6 | 1966 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1966 | natural gas peaker | TRUE | 5109 | DTE Electric Company | 1734 | Northeast (MI) | MI | Macomb | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 16 | 0.85 | 14 | 20 | 6.5 | N |  |  | OP | X | 5 | 1966 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1966 | natural gas peaker | TRUE | 5109 | DTE Electric Company | 1734 | Northeast (MI) | MI | Macomb | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 16 | 0.85 | 15 | 20 | 6.5 | N |  |  | OP | X | 5 | 1966 |  |  | N | Electric Utility | 1 | X | NG | [9 empty] | N | N |  | 1H | [23 empty] | N
Vintage1971 | natural gas peaker | TRUE | 5109 | DTE Electric Company | 1734 | Northeast (MI) | MI | Macomb | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 23.4 | 0.85 | 18 | 24 | 8 | N |  |  | OP | X | 6 | 1971 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1971 | petroleum | TRUE | 5109 | DTE Electric Company | 1734 | Northeast (MI) | MI | Macomb | 6 | Petroleum Liquids | GT |  | S | X | X |  |  | 21.2 | 0.85 | 19 | 23 | 8 | N |  |  | OP | X | 5 | 1971 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1971 | petroleum | TRUE | 5109 | DTE Electric Company | 1734 | Northeast (MI) | MI | Macomb | 7 | Petroleum Liquids | GT |  | S | X | X |  |  | 21.2 | 0.85 | 20 | 23 | 8 | N |  |  | OP | X | 5 | 1971 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N |  |  | 10M | [23 empty] | N
Vintage1970 | petroleum | TRUE | 5109 | DTE Electric Company | 1735 | Oliver | MI | Huron | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2 | 2 | 0.6 | N |  |  | OP | X | 1 | 1970 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1970 | petroleum | TRUE | 5109 | DTE Electric Company | 1735 | Oliver | MI | Huron | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 1 | 1970 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1970 | petroleum | TRUE | 5109 | DTE Electric Company | 1735 | Oliver | MI | Huron | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 1 | 1970 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1970 | petroleum | TRUE | 5109 | DTE Electric Company | 1735 | Oliver | MI | Huron | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 1 | 1970 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1970 | petroleum | TRUE | 5109 | DTE Electric Company | 1735 | Oliver | MI | Huron | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 1 | 1970 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1970 | petroleum | TRUE | 5109 | DTE Electric Company | 1737 | Placid 12 | MI | Oakland | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2 | 2 | 0.6 | N |  |  | OP | X | 11 | 1970 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1970 | petroleum | TRUE | 5109 | DTE Electric Company | 1737 | Placid 12 | MI | Oakland | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 12 | 1970 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1970 | petroleum | TRUE | 5109 | DTE Electric Company | 1737 | Placid 12 | MI | Oakland | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 11 | 1970 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1970 | petroleum | TRUE | 5109 | DTE Electric Company | 1737 | Placid 12 | MI | Oakland | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 11 | 1970 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1970 | petroleum | TRUE | 5109 | DTE Electric Company | 1737 | Placid 12 | MI | Oakland | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 11 | 1970 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1971 | petroleum | TRUE | 5109 | DTE Electric Company | 1739 | Putnam (MI) | MI | Oakland | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2 | 2 | 0.6 | N |  |  | OP | X | 6 | 1971 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1971 | petroleum | TRUE | 5109 | DTE Electric Company | 1739 | Putnam (MI) | MI | Oakland | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 6 | 1971 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1971 | petroleum | TRUE | 5109 | DTE Electric Company | 1739 | Putnam (MI) | MI | Oakland | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 6 | 1971 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1971 | petroleum | TRUE | 5109 | DTE Electric Company | 1739 | Putnam (MI) | MI | Oakland | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 6 | 1971 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1971 | petroleum | TRUE | 5109 | DTE Electric Company | 1739 | Putnam (MI) | MI | Oakland | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 6 | 1971 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1967 | petroleum | TRUE | 5109 | DTE Electric Company | 1740 | River Rouge | MI | Wayne | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2 | 2 | 0.8 | N |  |  | OP | X | 11 | 1967 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1967 | petroleum | TRUE | 5109 | DTE Electric Company | 1740 | River Rouge | MI | Wayne | IC2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.8 | N |  |  | OP | X | 12 | 1967 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1967 | petroleum | TRUE | 5109 | DTE Electric Company | 1740 | River Rouge | MI | Wayne | IC3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.8 | N |  |  | OP | X | 11 | 1967 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1967 | petroleum | TRUE | 5109 | DTE Electric Company | 1740 | River Rouge | MI | Wayne | IC4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.8 | N |  |  | OP | X | 11 | 1967 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1968 | petroleum | TRUE | 5109 | DTE Electric Company | 1741 | Slocum | MI | Wayne | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2 | 2 | 0.6 | N |  |  | OP | X | 12 | 1968 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1968 | petroleum | TRUE | 5109 | DTE Electric Company | 1741 | Slocum | MI | Wayne | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 12 | 1968 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1968 | petroleum | TRUE | 5109 | DTE Electric Company | 1741 | Slocum | MI | Wayne | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 11 | 1968 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1968 | petroleum | TRUE | 5109 | DTE Electric Company | 1741 | Slocum | MI | Wayne | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 11 | 1968 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1968 | petroleum | TRUE | 5109 | DTE Electric Company | 1741 | Slocum | MI | Wayne | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 11 | 1968 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M | [23 empty] | N
Vintage1968 | natural gas peaker | TRUE | 5109 | DTE Electric Company | 1743 | St Clair | MI | St Clair | 11 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 18.5 | 0.85 | 19 | 23 | 3 | N |  |  | OP | X | 5 | 1968 |  |  | N | Electric Utility | 1 | X | NG | DFO | [8 empty] | N | N |  | 1H |  | N | [21 empty] | Y | N | Y
Vintage1970 | petroleum | TRUE | 5109 | DTE Electric Company | 1743 | St Clair | MI | St Clair | 12A | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2 | 2 | 0.6 | N |  |  | OP | X | 12 | 1970 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M |  | N |  |  | N | [18 empty] | N | N | N
Vintage1970 | petroleum | TRUE | 5109 | DTE Electric Company | 1743 | St Clair | MI | St Clair | 12B | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 12 | 1970 |  |  | N | Electric Utility | 1 | X | DFO | [9 empty] | N | N |  | 10M |  | N |  |  | N | [18 empty] | N | N | N
Vintage1953 | hard coal | TRUE | 5109 | DTE Electric Company | 1743 | St Clair | MI | St Clair | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 156.2 | 0.8 | 154 | 162 | 35 | N |  |  | OP | X | 11 | 1953 | 12 | 2022 | N | Electric Utility | 1 | X | RC | SUB | DFO | RFO | WO | BIT | DFO | NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1954 | hard coal | TRUE | 5109 | DTE Electric Company | 1743 | St Clair | MI | St Clair | 3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 156.2 | 0.8 | 160 | 168 | 35 | N |  |  | OP | X | 6 | 1954 | 12 | 2022 | N | Electric Utility | 1 | X | RC | SUB | DFO | RFO | WO | BIT | DFO | NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1961 | hard coal | TRUE | 5109 | DTE Electric Company | 1743 | St Clair | MI | St Clair | 6 | Conventional Steam Coal | ST |  | S | X | X |  |  | 352.7 | 0.85 | 311 | 320 | 125 | N |  |  | OP | X | 4 | 1961 | 12 | 2022 | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: SUB; DFO DFO DFO: BIT; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1969 | hard coal | TRUE | 5109 | DTE Electric Company | 1743 | St Clair | MI | St Clair | 7 | Conventional Steam Coal | ST |  | S | X | X |  |  | 544.5 | 0.9 | 440 | 450 | 125 | N |  |  | OP | X | 4 | 1969 | 12 | 2022 | N | Electric Utility | 1 | X | RC | SUB | DFO | BIT |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1966 | petroleum | TRUE | 5109 | DTE Electric Company | 1744 | Superior | MI | Washtenaw | 1 | Petroleum Liquids | GT |  | S | X | X |  |  | 16 | 0.85 | 13 | 19 | 5 | N |  |  | OP | X | 10 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N
Vintage1966 | petroleum | TRUE | 5109 | DTE Electric Company | 1744 | Superior | MI | Washtenaw | 2 | Petroleum Liquids | GT |  | S | X | X |  |  | 16 | 0.85 | 13 | 19 | 5 | N |  |  | OP | X | 10 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N
Vintage1966 | petroleum | TRUE | 5109 | DTE Electric Company | 1744 | Superior | MI | Washtenaw | 3 | Petroleum Liquids | GT |  | S | X | X |  |  | 16 | 0.85 | 12 | 18 | 5 | N |  |  | OP | X | 10 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N
Vintage1966 | petroleum | TRUE | 5109 | DTE Electric Company | 1744 | Superior | MI | Washtenaw | 4 | Petroleum Liquids | GT |  | S | X | X |  |  | 16 | 0.85 | 14 | 20 | 5 | N |  |  | OP | X | 10 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1968 | hard coal | TRUE | 5109 | DTE Electric Company | 1745 | Trenton Channel | MI | Wayne | 9 | Conventional Steam Coal | ST |  | S | X | X |  |  | 535.5 | 0.9 | 495 | 495 | 158 | N |  |  | OP | X | 1 | 1968 | 12 | 2022 | N | Electric Utility | 1 | X | SUB | BIT | OTH | DFO |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1968 | petroleum | TRUE | 5109 | DTE Electric Company | 1746 | Wilmot | MI | Tuscola | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2 | 2 | 0.6 | N |  |  | OP | X | 12 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1968 | petroleum | TRUE | 5109 | DTE Electric Company | 1746 | Wilmot | MI | Tuscola | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 12 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1968 | petroleum | TRUE | 5109 | DTE Electric Company | 1746 | Wilmot | MI | Tuscola | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 12 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1968 | petroleum | TRUE | 5109 | DTE Electric Company | 1746 | Wilmot | MI | Tuscola | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 12 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1968 | petroleum | TRUE | 5109 | DTE Electric Company | 1746 | Wilmot | MI | Tuscola | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 12 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1960 | petroleum | TRUE | 3828 | Cloverland Electric Co-op | 1750 | Manistique | MI | Schoolcraft | 1 | Petroleum Liquids | IC |  | S | X | X | MIUP.MANSTQN1 |  | 2 | 0.9 | 2 | 2 | 2 | N |  |  | OP | X | 7 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1972 | petroleum | TRUE | 3828 | Cloverland Electric Co-op | 1750 | Manistique | MI | Schoolcraft | 2 | Petroleum Liquids | IC |  | S | X | X | MIUP.MANSTQN1 |  | 2.8 | 0.9 | 2.8 | 2.8 | 2.8 | N |  |  | OP | X | 12 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 10 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 11 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 12 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 13 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 14 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 15 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 16 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 17 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 18 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 19 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 20 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 21 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 22 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 23 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 24 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 25 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 26 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 27 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 28 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 29 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 30 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 31 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 32 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 33 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 34 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 35 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 36 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 37 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 38 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 39 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 40 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1901 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 41 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1901 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1901 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 42 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.5 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1901 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1916 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 45 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 46 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.4 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 47 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.4 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 48 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.4 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 49 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.4 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 50 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.4 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 51 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.4 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 52 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 53 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 54 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 55 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 56 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 57 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 58 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 59 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 6 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 60 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 61 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1916 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 62 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.5 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1916 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 63 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.5 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1916 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 64 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.5 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1916 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 65 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.5 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1916 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 66 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.5 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1916 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 67 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.5 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1916 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 68 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.5 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1916 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 69 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.5 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 7 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1916 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 70 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.5 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1916 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 71 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.5 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1916 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 72 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.5 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1916 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 73 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.5 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1916 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 74 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.5 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1916 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 75 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.5 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1916 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 76 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.5 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1916 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 77 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.5 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1916 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 78 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.5 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1916 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 79 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.5 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 8 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1916 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 80 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.5 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 3828 | Cloverland Electric Co-op | 1751 | Edison Sault | MI | Chippewa | 9 | Conventional Hydroelectric | HY |  | S | X | X | MIUP.CLVHDRTN1 |  | 0.6 | 0.9 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1996 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1753 | Berrien Springs | MI | Berrien | 10 | Conventional Hydroelectric | HY |  | S | X | X | 32418285 | 34497125 | 0.6 | 0.8 | 0.4 | 0.2 | 0.1 | N |  |  | OP | X | 11 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1996 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1753 | Berrien Springs | MI | Berrien | 11 | Conventional Hydroelectric | HY |  | S | X | X | 32418287 | 34497125 | 0.6 | 0.8 | 0.4 | 0.2 | 0.1 | N |  |  | OP | X | 11 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1996 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1753 | Berrien Springs | MI | Berrien | 12 | Conventional Hydroelectric | HY |  | S | X | X | 32418289 | 34497125 | 0.6 | 0.8 | 0.4 | 0.2 | 0.1 | N |  |  | OP | X | 11 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1996 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1753 | Berrien Springs | MI | Berrien | 1A | Conventional Hydroelectric | HY |  | S | X | X | 32418283 | 34497125 | 0.6 | 0.8 | 0.4 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1996 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1753 | Berrien Springs | MI | Berrien | 2A | Conventional Hydroelectric | HY |  | S | X | X | 32418291 | 34497125 | 0.6 | 1 | 0.4 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1996 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1753 | Berrien Springs | MI | Berrien | 3A | Conventional Hydroelectric | HY |  | S | X | X | 32418293 | 34497125 | 0.6 | 1 | 0.4 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1996 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1753 | Berrien Springs | MI | Berrien | 4A | Conventional Hydroelectric | HY |  | S | X | X | 32418295 | 34497125 | 0.6 | 1 | 0.4 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1996 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1753 | Berrien Springs | MI | Berrien | 5 | Conventional Hydroelectric | HY |  | S | X | X | 32418297 | 34497125 | 0.6 | 0.8 | 0.4 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1996 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1753 | Berrien Springs | MI | Berrien | 6 | Conventional Hydroelectric | HY |  | S | X | X | 32418299 | 34497125 | 0.6 | 0.8 | 0.4 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1996 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1753 | Berrien Springs | MI | Berrien | 7 | Conventional Hydroelectric | HY |  | S | X | X | 32418301 | 34497125 | 0.6 | 0.8 | 0.4 | 0.2 | 0.1 | N |  |  | OP | X | 11 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1996 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1753 | Berrien Springs | MI | Berrien | 8 | Conventional Hydroelectric | HY |  | S | X | X | 32418303 | 34497125 | 0.6 | 0.8 | 0.4 | 0.2 | 0.1 | N |  |  | OP | X | 11 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1996 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1753 | Berrien Springs | MI | Berrien | 9 | Conventional Hydroelectric | HY |  | S | X | X | 32418305 | 34497125 | 0.6 | 0.8 | 0.4 | 0.2 | 0.1 | N |  |  | OP | X | 11 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1919 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1754 | Buchanan (MI) | MI | Berrien | 1 | Conventional Hydroelectric | HY |  | S | X | X | 32418309 | 34497125 | 0.4 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1919 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1927 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1754 | Buchanan (MI) | MI | Berrien | 10 | Conventional Hydroelectric | HY |  | S | X | X | 32418311 | 34497125 | 0.5 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1919 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1754 | Buchanan (MI) | MI | Berrien | 2 | Conventional Hydroelectric | HY |  | S | X | X | 32418313 | 34497125 | 0.4 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1919 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1919 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1754 | Buchanan (MI) | MI | Berrien | 3 | Conventional Hydroelectric | HY |  | S | X | X | 32418315 | 34497125 | 0.4 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1919 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1919 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1754 | Buchanan (MI) | MI | Berrien | 4 | Conventional Hydroelectric | HY |  | S | X | X | 32418317 | 34497125 | 0.4 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1919 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1919 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1754 | Buchanan (MI) | MI | Berrien | 5 | Conventional Hydroelectric | HY |  | S | X | X | 32418319 | 34497125 | 0.4 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1919 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1919 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1754 | Buchanan (MI) | MI | Berrien | 6 | Conventional Hydroelectric | HY |  | S | X | X | 32418321 | 34497125 | 0.4 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1919 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1927 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1754 | Buchanan (MI) | MI | Berrien | 7 | Conventional Hydroelectric | HY |  | S | X | X | 32418323 | 34497125 | 0.5 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1927 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1754 | Buchanan (MI) | MI | Berrien | 8 | Conventional Hydroelectric | HY |  | S | X | X | 32418325 | 34497125 | 0.5 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1927 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1754 | Buchanan (MI) | MI | Berrien | 9 | Conventional Hydroelectric | HY |  | S | X | X | 32418327 | 34497125 | 0.5 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1913 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 1756 | Saxon Falls | WI | Iron | 1 | Conventional Hydroelectric | HY |  | S | X | X | Saxon Falls |  | 0.8 | 1 | 0.5 | 0.5 | 0.2 | N |  |  | OP | X | 1 | 1913 | 12 | 2064 | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1913 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 1756 | Saxon Falls | WI | Iron | 2 | Conventional Hydroelectric | HY |  | S | X | X | Saxon Falls |  | 0.8 | 1 | 0.5 | 0.6 | 0.2 | N |  |  | OP | X | 1 | 1913 | 12 | 2064 | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1917 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 1757 | Superior Falls | MI | Gogebic | 1 | Conventional Hydroelectric | HY |  | S | X | X | Superior Falls |  | 0.7 | 0.8 | 0.5 | 0.6 | 0.2 | N |  |  | OP | X | 1 | 1917 | 12 | 2064 | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1917 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 1757 | Superior Falls | MI | Gogebic | 2 | Conventional Hydroelectric | HY |  | S | X | X | Superior Falls |  | 0.7 | 0.8 | 0.5 | 0.6 | 0.2 | N |  |  | OP | X | 1 | 1917 | 12 | 2064 | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1923 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1760 | Constantine | MI | St Joseph | 1 | Conventional Hydroelectric | HY |  | S | X | X | 32418375 | 34497125 | 0.3 | 0.8 | 0.1 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1923 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1923 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1760 | Constantine | MI | St Joseph | 2 | Conventional Hydroelectric | HY |  | S | X | X | 32418377 | 34497125 | 0.3 | 0.8 | 0.1 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1923 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1929 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1760 | Constantine | MI | St Joseph | 3 | Conventional Hydroelectric | HY |  | S | X | X | 32418379 | 34497125 | 0.3 | 0.8 | 0.1 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1929 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1923 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1760 | Constantine | MI | St Joseph | 4 | Conventional Hydroelectric | HY |  | S | X | X | 32418381 | 34497125 | 0.3 | 0.8 | 0.1 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1923 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1923 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1761 | Mottville | MI | St Joseph | 1 | Conventional Hydroelectric | HY |  | S | X | X | 32418473 | 34497125 | 0.4 | 0.8 | 0.1 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1923 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1923 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1761 | Mottville | MI | St Joseph | 2 | Conventional Hydroelectric | HY |  | S | X | X | 32418475 | 34497125 | 0.4 | 0.8 | 0.1 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1923 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1923 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1761 | Mottville | MI | St Joseph | 3 | Conventional Hydroelectric | HY |  | S | X | X | 32418477 | 34497125 | 0.4 | 0.8 | 0.1 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1923 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1923 | hydro | TRUE | 9324 | Indiana Michigan Power Co | 1761 | Mottville | MI | St Joseph | 4 | Conventional Hydroelectric | HY |  | S | X | X | 32418479 | 34497125 | 0.4 | 0.8 | 0.1 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1923 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1959 | biomass | TRUE | 56133 | L'Anse Warden Electric Company LLC | 1772 | John H Warden | MI | Baraga | 1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 22 | 0.85 | 17.7 | 17.7 | 6 | N |  |  | OP | X | 8 | 1959 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WDS; DFO SUB SUB: TDF; DFO DFO DFO: NG |  |  | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage1931 | hydro | TRUE | 19578 | Upper Peninsula Power Company | 1773 | Prickett | MI | Baraga | 1 | Conventional Hydroelectric | HY |  | S | X | X | UPPC.INTEGRATD | UPPC.INTEGRATD | 1.1 | 0.8 | 0.4 | 0.4 | 0 | N |  |  | OP | X | 11 | 1931 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1931 | hydro | TRUE | 19578 | Upper Peninsula Power Company | 1773 | Prickett | MI | Baraga | 2 | Conventional Hydroelectric | HY |  | S | X | X | UPPC.INTEGRATD | UPPC.INTEGRATD | 1.1 | 0.8 | 0.4 | 0.4 | 0 | N |  |  | OP | X | 11 | 1931 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1931 | hydro | TRUE | 19578 | Upper Peninsula Power Company | 1774 | Victoria Dam | MI | Ontonagon | 1 | Conventional Hydroelectric | HY |  | S | X | X | UPPC.VICTORIA1 | UPPC.VICTORIA1 | 6 | 0.8 | 5.9 | 5.9 | 0 | N |  |  | OP | X | 1 | 1931 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1931 | hydro | TRUE | 19578 | Upper Peninsula Power Company | 1774 | Victoria Dam | MI | Ontonagon | 2 | Conventional Hydroelectric | HY |  | S | X | X | UPPC.VICTORIA2 | UPPC.VICTORIA2 | 6 | 0.8 | 5.9 | 5.9 | 0 | N |  |  | OP | X | 1 | 1931 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1919 | hydro | TRUE | 20847 | Wisconsin Electric Power Co | 1775 | Brule | WI | Florence | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 0.1 | N |  |  | OP | X | 8 | 1919 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1919 | hydro | TRUE | 20847 | Wisconsin Electric Power Co | 1775 | Brule | WI | Florence | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | OP | X | 1 | 1919 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1921 | hydro | TRUE | 20847 | Wisconsin Electric Power Co | 1775 | Brule | WI | Florence | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | OP | X | 4 | 1921 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1927 | hydro | TRUE | 20847 | Wisconsin Electric Power Co | 1776 | Chalk Hill | MI | Menominee | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.6 | 0.8 | 2.6 | 2.6 | 0.6 | N |  |  | OP | X | 5 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1927 | hydro | TRUE | 20847 | Wisconsin Electric Power Co | 1776 | Chalk Hill | MI | Menominee | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.6 | 0.8 | 2.6 | 2.6 | 0.7 | N |  |  | OP | X | 5 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1927 | hydro | TRUE | 20847 | Wisconsin Electric Power Co | 1776 | Chalk Hill | MI | Menominee | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.6 | 0.8 | 2.6 | 2.6 | 1.7 | N |  |  | OP | X | 5 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1953 | hydro | TRUE | 20847 | Wisconsin Electric Power Co | 1777 | Hemlock Falls | MI | Iron | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.8 | 0.9 | 2.8 | 2.8 | 0.4 | N |  |  | OP | X | 8 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1924 | hydro | TRUE | 20847 | Wisconsin Electric Power Co | 1778 | Kingsford | MI | Dickinson | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 2.4 | 2.4 | 0.9 | N |  |  | OP | X | 5 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1924 | hydro | TRUE | 20847 | Wisconsin Electric Power Co | 1778 | Kingsford | MI | Dickinson | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 2.4 | 2.4 | 0.9 | N |  |  | OP | X | 5 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1924 | hydro | TRUE | 20847 | Wisconsin Electric Power Co | 1778 | Kingsford | MI | Dickinson | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 2.4 | 2.4 | 0.9 | N |  |  | OP | X | 5 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1953 | hydro | TRUE | 20847 | Wisconsin Electric Power Co | 1780 | Michigamme Falls | MI | Iron | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.8 | 0.9 | 4.8 | 4.8 | 0.6 | N |  |  | OP | X | 6 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1953 | hydro | TRUE | 20847 | Wisconsin Electric Power Co | 1780 | Michigamme Falls | MI | Iron | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.8 | 0.9 | 4.8 | 4.8 | 0.5 | N |  |  | OP | X | 7 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1943 | hydro | TRUE | 20847 | Wisconsin Electric Power Co | 1781 | Peavy Falls | MI | Iron | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6 | 0.8 | 6 | 6 | 5.2 | N |  |  | OP | X | 1 | 1943 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1943 | hydro | TRUE | 20847 | Wisconsin Electric Power Co | 1781 | Peavy Falls | MI | Iron | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6 | 0.8 | 6 | 6 | 5.2 | N |  |  | OP | X | 2 | 1943 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1949 | hydro | TRUE | 20847 | Wisconsin Electric Power Co | 1785 | Way Dam | MI | Iron | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.1 | N |  |  | OP | X | 12 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1927 | hydro | TRUE | 20847 | Wisconsin Electric Power Co | 1786 | White Rapids | MI | Menominee | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.8 | 2.6 | 2.6 | 1.1 | N |  |  | OP | X | 10 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1927 | hydro | TRUE | 20847 | Wisconsin Electric Power Co | 1786 | White Rapids | MI | Menominee | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.8 | 2 | 2 | 0.1 | N |  |  | OP | X | 10 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1927 | hydro | TRUE | 20847 | Wisconsin Electric Power Co | 1786 | White Rapids | MI | Menominee | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.8 | 2.6 | 2.6 | 1.3 | N |  |  | OP | X | 10 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1940 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 1787 | Grand Rapids | MI | Menominee | 1 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 1.1 | 1 | 1.1 | 1.1 | 0 | N |  |  | OP | X | 7 | 1940 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1941 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 1787 | Grand Rapids | MI | Menominee | 2 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 1.1 | 1 | 1.1 | 1.1 | 0 | N |  |  | OP | X | 7 | 1941 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1945 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 1787 | Grand Rapids | MI | Menominee | 3 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 1.5 | 1 | 1.5 | 1.5 | 0 | N |  |  | OP | X | 6 | 1945 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1918 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 1787 | Grand Rapids | MI | Menominee | 4 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 1.9 | 0.8 | 1.9 | 1.9 | 0 | N |  |  | OP | X | 6 | 1918 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1923 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 1787 | Grand Rapids | MI | Menominee | 5 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 1.9 | 0.85 | 1.9 | 1.9 | 0 | N |  |  | OP | X | 6 | 1923 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1914 | hydro | TRUE | 4604 | City of Crystal Falls | 1821 | Crystal Falls | MI | Iron | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 6 | 1914 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1924 | hydro | TRUE | 4604 | City of Crystal Falls | 1821 | Crystal Falls | MI | Iron | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 6 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1954 | hydro | TRUE | 4604 | City of Crystal Falls | 1821 | Crystal Falls | MI | Iron | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 1 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 6 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1964 | natural gas peaker | TRUE | 8205 | City of Hart Hydro - (MI) | 1827 | Hart | MI | Oceana | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.4 | 0.8 | 1.4 | 1.4 | 0.4 | N |  |  | OP | X | 3 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1985 | petroleum | TRUE | 8205 | City of Hart Hydro - (MI) | 1827 | Hart | MI | Oceana | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.7 | 0.8 | 1.7 | 1.7 | 0.4 | N |  |  | OP | X | 3 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1985 | petroleum | TRUE | 8205 | City of Hart Hydro - (MI) | 1827 | Hart | MI | Oceana | IC3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.4 | N |  |  | OP | X | 4 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1973 | natural gas peaker | TRUE | 8631 | Hillsdale Board of Public Wks | 1829 | Hillsdale | MI | Hillsdale | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 5.6 | 0.8 | 5.6 | 5.6 | 4.5 | N |  |  | OP | X | 9 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1976 | natural gas peaker | TRUE | 8631 | Hillsdale Board of Public Wks | 1829 | Hillsdale | MI | Hillsdale | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 6 | 0.8 | 6 | 6 | 4.8 | N |  |  | OP | X | 4 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1973 | hard coal | TRUE | 56155 | Lansing Board of Water and Light | 1832 | Erickson Station | MI | Eaton | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 154.7 | 0.85 | 154.5 | 156.1 | 100 | N |  |  | OP | X | 2 | 1973 | 12 | 2025 | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO DFO DFO: DFO |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N
Vintage1979 | petroleum | TRUE | 11701 | City of Marquette - (MI) | 1840 | Plant Four | MI | Marquette | CT1 | Petroleum Liquids | GT |  | S | X | X |  |  | 24 | 0.95 | 20 | 22 | 5 | N |  |  | SB | Y | 5 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N |  | N
Vintage1919 | hydro | TRUE | 11701 | City of Marquette - (MI) | 1842 | James R Smith | MI | Marquette | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.1 | N |  |  | OP | X | 1 | 1919 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H | [23 empty] | N
Vintage1922 | hydro | TRUE | 11701 | City of Marquette - (MI) | 1842 | James R Smith | MI | Marquette | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.1 | N |  |  | OP | X | 1 | 1922 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H | [23 empty] | N
Vintage1928 | hydro | TRUE | 11713 | City of Marshall - (MI) | 1844 | Marshall (MI) | MI | Calhoun | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 6 | 1928 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1929 | hydro | TRUE | 11713 | City of Marshall - (MI) | 1844 | Marshall (MI) | MI | Calhoun | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OS | X | 6 | 1929 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1973 | natural gas peaker | TRUE | 11713 | City of Marshall - (MI) | 1844 | Marshall (MI) | MI | Calhoun | IC3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.1 | 0.8 | 1.9 | 1.9 | 1 | N |  |  | OP | X | 8 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1948 | natural gas peaker | TRUE | 11713 | City of Marshall - (MI) | 1844 | Marshall (MI) | MI | Calhoun | IC5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.7 | 0.8 | 1.4 | 1.4 | 0.5 | N |  |  | OP | X | 4 | 1948 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1978 | natural gas peaker | TRUE | 11713 | City of Marshall - (MI) | 1844 | Marshall (MI) | MI | Calhoun | IC6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 5.7 | 0.8 | 5.6 | 5.6 | 1.2 | N |  |  | OP | X | 7 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  |  | N |  | 1H | [23 empty] | Y | N | Y
Vintage1974 | petroleum | TRUE | 13525 | Newberry Water & Light Board | 1846 | Newberry | MI | Luce | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.9 | 2.5 | 2.5 | 2.5 | N |  |  | OS | X | 6 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N | 0 | OVER | [20 empty] | N |  |  | N | N | N
Vintage1948 | petroleum | TRUE | 13525 | Newberry Water & Light Board | 1846 | Newberry | MI | Luce | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.7 | 0.9 | 0.5 | 0.5 | 0.5 | N |  |  | OS | X | 9 | 1948 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | OVER | [20 empty] | N |  |  | N | N | N
Vintage1988 | petroleum | TRUE | 13525 | Newberry Water & Light Board | 1846 | Newberry | MI | Luce | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.9 | 1.5 | 1.5 | 1.5 | N |  |  | OS | X | 7 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N | 0 | OVER | [20 empty] | N |  |  | N | N | N
Vintage1905 | hydro | TRUE | 13826 | City of Norway | 1848 | Norway (MI) | MI | Dickinson | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.7 | 1 | 3 | 3 | 1 | N |  |  | OP | X | 6 | 1905 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 1H
Vintage1905 | hydro | TRUE | 13826 | City of Norway | 1848 | Norway (MI) | MI | Dickinson | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 1 | 1.2 | 1.2 | 0.8 | N |  |  | OP | X | 6 | 1905 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 1H
Vintage1988 | hydro | TRUE | 13826 | City of Norway | 1848 | Norway (MI) | MI | Dickinson | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 1 | 1.1 | 1.1 | 0.8 | N |  |  | OP | X | 11 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 1H
Vintage1986 | hydro | TRUE | 13826 | City of Norway | 1848 | Norway (MI) | MI | Dickinson | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 1 | 0.9 | 0.9 | 0.8 | N |  |  | OP | X | 7 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 1H
Vintage1950 | petroleum | TRUE | 15246 | City of Portland - (MI) | 1851 | Frank Jenkins | MI | Ionia | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 1 | 0.8 | 0.8 | 0.1 | N |  |  | SB | Y | 5 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 12H | [23 empty] | N | N
Vintage1995 | petroleum | TRUE | 15246 | City of Portland - (MI) | 1851 | Frank Jenkins | MI | Ionia | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 1 | 1.7 | 1.7 | 0.2 | N |  |  | SB | Y | 8 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage2002 | petroleum | TRUE | 15246 | City of Portland - (MI) | 1851 | Frank Jenkins | MI | Ionia | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 1 | 1 | 1 | 0.1 | N |  |  | SB | Y | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1958 | petroleum | TRUE | 17886 | City of St Louis - (MI) | 1852 | St Louis | MI | Gratiot | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.9 | 1.3 | 1.3 | 0.1 | N |  |  | SB | Y | 1 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1945 | petroleum | TRUE | 17886 | City of St Louis - (MI) | 1852 | St Louis | MI | Gratiot | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.9 | 0.6 | 0.6 | 0.1 | N |  |  | SB | Y | 1 | 1945 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N
Vintage1951 | petroleum | TRUE | 17886 | City of St Louis - (MI) | 1852 | St Louis | MI | Gratiot | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.1 | N |  |  | SB | Y | 1 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N
Vintage1919 | hydro | TRUE | 17886 | City of St Louis - (MI) | 1852 | St Louis | MI | Gratiot | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 0.9 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1919 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1919 | hydro | TRUE | 17886 | City of St Louis - (MI) | 1852 | St Louis | MI | Gratiot | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 0.9 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1919 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1996 | petroleum | TRUE | 17886 | City of St Louis - (MI) | 1852 | St Louis | MI | Gratiot | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.9 | 1.1 | 1.1 | 0.1 | N |  |  | SB | Y | 7 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage2003 | petroleum | TRUE | 17886 | City of St Louis - (MI) | 1852 | St Louis | MI | Gratiot | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.9 | 1.5 | 1.5 | 0.1 | N |  |  | OP | X | 5 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage2003 | petroleum | TRUE | 17886 | City of St Louis - (MI) | 1852 | St Louis | MI | Gratiot | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.9 | 1.1 | 1.1 | 0.1 | N |  |  | SB | Y | 5 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1961 | petroleum | TRUE | 16873 | Village of Sebewaing - (MI) | 1853 | Main Street (MI) | MI | Huron | 1 | Petroleum Liquids | IC |  | S | X | X | CONS.MPPA | MISO-CONS.MPPA | 1 | 0.95 | 0.9 | 1 | 0.1 | N |  |  | SB | Y | 3 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1947 | petroleum | TRUE | 16873 | Village of Sebewaing - (MI) | 1853 | Main Street (MI) | MI | Huron | 2 | Petroleum Liquids | IC |  | S | X | X | CONS.MPPA | MISO-CONS.MPPA | 0.9 | 0.95 | 0.8 | 0.9 | 0.1 | N |  |  | SB | Y | 6 | 1947 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1966 | petroleum | TRUE | 16873 | Village of Sebewaing - (MI) | 1853 | Main Street (MI) | MI | Huron | 3 | Petroleum Liquids | IC |  | S | X | X | CONS.MPPA | MISO-CONS.MPPA | 1.1 | 0.95 | 1.1 | 1.1 | 0.1 | N |  |  | SB | Y | 8 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1966 | petroleum | TRUE | 16873 | Village of Sebewaing - (MI) | 1853 | Main Street (MI) | MI | Huron | 4 | Petroleum Liquids | IC |  | S | X | X | CONS.MPPA | MISO-CONS.MPPA | 1.3 | 0.95 | 1.2 | 1.3 | 0.1 | N |  |  | SB | Y | 10 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1979 | petroleum | TRUE | 16873 | Village of Sebewaing - (MI) | 1853 | Main Street (MI) | MI | Huron | 5 | Petroleum Liquids | IC |  | S | X | X | CONS.MPPA | MISO-CONS.MPPA | 1.1 | 0.95 | 1 | 1.1 | 0.1 | N |  |  | SB | Y | 9 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1967 | petroleum | TRUE | 16873 | Village of Sebewaing - (MI) | 1853 | Main Street (MI) | MI | Huron | 6 | Petroleum Liquids | IC |  | S | X | X | CONS.MPPA | MISO-CONS.MPPA | 0.6 | 0.95 | 0.6 | 0.6 | 0.1 | N |  |  | SB | Y | 4 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1981 | natural gas peaker | TRUE | 18252 | City of Sturgis | 1855 | Sturgis City Diesel Plant | MI | St Joseph | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 6 | 1 | 6 | 6 | 3 | N |  |  | OP | X | 12 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1911 | hydro | TRUE | 18252 | City of Sturgis | 1856 | Hydro Plant | MI | St Joseph | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 9 | 1911 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1911 | hydro | TRUE | 18252 | City of Sturgis | 1856 | Hydro Plant | MI | St Joseph | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 9 | 1911 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1983 | hydro | TRUE | 18252 | City of Sturgis | 1856 | Hydro Plant | MI | St Joseph | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 1 | 0.7 | 0.7 | 0.4 | N |  |  | OP | X | 4 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1983 | hydro | TRUE | 18252 | City of Sturgis | 1856 | Hydro Plant | MI | St Joseph | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 1 | 0.7 | 0.7 | 0.4 | N |  |  | OP | X | 4 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1951 | hydro | TRUE | 21264 | USACE-Detroit District | 1865 | Saint Marys Falls | MI | Chippewa | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.2 | 0.9 | 5.1 | 5.1 | 1 | N |  |  | OP | X | 10 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 1H
Vintage1932 | hydro | TRUE | 21264 | USACE-Detroit District | 1865 | Saint Marys Falls | MI | Chippewa | 10 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.6 | 0.8 | 2.6 | 2.6 | 1.2 | N |  |  | OP | X | 7 | 1932 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 1H
Vintage1951 | hydro | TRUE | 21264 | USACE-Detroit District | 1865 | Saint Marys Falls | MI | Chippewa | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.2 | 0.9 | 5.2 | 5.2 | 1 | N |  |  | OP | X | 11 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 1H
Vintage1952 | hydro | TRUE | 21264 | USACE-Detroit District | 1865 | Saint Marys Falls | MI | Chippewa | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.2 | 0.9 | 5.2 | 5.2 | 1 | N |  |  | OP | X | 1 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 1H
Vintage1954 | hydro | TRUE | 21264 | USACE-Detroit District | 1865 | Saint Marys Falls | MI | Chippewa | 3A | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 0.91 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 2 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 1H
Vintage1948 | natural gas steam turbine | TRUE | 21048 | Wyandotte Municipal Serv Comm | 1866 | Wyandotte | MI | Wayne | 4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 11.5 | 0.85 | 10.5 | 11.5 | 5 | N |  |  | OP | X | 1 | 1948 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | N | N |  |  | N | [18 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1986 | natural gas steam turbine | TRUE | 21048 | Wyandotte Municipal Serv Comm | 1866 | Wyandotte | MI | Wayne | 7 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 32 | 0.85 | 32 | 35 | 5 | N |  |  | OP | X | 7 | 1986 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | N | N | [21 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage2007 | petroleum | TRUE | 21048 | Wyandotte Municipal Serv Comm | 1866 | Wyandotte | MI | Wayne | DG1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.85 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 1 | 2007 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2007 | petroleum | TRUE | 21048 | Wyandotte Municipal Serv Comm | 1866 | Wyandotte | MI | Wayne | DG2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.85 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 1 | 2007 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2007 | petroleum | TRUE | 21048 | Wyandotte Municipal Serv Comm | 1866 | Wyandotte | MI | Wayne | DG3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.85 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 1 | 2007 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1966 | natural gas peaker | TRUE | 21158 | City of Zeeland - (MI) | 1867 | Zeeland | MI | Ottawa | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | CONS.MPPA | CONS.MPPA | 1.4 | 0.8 | 1.5 | 1.5 | 0.7 | N |  |  | OP | X | 11 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1974 | natural gas peaker | TRUE | 21158 | City of Zeeland - (MI) | 1867 | Zeeland | MI | Ottawa | 10 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | CONS.MPPA | CONS.MPPA | 5.6 | 0.8 | 6 | 6.2 | 2.8 | N |  |  | OP | X | 12 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1980 | natural gas peaker | TRUE | 21158 | City of Zeeland - (MI) | 1867 | Zeeland | MI | Ottawa | 11 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | CONS.MPPA | CONS.MPPA | 6 | 0.8 | 6.4 | 6.6 | 3 | N |  |  | OP | X | 7 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1967 | natural gas peaker | TRUE | 21158 | City of Zeeland - (MI) | 1867 | Zeeland | MI | Ottawa | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | CONS.MPPA | CONS.MPPA | 1.1 | 0.8 | 1.2 | 1.2 | 0.6 | N |  |  | OP | X | 3 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1957 | natural gas peaker | TRUE | 21158 | City of Zeeland - (MI) | 1867 | Zeeland | MI | Ottawa | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | CONS.MPPA | CONS.MPPA | 2 | 0.8 | 2 | 2 | 1 | N |  |  | OP | X | 1 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1963 | natural gas peaker | TRUE | 21158 | City of Zeeland - (MI) | 1867 | Zeeland | MI | Ottawa | 8 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | CONS.MPPA | CONS.MPPA | 1.7 | 0.8 | 1.6 | 1.6 | 0.9 | N |  |  | OP | X | 1 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1971 | natural gas peaker | TRUE | 21158 | City of Zeeland - (MI) | 1867 | Zeeland | MI | Ottawa | 9 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | CONS.MPPA | CONS.MPPA | 4.5 | 0.8 | 5 | 5 | 2.3 | N |  |  | OP | X | 1 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage2021 | petroleum | TRUE | 3828 | Cloverland Electric Co-op | 1868 | Dafter | MI | Chippewa | 1C | Petroleum Liquids | IC |  | S | X | X | MIUP.DFTR13N1 |  | 2 | 0.9 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 12 | 2021 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N
Vintage2021 | petroleum | TRUE | 3828 | Cloverland Electric Co-op | 1868 | Dafter | MI | Chippewa | 2C | Petroleum Liquids | IC |  | S | X | X | MIUP.DFTR13N1 |  | 2 | 0.9 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 12 | 2021 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N
Vintage2021 | petroleum | TRUE | 3828 | Cloverland Electric Co-op | 1868 | Dafter | MI | Chippewa | 3C | Petroleum Liquids | IC |  | S | X | X | MIUP.DFTR13N1 |  | 2 | 0.9 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 12 | 2021 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N
Vintage1960 | petroleum | TRUE | 3828 | Cloverland Electric Co-op | 1868 | Dafter | MI | Chippewa | 4 | Petroleum Liquids | IC |  | S | X | X | MIUP.DFTR13N1 |  | 3 | 0.9 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 6 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage2021 | petroleum | TRUE | 3828 | Cloverland Electric Co-op | 1868 | Dafter | MI | Chippewa | 4C | Petroleum Liquids | IC |  | S | X | X | MIUP.DFTR13N1 |  | 2 | 0.9 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 12 | 2021 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N
Vintage1949 | hydro | TRUE | 19037 | Tower Kleber Ltd Partnership | 1871 | Kleber | MI | Cheboygan | K1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 1 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 1 | 1949 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1949 | hydro | TRUE | 19037 | Tower Kleber Ltd Partnership | 1871 | Kleber | MI | Cheboygan | K2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 1 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 1 | 1949 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1925 | hydro | TRUE | 19037 | Tower Kleber Ltd Partnership | 1871 | Kleber | MI | Cheboygan | T1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 1 | 1925 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1925 | hydro | TRUE | 19037 | Tower Kleber Ltd Partnership | 1871 | Kleber | MI | Cheboygan | T2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 1 | 1925 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1971 | petroleum | TRUE | 20910 | Wolverine Power Supply Coop | 1873 | Tower | MI | Cheboygan | GT4 | Petroleum Liquids | GT |  | S | X | X |  |  | 21.3 | 0.85 | 19.3 | 24.7 | 5 | N |  |  | OP | X | 3 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1949 | petroleum | TRUE | 18895 | Thumb Electric Coop of Mich | 1874 | Caro | MI | Tuscola | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1 | 1 | 0.5 | N |  |  | OP | X | 8 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage1949 | petroleum | TRUE | 18895 | Thumb Electric Coop of Mich | 1874 | Caro | MI | Tuscola | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1 | 1 | 0.5 | N |  |  | OP | X | 8 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N |  | N
Vintage1952 | petroleum | TRUE | 18895 | Thumb Electric Coop of Mich | 1874 | Caro | MI | Tuscola | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1 | 1 | 0.5 | N |  |  | OP | X | 8 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N |  | N
Vintage1984 | petroleum | TRUE | 18895 | Thumb Electric Coop of Mich | 1874 | Caro | MI | Tuscola | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 1 | 1.5 | 1.5 | 0.8 | N |  |  | OP | X | 8 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage1999 | petroleum | TRUE | 18895 | Thumb Electric Coop of Mich | 1874 | Caro | MI | Tuscola | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 1 | 2 | 2 | 1 | N |  |  | OP | X | 5 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage2000 | petroleum | TRUE | 18895 | Thumb Electric Coop of Mich | 1874 | Caro | MI | Tuscola | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 1 | 2 | 2 | 1 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage1938 | petroleum | TRUE | 18895 | Thumb Electric Coop of Mich | 1875 | Ubly | MI | Huron | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.3 | N |  |  | OP | X | 6 | 1938 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage1938 | petroleum | TRUE | 18895 | Thumb Electric Coop of Mich | 1875 | Ubly | MI | Huron | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.7 | 0.8 | 0.6 | 0.6 | 0.3 | N |  |  | OP | X | 6 | 1938 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage1938 | petroleum | TRUE | 18895 | Thumb Electric Coop of Mich | 1875 | Ubly | MI | Huron | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.7 | 0.8 | 0.7 | 0.7 | 0.4 | N |  |  | OP | X | 6 | 1938 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage1947 | petroleum | TRUE | 18895 | Thumb Electric Coop of Mich | 1875 | Ubly | MI | Huron | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.9 | 0.9 | 0.5 | N |  |  | OP | X | 8 | 1947 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage1987 | petroleum | TRUE | 18895 | Thumb Electric Coop of Mich | 1875 | Ubly | MI | Huron | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.8 | N |  |  | OP | X | 10 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage1993 | petroleum | TRUE | 18895 | Thumb Electric Coop of Mich | 1875 | Ubly | MI | Huron | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.8 | N |  |  | OP | X | 11 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2000 | petroleum | TRUE | 18895 | Thumb Electric Coop of Mich | 1875 | Ubly | MI | Huron | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 1.8 | N |  |  | OP | X | 5 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage2001 | petroleum | TRUE | 18895 | Thumb Electric Coop of Mich | 1875 | Ubly | MI | Huron | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 1.8 | N |  |  | OP | X | 10 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | petroleum | TRUE | 18895 | Thumb Electric Coop of Mich | 1875 | Ubly | MI | Huron | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 1 | 1.5 | 1.5 | 0.8 | N |  |  | OP | X | 8 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 20910 | Wolverine Power Supply Coop | 1877 | George Johnson | MI | Osceola | 10 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 25 | 0.85 | 24.3 | 30.4 | 19 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1993 | petroleum | TRUE | 20910 | Wolverine Power Supply Coop | 1877 | George Johnson | MI | Osceola | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.6 | N |  |  | SB | Y | 9 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage2000 | natural gas peaker | TRUE | 20910 | Wolverine Power Supply Coop | 1877 | George Johnson | MI | Osceola | 9 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 25 | 0.85 | 24.4 | 29.7 | 19 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2001 | natural gas peaker | TRUE | 20910 | Wolverine Power Supply Coop | 1880 | Claude Vandyke | MI | Allegan | 8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 24.8 | 0.8 | 20.2 | 27.3 | 17.4 | N |  |  | OP | X | 9 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1972 | natural gas peaker | TRUE | 20910 | Wolverine Power Supply Coop | 1881 | Vestaburg | MI | Montcalm | 8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 23.7 | 0.9 | 18.5 | 25.5 | 5 | N |  |  | OP | X | 7 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1953 | natural gas steam turbine | TRUE | 12647 | ALLETE, Inc. | 1891 | Syl Laskin | MN | St Louis | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | MP.LASKIN1 | MP.LASKIN1 | 58 | 0.85 | 49 | 49 | 17 | N |  |  | OP | X | 6 | 1953 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER |  | N |  |  | N | N | [14 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1953 | natural gas steam turbine | TRUE | 12647 | ALLETE, Inc. | 1891 | Syl Laskin | MN | St Louis | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | MP.LASKIN2 | MP.LASKIN2 | 58 | 0.85 | 49 | 49 | 17 | N |  |  | OP | X | 9 | 1953 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER |  | N |  |  | N | N | [14 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1925 | hydro | TRUE | 12647 | ALLETE, Inc. | 1892 | Blanchard | MN | Morrison | 1 | Conventional Hydroelectric | HY |  | S | X | X | MP.BLNCHR123 | MP.BLNCHR123 | 6 | 0.8 | 5.4 | 5.4 | 0.8 | N |  |  | OP | X | 2 | 1925 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1925 | hydro | TRUE | 12647 | ALLETE, Inc. | 1892 | Blanchard | MN | Morrison | 2 | Conventional Hydroelectric | HY |  | S | X | X | MP.BLNCHR123 | MP.BLNCHR123 | 6 | 0.8 | 5.4 | 5.4 | 0.8 | N |  |  | OP | X | 2 | 1925 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1988 | hydro | TRUE | 12647 | ALLETE, Inc. | 1892 | Blanchard | MN | Morrison | 3 | Conventional Hydroelectric | HY |  | S | X | X | MP.BLNCHR123 | MP.BLNCHR123 | 6 | 1 | 5.4 | 5.4 | 0.8 | N |  |  | OP | X | 8 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1973 | hard coal | TRUE | 12647 | ALLETE, Inc. | 1893 | Clay Boswell | MN | Itasca | 3 | Conventional Steam Coal | ST |  | S | X | X | MP.BOS233 | MP.BOS233 | 364.5 | 0.9 | 352 | 352 | 75 | N |  |  | OP | X | 5 | 1973 | 12 | 2029 | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: SUB; DFO DFO DFO: NG; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | N | [14 empty] | N |  |  | Y | Y | N
Vintage1980 | hard coal | TRUE | 12647 | ALLETE, Inc. | 1893 | Clay Boswell | MN | Itasca | 4 | Conventional Steam Coal | ST |  | J | X | X | MP.MP_BOS4 | MP.MP_BOS4 | 558 | 0.9 | 585 | 585 | 185 | N |  |  | OP | X | 5 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: SUB; DFO DFO DFO: NG; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | N | [14 empty] | N |  |  | Y | Y | N
Vintage1980 | petroleum | TRUE | 12647 | ALLETE, Inc. | 1893 | Clay Boswell | MN | Itasca | D4 | Petroleum Liquids | IC |  | J | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | N |  |  | SB | Y | 4 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [20 empty] | N |  |  | N
Vintage1924 | hydro | TRUE | 12647 | ALLETE, Inc. | 1894 | Fond Du Lac | MN | St Louis | 1 | Conventional Hydroelectric | HY |  | S | X | X | MP.FONDLA1 | MP.FONDLA1 | 12 | 0.8 | 13.1 | 13.1 | 0.5 | N |  |  | OP | X | 1 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1922 | hydro | TRUE | 12647 | ALLETE, Inc. | 1895 | Knife Falls | MN | Carlton | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.1 | N |  |  | OP | X | 1 | 1922 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1922 | hydro | TRUE | 12647 | ALLETE, Inc. | 1895 | Knife Falls | MN | Carlton | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.1 | N |  |  | OP | X | 1 | 1922 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1922 | hydro | TRUE | 12647 | ALLETE, Inc. | 1895 | Knife Falls | MN | Carlton | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 1 | 1922 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1919 | hydro | TRUE | 12647 | ALLETE, Inc. | 1896 | Little Falls (MN) | MN | Morrison | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 1 | 1919 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1919 | hydro | TRUE | 12647 | ALLETE, Inc. | 1896 | Little Falls (MN) | MN | Morrison | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 1 | 1919 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1920 | hydro | TRUE | 12647 | ALLETE, Inc. | 1896 | Little Falls (MN) | MN | Morrison | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.3 | N |  |  | OP | X | 1 | 1920 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1979 | hydro | TRUE | 12647 | ALLETE, Inc. | 1896 | Little Falls (MN) | MN | Morrison | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.8 | 1.3 | 1.3 | 0.5 | N |  |  | OP | X | 11 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1906 | hydro | TRUE | 12647 | ALLETE, Inc. | 1896 | Little Falls (MN) | MN | Morrison | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 1 | 1906 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1906 | hydro | TRUE | 12647 | ALLETE, Inc. | 1896 | Little Falls (MN) | MN | Morrison | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 1 | 1906 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1949 | biomass | TRUE | 12647 | ALLETE, Inc. | 1897 | M L Hibbard | MN | St Louis | 3 | Wood/Wood Waste Biomass | ST |  | S | X | X | MP.HIBBAR3 | MP.HIBBAR3 | 35.3 | 0.85 | 30 | 30 | 10 | N |  |  | OP | X | 6 | 1949 |  |  | Y | Commercial CHP | 5 | T | WDS | SUB | NG |  |  |  | NG | SUB | WDS |  | N | N |  | 12H |  | N | Y |  | Y | [15 empty] | N |  |  | Y | Y | N
Vintage1951 | biomass | TRUE | 12647 | ALLETE, Inc. | 1897 | M L Hibbard | MN | St Louis | 4 | Wood/Wood Waste Biomass | ST |  | S | X | X | MP.HIBBAR4 | MP.HIBBAR4 | 37.5 | 0.85 | 30 | 30 | 10 | N |  |  | OP | X | 6 | 1951 |  |  | Y | Commercial CHP | 5 | T | WDS | SUB | NG |  |  |  | NG | SUB | WDS |  | N | N |  | 12H |  | N | Y |  | Y | [15 empty] | N |  |  | Y | Y | N
Vintage1917 | hydro | TRUE | 12647 | ALLETE, Inc. | 1898 | Pillager | MN | Cass | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 1 | 1917 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1917 | hydro | TRUE | 12647 | ALLETE, Inc. | 1898 | Pillager | MN | Cass | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.1 | N |  |  | OP | X | 1 | 1917 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1923 | hydro | TRUE | 12647 | ALLETE, Inc. | 1899 | Scanlon | MN | Carlton | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 1 | 1923 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1923 | hydro | TRUE | 12647 | ALLETE, Inc. | 1899 | Scanlon | MN | Carlton | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 1 | 1923 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1923 | hydro | TRUE | 12647 | ALLETE, Inc. | 1899 | Scanlon | MN | Carlton | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 1 | 1923 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1923 | hydro | TRUE | 12647 | ALLETE, Inc. | 1899 | Scanlon | MN | Carlton | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 1 | 1923 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1913 | hydro | TRUE | 12647 | ALLETE, Inc. | 1900 | Sylvan | MN | Cass | 1 | Conventional Hydroelectric | HY |  | S | X | X | MP.LASKIN1 | MP.LASKIN1 | 0.6 | 1 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 1 | 1913 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1913 | hydro | TRUE | 12647 | ALLETE, Inc. | 1900 | Sylvan | MN | Cass | 2 | Conventional Hydroelectric | HY |  | S | X | X | MP.LASKIN2 | MP.LASKIN2 | 0.6 | 1 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 1 | 1913 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1915 | hydro | TRUE | 12647 | ALLETE, Inc. | 1900 | Sylvan | MN | Cass | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 1 | 1915 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1907 | hydro | TRUE | 12647 | ALLETE, Inc. | 1901 | Thomson | MN | Carlton | 1 | Conventional Hydroelectric | HY |  | S | X | X | MP.THOMSON | MP.THOMSON | 13 | 0.8 | 12.5 | 12.5 | 0.5 | N |  |  | OP | X | 1 | 1907 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1907 | hydro | TRUE | 12647 | ALLETE, Inc. | 1901 | Thomson | MN | Carlton | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 13 | 0.8 | 12.5 | 12.5 | 0.5 | N |  |  | OP | X | 1 | 1907 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1907 | hydro | TRUE | 12647 | ALLETE, Inc. | 1901 | Thomson | MN | Carlton | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 13 | 0.8 | 12.5 | 12.5 | 0.5 | N |  |  | OP | X | 1 | 1907 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1914 | hydro | TRUE | 12647 | ALLETE, Inc. | 1901 | Thomson | MN | Carlton | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10.8 | 0.8 | 12.1 | 12.1 | 0.5 | N |  |  | OP | X | 1 | 1914 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1919 | hydro | TRUE | 12647 | ALLETE, Inc. | 1901 | Thomson | MN | Carlton | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10.8 | 0.8 | 11.9 | 11.9 | 0.5 | N |  |  | OP | X | 1 | 1919 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1949 | hydro | TRUE | 12647 | ALLETE, Inc. | 1901 | Thomson | MN | Carlton | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 12 | 0.8 | 14.7 | 14.7 | 0.5 | N |  |  | OP | X | 1 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1923 | hydro | TRUE | 12647 | ALLETE, Inc. | 1902 | Winton | MN | Lake | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.8 | 2.1 | 2.1 | 0.3 | N |  |  | OP | X | 8 | 1923 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1923 | hydro | TRUE | 12647 | ALLETE, Inc. | 1902 | Winton | MN | Lake | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.3 | N |  |  | OP | X | 9 | 1923 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1954 | natural gas combined cycle | TRUE | 13781 | Northern States Power Co - Minnesota | 1904 | Black Dog | MN | Dakota | 2 | Natural Gas Fired Combined Cycle | CA | BDS0 | S | Y | X | NSP BLK_DOG BLK_DO_2_UNIT | CC_BLACKDOG52 | 136.9 | 0.88 | 117 | 117 | 66 | N |  |  | OP | X | 10 | 1954 | 12 | 2031 | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | bar: X X X to DFO RC RC
Vintage2002 | natural gas combined cycle | TRUE | 13781 | Northern States Power Co - Minnesota | 1904 | Black Dog | MN | Dakota | 5 | Natural Gas Fired Combined Cycle | CT | BDS0 | S | X | Y | NSP BLK_DOG BLK_DO_5_UNIT | NSP BLK_DOG BLK_DO_5_UNIT | 187.9 | 0.85 | 165 | 181 | 94 | N |  |  | OP | X | 6 | 2002 | 12 | 2031 | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2018 | natural gas peaker | TRUE | 13781 | Northern States Power Co - Minnesota | 1904 | Black Dog | MN | Dakota | 6-1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | NSP.BLKDO6 | NSP BLK_DOG BLK_DO_6_UNIT | 238 | 0.85 | 212 | 228 | 60 | N |  |  | OP | X | 4 | 2018 | 12 | 2058 | N | Electric Utility | 1 | [14 empty] | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1954 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 1911 | Hennepin Island | MN | Hennepin | 1 | Conventional Hydroelectric | HY |  | S | X | X | NSP MAIN_ST MAIN_S_1 | NSP MAIN_ST MAIN_S_1 | 2.8 | 0.9 | 1.2 | 1.4 | 0.6 | N |  |  | OP | X | 10 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1955 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 1911 | Hennepin Island | MN | Hennepin | 2 | Conventional Hydroelectric | HY |  | S | X | X | NSP MAIN_ST MAIN_S_1 | NSP MAIN_ST MAIN_S_1 | 2.8 | 0.9 | 1.2 | 1.4 | 0.6 | N |  |  | OP | X | 3 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1955 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 1911 | Hennepin Island | MN | Hennepin | 3 | Conventional Hydroelectric | HY |  | S | X | X | NSP MAIN_ST MAIN_S_1 | NSP MAIN_ST MAIN_S_1 | 2.8 | 0.9 | 1.2 | 1.4 | 0.6 | N |  |  | OP | X | 10 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1954 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 1911 | Hennepin Island | MN | Hennepin | 4 | Conventional Hydroelectric | HY |  | S | X | X | NSP MAIN_ST MAIN_S_1 | NSP MAIN_ST MAIN_S_1 | 2.8 | 0.9 | 1.2 | 1.4 | 0.6 | N |  |  | OP | X | 10 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1955 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 1911 | Hennepin Island | MN | Hennepin | 5 | Conventional Hydroelectric | HY |  | S | X | X | NSP MAIN_ST MAIN_S_1 | NSP MAIN_ST MAIN_S_1 | 2.5 | 0.8 | 1.3 | 1.5 | 0.6 | N |  |  | OP | X | 11 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage2008 | natural gas combined cycle | TRUE | 13781 | Northern States Power Co - Minnesota | 1912 | High Bridge | MN | Ramsey | 7 | Natural Gas Fired Combined Cycle | CT | HBR0 | S | X | Y | NSP HIBRDGE HIBRDG_7_UNIT | NSP HIBRDGE HIBRDG_7_UNIT | 197 | 0.85 | 152 | 185 | 88 | N |  |  | OP | X | 5 | 2008 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | bar: X X X to DFO RC RC
Vintage2008 | natural gas combined cycle | TRUE | 13781 | Northern States Power Co - Minnesota | 1912 | High Bridge | MN | Ramsey | 8 | Natural Gas Fired Combined Cycle | CT | HBR0 | S | X | Y | NSP HIBRDGE HIBRDG_8_UNIT | NSP HIBRDGE HIBRDG_8_UNIT | 197 | 0.85 | 152 | 185 | 88 | N |  |  | OP | X | 5 | 2008 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | bar: X X X to DFO RC RC
Vintage2008 | natural gas combined cycle | TRUE | 13781 | Northern States Power Co - Minnesota | 1912 | High Bridge | MN | Ramsey | 9 | Natural Gas Fired Combined Cycle | CA | HBR0 | S | Y | X | NSP HIBRDGE HIBRD9_1_UNIT | NSP HIBRDGE HIBRD9_1_UNIT | 250 | 0.85 | 226 | 236 | 162 | N |  |  | OP | X | 5 | 2008 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | bar: X X X to DFO RC RC
Vintage1972 | natural gas peaker | TRUE | 13781 | Northern States Power Co - Minnesota | 1913 | Inver Hills | MN | Dakota | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | NSP INVRHLS INVRHL_1_UNIT | NSP INVRHLS INVRHL_1_UNIT | 46.8 | 0.85 | 47 | 62 | 10 | N |  |  | OP | X | 4 | 1972 | 12 | 2026 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1972 | natural gas peaker | TRUE | 13781 | Northern States Power Co - Minnesota | 1913 | Inver Hills | MN | Dakota | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | NSP INVRHLS INVRHL_2_UNIT | NSP INVRHLS INVRHL_2_UNIT | 46.8 | 0.85 | 47 | 62 | 10 | N |  |  | OP | X | 4 | 1972 | 12 | 2026 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1972 | natural gas peaker | TRUE | 13781 | Northern States Power Co - Minnesota | 1913 | Inver Hills | MN | Dakota | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | NSP INVRHLS INVRHL_3_UNIT | NSP INVRHLS INVRHL_3_UNIT | 46.8 | 0.85 | 47 | 62 | 10 | N |  |  | OP | X | 4 | 1972 | 12 | 2026 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1972 | natural gas peaker | TRUE | 13781 | Northern States Power Co - Minnesota | 1913 | Inver Hills | MN | Dakota | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | NSP INVRHLS INVRHL_4_UNIT | NSP INVRHLS INVRHL_4_UNIT | 46.8 | 0.85 | 47 | 62 | 10 | N |  |  | OP | X | 4 | 1972 | 12 | 2026 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1972 | natural gas peaker | TRUE | 13781 | Northern States Power Co - Minnesota | 1913 | Inver Hills | MN | Dakota | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | NSP INVRHLS INVRHL_5_UNIT | NSP INVRHLS INVRHL_5_UNIT | 46.8 | 0.85 | 47 | 61 | 10 | N |  |  | OP | X | 4 | 1972 | 12 | 2026 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1972 | natural gas peaker | TRUE | 13781 | Northern States Power Co - Minnesota | 1913 | Inver Hills | MN | Dakota | 6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | NSP INVRHLS INVRHL_6_UNIT | NSP INVRHLS INVRHL_6_UNIT | 46.8 | 0.85 | 47 | 62 | 10 | N |  |  | OP | X | 4 | 1972 | 12 | 2026 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1997 | petroleum | TRUE | 13781 | Northern States Power Co - Minnesota | 1913 | Inver Hills | MN | Dakota | 7 | Petroleum Liquids | GT |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.8 | N |  |  | SB | Y | 6 | 1997 | 12 | 2026 | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N
Vintage1997 | petroleum | TRUE | 13781 | Northern States Power Co - Minnesota | 1913 | Inver Hills | MN | Dakota | 8 | Petroleum Liquids | GT |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.8 | N |  |  | SB | Y | 6 | 1997 | 12 | 2026 | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N
Vintage1958 | hard coal | TRUE | 13781 | Northern States Power Co - Minnesota | 1915 | Allen S King | MN | Washington | 1 | Conventional Steam Coal | ST |  | S | X | X | NSP KING KING_1_UNIT | NSP KING KING_1_UNIT | 598.4 | 0.85 | 511 | 511 | 345 | N |  |  | OP | X | 3 | 1958 |  |  | N | Electric Utility | 1 | X | SUB | NG | DFO |  |  |  | NG | DFO |  |  | N | N |  | OVER |  | N |  | Y |  | Y | [17 empty] | Y | N | N
Vintage1971 | nuclear | TRUE | 13781 | Northern States Power Co - Minnesota | 1922 | Monticello Nuclear Facility | MN | Wright | 1 | Nuclear | ST |  | S | X | X | NSP MNTCELO MNTCEL_1_UNIT | NSP MNTCELO MNTCEL_1_UNIT | 685 | 0.95 | 617 | 646 | 500 | N |  |  | OP | X | 6 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1974 | nuclear | TRUE | 13781 | Northern States Power Co - Minnesota | 1925 | Prairie Island | MN | Goodhue | 1 | Nuclear | ST |  | S | X | X | NSP PR_ISLD PR_ISL_1_UNIT | NSP PR_ISLD PR_ISL_1_UNIT | 593.1 | 0.9 | 521 | 546 | 500 | N |  |  | OP | X | 2 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N
Vintage1974 | nuclear | TRUE | 13781 | Northern States Power Co - Minnesota | 1925 | Prairie Island | MN | Goodhue | 2 | Nuclear | ST |  | S | X | X | NSP PR_ISLD PR_ISL_2_UNIT | NSP PR_ISLD PR_ISL_2_UNIT | 593.1 | 0.9 | 519 | 546 | 500 | N |  |  | OP | X | 10 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N
Vintage1949 | municipal solid waste | TRUE | 13781 | Northern States Power Co - Minnesota | 1926 | Red Wing | MN | Goodhue | 1 | Municipal Solid Waste | ST |  | S | X | X | NSP REDWING REDWIN_1_UNIT | NSP REDWING REDWIN_1_UNIT | 11.5 | 0.85 | 9 | 9 | 6 | N |  |  | OP | X | 10 | 1949 | 12 | 2027 | N | Electric Utility | 1 | X X X: X; DFO RC RC: MSW; DFO SUB SUB: WDS; DFO DFO DFO: NG; DFO DFO DFO: NG |  |  | N | N |  | 12H |  |  | N |  | N | [18 empty] | Y | Y | N
Vintage1949 | municipal solid waste | TRUE | 13781 | Northern States Power Co - Minnesota | 1926 | Red Wing | MN | Goodhue | 2 | Municipal Solid Waste | ST |  | S | X | X | NSP REDWING REDWIN_2_UNIT | NSP REDWING REDWIN_2_UNIT | 11.5 | 0.85 | 9 | 9 | 6 | N |  |  | OP | X | 11 | 1949 | 12 | 2027 | N | Electric Utility | 1 | X X X: X; DFO RC RC: MSW; DFO SUB SUB: WDS; DFO DFO DFO: NG; DFO DFO DFO: NG |  |  | N | N |  | 12H |  |  | N |  | N | [18 empty] | Y | Y | N
Vintage2009 | natural gas combined cycle | TRUE | 13781 | Northern States Power Co - Minnesota | 1927 | Riverside (MN) | MN | Hennepin | 10 | Natural Gas Fired Combined Cycle | CT | RIV0 | S | X | Y | NSP RIVRSID RIVRS_10_UN | NSP RIVRSID RIVRS_10_UN | 210.6 | 0.9 | 147 | 171 | 79 | N |  |  | OP | X | 5 | 2009 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | N
Vintage2009 | natural gas combined cycle | TRUE | 13781 | Northern States Power Co - Minnesota | 1927 | Riverside (MN) | MN | Hennepin | 9 | Natural Gas Fired Combined Cycle | CT | RIV0 | S | X | Y | NSP RIVRSID RIVRSI_9_UN | NSP RIVRSID RIVRSI_9_UN | 210.6 | 0.9 | 147 | 171 | 79 | N |  |  | OP | X | 5 | 2009 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | N
Vintage1987 | natural gas combined cycle | TRUE | 13781 | Northern States Power Co - Minnesota | 1927 | Riverside (MN) | MN | Hennepin | ST7 | Natural Gas Fired Combined Cycle | CA | RIV0 | S | N | X | NSP RIVRSID RIVRSI_7_UN1 | NSP RIVRSID RIVRSI_7_UN1 | 164.7 | 0.9 | 160 | 158 | 76 | N |  |  | OP | X | 4 | 1987 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H |  | N | [21 empty] | N | N | bar: X X X to DFO RC RC
Vintage2002 | petroleum | TRUE | 17876 | City of St James - (MN) | 1929 | St James | MN | Watonwan | 1 | Petroleum Liquids | IC |  | S | X | X | NSP.MRES.STJM |  | 2 | 0.8 | 2 | 2 | 1.5 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage2002 | petroleum | TRUE | 17876 | City of St James - (MN) | 1929 | St James | MN | Watonwan | 2 | Petroleum Liquids | IC |  | S | X | X | NSP.MRES.STJM |  | 2 | 0.8 | 2 | 2 | 1.5 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage2002 | petroleum | TRUE | 17876 | City of St James - (MN) | 1929 | St James | MN | Watonwan | 3 | Petroleum Liquids | IC |  | S | X | X | NSP.MRES.STJM |  | 2 | 0.8 | 2 | 2 | 1.5 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage2002 | petroleum | TRUE | 17876 | City of St James - (MN) | 1929 | St James | MN | Watonwan | 4 | Petroleum Liquids | IC |  | S | X | X | NSP.MRES.STJM |  | 2 | 0.8 | 2 | 2 | 1.5 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage2002 | petroleum | TRUE | 17876 | City of St James - (MN) | 1929 | St James | MN | Watonwan | 5 | Petroleum Liquids | IC |  | S | X | X | NSP.MRES.STJM |  | 2 | 0.8 | 2 | 2 | 1.5 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage2002 | petroleum | TRUE | 17876 | City of St James - (MN) | 1929 | St James | MN | Watonwan | 6 | Petroleum Liquids | IC |  | S | X | X | NSP.MRES.STJM |  | 2 | 0.8 | 2 | 2 | 1.5 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage1948 | municipal solid waste | TRUE | 13781 | Northern States Power Co - Minnesota | 1934 | Wilmarth | MN | Blue Earth | 1 | Municipal Solid Waste | ST |  | S | X | X | NSP WILMART WILMAR_1_UNIT | NSP WILMART WILMAR_1_UNIT | 12.5 | 0.8 | 9 | 9 | 1 | N |  |  | OP | X | 9 | 1948 | 12 | 2027 | N | Electric Utility | 1 | X X X: X; DFO RC RC: MSW; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1951 | municipal solid waste | TRUE | 13781 | Northern States Power Co - Minnesota | 1934 | Wilmarth | MN | Blue Earth | 2 | Municipal Solid Waste | ST |  | S | X | X | NSP WILMART WILMAR_2_UNIT | NSP WILMART WILMAR_2_UNIT | 12.5 | 0.8 | 9 | 9 | 1 | N |  |  | OP | X | 3 | 1951 | 12 | 2027 | N | Electric Utility | 1 | X X X: X; DFO RC RC: MSW; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1914 | hydro | TRUE | 14232 | Otter Tail Power Co | 1943 | Hoot Lake | MN | Otter Tail | H1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.8 | 0.8 | 0.8 | 0 | N |  |  | OP | X | 9 | 1914 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage2005 | petroleum | TRUE | 150 | Adrian Public Utilities Comm | 1956 | Adrian | MN | Nobles | 5 | Petroleum Liquids | IC |  | S | X | X | ALTW.MRES |  | 2 | 0.8 | 2 | 2 | 0.8 | N |  |  | OP | X | 5 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage1948 | petroleum | TRUE | 295 | City of Alexandria - (MN) | 1958 | Alexandria | MN | Douglas | IC1 | Petroleum Liquids | IC |  | S | X | X | OTP.MRES |  | 1.2 | 0.8 | 1 | 1 | 0.1 | N |  |  | SB | Y | 1 | 1948 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N |  | N
Vintage1967 | petroleum | TRUE | 295 | City of Alexandria - (MN) | 1958 | Alexandria | MN | Douglas | IC2 | Petroleum Liquids | IC |  | S | X | X | OTP.MRES |  | 4 | 0.8 | 3.6 | 3.6 | 0.1 | N |  |  | SB | Y | 1 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [20 empty] | N |  |  | N |  | N
Vintage1967 | petroleum | TRUE | 295 | City of Alexandria - (MN) | 1958 | Alexandria | MN | Douglas | IC3 | Petroleum Liquids | IC |  | S | X | X | OTP.MRES |  | 4 | 0.8 | 3.6 | 3.6 | 0.1 | N |  |  | SB | Y | 1 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [20 empty] | N |  |  | N |  | N
Vintage2002 | petroleum | TRUE | 1573 | City of Benson - (MN) | 1964 | Benson City of | MN | Swift | 10 | Petroleum Liquids | IC |  | S | X | X | OTP.MRES |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.4 | N |  |  | OP | X | 5 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage2002 | petroleum | TRUE | 1573 | City of Benson - (MN) | 1964 | Benson City of | MN | Swift | 11 | Petroleum Liquids | IC |  | S | X | X | OTP.MRES |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.4 | N |  |  | OP | X | 5 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage2002 | petroleum | TRUE | 1573 | City of Benson - (MN) | 1964 | Benson City of | MN | Swift | 7 | Petroleum Liquids | IC |  | S | X | X | OTP.MRES |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.4 | N |  |  | OP | X | 5 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage2002 | petroleum | TRUE | 1573 | City of Benson - (MN) | 1964 | Benson City of | MN | Swift | 8 | Petroleum Liquids | IC |  | S | X | X | OTP.MRES |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.4 | N |  |  | OP | X | 5 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage2002 | petroleum | TRUE | 1573 | City of Benson - (MN) | 1964 | Benson City of | MN | Swift | 9 | Petroleum Liquids | IC |  | S | X | X | OTP.MRES |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.4 | N |  |  | OP | X | 5 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage1974 | petroleum | TRUE | 1871 | City of Blooming Prairie - (MN) | 1966 | Blooming Prairie | MN | Steele | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.96 | 1.3 | 1.3 | 0.8 | N |  |  | SB | Y | 8 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage2003 | petroleum | TRUE | 1871 | City of Blooming Prairie - (MN) | 1966 | Blooming Prairie | MN | Steele | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.3 | 0.96 | 2 | 2 | 1 | N |  |  | SB | Y | 4 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N | N | N
Vintage2009 | petroleum | TRUE | 1871 | City of Blooming Prairie - (MN) | 1966 | Blooming Prairie | MN | Steele | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.96 | 1.9 | 1.9 | 1 | N |  |  | SB | Y | 4 | 2009 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N | N | N
Vintage2012 | petroleum | TRUE | 1871 | City of Blooming Prairie - (MN) | 1966 | Blooming Prairie | MN | Steele | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.96 | 1.3 | 1.3 | 1.3 | N |  |  | SB | Y | 10 | 2012 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H |  |  |  | N | [19 empty] | N | N | N
Vintage1960 | petroleum | TRUE | 1883 | Blue Earth Light & Water | 1967 | Blue Earth | MN | Faribault | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.9 | 1.5 | 1.5 | 0.5 | N |  |  | OP | X | 11 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1993 | petroleum | TRUE | 1883 | Blue Earth Light & Water | 1967 | Blue Earth | MN | Faribault | IC3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.9 | 1.6 | 1.6 | 0.5 | N |  |  | OP | X | 11 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage1993 | petroleum | TRUE | 1883 | Blue Earth Light & Water | 1967 | Blue Earth | MN | Faribault | IC4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.9 | 1.6 | 1.6 | 0.5 | N |  |  | OP | X | 11 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage1993 | petroleum | TRUE | 1883 | Blue Earth Light & Water | 1967 | Blue Earth | MN | Faribault | IC5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.9 | 1.6 | 1.6 | 0.5 | N |  |  | OP | X | 11 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1996 | petroleum | TRUE | 1883 | Blue Earth Light & Water | 1967 | Blue Earth | MN | Faribault | IC6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.9 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 2 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [20 empty] | N |  |  | N | N
Vintage2015 | petroleum | TRUE | 1883 | Blue Earth Light & Water | 1967 | Blue Earth | MN | Faribault | IC7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.9 | 1.1 | 1.1 | 0.5 | N |  |  | OP | X | 9 | 2015 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [20 empty] | N |  |  | N | N
Vintage2015 | petroleum | TRUE | 1883 | Blue Earth Light & Water | 1967 | Blue Earth | MN | Faribault | IC8 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.9 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 9 | 2015 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [20 empty] | N |  |  | N | N
Vintage1972 | natural gas peaker | TRUE | 5015 | Delano Municipal Utilities | 1969 | Delano | MN | Wright | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.3 | N |  |  | OP | X | 11 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1973 | natural gas peaker | TRUE | 5015 | Delano Municipal Utilities | 1969 | Delano | MN | Wright | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 0.4 | N |  |  | OP | X | 3 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1946 | petroleum | TRUE | 5015 | Delano Municipal Utilities | 1969 | Delano | MN | Wright | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 10 | 1946 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage1989 | petroleum | TRUE | 5015 | Delano Municipal Utilities | 1969 | Delano | MN | Wright | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 0.4 | N |  |  | OP | X | 8 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage1994 | petroleum | TRUE | 5015 | Delano Municipal Utilities | 1969 | Delano | MN | Wright | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 0.9 | N |  |  | OP | X | 8 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage1999 | petroleum | TRUE | 5015 | Delano Municipal Utilities | 1969 | Delano | MN | Wright | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.1 | 0.8 | 3.1 | 3.1 | 0.9 | N |  |  | OP | X | 6 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage1968 | petroleum | TRUE | 5111 | City of Detroit Lakes - (MN) | 1970 | Detroit Lakes | MN | Becker | 1 | Petroleum Liquids | GT |  | S | X | X | OTP.MRES |  | 12.5 | 0.8 | 9.6 | 10.6 | 5 | N |  |  | OP | X | 7 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage1948 | petroleum | TRUE | 5773 | City of Elk River | 1971 | Elk River City of | MN | Sherburne | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.4 | N |  |  | SB | Y | 3 | 1948 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | U |  | N
Vintage1948 | petroleum | TRUE | 5773 | City of Elk River | 1971 | Elk River City of | MN | Sherburne | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.4 | N |  |  | SB | Y | 3 | 1948 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | U |  | N
Vintage1962 | petroleum | TRUE | 5773 | City of Elk River | 1971 | Elk River City of | MN | Sherburne | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 2.8 | N |  |  | SB | Y | 3 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1972 | petroleum | TRUE | 5773 | City of Elk River | 1971 | Elk River City of | MN | Sherburne | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 5 | 0.8 | 5 | 5 | 4.3 | N |  |  | SB | Y | 8 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | biomass | TRUE | 5773 | City of Elk River | 1971 | Elk River City of | MN | Sherburne | 5 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.2 | N |  |  | OP | X | 10 | 2002 | 10 | 2022 | N | Electric Utility | 1 | X X X: X; DFO RC RC: LFG |  |  | N | N |  | 1H | [23 empty] | U |  | N
Vintage2002 | biomass | TRUE | 5773 | City of Elk River | 1971 | Elk River City of | MN | Sherburne | 6 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.2 | N |  |  | OP | X | 10 | 2002 | 10 | 2022 | N | Electric Utility | 1 | X X X: X; DFO RC RC: LFG |  |  | N | N |  | 1H | [23 empty] | U |  | N
Vintage2002 | biomass | TRUE | 5773 | City of Elk River | 1971 | Elk River City of | MN | Sherburne | 7 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.2 | N |  |  | OP | X | 10 | 2002 | 10 | 2022 | N | Electric Utility | 1 | X X X: X; DFO RC RC: LFG |  |  | N | N |  | 1H | [23 empty] | U |  | N
Vintage2006 | biomass | TRUE | 5773 | City of Elk River | 1971 | Elk River City of | MN | Sherburne | 8 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.2 | N |  |  | OP | X | 7 | 2006 | 10 | 2022 | N | Electric Utility | 1 | X X X: X; DFO RC RC: LFG |  |  | N | N |  | 1H | [23 empty] | U |  | N
Vintage2001 | petroleum | TRUE | 6138 | City of Fairfax - (MN) | 1972 | Fairfax | MN | Renville | 2A | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.9 | 1.9 | 1.5 | N |  |  | SB | Y | 8 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N | N | N
Vintage2014 | natural gas peaker | TRUE | 40580 | Southern Minnesota Mun P Agny | 1973 | Fairmont (MN) | MN | Martin | 10 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | ALTW.FAIR_SIG | ALTW.FAIR_SIG | 6.5 | 0.8 | 6.5 | 6.5 | 3 | N |  |  | OP | X | 3 | 2014 |  |  | N | Electric Utility | 1 | [14 empty] | 1H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2014 | natural gas peaker | TRUE | 40580 | Southern Minnesota Mun P Agny | 1973 | Fairmont (MN) | MN | Martin | 11 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | ALTW.FAIR_SIG | ALTW.FAIR_SIG | 6.5 | 0.8 | 6.5 | 6.5 | 3 | N |  |  | OP | X | 3 | 2014 |  |  | N | Electric Utility | 1 | [14 empty] | 1H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2014 | natural gas peaker | TRUE | 40580 | Southern Minnesota Mun P Agny | 1973 | Fairmont (MN) | MN | Martin | 12 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | ALTW.FAIR_SIG | ALTW.FAIR_SIG | 6.5 | 0.8 | 6.5 | 6.5 | 3 | N |  |  | OP | X | 3 | 2014 |  |  | N | Electric Utility | 1 | [14 empty] | 1H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1975 | petroleum | TRUE | 40580 | Southern Minnesota Mun P Agny | 1973 | Fairmont (MN) | MN | Martin | 6 | Petroleum Liquids | IC |  | S | X | X | ALTW.FAIR_DSL | ALTW.FAIR_DSL | 6.5 | 0.8 | 6 | 6 | 3.5 | N |  |  | OP | X | 1 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1975 | petroleum | TRUE | 40580 | Southern Minnesota Mun P Agny | 1973 | Fairmont (MN) | MN | Martin | 7 | Petroleum Liquids | IC |  | S | X | X | ALTW.FAIR_DSL | ALTW.FAIR_DSL | 6.5 | 0.8 | 6 | 6 | 3.5 | N |  |  | OP | X | 1 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage2014 | natural gas peaker | TRUE | 40580 | Southern Minnesota Mun P Agny | 1973 | Fairmont (MN) | MN | Martin | 9 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | ALTW.FAIR_SIG | ALTW.FAIR_SIG | 6.5 | 0.8 | 6.5 | 6.5 | 3 | N |  |  | OP | X | 3 | 2014 |  |  | N | Electric Utility | 1 | [14 empty] | 1H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1985 | petroleum | TRUE | 7292 | Glencoe Light & Power Comm | 1975 | Glencoe | MN | McLeod | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 7 | 0.8 | 5.6 | 5.6 | 3 | N |  |  | OP | X | 10 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1998 | petroleum | TRUE | 7292 | Glencoe Light & Power Comm | 1975 | Glencoe | MN | McLeod | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.8 | 0.8 | 4.8 | 4.8 | 2 | N |  |  | OP | X | 6 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1998 | petroleum | TRUE | 7292 | Glencoe Light & Power Comm | 1975 | Glencoe | MN | McLeod | 12 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.8 | 0.8 | 4.8 | 4.8 | 2 | N |  |  | OP | X | 7 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2006 | petroleum | TRUE | 7292 | Glencoe Light & Power Comm | 1975 | Glencoe | MN | McLeod | 14 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.8 | 0.8 | 4.8 | 4.8 | 2 | N |  |  | OP | X | 9 | 2006 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1957 | petroleum | TRUE | 7292 | Glencoe Light & Power Comm | 1975 | Glencoe | MN | McLeod | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1 | 1 | 0.5 | N |  |  | OP | X | 6 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1966 | petroleum | TRUE | 7292 | Glencoe Light & Power Comm | 1975 | Glencoe | MN | McLeod | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.1 | 0.8 | 3.2 | 3.2 | 2 | N |  |  | OP | X | 11 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1969 | petroleum | TRUE | 7292 | Glencoe Light & Power Comm | 1975 | Glencoe | MN | McLeod | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 5.6 | 0.8 | 5.4 | 5.4 | 2 | N |  |  | OP | X | 7 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1973 | petroleum | TRUE | 7292 | Glencoe Light & Power Comm | 1975 | Glencoe | MN | McLeod | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 7.1 | 0.8 | 6.1 | 6.1 | 3 | N |  |  | OP | X | 8 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2004 | petroleum | TRUE | 7487 | City of Grand Marais - (MN) | 1976 | Grand Marais | MN | Cook | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2.5 | 2.5 | 1.8 | N |  |  | OP | X | 2 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage2004 | petroleum | TRUE | 7487 | City of Grand Marais - (MN) | 1976 | Grand Marais | MN | Cook | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 2 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage2004 | petroleum | TRUE | 7487 | City of Grand Marais - (MN) | 1976 | Grand Marais | MN | Cook | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 2 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage1940 | hydro | TRUE | 7494 | City of Granite Falls - (MN) | 1977 | Granite Falls | MN | Chippewa | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.8 | 0.2 | 0.2 | 0.2 | N |  |  | OP | X | 8 | 1940 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1932 | hydro | TRUE | 7494 | City of Granite Falls - (MN) | 1977 | Granite Falls | MN | Chippewa | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0.2 | N |  |  | OP | X | 8 | 1932 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1986 | hydro | TRUE | 7494 | City of Granite Falls - (MN) | 1977 | Granite Falls | MN | Chippewa | HC3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.834 | 0.7 | 0.7 | 0.7 | N |  |  | OS | X | 6 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [15 empty] | HA | WAT | 0.8 | 6 | 2022 |  |  |  | N
Vintage1965 | hard coal | TRUE | 8543 | Hibbing Public Utilities Comm | 1979 | Hibbing | MN | St Louis | 3 | Conventional Steam Coal | ST |  | S | X | X | MISO | MISO | 10 | 0.8 | 10 | 10 | 4 | N |  |  | SB | Y | 4 | 1965 |  |  | Y | Electric Utility | 1 | T | SUB | NG | WDS | BIT | LIG |  | NG | SUB | WDS |  | N | N |  | 12H |  | N | Y |  | Y | [18 empty] | Y | Y | N
Vintage1985 | hard coal | TRUE | 8543 | Hibbing Public Utilities Comm | 1979 | Hibbing | MN | St Louis | 5 | Conventional Steam Coal | ST |  | S | X | X | MISO | MISO | 19.5 | 0.85 | 19.5 | 19.5 | 5 | N |  |  | SB | Y | 8 | 1985 |  |  | Y | Electric Utility | 1 | T | SUB | NG | WDS | BIT | LIG |  | NG | SUB | WDS |  | N | N |  | 12H |  | N | Y |  | Y | [18 empty] | Y | Y | N
Vintage1996 | hard coal | TRUE | 8543 | Hibbing Public Utilities Comm | 1979 | Hibbing | MN | St Louis | 6 | Conventional Steam Coal | ST |  | S | X | X | MISO | MISO | 6.4 | 0.85 | 1 | 6.4 | 1 | N |  |  | SB | Y | 2 | 1996 |  |  | Y | Electric Utility | 1 | T | SUB | NG | WDS | BIT | LIG |  | NG | SUB | WDS |  | N | N |  | 12H |  |  | Y |  | Y | [18 empty] | Y | Y | N
Vintage2013 | natural gas peaker | TRUE | 9130 | Hutchinson Utilities Comm | 1980 | Hutchinson Plant #1 | MN | McLeod | 10 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | GRE.HUC | GRE.HUC | 8.8 | 0.8 | 9.3 | 9.3 | 1 | N |  |  | OP | X | 2 | 2013 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2019 | natural gas peaker | TRUE | 9130 | Hutchinson Utilities Comm | 1980 | Hutchinson Plant #1 | MN | McLeod | 11 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | GRE.HUC | GRE.HUC | 9.8 | 0.8 | 9.8 | 9.8 | 1 | N |  |  | OP | X | 11 | 2019 |  |  | N | Electric Utility | 1 | [14 empty] | 10M | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2019 | natural gas peaker | TRUE | 9130 | Hutchinson Utilities Comm | 1980 | Hutchinson Plant #1 | MN | McLeod | 12 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | GRE.HUC | GRE.HUC | 9.8 | 0.8 | 9.8 | 9.8 | 1 | N |  |  | OP | X | 11 | 2019 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1968 | natural gas peaker | TRUE | 9130 | Hutchinson Utilities Comm | 1980 | Hutchinson Plant #1 | MN | McLeod | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | GRE.HUC | GRE.HUC | 4.5 | 0.8 | 3.9 | 3.9 | 3 | N |  |  | OP | X | 1 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | N
Vintage1965 | petroleum | TRUE | 9650 | City of Janesville - (MN) | 1982 | Janesville | MN | Waseca | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 0.9 | 1 | 0.5 | N |  |  | OP | X | 5 | 1965 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | Y | Y
Vintage1972 | petroleum | TRUE | 9650 | City of Janesville - (MN) | 1982 | Janesville | MN | Waseca | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.1 | 1.2 | 0.6 | N |  |  | OP | X | 5 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | Y | Y
Vintage1955 | petroleum | TRUE | 9650 | City of Janesville - (MN) | 1982 | Janesville | MN | Waseca | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.7 | 0.8 | 0.5 | 0.6 | 0.3 | N |  |  | OP | X | 5 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | Y | Y
Vintage1998 | petroleum | TRUE | 9650 | City of Janesville - (MN) | 1982 | Janesville | MN | Waseca | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.9 | N |  |  | OP | X | 12 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1997 | petroleum | TRUE | 10179 | Kenyon Municipal Utilities | 1983 | Kenyon Municipal | MN | Goodhue | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0 | N |  |  | SB | Y | 8 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1997 | petroleum | TRUE | 10179 | Kenyon Municipal Utilities | 1983 | Kenyon Municipal | MN | Goodhue | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0 | N |  |  | SB | Y | 8 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1997 | petroleum | TRUE | 10179 | Kenyon Municipal Utilities | 1983 | Kenyon Municipal | MN | Goodhue | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0 | N |  |  | SB | Y | 8 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1952 | petroleum | TRUE | 10596 | City of Lake Crystal - (MN) | 1985 | Lake Crystal | MN | Blue Earth | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.95 | 0.6 | 0.6 | 0.6 | N |  |  | OP | X | 5 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1971 | petroleum | TRUE | 10596 | City of Lake Crystal - (MN) | 1985 | Lake Crystal | MN | Blue Earth | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.95 | 2 | 2 | 2 | N |  |  | OP | X | 5 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1955 | petroleum | TRUE | 10596 | City of Lake Crystal - (MN) | 1985 | Lake Crystal | MN | Blue Earth | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.95 | 1.2 | 1.2 | 1.2 | N |  |  | OP | X | 5 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 10596 | City of Lake Crystal - (MN) | 1985 | Lake Crystal | MN | Blue Earth | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.95 | 2 | 2 | 2 | N |  |  | OP | X | 11 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1923 | hydro | TRUE | 10685 | Lanesboro Public Utility Comm | 1987 | Lanesboro | MN | Fillmore | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1923 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage2004 | petroleum | TRUE | 10685 | Lanesboro Public Utility Comm | 1987 | Lanesboro | MN | Fillmore | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.3 | 0.8 | 2.1 | 2.1 | 1 | N |  |  | OP | X | 6 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1963 | petroleum | TRUE | 11064 | Litchfield Public Utilities | 1989 | Litchfield | MN | Meeker | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.1 | 0.8 | 2.1 | 2.1 | 1 | N |  |  | SB | Y | 9 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1963 | petroleum | TRUE | 11064 | Litchfield Public Utilities | 1989 | Litchfield | MN | Meeker | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.1 | 0.8 | 2.1 | 2.1 | 1 | N |  |  | SB | Y | 10 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage2010 | petroleum | TRUE | 11064 | Litchfield Public Utilities | 1989 | Litchfield | MN | Meeker | QS 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.3 | 0.8 | 2.3 | 2.3 | 1 | N |  |  | SB | Y | 4 | 2010 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage2010 | petroleum | TRUE | 11064 | Litchfield Public Utilities | 1989 | Litchfield | MN | Meeker | QS 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.3 | 0.8 | 2.3 | 2.3 | 1 | N |  |  | SB | Y | 4 | 2010 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage2010 | petroleum | TRUE | 11064 | Litchfield Public Utilities | 1989 | Litchfield | MN | Meeker | QS 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.3 | 0.8 | 2.3 | 2.3 | 1 | N |  |  | SB | Y | 4 | 2010 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage2010 | petroleum | TRUE | 11064 | Litchfield Public Utilities | 1989 | Litchfield | MN | Meeker | QS 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.3 | 0.8 | 2.3 | 2.3 | 1 | N |  |  | SB | Y | 4 | 2010 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage2010 | petroleum | TRUE | 11064 | Litchfield Public Utilities | 1989 | Litchfield | MN | Meeker | QS 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.3 | 0.8 | 2.3 | 2.3 | 1 | N |  |  | SB | Y | 4 | 2010 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage2021 | petroleum | TRUE | 11064 | Litchfield Public Utilities | 1989 | Litchfield | MN | Meeker | QS6 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.1 | 0.8 | 3.1 | 3.1 | 1 | Y | 9 | 2021 | SB | Y | 12 | 2021 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage2021 | petroleum | TRUE | 11064 | Litchfield Public Utilities | 1989 | Litchfield | MN | Meeker | QS7 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.1 | 0.8 | 3.1 | 3.1 | 1 | Y | 9 | 2021 | SB | Y | 12 | 2021 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1967 | petroleum | TRUE | 11332 | City of Luverne - (MN) | 1990 | Luverne | MN | Rock | 4C | Petroleum Liquids | IC |  | S | X | X |  |  | 3.5 | 0.8 | 3.5 | 3.5 | 2.5 | N |  |  | OP | X | 5 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N |  | N
Vintage1969 | petroleum | TRUE | 11731 | City of Marshall - (MN) | 1993 | Marshall (MN) | MN | Lyon | 6 | Petroleum Liquids | GT |  | S | X | X | NSP.MRES.MMU |  | 18 | 0.85 | 15.4 | 17.6 | 4 | N |  |  | OP | X | 7 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N |  | N
Vintage1945 | petroleum | TRUE | 12286 | Melrose Public Utilities | 1994 | Melrose | MN | Stearns | 1 | Petroleum Liquids | IC |  | S | X | X | NSP.MRES.MLRS |  | 1 | 0.85 | 0.8 | 0.8 | 0.8 | N |  |  | SB | N | 7 | 1945 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N |  | N
Vintage1948 | petroleum | TRUE | 12286 | Melrose Public Utilities | 1994 | Melrose | MN | Stearns | 2 | Petroleum Liquids | IC |  | S | X | X | NSP.MRES.MLRS |  | 1.1 | 0.85 | 1.1 | 1.1 | 0.8 | N |  |  | OP | X | 7 | 1948 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N |  | N
Vintage1969 | petroleum | TRUE | 12286 | Melrose Public Utilities | 1994 | Melrose | MN | Stearns | 3 | Petroleum Liquids | IC |  | S | X | X | NSP.MRES.MLRS |  | 3.1 | 0.85 | 3.1 | 3.1 | 2.5 | N |  |  | OP | X | 7 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N |  | N
Vintage1969 | petroleum | TRUE | 12286 | Melrose Public Utilities | 1994 | Melrose | MN | Stearns | 4 | Petroleum Liquids | IC |  | S | X | X | NSP.MRES.MLRS |  | 3 | 0.85 | 3.1 | 3.1 | 2.5 | N |  |  | OP | X | 1 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N |  | N
Vintage1973 | petroleum | TRUE | 12897 | Moose Lake Water & Light Comm | 1996 | Moose Lake | MN | Carlton | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 1.3 | N |  |  | SB | Y | 7 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage2005 | petroleum | TRUE | 12897 | Moose Lake Water & Light Comm | 1996 | Moose Lake | MN | Carlton | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.1 | 0.8 | 2.3 | 2.3 | 2.1 | N |  |  | OP | X | 4 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2005 | petroleum | TRUE | 12897 | Moose Lake Water & Light Comm | 1996 | Moose Lake | MN | Carlton | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.1 | 0.8 | 2.3 | 2.3 | 2.1 | N |  |  | OP | X | 4 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2005 | petroleum | TRUE | 12897 | Moose Lake Water & Light Comm | 1996 | Moose Lake | MN | Carlton | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.1 | 0.8 | 2.3 | 2.3 | 2.1 | N |  |  | OP | X | 4 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2019 | natural gas peaker | TRUE | 12897 | Moose Lake Water & Light Comm | 1996 | Moose Lake | MN | Carlton | 8NG | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.6 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 1 | 2019 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1957 | natural gas peaker | TRUE | 12900 | City of Mora - (MN) | 1997 | Mora | MN | Kanabec | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.2 | 1.2 | 0.2 | N |  |  | OP | X | 9 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1972 | natural gas peaker | TRUE | 12900 | City of Mora - (MN) | 1997 | Mora | MN | Kanabec | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 5.7 | 0.8 | 5.7 | 5.7 | 0.5 | N |  |  | OP | X | 6 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1975 | petroleum | TRUE | 12900 | City of Mora - (MN) | 1997 | Mora | MN | Kanabec | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 7 | 0.8 | 6.3 | 6.3 | 0.5 | N |  |  | OP | X | 7 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1954 | petroleum | TRUE | 13048 | City of Mountain Lake - (MN) | 1998 | Mountain Lake | MN | Cottonwood | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 1 | 0.9 | 1.1 | 0.9 | N |  |  | OP | X | 5 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1968 | petroleum | TRUE | 13048 | City of Mountain Lake - (MN) | 1998 | Mountain Lake | MN | Cottonwood | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 1 | 1.8 | 1.9 | 1.8 | N |  |  | OP | X | 5 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1959 | petroleum | TRUE | 13048 | City of Mountain Lake - (MN) | 1998 | Mountain Lake | MN | Cottonwood | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 1 | 1.2 | 1.3 | 1.2 | N |  |  | OP | X | 5 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1998 | petroleum | TRUE | 13048 | City of Mountain Lake - (MN) | 1998 | Mountain Lake | MN | Cottonwood | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 1 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 2 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N
Vintage1998 | petroleum | TRUE | 13048 | City of Mountain Lake - (MN) | 1998 | Mountain Lake | MN | Cottonwood | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 1 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 1 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N
Vintage2007 | onshore wind | TRUE | 13048 | City of Mountain Lake - (MN) | 1998 | Mountain Lake | MN | Cottonwood | 8 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 1.2 |  | 1.2 | 1.2 | 1.2 | N |  |  | OP | X | 7 | 2007 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WND |  |  | N | N | 1 | [24 empty] | N
Vintage1974 | natural gas peaker | TRUE | 13480 | New Prague Utilities Comm | 1999 | New Prague | MN | Le Sueur | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | NSP.NEW_PNEW_ | NSP.NEW_PNEW_ | 4.4 | 0.8 | 4.4 | 4.4 | 4 | N |  |  | OP | X | 7 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1962 | natural gas peaker | TRUE | 13480 | New Prague Utilities Comm | 1999 | New Prague | MN | Le Sueur | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | NSP.NEW_PNEW_ | NSP.NEW_PNEW_ | 2.4 | 0.8 | 2.4 | 2.4 | 2 | N |  |  | OP | X | 8 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1968 | natural gas peaker | TRUE | 13480 | New Prague Utilities Comm | 1999 | New Prague | MN | Le Sueur | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | NSP.NEW_PNEW_ | NSP.NEW_PNEW_ | 3.5 | 0.8 | 3.5 | 3.5 | 3 | N |  |  | OP | X | 8 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1944 | natural gas peaker | TRUE | 13480 | New Prague Utilities Comm | 1999 | New Prague | MN | Le Sueur | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.6 | N |  |  | OP | X | 8 | 1944 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1982 | natural gas peaker | TRUE | 13480 | New Prague Utilities Comm | 1999 | New Prague | MN | Le Sueur | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | NSP.NEW_PNEW_ | NSP.NEW_PNEW_ | 6 | 0.8 | 5.9 | 5.9 | 4.5 | N |  |  | OP | X | 6 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1957 | natural gas steam turbine | TRUE | 13488 | New Ulm Public Utilities Comm | 2001 | New Ulm | MN | Brown | 3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 6 | 0.85 | 4.7 | 4.7 | 1 | N |  |  | OS | X | 1 | 1957 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1965 | natural gas steam turbine | TRUE | 13488 | New Ulm Public Utilities Comm | 2001 | New Ulm | MN | Brown | 4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 15 | 0.85 | 13.2 | 13.2 | 2 | N |  |  | OP | X | 1 | 1965 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1975 | petroleum | TRUE | 13488 | New Ulm Public Utilities Comm | 2001 | New Ulm | MN | Brown | 5 | Petroleum Liquids | GT |  | S | X | X |  |  | 24 | 0.85 | 23 | 25 | 2.5 | N |  |  | OP | X | 5 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO DFO DFO: DFO |  |  | N | N |  | 10M |  |  |  | N | [19 empty] | N | N | N
Vintage1997 | natural gas steam turbine | TRUE | 13488 | New Ulm Public Utilities Comm | 2001 | New Ulm | MN | Brown | 6 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 6 | 0.85 | 4.7 | 4.7 | 1 | N |  |  | OP | X | 5 | 1997 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage2001 | petroleum | TRUE | 13488 | New Ulm Public Utilities Comm | 2001 | New Ulm | MN | Brown | 7 | Petroleum Liquids | GT |  | S | X | X |  |  | 27.5 | 0.85 | 25 | 25 | 8 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO DFO DFO: DFO |  |  | N | N |  | 10M |  |  |  | N | [19 empty] | N | N
Vintage2003 | petroleum | TRUE | 13681 | North Branch Water & Light Comm | 2002 | North Branch (MN) | MN | Chisago | 3 | Petroleum Liquids | IC |  | S | X | X | GRE.NBRNCG_QS | GRE.NBRNCG_QS | 2.2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 10 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2003 | petroleum | TRUE | 13681 | North Branch Water & Light Comm | 2002 | North Branch (MN) | MN | Chisago | 4 | Petroleum Liquids | IC |  | S | X | X | GRE.NBRNCG_QS | GRE.NBRNCG_QS | 2.2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 10 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2011 | petroleum | TRUE | 13681 | North Branch Water & Light Comm | 2002 | North Branch (MN) | MN | Chisago | 5 | Petroleum Liquids | IC |  | S | X | X | GRE.NBRNCG_QS | GRE.NBRNCG_QS | 2.2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 12 | 2011 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2011 | petroleum | TRUE | 13681 | North Branch Water & Light Comm | 2002 | North Branch (MN) | MN | Chisago | 6 | Petroleum Liquids | IC |  | S | X | X | GRE.NBRNCG_QS | GRE.NBRNCG_QS | 2.2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 12 | 2011 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  |  | N |  | 1H | [23 empty] | N | N | N
Vintage2011 | petroleum | TRUE | 13681 | North Branch Water & Light Comm | 2002 | North Branch (MN) | MN | Chisago | 7 | Petroleum Liquids | IC |  | S | X | X | GRE.NBRNCG_QS | GRE.NBRNCG_QS | 2.2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 12 | 2011 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  |  | N |  | 1H | [23 empty] | N | N | N
Vintage1982 | natural gas peaker | TRUE | 14246 | City of Owatonna - (MN) | 2003 | Owatonna | MN | Steele | 7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SMP.OWANASM7 | SMP.OWANASM7 | 19 | 0.8 | 16.6 | 16.6 | 7 | N |  |  | OP | X | 4 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1949 | petroleum | TRUE | 15348 | Preston Public Utilities Comm | 2004 | Preston (MN) | MN | Fillmore | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 1 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1954 | natural gas peaker | TRUE | 15348 | Preston Public Utilities Comm | 2004 | Preston (MN) | MN | Fillmore | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.8 | N |  |  | OP | X | 1 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1974 | natural gas peaker | TRUE | 15348 | Preston Public Utilities Comm | 2004 | Preston (MN) | MN | Fillmore | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2 | 0.8 | 2.2 | 2.2 | 1.5 | N |  |  | OP | X | 1 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1978 | petroleum | TRUE | 15387 | Princeton Public Utils Comm | 2005 | Princeton (MN) | MN | Mille Lacs | 3 | Petroleum Liquids | IC |  | S | X | X | GRE.PRINC1 | GRE.PRINC1 | 2.4 | 0.8 | 2.6 | 2.6 | 2 | N |  |  | OP | X | 12 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1967 | petroleum | TRUE | 15387 | Princeton Public Utils Comm | 2005 | Princeton (MN) | MN | Mille Lacs | 4 | Petroleum Liquids | IC |  | S | X | X | GRE.PRINC1 | GRE.PRINC1 | 1.2 | 0.8 | 1.3 | 1.3 | 1 | N |  |  | OP | X | 9 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1953 | petroleum | TRUE | 15387 | Princeton Public Utils Comm | 2005 | Princeton (MN) | MN | Mille Lacs | 5 | Petroleum Liquids | IC |  | S | X | X | GRE.PRINC1 | GRE.PRINC1 | 1 | 0.8 | 1 | 1 | 1 | N |  |  | OP | X | 9 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1963 | petroleum | TRUE | 15387 | Princeton Public Utils Comm | 2005 | Princeton (MN) | MN | Mille Lacs | 6 | Petroleum Liquids | IC |  | S | X | X | GRE.PRINC1 | GRE.PRINC1 | 2.7 | 0.8 | 2.9 | 2.9 | 2 | N |  |  | OP | X | 9 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2003 | petroleum | TRUE | 15387 | Princeton Public Utils Comm | 2005 | Princeton (MN) | MN | Mille Lacs | 7 | Petroleum Liquids | IC |  | S | X | X | GEE.PRINC2 | GRE.PRINC2 | 5 | 0.8 | 5 | 5 | 4 | N |  |  | OP | X | 7 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1984 | hydro | TRUE | 16181 | Rochester Public Utilities | 2007 | Rochester Hydro | MN | Wabasha | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 0.95 | 1.3 | 1.3 | 0.5 | N |  |  | OP | X | 9 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1984 | hydro | TRUE | 16181 | Rochester Public Utilities | 2007 | Rochester Hydro | MN | Wabasha | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 0.95 | 1.3 | 1.3 | 0.5 | N |  |  | OP | X | 11 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1970 | petroleum | TRUE | 15793 | Redwood Falls Public Util Comm | 2009 | Redwood Falls | MN | Redwood | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.2 | 0.8 | 2.1 | 2.1 | 0.5 | N |  |  | OP | X | 1 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1974 | natural gas peaker | TRUE | 15793 | Redwood Falls Public Util Comm | 2009 | Redwood Falls | MN | Redwood | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 5.8 | 0.8 | 6 | 6 | 0.7 | N |  |  | OP | X | 1 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage2013 | hydro | TRUE | 15793 | Redwood Falls Public Util Comm | 2009 | Redwood Falls | MN | Redwood | 8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 10 | 2013 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 1H | [23 empty] | N
Vintage1999 | petroleum | TRUE | 17320 | Sleepy Eye Public Utility Comm | 2011 | Sleepy Eye | MN | Brown | 1A | Petroleum Liquids | IC |  | S | X | X | NSP.CMMPA.SE | MISO | 1.8 | 0.8 | 1.8 | 1.8 | 0.2 | N |  |  | SB | Y | 4 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H |  |  |  | N | [19 empty] | N
Vintage1996 | petroleum | TRUE | 17320 | Sleepy Eye Public Utility Comm | 2011 | Sleepy Eye | MN | Brown | 5 | Petroleum Liquids | IC |  | S | X | X | NSP.CMMPA.SE |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.2 | N |  |  | SB | Y | 6 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage2009 | petroleum | TRUE | 17320 | Sleepy Eye Public Utility Comm | 2011 | Sleepy Eye | MN | Brown | 6 | Petroleum Liquids | IC |  | S | X | X | NSP.CMMPA.SE |  | 2 | 0.8 | 2 | 2 | 0.2 | N |  |  | SB | Y | 9 | 2009 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage2009 | petroleum | TRUE | 17320 | Sleepy Eye Public Utility Comm | 2011 | Sleepy Eye | MN | Brown | 7 | Petroleum Liquids | IC |  | S | X | X | NSP.CMMPA.SE |  | 2 | 0.8 | 2 | 2 | 0.2 | N |  |  | SB | Y | 9 | 2009 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage1995 | petroleum | TRUE | 17320 | Sleepy Eye Public Utility Comm | 2011 | Sleepy Eye | MN | Brown | IC4 | Petroleum Liquids | IC |  | S | X | X | NSP.CMMPA.SE |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.2 | N |  |  | SB | Y | 7 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage2001 | petroleum | TRUE | 17320 | Sleepy Eye Public Utility Comm | 2011 | Sleepy Eye | MN | Brown | NEW | Petroleum Liquids | IC |  | S | X | X | NSP.CMMPA.SE |  | 2 | 0.8 | 1.8 | 1.8 | 0.2 | N |  |  | SB | Y | 6 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage1994 | petroleum | TRUE | 17836 | Springfield Public Utils Comm - (MN) | 2012 | Springfield (MN) | MN | Brown | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 1 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 6 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N | N | N
Vintage1996 | petroleum | TRUE | 17836 | Springfield Public Utils Comm - (MN) | 2012 | Springfield (MN) | MN | Brown | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 1 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 4 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N | N | N
Vintage1998 | petroleum | TRUE | 17836 | Springfield Public Utils Comm - (MN) | 2012 | Springfield (MN) | MN | Brown | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 1 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 4 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1998 | petroleum | TRUE | 17836 | Springfield Public Utils Comm - (MN) | 2012 | Springfield (MN) | MN | Brown | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 1 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 4 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage2001 | petroleum | TRUE | 17836 | Springfield Public Utils Comm - (MN) | 2012 | Springfield (MN) | MN | Brown | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 1 | 1.8 | 1.8 | 0.5 | N |  |  | OS | X | 3 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1952 | petroleum | TRUE | 17824 | Spring Valley Pub Utils Comm | 2013 | Spring Valley | MN | Fillmore | 2 | Petroleum Liquids | IC |  | S | X | X | ALTW.SPRVAUN1 | ALTW.SPRVAUN1 | 1.1 | 0.8 | 1.1 | 1.1 | 1 | N |  |  | OP | X | 1 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1960 | petroleum | TRUE | 17824 | Spring Valley Pub Utils Comm | 2013 | Spring Valley | MN | Fillmore | 3 | Petroleum Liquids | IC |  | S | X | X | ALTW.SPRVAUN1 | ALTW.SPRVAUN1 | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 5 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2009 | petroleum | TRUE | 17824 | Spring Valley Pub Utils Comm | 2013 | Spring Valley | MN | Fillmore | 4 | Petroleum Liquids | IC |  | S | X | X | ALTW.SPRVAUN1 | ALTW.SPRVAUN1 | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 6 | 2009 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2009 | petroleum | TRUE | 17824 | Spring Valley Pub Utils Comm | 2013 | Spring Valley | MN | Fillmore | 5 | Petroleum Liquids | IC |  | S | X | X | ALTW.SPRVAUN1 | ALTW.SPRVAUN1 | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 6 | 2009 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1927 | hydro | TRUE | 18820 | City of Thief River Falls | 2014 | Thief River Falls | MN | Pennington | HY1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0 | N |  |  | OP | X | 8 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1927 | hydro | TRUE | 18820 | City of Thief River Falls | 2014 | Thief River Falls | MN | Pennington | HY2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0 | N |  |  | OS | X | 8 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1956 | petroleum | TRUE | 18820 | City of Thief River Falls | 2014 | Thief River Falls | MN | Pennington | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.2 | 0.8 | 1.9 | 1.9 | 0.2 | N |  |  | OP | X | 11 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1952 | petroleum | TRUE | 18820 | City of Thief River Falls | 2014 | Thief River Falls | MN | Pennington | IC2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1 | 1 | 0.2 | N |  |  | OP | X | 2 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2001 | petroleum | TRUE | 18820 | City of Thief River Falls | 2014 | Thief River Falls | MN | Pennington | IC3A | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 0 | N |  |  | OP | X | 2 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1948 | petroleum | TRUE | 18820 | City of Thief River Falls | 2014 | Thief River Falls | MN | Pennington | IC4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.4 | 0.8 | 1.2 | 1.2 | 0.2 | N |  |  | OP | X | 10 | 1948 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1975 | petroleum | TRUE | 63000 | City of Truman | 2015 | Truman | MN | Martin | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.2 | 0.8 | 2 | 2 | 0 | N |  |  | SB | Y | 8 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1997 | petroleum | TRUE | 63000 | City of Truman | 2015 | Truman | MN | Martin | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0 | N |  |  | SB | Y | 7 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N
Vintage2005 | petroleum | TRUE | 63000 | City of Truman | 2015 | Truman | MN | Martin | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.2 | 0.8 | 2.2 | 2.2 | 0 | N |  |  | SB | Y | 1 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N
Vintage1954 | natural gas steam turbine | TRUE | 19883 | City of Virginia - (MN) | 2018 | Virginia | MN | St Louis | 5 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 7.5 | 0.8 | 8 | 8 | 2 | N |  |  | OP | X | 8 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO DFO DFO: SUB; DFO DFO DFO: SUB |  |  | N | N |  | 12H |  |  | Y |  | Y | [18 empty] | N | N | N
Vintage1971 | natural gas steam turbine | TRUE | 19883 | City of Virginia - (MN) | 2018 | Virginia | MN | St Louis | 6 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 18.7 | 0.85 | 17 | 18.7 | 6 | N |  |  | OP | X | 8 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO DFO DFO: SUB; DFO DFO DFO: SUB |  |  | N | N |  | 12H |  |  | Y |  | Y | [18 empty] | N | N | N
Vintage1953 | natural gas peaker | TRUE | 29295 | City of Wells - (MN) | 2020 | Wells IC | MN | Faribault | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 1 | N |  |  | OP | X | 3 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1957 | natural gas peaker | TRUE | 29295 | City of Wells - (MN) | 2020 | Wells IC | MN | Faribault | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 1 | N |  |  | OP | X | 4 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1966 | natural gas peaker | TRUE | 29295 | City of Wells - (MN) | 2020 | Wells IC | MN | Faribault | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.3 | 0.8 | 2.1 | 2.1 | 1.8 | N |  |  | OP | X | 5 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1975 | natural gas peaker | TRUE | 29295 | City of Wells - (MN) | 2020 | Wells IC | MN | Faribault | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.3 | 0.8 | 2.3 | 2.3 | 1.8 | N |  |  | OP | X | 1 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2003 | petroleum | TRUE | 20430 | City of Westbrook | 2021 | Westbrook | MN | Cottonwood | 5 | Petroleum Liquids | IC |  | S | X | X | ALTW.MRES |  | 2.3 | 0.8 | 2 | 2 | 1.5 | N |  |  | OP | X | 10 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage2009 | onshore wind | TRUE | 20737 | Willmar Municipal Utilities | 2022 | Willmar | MN | Kandiyohi | WTG3 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 2 |  | 2 | 2 | 0.1 | N |  |  | OP | X | 8 | 2009 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WND |  |  | N |  | 1 | [24 empty] | N
Vintage2009 | onshore wind | TRUE | 20737 | Willmar Municipal Utilities | 2022 | Willmar | MN | Kandiyohi | WTG4 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 2 |  | 2 | 2 | 0.1 | N |  |  | OP | X | 8 | 2009 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WND |  |  | N |  | 1 | [24 empty] | N
Vintage2001 | petroleum | TRUE | 20806 | City of Windom | 2023 | Windom | MN | Cottonwood | CAT2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.7 | 1.8 | 0.5 | N |  |  | SB | Y | 4 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2001 | petroleum | TRUE | 20806 | City of Windom | 2023 | Windom | MN | Cottonwood | CAT3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.7 | 1.8 | 0.5 | N |  |  | SB | Y | 4 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2001 | petroleum | TRUE | 20806 | City of Windom | 2023 | Windom | MN | Cottonwood | CAT4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.7 | 1.8 | 0.5 | N |  |  | SB | Y | 4 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1980 | petroleum | TRUE | 20806 | City of Windom | 2023 | Windom | MN | Cottonwood | GT1 | Petroleum Liquids | GT |  | S | X | X |  |  | 3 | 0.85 | 2.5 | 3 | 1 | N |  |  | SB | Y | 6 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2002 | petroleum | TRUE | 21013 | City of Worthington - (MN) | 2024 | Worthington | MN | Nobles | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1.5 | N |  |  | OP | X | 8 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage2002 | onshore wind | TRUE | 21013 | City of Worthington - (MN) | 2024 | Worthington | MN | Nobles | 10 | Onshore Wind Turbine | WT |  | W | X | X |  |  | 0.9 |  | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WND |  |  | N |  | 1 | [24 empty] | N
Vintage2002 | onshore wind | TRUE | 21013 | City of Worthington - (MN) | 2024 | Worthington | MN | Nobles | 11 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 0.9 |  | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WND |  |  | N |  | 1 | [24 empty] | N
Vintage2003 | onshore wind | TRUE | 21013 | City of Worthington - (MN) | 2024 | Worthington | MN | Nobles | 12 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 1 |  | 1 | 1 | 0.1 | N |  |  | OP | X | 12 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WND |  |  | N |  | 1 | [24 empty] | N
Vintage2003 | onshore wind | TRUE | 21013 | City of Worthington - (MN) | 2024 | Worthington | MN | Nobles | 13 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 1 |  | 1 | 1 | 0.1 | N |  |  | OP | X | 12 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WND |  |  | N |  | 1 | [24 empty] | N
Vintage2002 | petroleum | TRUE | 21013 | City of Worthington - (MN) | 2024 | Worthington | MN | Nobles | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1.5 | N |  |  | OP | X | 8 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage2002 | petroleum | TRUE | 21013 | City of Worthington - (MN) | 2024 | Worthington | MN | Nobles | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1.5 | N |  |  | OP | X | 8 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage2002 | petroleum | TRUE | 21013 | City of Worthington - (MN) | 2024 | Worthington | MN | Nobles | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1.5 | N |  |  | OP | X | 8 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage2002 | petroleum | TRUE | 21013 | City of Worthington - (MN) | 2024 | Worthington | MN | Nobles | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1.5 | N |  |  | OP | X | 8 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage2002 | petroleum | TRUE | 21013 | City of Worthington - (MN) | 2024 | Worthington | MN | Nobles | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1.5 | N |  |  | OP | X | 8 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage2002 | petroleum | TRUE | 21013 | City of Worthington - (MN) | 2024 | Worthington | MN | Nobles | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1.5 | N |  |  | OP | X | 2 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage2002 | onshore wind | TRUE | 21013 | City of Worthington - (MN) | 2024 | Worthington | MN | Nobles | 8 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 0.9 |  | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WND |  |  | N |  | 1 | [24 empty] | N
Vintage2002 | onshore wind | TRUE | 21013 | City of Worthington - (MN) | 2024 | Worthington | MN | Nobles | 9 | Onshore Wind Turbine | WT |  | W | X | X |  |  | 0.9 |  | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WND |  |  | N |  | 1 | [24 empty] | N
Vintage1978 | petroleum | TRUE | 7570 | Great River Energy | 2038 | Cambridge CT Hybrid | MN | Isanti | GT1 | Petroleum Liquids | GT |  | S | X | X | GRE.CAMBRCAMB | GRE.CAMBRCAMB | 25.1 | 0.85 | 20.3 | 29.2 | 15 | N |  |  | OP | X | 5 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2007 | natural gas peaker | TRUE | 7570 | Great River Energy | 2038 | Cambridge CT Hybrid | MN | Isanti | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | GRE.CAMBRCAMB2 | GRE.CAMBRCAMB2 | 169.2 | 0.85 | 151 | 190 | 40 | N |  |  | OP | X | 5 | 2007 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2009 | natural gas peaker | TRUE | 7570 | Great River Energy | 2039 | Elk River | MN | Sherburne | CT | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | GRE.ELKRI4 | GRE.ELKRI4 | 191.3 | 0.85 | 189.1 | 200 | 110 | N |  |  | OP | X | 7 | 2009 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1978 | petroleum | TRUE | 7570 | Great River Energy | 2042 | Maple Lake | MN | Wright | 5A | Petroleum Liquids | GT |  | S | X | X | GRE.MAPLEMAPL | GRE.MAPLEMAPL | 25 | 0.85 | 18.7 | 29.4 | 15 | N |  |  | OP | X | 5 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1967 | natural gas peaker | TRUE | 12686 | Mississippi Power Co | 2047 | Chevron Oil | MS | Jackson | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 16.6 | 0.85 | 17 | 18 | 8 | N |  |  | OP | X | 7 | 1967 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1967 | natural gas peaker | TRUE | 12686 | Mississippi Power Co | 2047 | Chevron Oil | MS | Jackson | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 16.6 | 0.85 | 18 | 19 | 8 | N |  |  | OP | X | 7 | 1967 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1971 | natural gas peaker | TRUE | 12686 | Mississippi Power Co | 2047 | Chevron Oil | MS | Jackson | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 18 | 0.85 | 16 | 18 | 8 | N |  |  | OP | X | 10 | 1971 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1971 | natural gas peaker | TRUE | 12686 | Mississippi Power Co | 2047 | Chevron Oil | MS | Jackson | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 18 | 0.85 | 16 | 18 | 8 | N |  |  | OP | X | 9 | 1971 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1994 | natural gas peaker | TRUE | 12686 | Mississippi Power Co | 2047 | Chevron Oil | MS | Jackson | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 101.3 | 0.85 | 70 | 80 | 70 | N |  |  | OP | X | 5 | 1994 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1971 | natural gas peaker | TRUE | 12686 | Mississippi Power Co | 2048 | Sweatt | MS | Lauderdale | A | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 41.9 | 0.9 | 32 | 41 | 21 | N |  |  | OP | X | 5 | 1971 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1968 | natural gas steam turbine | TRUE | 12686 | Mississippi Power Co | 2049 | Jack Watson | MS | Harrison | 4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 299.2 | 0.85 | 236 | 236 | 67.5 | N |  |  | OP | X | 6 | 1968 | 12 | 2023 | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M |  | N |  |  | N | [15 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1973 | natural gas steam turbine | TRUE | 12686 | Mississippi Power Co | 2049 | Jack Watson | MS | Harrison | 5 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 578 | 0.85 | 485 | 485 | 156.3 | N |  |  | OP | X | 5 | 1973 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER |  | N |  |  | N | [15 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1970 | natural gas peaker | TRUE | 12686 | Mississippi Power Co | 2049 | Jack Watson | MS | Harrison | A | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 41.9 | 0.9 | 33 | 41.2 | 21 | N |  |  | OP | X | 6 | 1970 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1967 | natural gas steam turbine | TRUE | 12685 | Entergy Mississippi LLC | 2050 | Baxter Wilson | MS | Warren | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | EES.B_WILSON1 | EES.B_WILSON1 | 544.6 | 0.85 | 494.3 | 505.6 | 190 | N |  |  | SB | Y | 3 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: RFO; DFO DFO DFO: DFO |  |  | N |  |  | OVER | [23 empty] | Y | Y | Y
Vintage1996 | natural gas combined cycle | TRUE | 3702 | Clarksdale Public Utilities | 2059 | L L Wilkins | MS | Coahoma | 6 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 6 | 1 | 6.8 | 6.8 | 5 | N |  |  | OP | X | 10 | 1996 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1961 | natural gas combined cycle | TRUE | 3702 | Clarksdale Public Utilities | 2059 | L L Wilkins | MS | Coahoma | 7 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 7.5 | 1 | 7.5 | 7.5 | 5 | N |  |  | OP | X | 10 | 1961 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1965 | natural gas combined cycle | TRUE | 3702 | Clarksdale Public Utilities | 2059 | L L Wilkins | MS | Coahoma | 8 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 16.2 | 1 | 13.2 | 15 | 5 | N |  |  | OP | X | 10 | 1965 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1971 | natural gas combined cycle | TRUE | 3702 | Clarksdale Public Utilities | 2059 | L L Wilkins | MS | Coahoma | 9 | Natural Gas Fired Combined Cycle | CS |  | S | N | N |  |  | 25.5 | 1 | 22 | 23 | 11 | N |  |  | OP | X | 10 | 1971 |  |  | N | Electric Utility | 1 | [14 empty] | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1945 | natural gas combined cycle | TRUE | 21095 | Public Serv Comm of Yazoo City | 2067 | Yazoo | MS | Yazoo | 2 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X |  |  | 5 | 0.8 | 5.6 | 5.6 | 3 | N |  |  | SB | Y | 6 | 1945 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1954 | natural gas combined cycle | TRUE | 21095 | Public Serv Comm of Yazoo City | 2067 | Yazoo | MS | Yazoo | 3 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X |  |  | 12.6 | 0.85 | 13 | 13 | 4 | N |  |  | OP | X | 7 | 1954 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1968 | natural gas combined cycle | TRUE | 21095 | Public Serv Comm of Yazoo City | 2067 | Yazoo | MS | Yazoo | GT1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 16.5 | 0.85 | 14.7 | 16.7 | 2 | N |  |  | OP | X | 4 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2020 | natural gas peaker | TRUE | 17568 | Cooperative Energy | 2068 | Benndale | MS | George | BENU1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | SME.BENN_R_U1 |  | 14.2 | 0.8 | 11.3 | 11.3 | 1.2 | N |  |  | OP | X | 4 | 2020 |  |  | N | Electric Utility | 1 | [14 empty] | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2020 | natural gas peaker | TRUE | 17568 | Cooperative Energy | 2068 | Benndale | MS | George | BENU2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | SME.BENN_R_U2 |  | 14.2 | 0.8 | 11.3 | 11.3 | 1.2 | N |  |  | OP | X | 4 | 2020 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1970 | natural gas combined cycle | TRUE | 17568 | Cooperative Energy | 2070 | Moselle | MS | Jones | 1 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | SME.MOS_STG_1 |  | 59 | 0.85 | 59 | 59 | 36 | N |  |  | OP | X | 8 | 1970 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1970 | natural gas combined cycle | TRUE | 17568 | Cooperative Energy | 2070 | Moselle | MS | Jones | 2 | Natural Gas Fired Combined Cycle | CA | CC2 | S | Y | X | SME.MOS_STG_2 |  | 59 | 0.85 | 59 | 59 | 36 | N |  |  | OP | X | 8 | 1970 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1970 | natural gas steam turbine | TRUE | 17568 | Cooperative Energy | 2070 | Moselle | MS | Jones | 3 | Natural Gas Steam Turbine | ST |  | S | X | X | SME.MOS_3 |  | 59 | 0.85 | 59 | 59 | 36 | N |  |  | OP | X | 8 | 1970 | 1 | 2025 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: RFO; DFO DFO DFO: NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1997 | natural gas peaker | TRUE | 17568 | Cooperative Energy | 2070 | Moselle | MS | Jones | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SME.MOS_4 |  | 83 | 0.85 | 75 | 83 | 53 | N |  |  | OP | X | 6 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2006 | natural gas peaker | TRUE | 17568 | Cooperative Energy | 2070 | Moselle | MS | Jones | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SME.MOS_5 |  | 83.5 | 0.85 | 75 | 83.5 | 53 | N |  |  | OP | X | 6 | 2006 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2012 | natural gas combined cycle | TRUE | 17568 | Cooperative Energy | 2070 | Moselle | MS | Jones | GTG1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y | SME.MOS_CTG_1 |  | 83.5 | 0.85 | 75 | 83.5 | 53 | N |  |  | OP | X | 5 | 2012 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2012 | natural gas combined cycle | TRUE | 17568 | Cooperative Energy | 2070 | Moselle | MS | Jones | GTG2 | Natural Gas Fired Combined Cycle | CT | CC2 | S | X | Y | SME.MOS_CTG_2 |  | 83.5 | 0.85 | 75 | 83.5 | 53 | N |  |  | OP | X | 11 | 2012 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1969 | hard coal | TRUE | 10000 | Evergy Metro | 2079 | Hawthorn | MO | Jackson | 5 | Conventional Steam Coal | ST |  | S | X | X | KCPLHAWTHORNUNHAW5 | HAWTHORNUNHAW5 | 569 | 0.9 | 552.2 | 552.2 | 285 | N |  |  | OP | X | 5 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1997 | natural gas combined cycle | TRUE | 10000 | Evergy Metro | 2079 | Hawthorn | MO | Jackson | 6 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | KCPLHAWTHORN6 | HAWTHORN6 | 170 | 0.85 | 120.7 |  | 68 | N |  |  | OP | X | 6 | 1997 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2000 | natural gas peaker | TRUE | 10000 | Evergy Metro | 2079 | Hawthorn | MO | Jackson | 7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | KCPLLEVEEUNHAW7 | LEVEEUNHAW7 | 82.2 | 0.85 | 76.2 | 76.2 | 50 | N |  |  | OP | X | 5 | 2000 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2000 | natural gas peaker | TRUE | 10000 | Evergy Metro | 2079 | Hawthorn | MO | Jackson | 8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | KCPLLEVEEUNHAW8 | LEVEEUNHAW8 | 82.2 | 0.85 | 77.2 |  | 50 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | [14 empty] | 1H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2000 | natural gas combined cycle | TRUE | 10000 | Evergy Metro | 2079 | Hawthorn | MO | Jackson | 9 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | KCPLHAWTHORN6 | HAWTHORN6 | 142.8 | 0.92 | 103.8 |  | 60 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | [14 empty] | 12H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1972 | petroleum | TRUE | 10000 | Evergy Metro | 2081 | Northeast (MO) | MO | Jackson | 11 | Petroleum Liquids | GT |  | S | X | X | KCPLNRTHEASTUNNE11 | NRTHEASTUNNE11 | 50 | 0.9 | 46.6 | 46.6 | 3 | N |  |  | OP | X | 5 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N
Vintage1972 | petroleum | TRUE | 10000 | Evergy Metro | 2081 | Northeast (MO) | MO | Jackson | 12 | Petroleum Liquids | GT |  | S | X | X | KCPLNRTHEASTUNNE12 | NRTHEASTUNNE12 | 50 | 0.9 | 46 | 46 | 3 | N |  |  | OP | X | 5 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N
Vintage1975 | petroleum | TRUE | 10000 | Evergy Metro | 2081 | Northeast (MO) | MO | Jackson | 13 | Petroleum Liquids | GT |  | S | X | X | KCPLNRTHEASTUNNE13 | NRTHEASTUNNE13 | 64.7 | 0.9 | 46.1 | 46.1 | 3 | N |  |  | OP | X | 5 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N
Vintage1975 | petroleum | TRUE | 10000 | Evergy Metro | 2081 | Northeast (MO) | MO | Jackson | 14 | Petroleum Liquids | GT |  | S | X | X | KCPLNRTHEASTUNNE14 | NRTHEASTUNNE14 | 64.7 | 0.9 | 47.5 | 47.5 | 3 | N |  |  | OP | X | 5 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N
Vintage1976 | petroleum | TRUE | 10000 | Evergy Metro | 2081 | Northeast (MO) | MO | Jackson | 15 | Petroleum Liquids | GT |  | S | X | X | KCPLNRTHEASTUNNE15 | NRTHEASTUNNE15 | 64.7 | 0.9 | 47.5 | 47.5 | 3 | N |  |  | OP | X | 6 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N
Vintage1976 | petroleum | TRUE | 10000 | Evergy Metro | 2081 | Northeast (MO) | MO | Jackson | 16 | Petroleum Liquids | GT |  | S | X | X | KCPLNRTHEASTUNNE16 | NRTHEASTUNNE16 | 64.7 | 0.9 | 46 | 46 | 3 | N |  |  | OP | X | 6 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  |  | N |  | 1H | [23 empty] | N
Vintage1977 | petroleum | TRUE | 10000 | Evergy Metro | 2081 | Northeast (MO) | MO | Jackson | 17 | Petroleum Liquids | GT |  | S | X | X | KCPLNRTHEASTUNNE17 | NRTHEASTUNNE17 | 64.7 | 0.9 | 53.2 | 53.2 | 3 | N |  |  | OP | X | 5 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N
Vintage1977 | petroleum | TRUE | 10000 | Evergy Metro | 2081 | Northeast (MO) | MO | Jackson | 18 | Petroleum Liquids | GT |  | S | X | X | KCPLNRTHEASTUNNE18 | NRTHEASTUNNE18 | 64.7 | 0.9 | 47 | 47.1 | 3 | N |  |  | OP | X | 5 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N
Vintage1985 | petroleum | TRUE | 10000 | Evergy Metro | 2081 | Northeast (MO) | MO | Jackson | 19 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.9 | 2 | 2 | 1 | N |  |  | OP | X | 6 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N
Vintage1974 | petroleum | TRUE | 19436 | Union Electric Co - (MO) | 2082 | Fairgrounds | MO | Cole | 1 | Petroleum Liquids | GT |  | S | X | X | AMMOFGRDCTG1 | AMMOFGRDCTG1 | 68.3 | 0.9 | 55 | 69 | 5 | N |  |  | OP | X | 8 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1974 | petroleum | TRUE | 56211 | Evergy Missouri West | 2090 | Nevada | MO | Vernon | 1 | Petroleum Liquids | GT |  | S | X | X | MPSNEVADAUN1 | MPSNEVADAUN1 | 22 | 0.9 | 16 | 16 | 3 | N |  |  | OP | X | 6 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N
Vintage1981 | natural gas peaker | TRUE | 56211 | Evergy Missouri West | 2092 | Ralph Green | MO | Cass | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MPSRGREENUN3 | MPSRGREENUN3 | 85 | 0.9 | 69.4 | 10 | 10 | N |  |  | OP | X | 6 | 1981 |  |  | N | Electric Utility | 1 | [14 empty] | 1H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1950 | natural gas steam turbine | TRUE | 56211 | Evergy Missouri West | 2098 | Lake Road (MO) | MO | Buchanan | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | MPSLAKE-RDUN1 | MPSLAKE-RDUN1 | 23 | 0.85 | 18.4 | 18.4 | 6 | N |  |  | OP | X | 7 | 1950 |  |  | Y | Electric Utility | 1 | T | NG | DFO | PG | TDF |  |  | NG | PG | [5 empty] | 12H | [23 empty] | Y | N | N
Vintage1958 | natural gas steam turbine | TRUE | 56211 | Evergy Missouri West | 2098 | Lake Road (MO) | MO | Buchanan | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | MPSLAKE-RDUN2 | MPSLAKE-RDUN2 | 25 | 0.85 | 22.9 | 22.9 | 5 | N |  |  | OP | X | 8 | 1958 |  |  | Y | Electric Utility | 1 | T | NG | DFO | PG | TDF |  |  | NG | PG | [5 empty] | 12H | [23 empty] | Y | N | N
Vintage1962 | natural gas steam turbine | TRUE | 56211 | Evergy Missouri West | 2098 | Lake Road (MO) | MO | Buchanan | 3 | Natural Gas Steam Turbine | ST |  | S | X | X | MPSLAKE-RDUN3 | MPSLAKE-RDUN3 | 12.5 | 0.8 | 7.3 | 7.3 | 3 | N |  |  | OP | X | 6 | 1962 |  |  | Y | Electric Utility | 1 | T | NG | DFO | PG | TDF |  |  | NG | PG | [5 empty] | 12H | [23 empty] | Y | N | N
Vintage1966 | natural gas steam turbine | TRUE | 56211 | Evergy Missouri West | 2098 | Lake Road (MO) | MO | Buchanan | 4 | Natural Gas Steam Turbine | ST |  | S | X | X | MPSLAKE-RDUN4 | MPSLAKE-RDUN4 | 90 | 0.9 | 94.6 | 94.6 | 20 | N |  |  | OP | X | 8 | 1966 | 12 | 2024 | N | Electric Utility | 1 | X | NG | DFO | PG | TDF |  |  | NG | PG |  |  | N |  |  | 12H |  |  |  |  | N | [18 empty] | Y | N | N
Vintage1974 | natural gas peaker | TRUE | 56211 | Evergy Missouri West | 2098 | Lake Road (MO) | MO | Buchanan | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MPSLAKE-RDUN5 | MPSLAKE-RDUN5 | 85 | 0.9 | 48 | 48 | 2 | N |  |  | OP | X | 3 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: PG | [5 empty] | 1H | [23 empty] | Y | N | N
Vintage1989 | petroleum | TRUE | 56211 | Evergy Missouri West | 2098 | Lake Road (MO) | MO | Buchanan | 6 | Petroleum Liquids | GT |  | S | X | X | MPSLAKE-RDUN6 | MPSLAKE-RDUN6 | 24 | 0.85 | 20.3 | 20.3 | 5 | N |  |  | OP | X | 5 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: PG | [5 empty] | 10M | [23 empty] | Y | N | N
Vintage1990 | petroleum | TRUE | 56211 | Evergy Missouri West | 2098 | Lake Road (MO) | MO | Buchanan | 7 | Petroleum Liquids | GT |  | S | X | X | MPSLAKE-RDUN7 | MPSLAKE-RDUN7 | 18.9 | 0.85 | 21.1 | 21.1 | 5 | N |  |  | OP | X | 12 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 10M | [23 empty] | N |  | N
Vintage1930 | hydro | TRUE | 17106 | Sho-Me Power Electric Coop | 2099 | Niangua | MO | Camden | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.5 | N |  |  | OP | X | 11 | 1930 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1930 | hydro | TRUE | 17106 | Sho-Me Power Electric Coop | 2099 | Niangua | MO | Camden | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.5 | N |  |  | OP | X | 11 | 1930 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1970 | hard coal | TRUE | 19436 | Union Electric Co - (MO) | 2103 | Labadie | MO | Franklin | 1 | Conventional Steam Coal | ST |  | S | X | X | AMMO.LABADIE1 | AMMO.LABADIE1 | 573.7 | 0.85 | 593 | 616 | 290 | N |  |  | OP | X | 6 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: SUB; DFO DFO DFO: DFO |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1971 | hard coal | TRUE | 19436 | Union Electric Co - (MO) | 2103 | Labadie | MO | Franklin | 2 | Conventional Steam Coal | ST |  | S | X | X | AMMO.LABADIE2 | AMMO.LABADIE2 | 573.7 | 0.85 | 593 | 616 | 289 | N |  |  | OP | X | 6 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: SUB; DFO DFO DFO: DFO |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1972 | hard coal | TRUE | 19436 | Union Electric Co - (MO) | 2103 | Labadie | MO | Franklin | 3 | Conventional Steam Coal | ST |  | S | X | X | AMMO.LABADIE3 | AMMO.LABADIE3 | 621 | 0.9 | 593 | 616 | 280 | N |  |  | OP | X | 8 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: SUB; DFO DFO DFO: DFO |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1973 | hard coal | TRUE | 19436 | Union Electric Co - (MO) | 2103 | Labadie | MO | Franklin | 4 | Conventional Steam Coal | ST |  | S | X | X | AMMO.LABADIE4 | AMMO.LABADIE4 | 621 | 0.9 | 593 | 616 | 287 | N |  |  | OP | X | 8 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: SUB; DFO DFO DFO: DFO |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1953 | natural gas steam turbine | TRUE | 19436 | Union Electric Co - (MO) | 2104 | Meramec | MO | St Louis | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | AMMO.MERAMEC1 | AMMO.MERAMEC1 | 137.5 | 0.85 | 113 | 120 | 53 | N |  |  | OP | X | 5 | 1953 | 12 | 2022 | N | Electric Utility | 1 | [11 empty] | N |  |  | OVER | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1954 | natural gas steam turbine | TRUE | 19436 | Union Electric Co - (MO) | 2104 | Meramec | MO | St Louis | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | AMMO.MERAMEC2 | AMMO.MERAMEC2 | 137.5 | 0.85 | 113 | 120 | 46 | N |  |  | OP | X | 7 | 1954 | 12 | 2022 | N | Electric Utility | 1 | [11 empty] | N |  |  | OVER | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1959 | hard coal | TRUE | 19436 | Union Electric Co - (MO) | 2104 | Meramec | MO | St Louis | 3 | Conventional Steam Coal | ST |  | S | X | X | AMMO.MERAMEC3 | AMMO.MERAMEC3 | 289 | 0.85 | 220 | 240 | 125 | N |  |  | OP | X | 1 | 1959 | 12 | 2022 | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO DFO DFO: NG |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1961 | hard coal | TRUE | 19436 | Union Electric Co - (MO) | 2104 | Meramec | MO | St Louis | 4 | Conventional Steam Coal | ST |  | S | X | X | AMMO.MERAMEC4 | AMMO.MERAMEC4 | 359 | 0.85 | 320 | 340 | 165 | N |  |  | OP | X | 7 | 1961 | 12 | 2022 | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1974 | petroleum | TRUE | 19436 | Union Electric Co - (MO) | 2104 | Meramec | MO | St Louis | GT1 | Petroleum Liquids | GT |  | S | X | X |  |  | 62 | 0.9 | 54 | 68 | 6 | N |  |  | OP | X | 6 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | OVER | [23 empty] | N |  | N
Vintage2000 | natural gas peaker | TRUE | 19436 | Union Electric Co - (MO) | 2104 | Meramec | MO | St Louis | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 56 | 0.9 | 45 | 61 | 15 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 10M | [23 empty] | Y | N | N
Vintage1931 | hydro | TRUE | 19436 | Union Electric Co - (MO) | 2106 | Osage Dam | MO | Miller | 1 | Conventional Hydroelectric | HY |  | S | X | X | AMMO.OSAGE1 | AMMO.OSAGE1 | 27.5 | 0.9 | 31 | 31 | 0 | N |  |  | OP | X | 10 | 1931 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1931 | hydro | TRUE | 19436 | Union Electric Co - (MO) | 2106 | Osage Dam | MO | Miller | 2 | Conventional Hydroelectric | HY |  | S | X | X | AMMO.OSAGE2 | AMMO.OSAGE2 | 27.5 | 0.9 | 24 | 24 | 0 | N |  |  | OP | X | 10 | 1931 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1931 | hydro | TRUE | 19436 | Union Electric Co - (MO) | 2106 | Osage Dam | MO | Miller | 3 | Conventional Hydroelectric | HY |  | S | X | X | AMMO.OSAGE3 | AMMO.OSAGE3 | 27.5 | 0.9 | 31 | 31 | 0 | N |  |  | OP | X | 10 | 1931 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1931 | hydro | TRUE | 19436 | Union Electric Co - (MO) | 2106 | Osage Dam | MO | Miller | 4 | Conventional Hydroelectric | HY |  | S | X | X | AMMO.OSAGE4 | AMMO.OSAGE4 | 27.5 | 0.9 | 24 | 24 | 0 | N |  |  | OP | X | 10 | 1931 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1931 | hydro | TRUE | 19436 | Union Electric Co - (MO) | 2106 | Osage Dam | MO | Miller | 5 | Conventional Hydroelectric | HY |  | S | X | X | AMMO.OSAGE5 | AMMO.OSAGE5 | 27.5 | 0.9 | 31 | 31 | 0 | N |  |  | OP | X | 10 | 1931 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1931 | hydro | TRUE | 19436 | Union Electric Co - (MO) | 2106 | Osage Dam | MO | Miller | 6 | Conventional Hydroelectric | HY |  | S | X | X | AMMO.OSAGE6 | AMMO.OSAGE6 | 27.5 | 0.9 | 31 | 31 | 0 | N |  |  | OP | X | 10 | 1931 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1953 | hydro | TRUE | 19436 | Union Electric Co - (MO) | 2106 | Osage Dam | MO | Miller | 7 | Conventional Hydroelectric | HY |  | S | X | X | AMMO.OSAGE7 | AMMO.OSAGE7 | 21.5 | 0.9 | 31 | 31 | 0 | N |  |  | OP | X | 10 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1953 | hydro | TRUE | 19436 | Union Electric Co - (MO) | 2106 | Osage Dam | MO | Miller | 8 | Conventional Hydroelectric | HY |  | S | X | X | AMMO.OSAGE8 | AMMO.OSAGE8 | 21.5 | 0.9 | 31 | 31 | 0 | N |  |  | OP | X | 10 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1967 | hard coal | TRUE | 19436 | Union Electric Co - (MO) | 2107 | Sioux | MO | St Charles | 1 | Conventional Steam Coal | ST |  | S | X | X | AMMO.SIOUX1 | AMMO.SIOUX1 | 549.7 | 0.85 | 487 | 497 | 253 | N |  |  | OP | X | 5 | 1967 | 12 | 2028 | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: SUB; DFO DFO DFO: BIT; DFO DFO DFO: DFO |  |  | N |  |  | OVER |  | Y |  |  |  | Y | [17 empty] | Y | N | N
Vintage1968 | hard coal | TRUE | 19436 | Union Electric Co - (MO) | 2107 | Sioux | MO | St Charles | 2 | Conventional Steam Coal | ST |  | S | X | X | AMMO.SIOUX2 | AMMO.SIOUX2 | 549.7 | 0.85 | 487 | 497 | 252 | N |  |  | OP | X | 5 | 1968 | 12 | 2028 | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: SUB; DFO DFO DFO: BIT; DFO DFO DFO: DFO |  |  | N |  |  | OVER |  | Y |  |  |  | Y | [17 empty] | Y | N | N
Vintage1963 | other | TRUE | 19436 | Union Electric Co - (MO) | 2108 | Taum Sauk | MO | Reynolds | 1 | Hydroelectric Pumped Storage | PS |  | S | X | X | AMMO.TS1 | AMMO.TS1 | 204 | 0.9 | 220 | 220 | 165 | N |  |  | OP | X | 12 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1963 | other | TRUE | 19436 | Union Electric Co - (MO) | 2108 | Taum Sauk | MO | Reynolds | 2 | Hydroelectric Pumped Storage | PS |  | S | X | X | AMMO.TS2 | AMMO.TS2 | 204 | 0.9 | 220 | 220 | 165 | N |  |  | OP | X | 12 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1959 | petroleum | TRUE | 2647 | City of Butler - (MO) | 2115 | Butler Municipal Power Plant | MO | Bates | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.4 | 0.8 | 1 | 1 | 0.6 | N |  |  | SB | Y | 4 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 12H | [23 empty] | N |  | N
Vintage1965 | petroleum | TRUE | 2647 | City of Butler - (MO) | 2115 | Butler Municipal Power Plant | MO | Bates | IC6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.1 | 1.1 | 0.7 | N |  |  | SB | Y | 9 | 1965 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 12H | [23 empty] | N
Vintage2000 | petroleum | TRUE | 2647 | City of Butler - (MO) | 2115 | Butler Municipal Power Plant | MO | Bates | NG1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 1 | 1.8 | 1.8 | 0.3 | N |  |  | SB | Y | 1 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 2647 | City of Butler - (MO) | 2115 | Butler Municipal Power Plant | MO | Bates | NG2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 1 | 1.8 | 1.8 | 0.3 | N |  |  | SB | Y | 1 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 2647 | City of Butler - (MO) | 2115 | Butler Municipal Power Plant | MO | Bates | SG1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 1 | 1.8 | 1.8 | 0.3 | N |  |  | SB | Y | 1 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 2647 | City of Butler - (MO) | 2115 | Butler Municipal Power Plant | MO | Bates | SG2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 1 | 1.8 | 1.8 | 0.3 | N |  |  | SB | Y | 1 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1972 | natural gas peaker | TRUE | 3082 | Carrollton Board of Public Wks | 2120 | Carrollton | MO | Carroll | 10 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 6.1 | 0.9 | 6 | 6 | 0.1 | N |  |  | OP | X | 9 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 10M | [23 empty] | Y | Y | Y
Vintage2001 | petroleum | TRUE | 3082 | Carrollton Board of Public Wks | 2120 | Carrollton | MO | Carroll | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.92 | 1.8 | 1.8 | 0.1 | N |  |  | OP | X | 7 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage1947 | natural gas peaker | TRUE | 3082 | Carrollton Board of Public Wks | 2120 | Carrollton | MO | Carroll | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.8 | 0.9 | 1.8 | 1.8 | 0.1 | N |  |  | OP | X | 3 | 1947 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 10M | [23 empty] | Y | Y | Y
Vintage1959 | natural gas peaker | TRUE | 3082 | Carrollton Board of Public Wks | 2120 | Carrollton | MO | Carroll | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 0.1 | N |  |  | OP | X | 4 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 10M | [23 empty] | Y | Y | Y
Vintage1966 | natural gas peaker | TRUE | 3082 | Carrollton Board of Public Wks | 2120 | Carrollton | MO | Carroll | 8 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 4.1 | 0.9 | 3.7 | 3.7 | 0.1 | N |  |  | OP | X | 10 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 10M | [23 empty] | Y | Y | Y
Vintage1970 | natural gas peaker | TRUE | 3082 | Carrollton Board of Public Wks | 2120 | Carrollton | MO | Carroll | 9 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 4.1 | 0.91 | 3.7 | 3.7 | 0.1 | N |  |  | OP | X | 5 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 10M | [23 empty] | Y | Y | Y
Vintage1965 | petroleum | TRUE | 3113 | City of Carthage - (MO) | 2121 | Carthage | MO | Jasper | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 7 | 0.8 | 6 | 6 | 4 | N |  |  | SB | Y | 7 | 1965 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1970 | petroleum | TRUE | 3113 | City of Carthage - (MO) | 2121 | Carthage | MO | Jasper | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.5 | 0.8 | 4 | 4 | 3 | N |  |  | OP | X | 7 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1971 | petroleum | TRUE | 3113 | City of Carthage - (MO) | 2121 | Carthage | MO | Jasper | 12 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.5 | 0.8 | 4 | 4 | 3 | N |  |  | OP | X | 7 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1976 | petroleum | TRUE | 3113 | City of Carthage - (MO) | 2121 | Carthage | MO | Jasper | 13 | Petroleum Liquids | IC |  | S | X | X |  |  | 6 | 0.8 | 5.5 | 5.5 | 3 | N |  |  | OP | X | 2 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1976 | petroleum | TRUE | 3113 | City of Carthage - (MO) | 2121 | Carthage | MO | Jasper | 14 | Petroleum Liquids | IC |  | S | X | X |  |  | 6 | 0.8 | 5.5 | 5.5 | 3 | N |  |  | OP | X | 4 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1946 | petroleum | TRUE | 3113 | City of Carthage - (MO) | 2121 | Carthage | MO | Jasper | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2 | 2 | 1 | N |  |  | SB | Y | 7 | 1946 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1949 | petroleum | TRUE | 3113 | City of Carthage - (MO) | 2121 | Carthage | MO | Jasper | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.8 | 2.2 | 2.2 | 1.5 | N |  |  | SB | Y | 7 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1952 | petroleum | TRUE | 3113 | City of Carthage - (MO) | 2121 | Carthage | MO | Jasper | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.3 | 0.8 | 2.5 | 2.5 | 1.8 | N |  |  | SB | Y | 7 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1957 | petroleum | TRUE | 3113 | City of Carthage - (MO) | 2121 | Carthage | MO | Jasper | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 5 | 0.8 | 4 | 4 | 3 | N |  |  | SB | Y | 8 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2003 | petroleum | TRUE | 3486 | Chillicothe Municipal Utils | 2122 | Chillicothe | MO | Livingston | D1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage2003 | petroleum | TRUE | 3486 | Chillicothe Municipal Utils | 2122 | Chillicothe | MO | Livingston | D2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage2003 | petroleum | TRUE | 3486 | Chillicothe Municipal Utils | 2122 | Chillicothe | MO | Livingston | D3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2003 | petroleum | TRUE | 3486 | Chillicothe Municipal Utils | 2122 | Chillicothe | MO | Livingston | D4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2003 | petroleum | TRUE | 3486 | Chillicothe Municipal Utils | 2122 | Chillicothe | MO | Livingston | D5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1986 | natural gas peaker | TRUE | 3486 | Chillicothe Municipal Utils | 2122 | Chillicothe | MO | Livingston | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 40 | 0.9 | 40 | 42 | 0 | N |  |  | OP | X | 6 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1986 | natural gas peaker | TRUE | 3486 | Chillicothe Municipal Utils | 2122 | Chillicothe | MO | Livingston | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 40 | 0.9 | 40 | 42 | 0 | N |  |  | OP | X | 6 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1963 | natural gas peaker | TRUE | 4045 | City of Columbia - (MO) | 2123 | Columbia (MO) | MO | Boone | 6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | CWLD.CWLD | CWLD.CWLD | 12.5 | 0.8 | 12.5 | 12.5 | 9 | N |  |  | OP | X | 8 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 12H | [23 empty] | N |  | N
Vintage1970 | natural gas steam turbine | TRUE | 4045 | City of Columbia - (MO) | 2123 | Columbia (MO) | MO | Boone | 8 | Natural Gas Steam Turbine | ST |  | S | X | X | CWLD.CWLD | CWLD.CWLD | 35 | 0.85 | 35 | 35 | 12 | N |  |  | OP | X | 1 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | 12H |  | N | [21 empty] | N |  | N
Vintage2004 | petroleum | TRUE | 4045 | City of Columbia - (MO) | 2123 | Columbia (MO) | MO | Boone | DAN1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 8 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage2008 | biomass | TRUE | 4045 | City of Columbia - (MO) | 2123 | Columbia (MO) | MO | Boone | LF1 | Landfill Gas | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.6 | N |  |  | OP | X | 6 | 2008 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: LFG |  |  | N | N |  | 1H | [23 empty] | N
Vintage2008 | biomass | TRUE | 4045 | City of Columbia - (MO) | 2123 | Columbia (MO) | MO | Boone | LF2 | Landfill Gas | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.6 | N |  |  | OP | X | 6 | 2008 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: LFG |  |  |  | N |  | 1H | [23 empty] | N
Vintage2013 | biomass | TRUE | 4045 | City of Columbia - (MO) | 2123 | Columbia (MO) | MO | Boone | LF3 | Landfill Gas | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.6 | N |  |  | OP | X | 8 | 2013 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: LFG |  |  |  | N |  | 1H | [23 empty] | N
Vintage2008 | petroleum | TRUE | 4045 | City of Columbia - (MO) | 2123 | Columbia (MO) | MO | Boone | SF1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 1 | N |  |  | OP | X | 11 | 2008 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage2008 | petroleum | TRUE | 4045 | City of Columbia - (MO) | 2123 | Columbia (MO) | MO | Boone | SF2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 1 | N |  |  | OP | X | 11 | 2008 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage2002 | petroleum | TRUE | 4045 | City of Columbia - (MO) | 2123 | Columbia (MO) | MO | Boone | SH1 | Petroleum Liquids | IC |  | W | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 1.3 | N |  |  | OP | X | 4 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage2002 | petroleum | TRUE | 4045 | City of Columbia - (MO) | 2123 | Columbia (MO) | MO | Boone | SH2 | Petroleum Liquids | IC |  | W | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 1.3 | N |  |  | OP | X | 4 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M |  |  |  |  | N | [18 empty] | N
Vintage2004 | petroleum | TRUE | 4045 | City of Columbia - (MO) | 2123 | Columbia (MO) | MO | Boone | WTP1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 8 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage2004 | petroleum | TRUE | 4045 | City of Columbia - (MO) | 2123 | Columbia (MO) | MO | Boone | WTP2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 8 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M |  |  |  |  | N | [18 empty] | N
Vintage1973 | hydro | TRUE | 25477 | USCE-Kansas City District | 2124 | Stockton Hydro | MO | Cedar | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 52 | 0.95 | 52 | 52 | 5 | N |  |  | OP | X | 3 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1985 | petroleum | TRUE | 6231 | City of Fayette - (MO) | 2125 | Fayette | MO | Howard | GT1 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.5 | 0.8 | 3 | 3 | 3 | N |  |  | OS | X | 7 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 12H | [23 empty] | N |  | N
Vintage1985 | petroleum | TRUE | 6231 | City of Fayette - (MO) | 2125 | Fayette | MO | Howard | GT2 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.5 | 0.8 | 2.8 | 2.8 | 2.8 | N |  |  | OS | X | 7 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 12H | [23 empty] | N |  | N
Vintage1977 | petroleum | TRUE | 6231 | City of Fayette - (MO) | 2125 | Fayette | MO | Howard | GT3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.8 | 0.8 | 2.4 | 2.4 | 2.4 | N |  |  | OS | X | 7 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 12H | [23 empty] | N |  | N
Vintage1969 | petroleum | TRUE | 6231 | City of Fayette - (MO) | 2125 | Fayette | MO | Howard | GT4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1 | 1 | 1 | N |  |  | OS | X | 7 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 12H | [23 empty] | N
Vintage1972 | natural gas peaker | TRUE | 6839 | City of Fulton - (MO) | 2126 | Fulton (MO) | MO | Callaway | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 21.2 | 0.9 | 15 | 19.6 | 3 | N |  |  | OP | X | 8 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  |  | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1966 | petroleum | TRUE | 6839 | City of Fulton - (MO) | 2126 | Fulton (MO) | MO | Callaway | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 5 | 0.9 | 4.1 | 4.5 | 1 | N |  |  | OP | X | 9 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1975 | petroleum | TRUE | 6839 | City of Fulton - (MO) | 2126 | Fulton (MO) | MO | Callaway | IC3 | Petroleum Liquids | IC |  | S | X | X |  |  | 7 | 0.9 | 6.2 | 6.8 | 1 | N |  |  | OP | X | 5 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1993 | petroleum | TRUE | 6924 | City of Gallatin - (MO) | 2127 | Gallatin (MO) | MO | Daviess | 2A | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1 | 1 | 0.7 | N |  |  | SB | Y | 4 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1993 | petroleum | TRUE | 6924 | City of Gallatin - (MO) | 2127 | Gallatin (MO) | MO | Daviess | 3A | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1 | 1 | 0.7 | N |  |  | SB | Y | 4 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1983 | petroleum | TRUE | 6924 | City of Gallatin - (MO) | 2127 | Gallatin (MO) | MO | Daviess | IC4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 1.8 | N |  |  | SB | Y | 9 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1977 | petroleum | TRUE | 6924 | City of Gallatin - (MO) | 2127 | Gallatin (MO) | MO | Daviess | IC6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 1.8 | N |  |  | SB | Y | 12 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1945 | petroleum | TRUE | 8567 | City of Higginsville - (MO) | 2131 | Higginsville | MO | Lafayette | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 1 | 0.6 | 0.6 | 0.1 | N |  |  | OS | X | 1 | 1945 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1947 | petroleum | TRUE | 8567 | City of Higginsville - (MO) | 2131 | Higginsville | MO | Lafayette | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.7 | 1 | 1 | 1 | 0.4 | N |  |  | OS | X | 1 | 1947 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1981 | petroleum | TRUE | 8567 | City of Higginsville - (MO) | 2131 | Higginsville | MO | Lafayette | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.4 | 1 | 2.4 | 2.4 | 1 | N |  |  | OS | X | 5 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1996 | natural gas peaker | TRUE | 8567 | City of Higginsville - (MO) | 2131 | Higginsville | MO | Lafayette | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 40 | 1 | 37.5 | 40 | 20 | N |  |  | OP | X | 6 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage2004 | petroleum | TRUE | 8567 | City of Higginsville - (MO) | 2131 | Higginsville | MO | Lafayette | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 1 | 1.2 | 1.2 | 0.3 | N |  |  | OP | X | 10 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage2004 | petroleum | TRUE | 8567 | City of Higginsville - (MO) | 2131 | Higginsville | MO | Lafayette | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 5.5 | 1 | 4.5 | 5.4 | 1 | N |  |  | OP | X | 10 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1969 | petroleum | TRUE | 9231 | City of Independence - (MO) | 2134 | Jackson Square | MO | Jackson | 1 | Petroleum Liquids | GT |  | S | X | X | INDNSUB_J_1 | INDNSUB_J_1 | 18 | 0.85 | 15 | 15 | 2 | N |  |  | OP | X | 6 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO DFO DFO: DFO |  |  | N | N |  | 1H |  |  |  | N | [19 empty] | N | N
Vintage1969 | petroleum | TRUE | 9231 | City of Independence - (MO) | 2134 | Jackson Square | MO | Jackson | 2 | Petroleum Liquids | GT |  | S | X | X | INDNSUB_J_2 | INDNSUB_J_2 | 18 | 0.85 | 15 | 15 | 2 | N |  |  | OP | X | 6 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO DFO DFO: DFO |  |  | N | N |  | 1H |  |  |  | N | [19 empty] | N | N
Vintage1972 | natural gas peaker | TRUE | 9231 | City of Independence - (MO) | 2135 | Station H | MO | Jackson | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | INDNSUB_H_5 | INDNSUB_H_5 | 19 | 0.85 | 19 | 19 | 4 | N |  |  | OP | X | 6 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: DFO; DFO NG NG: NG |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1974 | natural gas peaker | TRUE | 9231 | City of Independence - (MO) | 2135 | Station H | MO | Jackson | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | INDNSUB_H_6 | INDNSUB_H_6 | 24 | 0.9 | 20 | 20 | 4 | N |  |  | OP | X | 6 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: DFO; DFO NG NG: NG |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1972 | petroleum | TRUE | 9231 | City of Independence - (MO) | 2136 | Station I | MO | Jackson | 1 | Petroleum Liquids | GT |  | S | X | X | INDNSUB_I_3 | INDNSUB_I_3 | 19 | 0.85 | 19 | 19 | 2 | N |  |  | OP | X | 6 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO DFO DFO: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1972 | petroleum | TRUE | 9231 | City of Independence - (MO) | 2136 | Station I | MO | Jackson | 2 | Petroleum Liquids | GT |  | S | X | X | INDNSUB_I_4 | INDNSUB_I_4 | 19 | 0.85 | 19 | 19 | 2 | N |  |  | OP | X | 6 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO DFO DFO: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2006 | petroleum | TRUE | 9603 | City of Jackson - (MO) | 2137 | Jackson (MO) | MO | Cape Girardeau | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | OP | X | 9 | 2006 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2006 | petroleum | TRUE | 9603 | City of Jackson - (MO) | 2137 | Jackson (MO) | MO | Cape Girardeau | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | OP | X | 9 | 2006 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2006 | petroleum | TRUE | 9603 | City of Jackson - (MO) | 2137 | Jackson (MO) | MO | Cape Girardeau | 12 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | OP | X | 9 | 2006 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1963 | petroleum | TRUE | 9603 | City of Jackson - (MO) | 2137 | Jackson (MO) | MO | Cape Girardeau | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.4 | N |  |  | OP | X | 4 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1963 | petroleum | TRUE | 9603 | City of Jackson - (MO) | 2137 | Jackson (MO) | MO | Cape Girardeau | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.4 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1936 | petroleum | TRUE | 9603 | City of Jackson - (MO) | 2137 | Jackson (MO) | MO | Cape Girardeau | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.7 | 0.8 | 0.6 | 0.6 | 0.6 | N |  |  | OP | X | 1 | 1936 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1946 | petroleum | TRUE | 9603 | City of Jackson - (MO) | 2137 | Jackson (MO) | MO | Cape Girardeau | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 1 | N |  |  | OP | X | 6 | 1946 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1973 | petroleum | TRUE | 9603 | City of Jackson - (MO) | 2137 | Jackson (MO) | MO | Cape Girardeau | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 6.8 | 0.8 | 6.5 | 6.8 | 2.5 | N |  |  | OP | X | 8 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1973 | petroleum | TRUE | 9603 | City of Jackson - (MO) | 2137 | Jackson (MO) | MO | Cape Girardeau | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 6.8 | 0.8 | 6.5 | 6.8 | 2.5 | N |  |  | OP | X | 7 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1983 | petroleum | TRUE | 9603 | City of Jackson - (MO) | 2137 | Jackson (MO) | MO | Cape Girardeau | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.8 | 2.7 | 3 | 0.5 | N |  |  | OP | X | 7 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1999 | petroleum | TRUE | 9973 | City of Kahoka | 2138 | Kahoka | MO | Clark | 10 | Petroleum Liquids | IC |  | S | X | X | NA | NA | 1.1 | 0.8 | 1.1 | 1.1 | 0.4 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1999 | petroleum | TRUE | 9973 | City of Kahoka | 2138 | Kahoka | MO | Clark | 11 | Petroleum Liquids | IC |  | S | X | X | NA | NA | 1.1 | 0.8 | 1.1 | 1.1 | 0.4 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1999 | petroleum | TRUE | 9973 | City of Kahoka | 2138 | Kahoka | MO | Clark | 12 | Petroleum Liquids | IC |  | S | X | X | NA | NA | 1.1 | 0.8 | 1.1 | 1.1 | 0.4 | N |  |  | OP | X | 9 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1941 | petroleum | TRUE | 9973 | City of Kahoka | 2138 | Kahoka | MO | Clark | 3 | Petroleum Liquids | IC |  | S | X | X | NA | NA | 0.2 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1941 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1952 | petroleum | TRUE | 9973 | City of Kahoka | 2138 | Kahoka | MO | Clark | 6 | Petroleum Liquids | IC |  | S | X | X | NA | NA | 0.7 | 0.8 | 0.7 | 0.7 | 0.4 | N |  |  | OP | X | 1 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1956 | natural gas peaker | TRUE | 9973 | City of Kahoka | 2138 | Kahoka | MO | Clark | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | NA | NA | 0.8 | 0.8 | 0.7 | 0.8 | 0.4 | N |  |  | SB | N | 1 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | Y | N
Vintage1969 | natural gas peaker | TRUE | 9973 | City of Kahoka | 2138 | Kahoka | MO | Clark | 8 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | NA | NA | 1.5 | 0.8 | 1.4 | 1.5 | 0.7 | N |  |  | SB | N | 9 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | Y | N
Vintage1982 | natural gas peaker | TRUE | 9973 | City of Kahoka | 2138 | Kahoka | MO | Clark | 9 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | NA | NA | 0.9 | 0.8 | 0.8 | 0.9 | 0.4 | N |  |  | SB | N | 7 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | Y | N
Vintage1971 | natural gas peaker | TRUE | 10152 | City of Kennett - (MO) | 2139 | Kennett | MO | Dunklin | 10 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | SPP/KENN |  | 6.2 | 0.8 | 5.6 | 5.6 | 5 | N |  |  | OP | X | 8 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1975 | natural gas peaker | TRUE | 10152 | City of Kennett - (MO) | 2139 | Kennett | MO | Dunklin | 11 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | SPP/KENN |  | 6.2 | 0.8 | 5.6 | 5.6 | 5 | N |  |  | OP | X | 8 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N | 0 | 1H | [23 empty] | Y | Y | Y
Vintage2001 | natural gas peaker | TRUE | 10152 | City of Kennett - (MO) | 2139 | Kennett | MO | Dunklin | 12 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | SPP/KENN |  | 6.4 | 0.8 | 5.7 | 5.7 | 5.1 | N |  |  | OP | X | 8 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2001 | natural gas peaker | TRUE | 10152 | City of Kennett - (MO) | 2139 | Kennett | MO | Dunklin | 13 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | SPP/KENN |  | 6.4 | 0.8 | 5.7 | 5.7 | 5.1 | N |  |  | OP | X | 8 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1965 | natural gas peaker | TRUE | 10152 | City of Kennett - (MO) | 2139 | Kennett | MO | Dunklin | 9 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | SPP/KENN |  | 6.2 | 0.8 | 5.6 | 5.6 | 5 | N |  |  | OP | X | 8 | 1965 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N | 0 | 1H | [23 empty] | Y | Y | Y
Vintage2013 | petroleum | TRUE | 10538 | City of La Plata - (MO) | 2140 | La Plata | MO | Macon | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.7 | 1.7 | 0.2 | N |  |  | OP | X | 3 | 2013 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage2013 | petroleum | TRUE | 10538 | City of La Plata - (MO) | 2140 | La Plata | MO | Macon | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.7 | 1.7 | 0.2 | N |  |  | OP | X | 3 | 2013 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1985 | petroleum | TRUE | 11460 | City of Macon - (MO) | 2141 | Macon | MO | Macon | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 0.7 | 0.7 | 0.4 | N |  |  | SB | Y | 9 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1996 | petroleum | TRUE | 11540 | City of Malden - (MO) | 2142 | Malden | MO | Dunklin | 2A | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.3 | N |  |  | SB | Y | 2 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1996 | petroleum | TRUE | 11540 | City of Malden - (MO) | 2142 | Malden | MO | Dunklin | 3A | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.3 | N |  |  | SB | Y | 2 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1996 | petroleum | TRUE | 11540 | City of Malden - (MO) | 2142 | Malden | MO | Dunklin | 4A | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.3 | N |  |  | SB | Y | 2 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1957 | petroleum | TRUE | 11540 | City of Malden - (MO) | 2142 | Malden | MO | Dunklin | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.4 | 0.8 | 1.2 | 1.2 | 0.7 | N |  |  | SB | Y | 8 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1963 | petroleum | TRUE | 11540 | City of Malden - (MO) | 2142 | Malden | MO | Dunklin | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 0.7 | N |  |  | SB | Y | 8 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1973 | petroleum | TRUE | 11540 | City of Malden - (MO) | 2142 | Malden | MO | Dunklin | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.8 | 0.8 | 2.5 | 2.5 | 1 | N |  |  | SB | Y | 8 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1973 | petroleum | TRUE | 11540 | City of Malden - (MO) | 2142 | Malden | MO | Dunklin | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.3 | 0.8 | 3.8 | 3.8 | 1.5 | N |  |  | SB | Y | 8 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1990 | natural gas peaker | TRUE | 11732 | City of Marshall - (MO) | 2144 | Marshall (MO) | MO | Saline | 10 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 6.3 | 0.8 | 6.3 | 6.3 | 3 | N |  |  | OP | X | 6 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1994 | natural gas peaker | TRUE | 11732 | City of Marshall - (MO) | 2144 | Marshall (MO) | MO | Saline | 11 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 6.3 | 0.8 | 6.3 | 6.3 | 3 | N |  |  | OP | X | 1 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1988 | petroleum | TRUE | 11732 | City of Marshall - (MO) | 2144 | Marshall (MO) | MO | Saline | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 1 | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 6 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1988 | petroleum | TRUE | 11732 | City of Marshall - (MO) | 2144 | Marshall (MO) | MO | Saline | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 1 | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 6 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1988 | petroleum | TRUE | 11732 | City of Marshall - (MO) | 2144 | Marshall (MO) | MO | Saline | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 1 | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 6 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1972 | natural gas peaker | TRUE | 11732 | City of Marshall - (MO) | 2144 | Marshall (MO) | MO | Saline | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MO.KC.MARS6.MP | MO.KC.MARS6.MP | 15.2 | 0.85 | 14 | 17 | 3 | N |  |  | OP | X | 5 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1972 | petroleum | TRUE | 12294 | City of Memphis - (MO) | 2145 | Memphis | MO | Scotland | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0 | N |  |  | OP | X | 12 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1989 | petroleum | TRUE | 12294 | City of Memphis - (MO) | 2145 | Memphis | MO | Scotland | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0 | N |  |  | OP | X | 8 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1989 | petroleum | TRUE | 12294 | City of Memphis - (MO) | 2145 | Memphis | MO | Scotland | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0 | N |  |  | OP | X | 8 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1989 | petroleum | TRUE | 12294 | City of Memphis - (MO) | 2145 | Memphis | MO | Scotland | 12 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0 | N |  |  | OP | X | 11 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1990 | petroleum | TRUE | 12294 | City of Memphis - (MO) | 2145 | Memphis | MO | Scotland | 13 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0 | N |  |  | OP | X | 9 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1945 | petroleum | TRUE | 12294 | City of Memphis - (MO) | 2145 | Memphis | MO | Scotland | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0 | N |  |  | OP | X | 12 | 1945 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1957 | petroleum | TRUE | 12294 | City of Memphis - (MO) | 2145 | Memphis | MO | Scotland | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.9 | 0.9 | 0 | N |  |  | OP | X | 12 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1960 | petroleum | TRUE | 12294 | City of Memphis - (MO) | 2145 | Memphis | MO | Scotland | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0 | N |  |  | OP | X | 12 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1966 | petroleum | TRUE | 12294 | City of Memphis - (MO) | 2145 | Memphis | MO | Scotland | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 0 | N |  |  | OP | X | 12 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1972 | petroleum | TRUE | 12294 | City of Memphis - (MO) | 2145 | Memphis | MO | Scotland | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 0 | N |  |  | OP | X | 12 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1989 | natural gas peaker | TRUE | 17833 | City Utilities of Springfield - (MO) | 2161 | James River Power Station | MO | Greene | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SPRM_JRCT1 | SPRM_JRCT1 | 96 | 0.9 | 75 | 75 | 25 | N |  |  | OP | X | 4 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1992 | natural gas peaker | TRUE | 17833 | City Utilities of Springfield - (MO) | 2161 | James River Power Station | MO | Greene | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SPRM_JRCT2 | SPRM_JRCT2 | 101.5 | 0.9 | 80 | 80 | 25 | N |  |  | OP | X | 6 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1970 | petroleum | TRUE | 19474 | City of Unionville - (MO) | 2164 | Unionville City of | MO | Putnam | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.9 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 12 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage1975 | petroleum | TRUE | 19474 | City of Unionville - (MO) | 2164 | Unionville City of | MO | Putnam | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.7 | 0.9 | 1.7 | 1.7 | 0.2 | N |  |  | OP | X | 10 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N |  |  | 10M | [23 empty] | Y | N | Y
Vintage1935 | petroleum | TRUE | 19474 | City of Unionville - (MO) | 2164 | Unionville City of | MO | Putnam | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.2 | 0.9 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1935 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage1970 | petroleum | TRUE | 19474 | City of Unionville - (MO) | 2164 | Unionville City of | MO | Putnam | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 1 | 0.9 | 0.9 | 0.2 | N |  |  | OP | X | 7 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 10M | [23 empty] | N
Vintage1955 | petroleum | TRUE | 19474 | City of Unionville - (MO) | 2164 | Unionville City of | MO | Putnam | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 1 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 10M | [23 empty] | N
Vintage1955 | petroleum | TRUE | 19474 | City of Unionville - (MO) | 2164 | Unionville City of | MO | Putnam | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 1 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 10M | [23 empty] | N
Vintage1962 | petroleum | TRUE | 19474 | City of Unionville - (MO) | 2164 | Unionville City of | MO | Putnam | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 1 | 0.9 | 0.9 | 0.2 | N |  |  | OP | X | 1 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage1967 | petroleum | TRUE | 19474 | City of Unionville - (MO) | 2164 | Unionville City of | MO | Putnam | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 1 | 1.1 | 1.1 | 0.2 | N |  |  | OP | X | 1 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N |  |  | 10M | [23 empty] | Y | N | Y
Vintage1994 | petroleum | TRUE | 19474 | City of Unionville - (MO) | 2164 | Unionville City of | MO | Putnam | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 1 | 2 | 2 | 0.2 | N |  |  | OP | X | 12 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage1959 | hydro | TRUE | 19647 | USCE-Little Rock District | 2166 | Table Rock | MO | Taney | 1 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 50 | 0.95 | 53 | 53 | 15 | N |  |  | OP | X | 5 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1959 | hydro | TRUE | 19647 | USCE-Little Rock District | 2166 | Table Rock | MO | Taney | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 50 | 0.95 | 53 | 53 | 15 | N |  |  | OP | X | 5 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1961 | hydro | TRUE | 19647 | USCE-Little Rock District | 2166 | Table Rock | MO | Taney | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 50 | 0.95 | 57.5 | 57.5 | 15 | N |  |  | OP | X | 5 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1961 | hydro | TRUE | 19647 | USCE-Little Rock District | 2166 | Table Rock | MO | Taney | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 50 | 0.95 | 53 | 53 | 15 | N |  |  | OP | X | 6 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1972 | hard coal | TRUE | 924 | Associated Electric Coop, Inc | 2167 | New Madrid | MO | New Madrid | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 650 | 0.9 | 575 | 590 | 175 | N |  |  | OP | X | 10 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  |  |  | Y | Y | [18 empty] | N | N | N
Vintage1977 | hard coal | TRUE | 924 | Associated Electric Coop, Inc | 2167 | New Madrid | MO | New Madrid | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 650 | 0.9 | 571 | 593 | 175 | N |  |  | OP | X | 6 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  |  |  | Y | Y | [15 empty] | Y | 5 | 2023 | N | N | N
Vintage1966 | hard coal | TRUE | 924 | Associated Electric Coop, Inc | 2168 | Thomas Hill | MO | Randolph | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 171.7 | 0.85 | 165 | 165 | 100 | N |  |  | OP | X | 12 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  |  |  | Y | Y | [18 empty] | N | N | N
Vintage1969 | hard coal | TRUE | 924 | Associated Electric Coop, Inc | 2168 | Thomas Hill | MO | Randolph | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 272 | 0.85 | 269 | 277 | 150 | N |  |  | OP | X | 3 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  |  |  | Y | Y | [18 empty] | N | N | N
Vintage1982 | hard coal | TRUE | 924 | Associated Electric Coop, Inc | 2168 | Thomas Hill | MO | Randolph | 3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 738 | 0.9 | 701 | 715 | 175 | N |  |  | OP | X | 5 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | Y | 11 | 2022 | N | N | N
Vintage2003 | natural gas peaker | TRUE | 12199 | Montana-Dakota Utilities Co | 2176 | Glendive GT | MT | Dawson | GT-2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MDU.GLENDC1 | MDU.GLENDC1 | 43 | 0.85 | 40.1 | 43.2 | 10 | N |  |  | OP | X | 5 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1979 | natural gas peaker | TRUE | 12199 | Montana-Dakota Utilities Co | 2176 | Glendive GT | MT | Dawson | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MDU.GLENDC2 | MDU.GLENDC2 | 40.7 | 0.9 | 34.8 | 40.9 | 9 | N |  |  | OP | X | 6 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1972 | natural gas peaker | TRUE | 12199 | Montana-Dakota Utilities Co | 2177 | Miles City GT | MT | Custer | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MDU.MCTURB1 | MDU.MCTURB1 | 23.3 | 0.9 | 23.6 | 27.5 | 7 | N |  |  | OP | X | 5 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1927 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2181 | Black Eagle | MT | Cascade | BLA1 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 7.8 | 0.8 | 7 | 7 | 1 | N |  |  | OA | X | 9 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [7 empty] | 1.5 | 1.5 | 6 | 2022 | [12 empty] | N
Vintage1927 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2181 | Black Eagle | MT | Cascade | BLA2 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 7.8 | 0.8 | 7 | 7 | 1 | N |  |  | OP | X | 9 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1927 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2181 | Black Eagle | MT | Cascade | BLA3 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 8.4 | 0.8 | 7 | 7 | 1 | N |  |  | OP | X | 9 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1958 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2182 | Cochrane | MT | Cascade | COC1 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 28.4 | 0.8 | 31 | 31 | 1 | N |  |  | OP | X | 7 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1958 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2182 | Cochrane | MT | Cascade | COC2 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 32 | 0.9 | 31 | 31 | 1 | N |  |  | OP | X | 7 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1911 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2185 | Hauser | MT | Lewis and Clark | HAU1 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 2.8 | 1 | 2.8 | 2.8 | 1 | N |  |  | OP | X | 11 | 1911 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1911 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2185 | Hauser | MT | Lewis and Clark | HAU2 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 3.9 | 0.9 | 3.9 | 3.9 | 1 | Y | 4 | 2021 | OP | X | 11 | 1911 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1911 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2185 | Hauser | MT | Lewis and Clark | HAU3 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 2.8 | 1 | 2.8 | 2.8 | 1 | N |  |  | OP | X | 11 | 1911 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1911 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2185 | Hauser | MT | Lewis and Clark | HAU5 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 2.8 | 1 | 2.8 | 2.8 | 1 | N |  |  | OA | X | 11 | 1911 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [7 empty] | 0.8 | 0.8 | 8 | 2022 | [12 empty] | N
Vintage1915 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2185 | Hauser | MT | Lewis and Clark | HAU6 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 3 | 0.8 | 3.8 | 3.8 | 1 | N |  |  | OP | X | 9 | 1915 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage2019 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2185 | Hauser | MT | Lewis and Clark | HAU7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.5 | 0.9 | 3.4 | 3.4 | 1 | N |  |  | OP | X | 5 | 2019 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1918 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2186 | Holter | MT | Cascade | HOL1 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 9.6 | 0.8 | 13.3 | 13.3 | 1 | N |  |  | OP | X | 7 | 1918 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [7 empty] | 4.1 | 4.1 | 6 | 2023 | [12 empty] | N
Vintage1918 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2186 | Holter | MT | Cascade | HOL2 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 9.6 | 0.8 | 13.3 | 13.3 | 1 | N |  |  | OP | X | 7 | 1918 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1918 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2186 | Holter | MT | Cascade | HOL3 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 9.6 | 0.8 | 13.3 | 13.3 | 1 | N |  |  | OA | X | 7 | 1918 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [7 empty] | 4.1 | 4.1 | 6 | 2022 | [12 empty] | N
Vintage1918 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2186 | Holter | MT | Cascade | HOL4 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 9.6 | 0.8 | 13.3 | 13.3 | 1 | N |  |  | OP | X | 7 | 1918 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1938 | hydro | TRUE | 60973 | Energy Keepers Inc | 2188 | Selis Ksanka Qlispe | MT | Lake | KER1 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 70.6 | 0.9 | 70.6 | 70.6 | 1 | N |  |  | OP | X | 10 | 1938 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1949 | hydro | TRUE | 60973 | Energy Keepers Inc | 2188 | Selis Ksanka Qlispe | MT | Lake | KER2 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 70.6 | 0.9 | 70.6 | 70.6 | 1 | N |  |  | OP | X | 5 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1954 | hydro | TRUE | 60973 | Energy Keepers Inc | 2188 | Selis Ksanka Qlispe | MT | Lake | KER3 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 86.6 | 0.96 | 86.6 | 86.6 | 1 | N |  |  | OP | X | 11 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1930 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2191 | Morony | MT | Cascade | MOR1 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 31.5 | 0.9 | 24.5 | 24.5 | 1 | N |  |  | OP | X | 1 | 1930 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1930 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2191 | Morony | MT | Cascade | MOR2 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 31.5 | 0.9 | 24.5 | 24.5 | 1 | N |  |  | OP | X | 1 | 1930 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1925 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2192 | Mystic | MT | Stillwater | MYS1 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 6 | 0.8 | 6 | 6 | 1 | N |  |  | OP | X | 5 | 1925 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1925 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2192 | Mystic | MT | Stillwater | MYS2 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 6 | 0.8 | 6 | 6 | 1 | N |  |  | OP | X | 5 | 1925 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage2013 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2193 | Rainbow (MT) | MT | Cascade | RAI9 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 59 | 0.9 | 64 | 64 | 1 | N |  |  | OP | X | 3 | 2013 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1915 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2194 | Ryan | MT | Cascade | RYA1 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 8 | 0.8 | 12 | 12 | 1 | N |  |  | OP | X | 8 | 1915 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1915 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2194 | Ryan | MT | Cascade | RYA2 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 9.2 | 0.8 | 12 | 12 | 1 | N |  |  | OP | X | 8 | 1915 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1915 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2194 | Ryan | MT | Cascade | RYA3 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 9.2 | 0.8 | 12 | 12 | 1 | N |  |  | OP | X | 8 | 1915 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1915 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2194 | Ryan | MT | Cascade | RYA4 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 9.2 | 0.8 | 12 | 12 | 1 | N |  |  | OP | X | 8 | 1915 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1916 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2194 | Ryan | MT | Cascade | RYA5 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 9.2 | 0.8 | 11.5 | 11.5 | 1 | N |  |  | OP | X | 9 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1916 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2194 | Ryan | MT | Cascade | RYA6 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 8 | 0.8 | 12 | 12 | 1 | N |  |  | OP | X | 9 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1917 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2195 | Thompson Falls | MT | Sanders | TF1 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 7 | 0.8 | 7.5 | 7.5 | 1 | N |  |  | OP | X | 7 | 1917 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1917 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2195 | Thompson Falls | MT | Sanders | TF2 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 7 | 0.8 | 6.5 | 6.5 | 1 | N |  |  | OP | X | 5 | 1917 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1916 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2195 | Thompson Falls | MT | Sanders | TF3 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 7 | 0.8 | 7.5 | 7.5 | 1 | N |  |  | OP | X | 11 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1916 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2195 | Thompson Falls | MT | Sanders | TF4 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 6 | 0.8 | 6.5 | 6.5 | 1 | N |  |  | OP | X | 11 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1915 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2195 | Thompson Falls | MT | Sanders | TF5 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 7 | 0.8 | 6 | 6.5 | 1 | N |  |  | OP | X | 7 | 1915 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1915 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2195 | Thompson Falls | MT | Sanders | TF6 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 7 | 0.8 | 6.5 | 6.5 | 1 | N |  |  | OP | X | 7 | 1915 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1915 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 2195 | Thompson Falls | MT | Sanders | TF7 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 57.1 | 0.9 | 53 | 53 | 10 | N |  |  | OP | X | 7 | 1915 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1979 | petroleum | TRUE | 56815 | NorthWestern Energy (MT wind/thermal) | 2196 | Old Faithful | WY | Teton | 1 | Petroleum Liquids | IC |  | S | X | X | NA | NA | 1 | 0.8 | 1 | 1 | 0.3 | N |  |  | SB | N | 12 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1979 | petroleum | TRUE | 56815 | NorthWestern Energy (MT wind/thermal) | 2196 | Old Faithful | WY | Teton | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.3 | N |  |  | SB | N | 12 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1959 | hydro | TRUE | 20169 | Avista Corp | 2199 | Noxon Rapids | MT | Sanders | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 99 | 0.9 | 113.9 | 120.3 | 30 | N |  |  | OP | X | 9 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1959 | hydro | TRUE | 20169 | Avista Corp | 2199 | Noxon Rapids | MT | Sanders | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 76.8 | 0.9 | 105 | 120 | 30 | N |  |  | OP | X | 10 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1959 | hydro | TRUE | 20169 | Avista Corp | 2199 | Noxon Rapids | MT | Sanders | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 99 | 0.9 | 113.9 | 120 | 30 | N |  |  | OP | X | 12 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1960 | hydro | TRUE | 20169 | Avista Corp | 2199 | Noxon Rapids | MT | Sanders | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 99 | 0.9 | 113.9 | 120 | 30 | N |  |  | OP | X | 4 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1977 | hydro | TRUE | 20169 | Avista Corp | 2199 | Noxon Rapids | MT | Sanders | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 114 | 0.95 | 134 | 142.2 | 40 | N |  |  | OP | X | 12 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1952 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 2203 | Hungry Horse | MT | Flathead | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 107 | 0.95 | 107 | 107 | 0 | N |  |  | OP | X | 10 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1952 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 2203 | Hungry Horse | MT | Flathead | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 107 | 0.95 | 107 | 107 | 0 | N |  |  | OP | X | 12 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1953 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 2203 | Hungry Horse | MT | Flathead | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 107 | 0.95 | 107 | 107 | 0 | N |  |  | OP | X | 7 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1953 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 2203 | Hungry Horse | MT | Flathead | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 107 | 0.95 | 107 | 107 | 0 | N |  |  | OP | X | 7 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1966 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 2204 | Yellowtail | MT | Big Horn | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 71.9 | 0.95 | 71.9 | 71.9 | 0 | N |  |  | OP | X | 11 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1966 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 2204 | Yellowtail | MT | Big Horn | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 62.5 | 0.95 | 71.9 | 71.9 | 0 | Y | 6 | 2021 | OP | X | 10 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1966 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 2204 | Yellowtail | MT | Big Horn | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 71.9 | 0.95 | 71.9 | 71.9 | 0 | N |  |  | OP | X | 8 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1966 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 2204 | Yellowtail | MT | Big Horn | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 71.9 | 0.95 | 71.8 | 71.8 | 0 | N |  |  | OP | X | 8 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1976 | natural gas peaker | TRUE | 695 | City of Ansley - (NE) | 2214 | Ansley | NE | Custer | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 10 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | Y | Y
Vintage1969 | petroleum | TRUE | 695 | City of Ansley - (NE) | 2214 | Ansley | NE | Custer | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.5 | 0.5 | 0.3 | N |  |  | OP | X | 6 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1982 | natural gas peaker | TRUE | 993 | Auburn Board of Public Works | 2215 | Auburn | NE | Nemaha | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.4 | 0.8 | 2.2 | 2.4 | 1 | N |  |  | OP | X | 4 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1949 | natural gas peaker | TRUE | 993 | Auburn Board of Public Works | 2215 | Auburn | NE | Nemaha | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1 | 0.8 | 0.9 | 1 | 0.7 | N |  |  | OP | X | 6 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1993 | natural gas peaker | TRUE | 993 | Auburn Board of Public Works | 2215 | Auburn | NE | Nemaha | 4A | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.7 | 0.8 | 3.7 | 3.7 | 2.5 | N |  |  | OP | X | 6 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1973 | natural gas peaker | TRUE | 993 | Auburn Board of Public Works | 2215 | Auburn | NE | Nemaha | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.3 | 0.8 | 3 | 3.3 | 1.8 | N |  |  | OP | X | 7 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1967 | natural gas peaker | TRUE | 993 | Auburn Board of Public Works | 2215 | Auburn | NE | Nemaha | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2.5 | 2.7 | 1.5 | N |  |  | OP | X | 5 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1987 | natural gas peaker | TRUE | 993 | Auburn Board of Public Works | 2215 | Auburn | NE | Nemaha | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 5.6 | 0.8 | 5.2 | 5.6 | 3.5 | N |  |  | OP | X | 7 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1960 | petroleum | TRUE | 871 | Village of Arnold - (NE) | 2216 | Arnold | NE | Custer | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0 | N |  |  | SB | Y | 1 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N
Vintage1937 | petroleum | TRUE | 871 | Village of Arnold - (NE) | 2216 | Arnold | NE | Custer | 2A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0 | N |  |  | OS | X | 1 | 1937 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N
Vintage1942 | petroleum | TRUE | 871 | Village of Arnold - (NE) | 2216 | Arnold | NE | Custer | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0 | N |  |  | OS | X | 1 | 1942 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N
Vintage1946 | petroleum | TRUE | 871 | Village of Arnold - (NE) | 2216 | Arnold | NE | Custer | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.2 | 0.2 | 0 | N |  |  | OS | X | 1 | 1946 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N
Vintage1957 | petroleum | TRUE | 1435 | City of Beaver City - (NE) | 2217 | Beaver City | NE | Furnas | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 10 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1963 | natural gas peaker | TRUE | 1435 | City of Beaver City - (NE) | 2217 | Beaver City | NE | Furnas | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 9 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1947 | petroleum | TRUE | 1435 | City of Beaver City - (NE) | 2217 | Beaver City | NE | Furnas | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 10 | 1947 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1967 | natural gas peaker | TRUE | 1435 | City of Beaver City - (NE) | 2217 | Beaver City | NE | Furnas | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.8 | 0.9 | 0.1 | N |  |  | OP | X | 9 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1936 | petroleum | TRUE | 2277 | City of Broken Bow - (NE) | 2221 | Broken Bow | NE | Custer | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 12 | 1936 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1970 | natural gas peaker | TRUE | 2277 | City of Broken Bow - (NE) | 2221 | Broken Bow | NE | Custer | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.5 | 0.8 | 3.5 | 3.5 | 0.5 | N |  |  | OP | X | 12 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1945 | petroleum | TRUE | 2277 | City of Broken Bow - (NE) | 2221 | Broken Bow | NE | Custer | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 12 | 1945 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1951 | natural gas peaker | TRUE | 2277 | City of Broken Bow - (NE) | 2221 | Broken Bow | NE | Custer | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.7 | 0.7 | 0.3 | N |  |  | OP | X | 12 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1951 | natural gas peaker | TRUE | 2277 | City of Broken Bow - (NE) | 2221 | Broken Bow | NE | Custer | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.4 | N |  |  | OP | X | 12 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1961 | natural gas peaker | TRUE | 2277 | City of Broken Bow - (NE) | 2221 | Broken Bow | NE | Custer | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.1 | 0.8 | 2 | 2 | 0.5 | N |  |  | OP | X | 12 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1972 | petroleum | TRUE | 2609 | City of Burwell - (NE) | 2222 | Burwell | NE | Garfield | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.9 | 1.3 | 1.3 | 0.1 | N |  |  | OP | X | 10 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1968 | petroleum | TRUE | 2609 | City of Burwell - (NE) | 2222 | Burwell | NE | Garfield | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.9 | 1.1 | 1.1 | 0.1 | N |  |  | OP | X | 1 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1960 | petroleum | TRUE | 2609 | City of Burwell - (NE) | 2222 | Burwell | NE | Garfield | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 7 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1955 | petroleum | TRUE | 2609 | City of Burwell - (NE) | 2222 | Burwell | NE | Garfield | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.9 | 0.6 | 0.6 | 0.1 | N |  |  | SB | Y | 3 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2005 | petroleum | TRUE | 2888 | City of Cambridge - (NE) | 2223 | Cambridge | NE | Furnas | CAT1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 1 | 2 | 2 | 0.1 | N |  |  | SB | Y | 6 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage2005 | petroleum | TRUE | 2888 | City of Cambridge - (NE) | 2223 | Cambridge | NE | Furnas | CAT2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 1 | 2 | 2 | 0.1 | N |  |  | OP | X | 6 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1983 | petroleum | TRUE | 2931 | Village of Campbell - (NE) | 2225 | Campbell Village | NE | Franklin | IC4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 1 | 1 | 1 | 1 | N |  |  | SB | Y | 9 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | [26 empty] | N
Vintage1958 | natural gas steam turbine | TRUE | 13337 | Nebraska Public Power District | 2226 | Canaday | NE | Gosper | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | NPPD_CANADAY | NPPD_CANADAY | 108.8 | 0.85 | 99.3 | 99.3 | 0 | N |  |  | OP | X | 1 | 1958 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1941 | hydro | TRUE | 3271 | Central Nebraska Pub P&I Dist | 2227 | Jeffrey | NE | Lincoln | 1 | Conventional Hydroelectric | HY |  | S | X | X | NPPDJEFFREYUN1 | NPPDJEFFREYUN1 | 10.8 | 0.9 | 10.5 | 10.5 | 2 | N |  |  | OP | X | 1 | 1941 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1941 | hydro | TRUE | 3271 | Central Nebraska Pub P&I Dist | 2227 | Jeffrey | NE | Lincoln | 2 | Conventional Hydroelectric | HY |  | S | X | X | NPPDJEFFREYUN2 | NPPDJEFFREYUN2 | 10.8 | 0.9 | 10.5 | 10.5 | 2 | N |  |  | OP | X | 1 | 1941 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1941 | hydro | TRUE | 3271 | Central Nebraska Pub P&I Dist | 2228 | Johnson 1 | NE | Gosper | 1 | Conventional Hydroelectric | HY |  | S | X | X | NPPDJOHNSON1UN1 | NPPDJOHNSON1UN1 | 10.8 | 0.9 | 10 | 10 | 2 | N |  |  | OP | X | 4 | 1941 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1941 | hydro | TRUE | 3271 | Central Nebraska Pub P&I Dist | 2228 | Johnson 1 | NE | Gosper | 2 | Conventional Hydroelectric | HY |  | S | X | X | NPPDJOHNSON1UN2 | NPPDJOHNSON1UN2 | 10.8 | 0.9 | 10 | 10 | 2 | N |  |  | OP | X | 4 | 1941 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1941 | hydro | TRUE | 3271 | Central Nebraska Pub P&I Dist | 2229 | Johnson 2 | NE | Gosper | 1 | Conventional Hydroelectric | HY |  | S | X | X | NPPDJOHNSON2UN1 | NPPDJOHNSON2UN1 | 22.5 | 0.9 | 22.5 | 22.5 | 3 | N |  |  | OP | X | 4 | 1941 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1982 | petroleum | TRUE | 3373 | City of Chappell - (NE) | 2230 | Chappell | NE | Deuel | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.9 | 1 | 1 | 0.1 | N |  |  | OP | X | 8 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1973 | petroleum | TRUE | 4527 | City of Crete | 2231 | Crete | NE | Saline | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 6 | 0.9 | 6 | 6.1 | 6 | N |  |  | OP | X | 6 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG | [5 empty] | 1H | [23 empty] | Y | Y | Y
Vintage1955 | natural gas peaker | TRUE | 4661 | City of Curtis - (NE) | 2232 | Curtis | NE | Frontier | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.9 | 0.9 | 0.8 | 0.8 | 0.1 | N |  |  | OP | X | 1 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1969 | natural gas peaker | TRUE | 4661 | City of Curtis - (NE) | 2232 | Curtis | NE | Frontier | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.1 | 0.9 | 1 | 1 | 0.1 | N |  |  | OP | X | 1 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1975 | natural gas peaker | TRUE | 4661 | City of Curtis - (NE) | 2232 | Curtis | NE | Frontier | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.4 | 0.9 | 1.2 | 1.2 | 0.1 | N |  |  | OP | X | 1 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1960 | natural gas peaker | TRUE | 4836 | City of David City | 2233 | David City | NE | Butler | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | N/A | N/A | 1.5 | 0.8 | 1.3 | 1.3 | 0 | N |  |  | OP | X | 1 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1949 | petroleum | TRUE | 4836 | City of David City | 2233 | David City | NE | Butler | 2 | Petroleum Liquids | IC |  | S | X | X | N/A | N/A | 1 | 0.8 | 0.8 | 0.8 | 0 | N |  |  | OP | X | 1 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1955 | natural gas peaker | TRUE | 4836 | City of David City | 2233 | David City | NE | Butler | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | N/A | N/A | 1 | 0.8 | 0.9 | 0.9 | 0 | N |  |  | OP | X | 1 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1966 | natural gas peaker | TRUE | 4836 | City of David City | 2233 | David City | NE | Butler | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | N/A | N/A | 2.3 | 0.8 | 1.8 | 1.8 | 0 | N |  |  | OP | X | 1 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1996 | petroleum | TRUE | 4836 | City of David City | 2233 | David City | NE | Butler | 5 | Petroleum Liquids | IC |  | S | X | X | N/A | N/A | 1.6 | 0.8 | 1.3 | 1.3 | 0 | N |  |  | OP | X | 12 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1996 | petroleum | TRUE | 4836 | City of David City | 2233 | David City | NE | Butler | 6 | Petroleum Liquids | IC |  | S | X | X | N/A | N/A | 1.6 | 0.8 | 1.3 | 1.3 | 0 | N |  |  | OP | X | 12 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1996 | petroleum | TRUE | 4836 | City of David City | 2233 | David City | NE | Butler | 7 | Petroleum Liquids | IC |  | S | X | X | N/A | N/A | 1.6 | 0.8 | 1.3 | 1.3 | 0 | N |  |  | OP | X | 12 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1956 | petroleum | TRUE | 5097 | City of Deshler - (NE) | 2234 | Deshler | NE | Thayer | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 1 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N
Vintage1999 | petroleum | TRUE | 5097 | City of Deshler - (NE) | 2234 | Deshler | NE | Thayer | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.3 | N |  |  | OP | X | 3 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1968 | natural gas peaker | TRUE | 5850 | City of Emerson - (NE) | 2235 | Emerson | NE | Dixon | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.1 | 1 | 1.1 | 1.1 | 0.2 | N |  |  | OP | X | 1 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1947 | petroleum | TRUE | 5850 | City of Emerson - (NE) | 2235 | Emerson | NE | Dixon | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.1 | 1 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 1 | 1947 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1960 | natural gas peaker | TRUE | 5850 | City of Emerson - (NE) | 2235 | Emerson | NE | Dixon | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.4 | 1 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 1 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1930 | petroleum | TRUE | 6175 | City of Falls City - (NE) | 2237 | Falls City | NE | Richardson | 1 | Petroleum Liquids | IC |  | S | X | X | MEAN_FCU_OPPD | MEAN_FCU_OPPD | 0.6 | 0.85 | 0.6 | 0.6 | 0.4 | N |  |  | OP | X | 8 | 1930 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1937 | petroleum | TRUE | 6175 | City of Falls City - (NE) | 2237 | Falls City | NE | Richardson | 2 | Petroleum Liquids | IC |  | S | X | X | MEAN_FCU_OPPD | MEAN_FCU_OPPD | 0.9 | 0.85 | 0.9 | 0.9 | 0.5 | N |  |  | OP | X | 8 | 1937 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1965 | natural gas peaker | TRUE | 6175 | City of Falls City - (NE) | 2237 | Falls City | NE | Richardson | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | MEAN_FCU_OPPD | MEAN_FCU_OPPD | 2.7 | 0.85 | 2.3 | 2.3 | 1.5 | N |  |  | OP | X | 2 | 1965 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1946 | natural gas peaker | TRUE | 6175 | City of Falls City - (NE) | 2237 | Falls City | NE | Richardson | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | MEAN_FCU_OPPD | MEAN_FCU_OPPD | 1.1 | 0.85 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 8 | 1946 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1950 | natural gas peaker | TRUE | 6175 | City of Falls City - (NE) | 2237 | Falls City | NE | Richardson | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | MEAN_FCU_OPPD | MEAN_FCU_OPPD | 2 | 0.85 | 1.4 | 1.4 | 0.8 | N |  |  | OP | X | 11 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1958 | natural gas peaker | TRUE | 6175 | City of Falls City - (NE) | 2237 | Falls City | NE | Richardson | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | MEAN_FCU_OPPD | MEAN_FCU_OPPD | 2.5 | 0.85 | 2 | 2 | 1.4 | N |  |  | OP | X | 2 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1972 | natural gas peaker | TRUE | 6175 | City of Falls City - (NE) | 2237 | Falls City | NE | Richardson | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | MEAN_FCU_OPPD | MEAN_FCU_OPPD | 6.2 | 0.85 | 5.9 | 5.9 | 4 | N |  |  | OP | X | 6 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1982 | natural gas peaker | TRUE | 6175 | City of Falls City - (NE) | 2237 | Falls City | NE | Richardson | 8 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | MEAN_FCU_OPPD | MEAN_FCU_OPPD | 6 | 0.85 | 6 | 6 | 3.8 | N |  |  | OP | X | 3 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2018 | natural gas peaker | TRUE | 6175 | City of Falls City - (NE) | 2237 | Falls City | NE | Richardson | 9 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | MEAN FCU OPPD | MEAN FCU OPPD | 9.3 | 0.8 | 9.3 | 9.3 | 3.9 | N |  |  | OP | X | 8 | 2018 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1963 | petroleum | TRUE | 6723 | City of Franklin - (NE) | 2238 | Franklin (NE) | NE | Franklin | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  |  | N |  | 10M | [23 empty] | Y | Y | N
Vintage1974 | petroleum | TRUE | 6723 | City of Franklin - (NE) | 2238 | Franklin (NE) | NE | Franklin | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 0.2 | N |  |  | OP | X | 10 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  |  | N |  | 10M | [23 empty] | Y | Y | N
Vintage1969 | petroleum | TRUE | 6723 | City of Franklin - (NE) | 2238 | Franklin (NE) | NE | Franklin | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.2 | N |  |  | OP | X | 11 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  |  | N |  | 10M | [23 empty] | Y | Y | N
Vintage1955 | petroleum | TRUE | 6723 | City of Franklin - (NE) | 2238 | Franklin (NE) | NE | Franklin | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.9 | 0.9 | 0.2 | N |  |  | OP | X | 1 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  |  | N |  | 10M | [23 empty] | Y | Y | N
Vintage2003 | natural gas peaker | TRUE | 6779 | City of Fremont - (NE) | 2240 | Lon Wright | NE | Dodge | 5OT | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | FREM_50T | FREM_50T | 40 | 0.9 | 38 | 40 | 20 | N |  |  | OP | X | 11 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1957 | hard coal | TRUE | 6779 | City of Fremont - (NE) | 2240 | Lon Wright | NE | Dodge | 6 | Conventional Steam Coal | ST |  | S | X | X | FREM_6 | FREM_6 | 16.5 | 0.85 | 15.5 | 15.5 | 6 | N |  |  | OP | X | 8 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: NG; DFO DFO DFO: PG; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1963 | hard coal | TRUE | 6779 | City of Fremont - (NE) | 2240 | Lon Wright | NE | Dodge | 7 | Conventional Steam Coal | ST |  | S | X | X | FREM_7 | FREM_7 | 22 | 0.85 | 21 | 21 | 6 | N |  |  | OP | X | 8 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: NG; DFO DFO DFO: PG; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1976 | hard coal | TRUE | 6779 | City of Fremont - (NE) | 2240 | Lon Wright | NE | Dodge | 8 | Conventional Steam Coal | ST |  | S | X | X | FREM_8 | FREM_8 | 91.5 | 0.9 | 82 | 82 | 30 | N |  |  | OP | X | 1 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: NG; DFO DFO DFO: PG; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage2017 | onshore wind | TRUE | 6779 | City of Fremont - (NE) | 2240 | Lon Wright | NE | Dodge | CTNWD | Onshore Wind Turbine | WT |  | S | X | X | NPPD.FREM.CTNWD1 | NPPD.FREM.CTNWD1 | 40.9 |  | 40.9 | 40.9 | 0.1 | N |  |  | OP | X | 11 | 2017 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WND |  |  |  |  | 19
Vintage2018 | solar pv | TRUE | 6779 | City of Fremont - (NE) | 2240 | Lon Wright | NE | Dodge | SLR1 | Solar Photovoltaic | PV |  | S | X | X | N/A | N/A | 1.3 |  | 1.3 | 1.3 |  | N |  |  | OP | X | 3 | 2018 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUN
Vintage2018 | solar pv | TRUE | 6779 | City of Fremont - (NE) | 2240 | Lon Wright | NE | Dodge | SLR2 | Solar Photovoltaic | PV |  | S | X | X | N/A | N/A | 1 |  | 1 | 1 |  | N |  |  | OP | X | 9 | 2018 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUN
Vintage1968 | natural gas peaker | TRUE | 40606 | City of Grand Island - (NE) | 2241 | C W Burdick | NE | Hall | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | NPPDGI_SUBHGRIS_GT1_RA | NPPDGI_SUBHGRIS_GT1_RA | 16 | 0.85 | 13.6 | 14.8 | 4 | N |  |  | OP | X | 3 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | Y | Y
Vintage2003 | natural gas peaker | TRUE | 40606 | City of Grand Island - (NE) | 2241 | C W Burdick | NE | Hall | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | NPPDGI_SUBHGRIS_GT2_RA | NPPDGI_SUBHGRIS_GT2_RA | 63.4 | 0.85 | 34 | 40 | 5 | N |  |  | OP | X | 4 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage2003 | natural gas peaker | TRUE | 40606 | City of Grand Island - (NE) | 2241 | C W Burdick | NE | Hall | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | NPPDGI_SUBHGRIS_GT3_RA | NPPDGI_SUBHGRIS_GT3_RA | 63.4 | 0.85 | 34 | 40 | 5 | N |  |  | OP | X | 4 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1972 | natural gas peaker | TRUE | 8245 | City of Hastings - (NE) | 2243 | Don Henry | NE | Adams | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 22 | 0.9 | 18 | 18 | 5 | N |  |  | SB | Y | 6 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1957 | natural gas steam turbine | TRUE | 8245 | City of Hastings - (NE) | 2244 | North Denver | NE | Adams | 4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 17 | 0.85 | 16 | 16 | 6 | N |  |  | SB | Y | 12 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | OVER | [23 empty] | Y | N | N
Vintage1967 | natural gas steam turbine | TRUE | 8245 | City of Hastings - (NE) | 2244 | North Denver | NE | Adams | 5 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 22 | 0.85 | 25 | 25 | 7 | N |  |  | SB | Y | 10 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | OVER | [23 empty] | Y | N | N
Vintage1956 | petroleum | TRUE | 10260 | City of Kimball - (NE) | 2248 | Kimball | NE | Kimball | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 0.7 | 0.8 | 0.5 | N |  |  | OP | X | 9 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1955 | petroleum | TRUE | 10260 | City of Kimball - (NE) | 2248 | Kimball | NE | Kimball | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 0.7 | 0.8 | 0.5 | N |  |  | OP | X | 9 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1959 | petroleum | TRUE | 10260 | City of Kimball - (NE) | 2248 | Kimball | NE | Kimball | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1 | 1.1 | 0.7 | N |  |  | OP | X | 9 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1960 | petroleum | TRUE | 10260 | City of Kimball - (NE) | 2248 | Kimball | NE | Kimball | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1 | 1.1 | 0.7 | N |  |  | OP | X | 9 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1944 | petroleum | TRUE | 10260 | City of Kimball - (NE) | 2248 | Kimball | NE | Kimball | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 0.6 | 0.6 | 0.5 | N |  |  | OP | X | 1 | 1944 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1974 | petroleum | TRUE | 10260 | City of Kimball - (NE) | 2248 | Kimball | NE | Kimball | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.9 | 0.8 | 3.6 | 3.7 | 2 | N |  |  | OP | X | 9 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1974 | natural gas peaker | TRUE | 10760 | City of Laurel - (NE) | 2249 | Laurel | NE | Cedar | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.9 | 1.1 | 1.2 | 0.1 | N |  |  | SB | Y | 10 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1970 | natural gas peaker | TRUE | 10760 | City of Laurel - (NE) | 2249 | Laurel | NE | Cedar | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.9 | 0.9 | 0.7 | 0.8 | 0.1 | N |  |  | SB | Y | 1 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1992 | natural gas peaker | TRUE | 10760 | City of Laurel - (NE) | 2249 | Laurel | NE | Cedar | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.9 | 1.1 | 1.2 | 0.1 | N |  |  | SB | Y | 10 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1972 | petroleum | TRUE | 11018 | Lincoln Electric System | 2250 | J Street | NE | Lancaster | 1 | Petroleum Liquids | GT |  | S | X | X | LES2_NUNJ_STREET_RA | LES_JSTREET | 27 | 0.85 | 29.3 | 31.7 | 4 | N |  |  | OP | X | 2 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H |  |  |  |  | N | N | [17 empty] | Y | N | Y
Vintage1953 | petroleum | TRUE | 11372 | City of Lyons - (NE) | 2253 | Lyons | NE | Burt | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.9 | 0.2 | 0.2 | 0.2 | N |  |  | OP | X | 1 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1960 | petroleum | TRUE | 11372 | City of Lyons - (NE) | 2253 | Lyons | NE | Burt | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.9 | 0.3 | 0.3 | 0.2 | N |  |  | OP | X | 1 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1967 | petroleum | TRUE | 11372 | City of Lyons - (NE) | 2253 | Lyons | NE | Burt | 4A | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.9 | 0.6 | 0.6 | 0.4 | N |  |  | OP | X | 1 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1979 | natural gas peaker | TRUE | 13334 | City of Nebraska City | 2255 | Nebraska City # 1 | NE | Otoe | 10 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 6.5 | 0.8 | 5.8 | 5.8 | 4 | N |  |  | OP | X | 4 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1953 | petroleum | TRUE | 13334 | City of Nebraska City | 2255 | Nebraska City # 1 | NE | Otoe | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1 | 1 | 1 | N |  |  | OP | X | 5 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage1955 | natural gas peaker | TRUE | 13334 | City of Nebraska City | 2255 | Nebraska City # 1 | NE | Otoe | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 5 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1957 | natural gas peaker | TRUE | 13334 | City of Nebraska City | 2255 | Nebraska City # 1 | NE | Otoe | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.1 | 0.8 | 2.7 | 2.7 | 2.5 | N |  |  | OP | X | 8 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1964 | natural gas peaker | TRUE | 13334 | City of Nebraska City | 2255 | Nebraska City # 1 | NE | Otoe | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2 | 0.8 | 1.7 | 1.7 | 1.5 | N |  |  | OP | X | 8 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1971 | natural gas peaker | TRUE | 13334 | City of Nebraska City | 2255 | Nebraska City # 1 | NE | Otoe | 8 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 4.1 | 0.8 | 3.6 | 3.6 | 3 | N |  |  | OP | X | 4 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1974 | natural gas peaker | TRUE | 13334 | City of Nebraska City | 2255 | Nebraska City # 1 | NE | Otoe | 9 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 6.4 | 0.8 | 5.8 | 5.8 | 4 | N |  |  | OP | X | 6 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1969 | natural gas peaker | TRUE | 13334 | City of Nebraska City | 2256 | Syracuse # 2 | NE | Otoe | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2 | 0.8 | 1.6 | 1.6 | 1.6 | N |  |  | OP | X | 4 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1970 | natural gas peaker | TRUE | 13334 | City of Nebraska City | 2256 | Syracuse # 2 | NE | Otoe | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2 | 0.8 | 1.6 | 1.6 | 1.6 | N |  |  | OP | X | 5 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1936 | hydro | TRUE | 11251 | Loup River Public Power Dist | 2260 | Columbus | NE | Platte | 1 | Conventional Hydroelectric | HY |  | S | X | X | NPPD_COLUMBS_1 | NPPD_COLUMBS_1 | 15.2 | 0.95 | 15 | 15 | 0 | N |  |  | OP | X | 1 | 1936 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1936 | hydro | TRUE | 11251 | Loup River Public Power Dist | 2260 | Columbus | NE | Platte | 2 | Conventional Hydroelectric | HY |  | S | X | X | NPPD_COLUMBS_2 | NPPD_COLUMBS_2 | 15.2 | 0.95 | 15 | 15 | 0 | N |  |  | OP | X | 1 | 1936 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1936 | hydro | TRUE | 11251 | Loup River Public Power Dist | 2260 | Columbus | NE | Platte | 3 | Conventional Hydroelectric | HY |  | S | X | X | NPPD_COLUMBS_3 | NPPD_COLUMBS_3 | 15.2 | 0.95 | 15 | 15 | 0 | N |  |  | OP | X | 1 | 1936 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1973 | petroleum | TRUE | 13337 | Nebraska Public Power District | 2265 | Hallam | NE | Lancaster | 1 | Petroleum Liquids | GT |  | S | X | X | NPPD_HALLAM | NPPD_HALLAM | 56.7 | 0.9 | 42.5 | 42.5 | 0 | N |  |  | OP | X | 6 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 10M | [23 empty] | Y | N | N
Vintage1973 | petroleum | TRUE | 13337 | Nebraska Public Power District | 2266 | Hebron | NE | Thayer | 1 | Petroleum Liquids | GT |  | S | X | X | NPPD_HEBRON | NPPD_HEBRON | 56.7 | 0.9 | 41.5 | 41.5 | 0 | N |  |  | OP | X | 6 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1921 | hydro | TRUE | 13337 | Nebraska Public Power District | 2268 | Kearney | NE | Buffalo | 1 | Conventional Hydroelectric | HY |  | S | X | X | N/A | N/A | 1.5 | 0.9 | 1 | 1 | 0 | N |  |  | OP | X | 1 | 1921 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1973 | petroleum | TRUE | 13337 | Nebraska Public Power District | 2271 | McCook | NE | Red Willow | 1 | Petroleum Liquids | GT |  | S | X | X | NPPD_MCCOOK | NPPD_MCCOOK | 56.7 | 0.9 | 39.7 | 39.7 | 0 | N |  |  | OP | X | 6 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1936 | hydro | TRUE | 11251 | Loup River Public Power Dist | 2273 | Monroe (NE) | NE | Platte | 1 | Conventional Hydroelectric | HY |  | S | X | X | N/A | N/A | 2.8 | 0.95 | 1 | 1 | 0 | N |  |  | OP | X | 1 | 1936 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1936 | hydro | TRUE | 11251 | Loup River Public Power Dist | 2273 | Monroe (NE) | NE | Platte | 2 | Conventional Hydroelectric | HY |  | S | X | X | N/A | N/A | 2.8 | 0.95 | 1 | 1 | 0 | N |  |  | OP | X | 1 | 1936 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1936 | hydro | TRUE | 11251 | Loup River Public Power Dist | 2273 | Monroe (NE) | NE | Platte | 3 | Conventional Hydroelectric | HY |  | S | X | X | N/A | N/A | 2.8 | 0.95 | 1 | 1 | 0 | N |  |  | OP | X | 1 | 1936 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1935 | hydro | TRUE | 13337 | Nebraska Public Power District | 2274 | North Platte | NE | Lincoln | 1 | Conventional Hydroelectric | HY |  | S | X | X | NPPD_NPLATTE_1 | NPPD_NPLATTE_1 | 13.1 | 0.9 | 12 | 12 | 0 | N |  |  | OP | X | 1 | 1935 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1935 | hydro | TRUE | 13337 | Nebraska Public Power District | 2274 | North Platte | NE | Lincoln | 2 | Conventional Hydroelectric | HY |  | S | X | X | NPPD_NPLATTE_2 | NPPD_NPLATTE_2 | 13.1 | 0.9 | 12 | 12 | 0 | N |  |  | OP | X | 1 | 1935 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1961 | hard coal | TRUE | 13337 | Nebraska Public Power District | 2277 | Sheldon | NE | Lancaster | 1 | Conventional Steam Coal | ST |  | S | X | X | NPPD_SHLD_1 | NPPD_SHLD_1 | 108.8 | 0.85 | 104 | 104 | 0 | N |  |  | OP | X | 1 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO DFO DFO: NG |  |  | N | N |  | OVER |  |  |  | Y | Y | [18 empty] | N | N | N
Vintage1965 | hard coal | TRUE | 13337 | Nebraska Public Power District | 2277 | Sheldon | NE | Lancaster | 2 | Conventional Steam Coal | ST |  | S | X | X | NPPD_SHLD_2 | NPPD_SHLD_2 | 119.9 | 0.85 | 115 | 115 | 0 | N |  |  | OP | X | 1 | 1965 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO DFO DFO: NG |  |  | N | N |  | OVER |  |  |  | Y | Y | [18 empty] | N | N | N
Vintage1973 | petroleum | TRUE | 14127 | Omaha Public Power District | 2290 | Jones Street | NE | Douglas | 1 | Petroleum Liquids | GT |  | S | X | X | JONES_STREET_1 |  | 65 | 0.9 | 61.2 | 61.2 | 23 | N |  |  | OP | X | 6 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1973 | petroleum | TRUE | 14127 | Omaha Public Power District | 2290 | Jones Street | NE | Douglas | 2 | Petroleum Liquids | GT |  | S | X | X | JONES_STREET 2 |  | 65 | 0.9 | 62.2 | 62.2 | 23 | N |  |  | OP | X | 6 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1954 | natural gas steam turbine | TRUE | 14127 | Omaha Public Power District | 2291 | North Omaha | NE | Douglas | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | NORTH_OMAHA_1 |  | 73.5 | 0.8 | 64.8 |  | 38 | N |  |  | OP | X | 7 | 1954 | 12 | 2023 | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER |  | N |  |  | N | [18 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1957 | natural gas steam turbine | TRUE | 14127 | Omaha Public Power District | 2291 | North Omaha | NE | Douglas | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | NORTH_OMAHA_2 |  | 108.8 | 0.85 | 90.8 |  | 55 | N |  |  | OP | X | 4 | 1957 | 12 | 2023 | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER |  | N |  |  | N | [18 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1959 | natural gas steam turbine | TRUE | 14127 | Omaha Public Power District | 2291 | North Omaha | NE | Douglas | 3 | Natural Gas Steam Turbine | ST |  | S | X | X | NORTH OMAHA 3 |  | 108.8 | 0.85 | 86 | 41.4 | 55 | N |  |  | OP | X | 4 | 1959 | 12 | 2023 | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER |  | N |  |  | N | [18 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1963 | hard coal | TRUE | 14127 | Omaha Public Power District | 2291 | North Omaha | NE | Douglas | 4 | Conventional Steam Coal | ST |  | S | X | X | NORTH_OMAHA_4 |  | 136 | 0.85 | 120.1 | 101.8 | 61 | N |  |  | OP | X | 3 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1968 | hard coal | TRUE | 14127 | Omaha Public Power District | 2291 | North Omaha | NE | Douglas | 5 | Conventional Steam Coal | ST |  | S | X | X | NORTH_OMAHA_5 |  | 217.6 | 0.85 | 216.2 | 174.9 | 75 | N |  |  | OP | X | 5 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1972 | natural gas peaker | TRUE | 14127 | Omaha Public Power District | 2292 | Sarpy County | NE | Sarpy | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SARPY_1 |  | 55.4 | 0.9 | 55.4 | 55.4 | 22 | N |  |  | OP | X | 6 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1972 | natural gas peaker | TRUE | 14127 | Omaha Public Power District | 2292 | Sarpy County | NE | Sarpy | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SARPY_2 |  | 55.4 | 0.9 | 55.9 | 55.9 | 22 | N |  |  | OP | X | 6 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1996 | natural gas peaker | TRUE | 14127 | Omaha Public Power District | 2292 | Sarpy County | NE | Sarpy | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SARPY_3 |  | 106.3 | 0.85 | 107.8 | 107.8 | 54 | N |  |  | OP | X | 5 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 14127 | Omaha Public Power District | 2292 | Sarpy County | NE | Sarpy | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SARPY_4 |  | 58.9 | 0.85 | 48.7 | 48.7 | 30 | N |  |  | OP | X | 5 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2000 | natural gas peaker | TRUE | 14127 | Omaha Public Power District | 2292 | Sarpy County | NE | Sarpy | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SARPY_5 |  | 58.9 | 0.85 | 47.9 | 47.9 | 24 | N |  |  | OP | X | 5 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1996 | petroleum | TRUE | 14127 | Omaha Public Power District | 2292 | Sarpy County | NE | Sarpy | BSD | Petroleum Liquids | IC |  | S | X | X |  |  | 3.5 | 0.8 | 3.4 | 3.4 | 3.4 | N |  |  | SB | Y | 5 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1973 | petroleum | TRUE | 14172 | City of Ord - (NE) | 2294 | Ord | NE | Valley | 1 | Petroleum Liquids | IC |  | S | X | X | N/A | N/A | 5 | 0.8 | 5 | 5 | 0 | N |  |  | OP | X | 1 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1966 | petroleum | TRUE | 14172 | City of Ord - (NE) | 2294 | Ord | NE | Valley | 2 | Petroleum Liquids | IC |  | S | X | X | N/A | N/A | 1.5 | 0.8 | 1 | 1 | 0 | N |  |  | OP | X | 1 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | N | [22 empty] | Y | N | Y
Vintage1963 | petroleum | TRUE | 14172 | City of Ord - (NE) | 2294 | Ord | NE | Valley | 3 | Petroleum Liquids | IC |  | S | X | X | N/A | N/A | 2.5 | 0.8 | 2 | 2 | 0 | N |  |  | OP | X | 1 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1997 | petroleum | TRUE | 14172 | City of Ord - (NE) | 2294 | Ord | NE | Valley | 4A | Petroleum Liquids | IC |  | S | X | X | N/A | N/A | 1.5 | 0.8 | 1.4 | 1.4 | 0 | N |  |  | OP | X | 4 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1997 | petroleum | TRUE | 14172 | City of Ord - (NE) | 2294 | Ord | NE | Valley | 5A | Petroleum Liquids | IC |  | S | X | X | N/A | N/A | 1.5 | 0.8 | 1.4 | 1.4 | 0 | N |  |  | OP | X | 4 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1953 | natural gas peaker | TRUE | 14277 | Village of Oxford - (NE) | 2295 | Oxford (NE) | NE | Furnas | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.5 | 0.6 | 0.3 | N |  |  | OP | X | 8 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 10M | [23 empty] | Y | Y | Y
Vintage1956 | natural gas peaker | TRUE | 14277 | Village of Oxford - (NE) | 2295 | Oxford (NE) | NE | Furnas | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.8 | 0.9 | 0.5 | N |  |  | OP | X | 1 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 10M | [23 empty] | Y | Y | Y
Vintage1956 | natural gas peaker | TRUE | 14277 | Village of Oxford - (NE) | 2295 | Oxford (NE) | NE | Furnas | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.5 | 0.6 | 0.3 | N |  |  | OP | X | 1 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 10M | [23 empty] | Y | Y | Y
Vintage1972 | natural gas peaker | TRUE | 14277 | Village of Oxford - (NE) | 2295 | Oxford (NE) | NE | Furnas | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.2 | 1.3 | 0.3 | N |  |  | OP | X | 10 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 10M | [23 empty] | Y | Y | Y
Vintage1968 | petroleum | TRUE | 14656 | City of Pender - (NE) | 2296 | Pender | NE | Thurston | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 1 | 1.2 | 1.2 | 1.1 | N |  |  | OP | X | 1 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1973 | petroleum | TRUE | 14656 | City of Pender - (NE) | 2296 | Pender | NE | Thurston | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 1 | 2 | 2 | 1.8 | N |  |  | OP | X | 1 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1953 | petroleum | TRUE | 14656 | City of Pender - (NE) | 2296 | Pender | NE | Thurston | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 1 | 0.5 | 0.5 | 0.5 | N |  |  | OP | X | 1 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1961 | petroleum | TRUE | 14656 | City of Pender - (NE) | 2296 | Pender | NE | Thurston | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 1 | 0.8 | 0.8 | 0.8 | N |  |  | OP | X | 1 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1949 | petroleum | TRUE | 13698 | North Central Public Pwr Dist | 2297 | Plainview Muncipal Power | NE | Pierce | 1 | Petroleum Liquids | IC |  | W | X | X |  |  | 1.1 | 0.88 | 1.1 | 1.1 | 1.1 | N |  |  | OP | X | 1 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N
Vintage1958 | petroleum | TRUE | 13698 | North Central Public Pwr Dist | 2297 | Plainview Muncipal Power | NE | Pierce | 3 | Petroleum Liquids | IC |  | W | X | X |  |  | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | N |  |  | OP | X | 1 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N
Vintage1963 | petroleum | TRUE | 13698 | North Central Public Pwr Dist | 2297 | Plainview Muncipal Power | NE | Pierce | 4 | Petroleum Liquids | IC |  | W | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 1.2 | N |  |  | OP | X | 1 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N
Vintage1999 | petroleum | TRUE | 13698 | North Central Public Pwr Dist | 2297 | Plainview Muncipal Power | NE | Pierce | 5 | Petroleum Liquids | IC |  | W | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 6 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N
Vintage1953 | petroleum | TRUE | 15773 | City of Red Cloud - (NE) | 2299 | Red Cloud | NE | Webster | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.9 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 6 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1960 | petroleum | TRUE | 15773 | City of Red Cloud - (NE) | 2299 | Red Cloud | NE | Webster | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.9 | 1.2 | 1.2 | 0.1 | N |  |  | OP | X | 12 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1968 | petroleum | TRUE | 15773 | City of Red Cloud - (NE) | 2299 | Red Cloud | NE | Webster | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.9 | 1.2 | 1.2 | 0.1 | N |  |  | OP | X | 8 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1973 | petroleum | TRUE | 15773 | City of Red Cloud - (NE) | 2299 | Red Cloud | NE | Webster | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.2 | 0.9 | 2.2 | 2.2 | 0.1 | N |  |  | OP | X | 9 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1968 | petroleum | TRUE | 16667 | City of Sargent - (NE) | 2300 | Sargent | NE | Custer | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.95 | 1.1 | 1.1 | 0.6 | N |  |  | OP | X | 3 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1964 | petroleum | TRUE | 16667 | City of Sargent - (NE) | 2300 | Sargent | NE | Custer | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.95 | 0.9 | 0.9 | 0.5 | N |  |  | OP | X | 2 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1954 | petroleum | TRUE | 16667 | City of Sargent - (NE) | 2300 | Sargent | NE | Custer | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.95 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 1 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1949 | natural gas peaker | TRUE | 17149 | City of Sidney - (NE) | 2302 | Sidney (NE) | NE | Cheyenne | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.2 | 0.9 | 1 | 1.1 | 0.1 | N |  |  | OP | X | 1 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1931 | petroleum | TRUE | 17149 | City of Sidney - (NE) | 2302 | Sidney (NE) | NE | Cheyenne | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.9 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 1 | 1931 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1955 | natural gas peaker | TRUE | 17149 | City of Sidney - (NE) | 2302 | Sidney (NE) | NE | Cheyenne | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.1 | 0.9 | 2.5 | 2.5 | 0.1 | N |  |  | OP | X | 1 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1919 | hydro | TRUE | 17727 | Village of Spalding - (NE) | 2303 | Spalding | NE | Greeley | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 7 | 1919 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1956 | hydro | TRUE | 17727 | Village of Spalding - (NE) | 2303 | Spalding | NE | Greeley | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 7 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1947 | petroleum | TRUE | 17727 | Village of Spalding - (NE) | 2303 | Spalding | NE | Greeley | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | SB | N | 8 | 1947 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1959 | petroleum | TRUE | 17727 | Village of Spalding - (NE) | 2303 | Spalding | NE | Greeley | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.1 | N |  |  | SB | N | 8 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1975 | petroleum | TRUE | 17727 | Village of Spalding - (NE) | 2303 | Spalding | NE | Greeley | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 0.3 | N |  |  | SB | N | 7 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1952 | natural gas peaker | TRUE | 18230 | City of Stuart - (NE) | 2305 | Stuart (NE) | NE | Holt | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.7 | 0.8 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 1 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  |  | N |  | 1H | [23 empty] | N |  | N
Vintage1960 | petroleum | TRUE | 18230 | City of Stuart - (NE) | 2305 | Stuart (NE) | NE | Holt | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | SB | Y | 1 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N
Vintage1952 | petroleum | TRUE | 18230 | City of Stuart - (NE) | 2305 | Stuart (NE) | NE | Holt | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | SB | Y | 1 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N
Vintage1997 | petroleum | TRUE | 18230 | City of Stuart - (NE) | 2305 | Stuart (NE) | NE | Holt | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.1 | N |  |  | OP | X | 8 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1948 | natural gas peaker | TRUE | 18525 | City of Tecumseh | 2308 | Tecumseh | NE | Johnson | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.7 | 0.9 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 1 | 1948 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1968 | natural gas peaker | TRUE | 18525 | City of Tecumseh | 2308 | Tecumseh | NE | Johnson | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.5 | 0.9 | 1.4 | 1.4 | 0.1 | N |  |  | OP | X | 1 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1953 | natural gas peaker | TRUE | 18525 | City of Tecumseh | 2308 | Tecumseh | NE | Johnson | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.1 | 0.9 | 1 | 1 | 0.1 | N |  |  | OP | X | 1 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1960 | natural gas peaker | TRUE | 18525 | City of Tecumseh | 2308 | Tecumseh | NE | Johnson | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.9 | 1.2 | 1.2 | 0.1 | N |  |  | OP | X | 1 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1993 | natural gas peaker | TRUE | 18525 | City of Tecumseh | 2308 | Tecumseh | NE | Johnson | 5A | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.4 | 0.9 | 2.4 | 2.4 | 0.1 | N |  |  | OP | X | 3 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1960 | natural gas peaker | TRUE | 19968 | City of Wahoo - (NE) | 2310 | Wahoo | NE | Saunders | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.1 | 2.1 | 0.5 | N |  |  | OP | X | 9 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1936 | petroleum | TRUE | 19968 | City of Wahoo - (NE) | 2310 | Wahoo | NE | Saunders | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 8 | 1936 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1973 | natural gas peaker | TRUE | 19968 | City of Wahoo - (NE) | 2310 | Wahoo | NE | Saunders | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 4.4 | 0.8 | 4.4 | 4.4 | 1 | N |  |  | OP | X | 8 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1947 | natural gas peaker | TRUE | 19968 | City of Wahoo - (NE) | 2310 | Wahoo | NE | Saunders | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1.1 | 1.1 | 0.2 | N |  |  | OP | X | 6 | 1947 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1952 | natural gas peaker | TRUE | 19968 | City of Wahoo - (NE) | 2310 | Wahoo | NE | Saunders | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.1 | 0.8 | 2.2 | 2.2 | 0.5 | N |  |  | OP | X | 9 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1969 | natural gas peaker | TRUE | 19968 | City of Wahoo - (NE) | 2310 | Wahoo | NE | Saunders | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.5 | 0.8 | 3.4 | 3.4 | 1 | N |  |  | OP | X | 7 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1915 | petroleum | TRUE | 19980 | City of Wakefield - (NE) | 2311 | Wakefield | NE | Dixon | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.5 | 0.5 | 0.5 | N |  |  | OP | X | 1 | 1915 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1966 | petroleum | TRUE | 19980 | City of Wakefield - (NE) | 2311 | Wakefield | NE | Dixon | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1 | 1 | 1 | N |  |  | OP | X | 1 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1971 | petroleum | TRUE | 19980 | City of Wakefield - (NE) | 2311 | Wakefield | NE | Dixon | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.1 | 1.1 | 1.1 | N |  |  | OP | X | 1 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1961 | petroleum | TRUE | 19980 | City of Wakefield - (NE) | 2311 | Wakefield | NE | Dixon | IC4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.6 | 0.6 | 0.6 | N |  |  | OP | X | 1 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1951 | petroleum | TRUE | 20219 | City of Wayne | 2312 | Wayne IC | NE | Wayne | 1 | Petroleum Liquids | IC |  | S | X | X | N/A | N/A | 1.3 | 0.8 | 0.8 | 0.8 | 0 | N |  |  | OP | X | 1 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1947 | petroleum | TRUE | 20219 | City of Wayne | 2312 | Wayne IC | NE | Wayne | 2 | Petroleum Liquids | IC |  | S | X | X | N/A | N/A | 1 | 0.8 | 0.9 | 0.9 | 0 | N |  |  | SB | Y | 1 | 1947 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1956 | petroleum | TRUE | 20219 | City of Wayne | 2312 | Wayne IC | NE | Wayne | 3 | Petroleum Liquids | IC |  | S | X | X | N/A | N/A | 1.9 | 0.8 | 1.8 | 1.8 | 0 | N |  |  | OP | X | 1 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1960 | petroleum | TRUE | 20219 | City of Wayne | 2312 | Wayne IC | NE | Wayne | 4 | Petroleum Liquids | IC |  | S | X | X | N/A | N/A | 2 | 0.8 | 1.9 | 1.9 | 0 | N |  |  | OP | X | 1 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1966 | petroleum | TRUE | 20219 | City of Wayne | 2312 | Wayne IC | NE | Wayne | 5 | Petroleum Liquids | IC |  | S | X | X | N/A | N/A | 3.5 | 0.8 | 3.3 | 3.3 | 0 | N |  |  | OP | X | 1 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1968 | petroleum | TRUE | 20219 | City of Wayne | 2312 | Wayne IC | NE | Wayne | 6 | Petroleum Liquids | IC |  | S | X | X | N/A | N/A | 5.1 | 0.8 | 4.9 | 4.9 | 0 | N |  |  | OP | X | 1 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1998 | petroleum | TRUE | 20219 | City of Wayne | 2312 | Wayne IC | NE | Wayne | 7 | Petroleum Liquids | IC |  | S | X | X | N/A | N/A | 3.5 | 0.8 | 3.3 | 3.3 | 0 | N |  |  | OP | X | 2 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1998 | petroleum | TRUE | 20219 | City of Wayne | 2312 | Wayne IC | NE | Wayne | 8 | Petroleum Liquids | IC |  | S | X | X | N/A | N/A | 3.5 | 0.8 | 3.3 | 3.3 | 0 | N |  |  | OP | X | 2 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1947 | petroleum | TRUE | 20397 | City of West Point - (NE) | 2313 | West Point Municipal | NE | Cuming | 2 | Petroleum Liquids | IC |  | S | X | X | SPP | SPP | 0.9 | 0.8 | 0.9 | 0.9 | 0.4 | N |  |  | OP | X | 5 | 1947 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N |  |  | 1H | [23 empty] | Y | Y | N
Vintage1959 | petroleum | TRUE | 20397 | City of West Point - (NE) | 2313 | West Point Municipal | NE | Cuming | 3 | Petroleum Liquids | IC |  | S | X | X | SPP | SPP | 1.2 | 0.8 | 1.2 | 1.2 | 0.6 | N |  |  | OP | X | 7 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1965 | petroleum | TRUE | 20397 | City of West Point - (NE) | 2313 | West Point Municipal | NE | Cuming | 4 | Petroleum Liquids | IC |  | S | X | X | SPP | SPP | 2.3 | 0.8 | 2.3 | 2.3 | 1.2 | N |  |  | OP | X | 8 | 1965 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1960 | petroleum | TRUE | 20632 | City of Wilber | 2315 | Wilber | NE | Saline | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.9 | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 1 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N
Vintage1960 | petroleum | TRUE | 20632 | City of Wilber | 2315 | Wilber | NE | Saline | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.9 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 1 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N
Vintage1997 | petroleum | TRUE | 20632 | City of Wilber | 2315 | Wilber | NE | Saline | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.9 | 1.6 | 1.6 | 0.1 | N |  |  | OP | X | 1 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N
Vintage1969 | petroleum | TRUE | 20880 | City of Wisner | 2316 | Wisner | NE | Cuming | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.9 | 0.8 | 0.8 | 0.1 | N |  |  | OP | X | 5 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2010 | petroleum | TRUE | 20880 | City of Wisner | 2316 | Wisner | NE | Cuming | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.9 | 1.5 | 1.5 | 0.1 | N |  |  | OP | X | 3 | 2010 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2010 | petroleum | TRUE | 20880 | City of Wisner | 2316 | Wisner | NE | Cuming | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.9 | 1.5 | 1.5 | 0.1 | N |  |  | OP | X | 3 | 2010 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1994 | natural gas combined cycle | TRUE | 13407 | Nevada Power Co | 2322 | Clark (NVE) | NV | Clark | 10 | Natural Gas Fired Combined Cycle | CA | PB1 | S | N | X |  |  | 104.4 | 0.9 | 85 | 88 | 32 | N |  |  | OP | X | 5 | 1994 |  |  | N | Electric Utility | 1 | [14 empty] | 12H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2008 | natural gas peaker | TRUE | 13407 | Nevada Power Co | 2322 | Clark (NVE) | NV | Clark | 11 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 60.5 | 0.85 | 52 | 57 | 50 | N |  |  | OP | X | 11 | 2008 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2008 | natural gas peaker | TRUE | 13407 | Nevada Power Co | 2322 | Clark (NVE) | NV | Clark | 12 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 60.5 | 0.85 | 52 | 57 | 50 | N |  |  | OP | X | 8 | 2008 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2008 | natural gas peaker | TRUE | 13407 | Nevada Power Co | 2322 | Clark (NVE) | NV | Clark | 13 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 60.5 | 0.85 | 52 | 57 | 50 | N |  |  | OP | X | 11 | 2008 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2008 | natural gas peaker | TRUE | 13407 | Nevada Power Co | 2322 | Clark (NVE) | NV | Clark | 14 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 60.5 | 0.85 | 52 | 57 | 50 | N |  |  | OP | X | 9 | 2008 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2008 | natural gas peaker | TRUE | 13407 | Nevada Power Co | 2322 | Clark (NVE) | NV | Clark | 15 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 60.5 | 0.85 | 52 | 57 | 50 | N |  |  | OP | X | 8 | 2008 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2008 | natural gas peaker | TRUE | 13407 | Nevada Power Co | 2322 | Clark (NVE) | NV | Clark | 16 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 60.5 | 0.85 | 52 | 57 | 50 | N |  |  | OP | X | 7 | 2008 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2008 | natural gas peaker | TRUE | 13407 | Nevada Power Co | 2322 | Clark (NVE) | NV | Clark | 17 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 60.5 | 0.85 | 52 | 57 | 50 | N |  |  | OP | X | 11 | 2008 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2008 | natural gas peaker | TRUE | 13407 | Nevada Power Co | 2322 | Clark (NVE) | NV | Clark | 18 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 60.5 | 0.85 | 52 | 57 | 50 | N |  |  | OP | X | 7 | 2008 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2008 | natural gas peaker | TRUE | 13407 | Nevada Power Co | 2322 | Clark (NVE) | NV | Clark | 19 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 60.5 | 0.85 | 52 | 57 | 50 | N |  |  | OP | X | 7 | 2008 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2008 | natural gas peaker | TRUE | 13407 | Nevada Power Co | 2322 | Clark (NVE) | NV | Clark | 20 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 60.5 | 0.85 | 52 | 57 | 50 | N |  |  | OP | X | 7 | 2008 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2008 | natural gas peaker | TRUE | 13407 | Nevada Power Co | 2322 | Clark (NVE) | NV | Clark | 21 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 58.9 | 0.85 | 52 | 57 | 50 | N |  |  | OP | X | 7 | 2008 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2008 | natural gas peaker | TRUE | 13407 | Nevada Power Co | 2322 | Clark (NVE) | NV | Clark | 22 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 60.5 | 0.85 | 52 | 57 | 50 | N |  |  | OP | X | 7 | 2008 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1993 | natural gas combined cycle | TRUE | 13407 | Nevada Power Co | 2322 | Clark (NVE) | NV | Clark | 9 | Natural Gas Fired Combined Cycle | CA | PB2 | S | N | X |  |  | 104.4 | 0.9 | 85 | 88 | 32 | N |  |  | OP | X | 5 | 1993 |  |  | N | Electric Utility | 1 | [14 empty] | 12H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1973 | natural gas peaker | TRUE | 13407 | Nevada Power Co | 2322 | Clark (NVE) | NV | Clark | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 72.4 | 0.9 | 55 | 59 | 5 | N |  |  | OP | X | 6 | 1973 |  |  | N | Electric Utility | 1 | [14 empty] | 1H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1979 | natural gas combined cycle | TRUE | 13407 | Nevada Power Co | 2322 | Clark (NVE) | NV | Clark | GT5 | Natural Gas Fired Combined Cycle | CT | PB1 | S | X | Y |  |  | 92.5 | 0.9 | 73 | 81 | 45 | N |  |  | OP | X | 5 | 1979 |  |  | N | Electric Utility | 1 | [14 empty] | 1H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1979 | natural gas combined cycle | TRUE | 13407 | Nevada Power Co | 2322 | Clark (NVE) | NV | Clark | GT6 | Natural Gas Fired Combined Cycle | CT | PB1 | S | X | Y |  |  | 92.5 | 0.9 | 73 | 81 | 45 | N |  |  | OP | X | 5 | 1979 |  |  | N | Electric Utility | 1 | [14 empty] | 1H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1980 | natural gas combined cycle | TRUE | 13407 | Nevada Power Co | 2322 | Clark (NVE) | NV | Clark | GT7 | Natural Gas Fired Combined Cycle | CT | PB2 | S | X | Y |  |  | 92.5 | 0.9 | 73 | 81 | 45 | N |  |  | OP | X | 6 | 1980 |  |  | N | Electric Utility | 1 | [14 empty] | 1H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1982 | natural gas combined cycle | TRUE | 13407 | Nevada Power Co | 2322 | Clark (NVE) | NV | Clark | GT8 | Natural Gas Fired Combined Cycle | CT | PB2 | S | X | Y |  |  | 92.5 | 0.9 | 73 | 81 | 45 | N |  |  | OP | X | 6 | 1982 |  |  | N | Electric Utility | 1 | [14 empty] | 1H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1968 | natural gas steam turbine | TRUE | 17166 | Sierra Pacific Power Co | 2330 | Fort Churchill | NV | Lyon | 1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 115 | 0.85 | 113 | 113 | 18 | N |  |  | OP | X | 9 | 1968 | 9 | 2028 | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1971 | natural gas steam turbine | TRUE | 17166 | Sierra Pacific Power Co | 2330 | Fort Churchill | NV | Lyon | 2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 115 | 0.85 | 113 | 113 | 18 | N |  |  | OP | X | 9 | 1971 | 9 | 2028 | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage2008 | natural gas combined cycle | TRUE | 17166 | Sierra Pacific Power Co | 2336 | Tracy | NV | Storey | 10 | Natural Gas Fired Combined Cycle | CA | PB1 | S | Y | X |  |  | 312 | 0.85 | 263 | 286 | 50 | N |  |  | OP | X | 7 | 2008 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [23 empty] | N |  | N | bar: X X X to DFO RC RC
Vintage1974 | natural gas steam turbine | TRUE | 17166 | Sierra Pacific Power Co | 2336 | Tracy | NV | Storey | 3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 119.8 | 0.9 | 108 | 108 | 32 | N |  |  | OP | X | 10 | 1974 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1994 | natural gas combined cycle | TRUE | 17166 | Sierra Pacific Power Co | 2336 | Tracy | NV | Storey | 4 | Natural Gas Fired Combined Cycle | CT | G240 | S | X | N |  |  | 69.7 | 0.85 | 64 | 68 | 35 | N |  |  | OP | X | 7 | 1994 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [23 empty] | N |  | N | bar: X X X to DFO RC RC
Vintage1996 | natural gas combined cycle | TRUE | 17166 | Sierra Pacific Power Co | 2336 | Tracy | NV | Storey | 5 | Natural Gas Fired Combined Cycle | CA | G240 | S | Y | X |  |  | 50.2 | 0.85 | 40 | 40 | 17 | N |  |  | OP | X | 12 | 1996 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [23 empty] | N |  | N | bar: X X X to DFO RC RC
Vintage2008 | natural gas combined cycle | TRUE | 17166 | Sierra Pacific Power Co | 2336 | Tracy | NV | Storey | 8 | Natural Gas Fired Combined Cycle | CT | PB1 | S | X | N |  |  | 155.6 | 0.85 | 145 | 146 | 100 | N |  |  | OP | X | 7 | 2008 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [23 empty] | N |  | N | bar: X X X to DFO RC RC
Vintage2008 | natural gas combined cycle | TRUE | 17166 | Sierra Pacific Power Co | 2336 | Tracy | NV | Storey | 9 | Natural Gas Fired Combined Cycle | CT | PB1 | S | X | N |  |  | 155.6 | 0.85 | 145 | 146 | 100 | N |  |  | OP | X | 7 | 2008 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [23 empty] | N |  | N | bar: X X X to DFO RC RC
Vintage1994 | natural gas peaker | TRUE | 17166 | Sierra Pacific Power Co | 2336 | Tracy | NV | Storey | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 85 | 0.85 | 66.3 | 72 | 35 | N |  |  | OP | X | 7 | 1994 |  |  | N | Electric Utility | 1 | [14 empty] | 10M | [23 empty] | N |  | N | bar: X X X to DFO RC RC
Vintage1994 | natural gas peaker | TRUE | 17166 | Sierra Pacific Power Co | 2336 | Tracy | NV | Storey | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 85 | 0.85 | 66.3 | 72 | 35 | N |  |  | OP | X | 7 | 1994 |  |  | N | Electric Utility | 1 | [14 empty] | 10M | [23 empty] | N |  | N | bar: X X X to DFO RC RC
Vintage1930 | hydro | TRUE | 61122 | Great River Hydro, LLC | 2349 | Comerford | NH | Grafton | GEN1 | Conventional Hydroelectric | HY |  | S | X | X | 47366 |  | 22 | 0.8 | 22.5 | 22.5 | 12 | N |  |  | OP | X | 9 | 1930 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1930 | hydro | TRUE | 61122 | Great River Hydro, LLC | 2349 | Comerford | NH | Grafton | GEN2 | Conventional Hydroelectric | HY |  | S | X | X | 47367 |  | 48.6 | 0.9 | 47.8 | 48.5 | 12 | N |  |  | OP | X | 9 | 1930 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1930 | hydro | TRUE | 61122 | Great River Hydro, LLC | 2349 | Comerford | NH | Grafton | GEN3 | Conventional Hydroelectric | HY |  | S | X | X | 47368 |  | 48.6 | 0.9 | 47.8 | 48.5 | 12 | N |  |  | OP | X | 9 | 1930 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1930 | hydro | TRUE | 61122 | Great River Hydro, LLC | 2349 | Comerford | NH | Grafton | GEN4 | Conventional Hydroelectric | HY |  | S | X | X | 47369 |  | 48.6 | 0.9 | 47.8 | 48.5 | 12 | N |  |  | OP | X | 9 | 1930 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1957 | hydro | TRUE | 61122 | Great River Hydro, LLC | 2351 | S C Moore | NH | Grafton | GEN1 | Conventional Hydroelectric | HY |  | S | X | X | 47370 |  | 47.7 | 0.9 | 47.2 | 47.7 | 1 | N |  |  | OP | X | 1 | 1957 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1957 | hydro | TRUE | 61122 | Great River Hydro, LLC | 2351 | S C Moore | NH | Grafton | GEN2 | Conventional Hydroelectric | HY |  | S | X | X | 47371 |  | 47.7 | 0.9 | 47.2 | 47.7 | 1 | N |  |  | OP | X | 1 | 1957 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1957 | hydro | TRUE | 61122 | Great River Hydro, LLC | 2351 | S C Moore | NH | Grafton | GEN3 | Conventional Hydroelectric | HY |  | S | X | X | 47372 |  | 47.7 | 0.9 | 47.2 | 47.7 | 1 | N |  |  | OP | X | 1 | 1957 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1957 | hydro | TRUE | 61122 | Great River Hydro, LLC | 2351 | S C Moore | NH | Grafton | GEN4 | Conventional Hydroelectric | HY |  | S | X | X | 47373 |  | 47.7 | 0.9 | 47.2 | 47.7 | 1 | N |  |  | OP | X | 1 | 1957 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1909 | hydro | TRUE | 61122 | Great River Hydro, LLC | 2352 | Vernon Dam | VT | Windham | 1 | Conventional Hydroelectric | HY |  | S | X | X | 599 |  | 2 | 0.8 | 2.4 | 2.4 | 2 | N |  |  | OP | X | 8 | 1909 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1921 | hydro | TRUE | 61122 | Great River Hydro, LLC | 2352 | Vernon Dam | VT | Windham | 10 | Conventional Hydroelectric | HY |  | S | X | X | 599 |  | 4.2 | 1 | 4 | 4 | 4 | N |  |  | OP | X | 1 | 1921 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1909 | hydro | TRUE | 61122 | Great River Hydro, LLC | 2352 | Vernon Dam | VT | Windham | 2 | Conventional Hydroelectric | HY |  | S | X | X | 599 |  | 2 | 0.8 | 2.4 | 2.4 | 2 | N |  |  | OP | X | 8 | 1909 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1909 | hydro | TRUE | 61122 | Great River Hydro, LLC | 2352 | Vernon Dam | VT | Windham | 3 | Conventional Hydroelectric | HY |  | S | X | X | 599 |  | 2 | 0.8 | 2.4 | 2.4 | 2 | N |  |  | OP | X | 8 | 1909 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1909 | hydro | TRUE | 61122 | Great River Hydro, LLC | 2352 | Vernon Dam | VT | Windham | 4 | Conventional Hydroelectric | HY |  | S | X | X | 599 |  | 2.5 | 0.8 | 2.4 | 2.4 | 2 | N |  |  | OP | X | 8 | 1909 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage2008 | hydro | TRUE | 61122 | Great River Hydro, LLC | 2352 | Vernon Dam | VT | Windham | 5 | Conventional Hydroelectric | HY |  | S | X | X | 599 |  | 4.5 | 0.9 | 3.6 | 3.6 | 3 | N |  |  | OP | X | 4 | 2008 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage2008 | hydro | TRUE | 61122 | Great River Hydro, LLC | 2352 | Vernon Dam | VT | Windham | 6A | Conventional Hydroelectric | HY |  | S | X | X | 599 |  | 5 | 0.9 | 4.5 | 4.5 | 3 | N |  |  | OP | X | 3 | 2008 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  | N |  | 10M | [23 empty] | N
Vintage2008 | hydro | TRUE | 61122 | Great River Hydro, LLC | 2352 | Vernon Dam | VT | Windham | 7A | Conventional Hydroelectric | HY |  | S | X | X | 599 |  | 5 | 0.9 | 4.5 | 4.5 | 3 | N |  |  | OP | X | 3 | 2008 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  | N |  | 10M | [23 empty] | N
Vintage2008 | hydro | TRUE | 61122 | Great River Hydro, LLC | 2352 | Vernon Dam | VT | Windham | 8 | Conventional Hydroelectric | HY |  | S | X | X | 599 |  | 4.5 | 0.9 | 3.6 | 3.6 | 3 | N |  |  | OP | X | 3 | 2008 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1921 | hydro | TRUE | 61122 | Great River Hydro, LLC | 2352 | Vernon Dam | VT | Windham | 9 | Conventional Hydroelectric | HY |  | S | X | X | 599 |  | 4.2 | 1 | 4 | 4 | 3 | N |  |  | OP | X | 1 | 1921 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1950 | hydro | TRUE | 61122 | Great River Hydro, LLC | 2353 | Wilder | VT | Windsor | GEN1 | Conventional Hydroelectric | HY |  | S | X | X | 620 |  | 16.2 | 0.9 | 18.1 | 19 | 3 | N |  |  | OP | X | 11 | 1950 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1950 | hydro | TRUE | 61122 | Great River Hydro, LLC | 2353 | Wilder | VT | Windsor | GEN2 | Conventional Hydroelectric | HY |  | S | X | X | 620 |  | 16.2 | 0.9 | 18.1 | 19 | 3 | N |  |  | OP | X | 11 | 1950 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1987 | hydro | TRUE | 61122 | Great River Hydro, LLC | 2353 | Wilder | VT | Windsor | GEN3 | Conventional Hydroelectric | HY |  | S | X | X | 620 |  | 3.2 | 0.95 | 2.8 | 2.8 | 2.8 | N |  |  | OP | X | 10 | 1987 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1924 | hydro | TRUE | 62775 | Central Rivers Power NH, LLC | 2354 | Amoskeag | NH | Hillsborough | 1 | Conventional Hydroelectric | HY |  | S | X | X | 4002 Z_NewHampshire |  | 6 | 0.8 | 6.2 | 6.5 | 0.7 | N |  |  | OP | X | 8 | 1924 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1922 | hydro | TRUE | 62775 | Central Rivers Power NH, LLC | 2354 | Amoskeag | NH | Hillsborough | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5 | 0.8 | 5.3 | 5.5 | 0.7 | N |  |  | OP | X | 8 | 1922 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1922 | hydro | TRUE | 62775 | Central Rivers Power NH, LLC | 2354 | Amoskeag | NH | Hillsborough | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5 | 0.8 | 5.3 | 5.5 | 0.7 | N |  |  | OP | X | 8 | 1922 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1925 | hydro | TRUE | 62775 | Central Rivers Power NH, LLC | 2355 | Ayers Island | NH | Grafton | 1 | Conventional Hydroelectric | HY |  | S | X | X | 4002 Z_NewHampshire |  | 2.8 | 0.8 | 2.8 | 3 | 0.5 | N |  |  | OP | X | 8 | 1925 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1925 | hydro | TRUE | 62775 | Central Rivers Power NH, LLC | 2355 | Ayers Island | NH | Grafton | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.8 | 0.8 | 2.8 | 3 | 0.5 | N |  |  | OP | X | 8 | 1925 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1925 | hydro | TRUE | 62775 | Central Rivers Power NH, LLC | 2355 | Ayers Island | NH | Grafton | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.8 | 0.8 | 2.8 | 3 | 0.5 | N |  |  | OP | X | 8 | 1925 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1937 | hydro | TRUE | 62775 | Central Rivers Power NH, LLC | 2356 | Eastman Falls | NH | Merrimack | 1 | Conventional Hydroelectric | HY |  | S | X | X | 4002 Z_NewHampshire |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 8 | 1937 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1983 | hydro | TRUE | 62775 | Central Rivers Power NH, LLC | 2356 | Eastman Falls | NH | Merrimack | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.6 | 0.9 | 3.8 | 4.7 | 0.9 | N |  |  | OP | X | 11 | 1983 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1981 | hydro | TRUE | 62775 | Central Rivers Power NH, LLC | 2357 | Garvins Falls | NH | Merrimack | 1 | Conventional Hydroelectric | HY |  | S | X | X | 4002 Z_NewHampshire |  | 3.4 | 0.85 | 3.4 | 3.4 | 1.3 | N |  |  | OP | X | 12 | 1981 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1981 | hydro | TRUE | 62775 | Central Rivers Power NH, LLC | 2357 | Garvins Falls | NH | Merrimack | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.4 | 0.85 | 3.3 | 3.4 | 1.3 | N |  |  | OP | X | 12 | 1981 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1925 | hydro | TRUE | 62775 | Central Rivers Power NH, LLC | 2357 | Garvins Falls | NH | Merrimack | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 2.4 | 2.4 | 0.5 | N |  |  | OP | X | 8 | 1925 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1925 | hydro | TRUE | 62775 | Central Rivers Power NH, LLC | 2357 | Garvins Falls | NH | Merrimack | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.2 | 0.8 | 3.2 | 3.2 | 0.5 | N |  |  | OP | X | 8 | 1925 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1917 | hydro | TRUE | 62775 | Central Rivers Power NH, LLC | 2358 | Gorham | NH | Coos | 1 | Conventional Hydroelectric | HY |  | S | X | X | 4002 Z_NewHampshire |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 8 | 1917 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1917 | hydro | TRUE | 62775 | Central Rivers Power NH, LLC | 2358 | Gorham | NH | Coos | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 8 | 1917 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1923 | hydro | TRUE | 62775 | Central Rivers Power NH, LLC | 2358 | Gorham | NH | Coos | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.9 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 8 | 1923 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1923 | hydro | TRUE | 62775 | Central Rivers Power NH, LLC | 2358 | Gorham | NH | Coos | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.9 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 8 | 1923 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1927 | hydro | TRUE | 62775 | Central Rivers Power NH, LLC | 2359 | Hooksett | NH | Merrimack | 1 | Conventional Hydroelectric | HY |  | S | X | X | 4002 Z_NewHampshire |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.5 | N |  |  | OP | X | 8 | 1927 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1926 | hydro | TRUE | 62775 | Central Rivers Power NH, LLC | 2360 | Jackman | NH | Hillsborough | 1 | Conventional Hydroelectric | HY |  | S | X | X | 4002 Z_NewHampshire |  | 3.2 | 0.8 | 3.6 | 3.4 | 0.5 | N |  |  | OP | X | 2 | 1926 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1969 | petroleum | TRUE | 62032 | Granite Shore Power | 2362 | Lost Nation | NH | Coos | GT1 | Petroleum Liquids | GT |  | S | X | X | 4002 Z_NewHampshire |  | 18 | 0.85 | 14 | 18.1 | 4 | N |  |  | OP | X | 9 | 1969 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO | [5 empty] | 10M | [23 empty] | N
Vintage1960 | hard coal | TRUE | 62032 | Granite Shore Power | 2364 | Merrimack | NH | Merrimack | 1 | Conventional Steam Coal | ST |  | S | X | X | 4002 Z_NewHampshire |  | 113.6 | 0.85 | 108 | 108 | 80 | N |  |  | OP | X | 12 | 1960 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: DFO |  |  | N |  |  | OVER |  |  |  | Y | Y | [18 empty] | N
Vintage1968 | hard coal | TRUE | 62032 | Granite Shore Power | 2364 | Merrimack | NH | Merrimack | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 345.6 | 0.9 | 330.5 | 330 | 120 | N |  |  | OP | X | 5 | 1968 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: DFO |  |  | N |  |  | OVER |  |  |  | Y | Y | [18 empty] | N
Vintage1968 | petroleum | TRUE | 62032 | Granite Shore Power | 2364 | Merrimack | NH | Merrimack | GT1 | Petroleum Liquids | GT |  | S | X | X |  |  | 18.6 | 0.85 | 16.8 | 21.7 | 4 | N |  |  | OP | X | 8 | 1968 |  |  | N | IPP Non-CHP | 2 | [14 empty] | 10M |  |  |  | N | [19 empty] | N | bar: X X X to DFO RC RC
Vintage1969 | petroleum | TRUE | 62032 | Granite Shore Power | 2364 | Merrimack | NH | Merrimack | GT2 | Petroleum Liquids | GT |  | S | X | X |  |  | 18.6 | 0.85 | 16.8 | 21.3 | 4 | N |  |  | OP | X | 8 | 1969 |  |  | N | IPP Non-CHP | 2 | [14 empty] | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1952 | hard coal | TRUE | 62032 | Granite Shore Power | 2367 | Schiller | NH | Rockingham | 4 | Conventional Steam Coal | ST |  | S | X | X | 4002 Z_NewHampshire |  | 50 | 0.85 | 47.5 | 48 | 13 | N |  |  | OS | X | 10 | 1952 |  |  | N | IPP Non-CHP | 2 | X | BIT | RFO | OBS |  |  |  | DFO | NG |  |  | N |  |  | 12H |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1955 | biomass | TRUE | 62032 | Granite Shore Power | 2367 | Schiller | NH | Rockingham | 5 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 50 | 0.85 | 43.1 | 42.6 | 35 | N |  |  | OS | X | 5 | 1955 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WDS; DFO SUB SUB: BIT; DFO DFO DFO: NG | [5 empty] | OVER | Y | N |  |  | Y | [18 empty] | Y | Y | N
Vintage1957 | hard coal | TRUE | 62032 | Granite Shore Power | 2367 | Schiller | NH | Rockingham | 6 | Conventional Steam Coal | ST |  | S | X | X |  |  | 50 | 0.85 | 47.9 | 48.6 | 13 | N |  |  | OS | X | 7 | 1957 |  |  | N | IPP Non-CHP | 2 | X | BIT | RFO | OBS |  |  |  | DFO | NG | [5 empty] | 12H |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1970 | petroleum | TRUE | 62032 | Granite Shore Power | 2367 | Schiller | NH | Rockingham | GT1 | Petroleum Liquids | GT |  | S | X | X |  |  | 21.2 | 0.85 | 17 | 18 | 5 | N |  |  | OP | X | 11 | 1970 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: JF; DFO SUB SUB: NG | [5 empty] | 10M | [23 empty] | N | N | N
Vintage1948 | hydro | TRUE | 62775 | Central Rivers Power NH, LLC | 2368 | Smith (NH) | NH | Coos | 1 | Conventional Hydroelectric | HY |  | S | X | X | 4002 Z_NewHampshire |  | 15 | 0.8 | 11.7 | 15.2 | 3 | N |  |  | OP | X | 8 | 1948 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1968 | petroleum | TRUE | 62032 | Granite Shore Power | 2369 | White Lake | NH | Carroll | GT1 | Petroleum Liquids | GT |  | S | X | X | 4002 Z_NewHampshire |  | 18.6 | 0.95 | 17.5 | 22.4 | 4 | N |  |  | OP | X | 7 | 1968 |  |  | N | IPP Non-CHP | 2 | [14 empty] | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1973 | natural gas peaker | TRUE | 56606 | Calpine New Jersey Generation LLC | 2379 | Carlls Corner | NJ | Cumberland | CA1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 41.9 | 0.9 | 37.6 | 49.8 | 33.8 | N |  |  | OP | X | 4 | 1973 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N |  |  | 10M | [23 empty] | Y | N | Y
Vintage1973 | natural gas peaker | TRUE | 56606 | Calpine New Jersey Generation LLC | 2379 | Carlls Corner | NJ | Cumberland | CA2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 41.9 | 0.9 | 39.2 | 49.8 | 35.3 | N |  |  | OP | X | 5 | 1973 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N |  |  | 10M | [23 empty] | Y | N | Y
Vintage1972 | natural gas peaker | TRUE | 63034 | Sayreville Power, LLC | 2390 | Sayreville | NJ | Middlesex | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 50727 | SAYREVIL 13 KV CT 1 | 53 | 0.85 | 57.1 | 70 | 50 | N |  |  | OP | X | 3 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1972 | natural gas peaker | TRUE | 63034 | Sayreville Power, LLC | 2390 | Sayreville | NJ | Middlesex | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 50728 | SAYREVIL 13 KV CT 2 | 53 | 0.85 | 56.7 | 70 | 50 | N |  |  | OP | X | 3 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1972 | natural gas peaker | TRUE | 63034 | Sayreville Power, LLC | 2390 | Sayreville | NJ | Middlesex | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 50729 | SAYREVIL 13KV CT 3 | 53 | 0.85 | 55.6 | 70 | 50 | N |  |  | OP | X | 6 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1973 | natural gas peaker | TRUE | 63034 | Sayreville Power, LLC | 2390 | Sayreville | NJ | Middlesex | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 50730 | SAYREVIL 13 KV CT 4 | 53 | 0.85 | 48.5 | 70 | 45 | N |  |  | OP | X | 10 | 1973 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1974 | natural gas combined cycle | TRUE | 63033 | Gilbert Power, LLC | 2393 | Gilbert | NJ | Hunterdon | 4 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y | 50703 | GILBERT 13KV UNIT 4 | 54 | 0.9 | 49 | 56 | 42 | N |  |  | OP | X | 1 | 1974 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1974 | natural gas combined cycle | TRUE | 63033 | Gilbert Power, LLC | 2393 | Gilbert | NJ | Hunterdon | 5 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y | 50696 | GILBERT 13KV UNIT 5 | 54 | 0.9 | 53 | 56 | 42 | N |  |  | OP | X | 4 | 1974 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1974 | natural gas combined cycle | TRUE | 63033 | Gilbert Power, LLC | 2393 | Gilbert | NJ | Hunterdon | 6 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y | 50697 | GILBERT 13 KV UNIT 6 | 54 | 0.9 | 55 | 56 | 42 | N |  |  | OP | X | 4 | 1974 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1974 | natural gas combined cycle | TRUE | 63033 | Gilbert Power, LLC | 2393 | Gilbert | NJ | Hunterdon | 7 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y | 50698 | GILBERT 13 KV UNIT 7 | 54 | 0.9 | 55.5 | 56 | 42 | N |  |  | OP | X | 5 | 1974 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1977 | natural gas combined cycle | TRUE | 63033 | Gilbert Power, LLC | 2393 | Gilbert | NJ | Hunterdon | 8 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X | 50699 | GILBERT 13 KV UNIT 8 | 135 | 0.9 | 90 | 104 | 37 | N |  |  | OP | X | 5 | 1977 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1996 | natural gas peaker | TRUE | 63033 | Gilbert Power, LLC | 2393 | Gilbert | NJ | Hunterdon | 9 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 50704 | GILBERT 13 KV UNIT 9 | 161 | 0.9 | 152.7 | 167 | 150 | N |  |  | OP | X | 7 | 1996 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1995 | natural gas combined cycle | TRUE | 15147 | PSEG Fossil LLC | 2398 | Bergen Generating Station | NJ | Bergen | 1101 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | 50397 | BERGEN 18 KV | 112.5 | 0.9 | 110 | 110 | 92 | N |  |  | OP | X | 6 | 1995 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1995 | natural gas combined cycle | TRUE | 15147 | PSEG Fossil LLC | 2398 | Bergen Generating Station | NJ | Bergen | 1201 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | 50398 | BERGEN 18 KV | 112.5 | 0.9 | 110 | 110 | 92 | N |  |  | OP | X | 6 | 1995 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1995 | natural gas combined cycle | TRUE | 15147 | PSEG Fossil LLC | 2398 | Bergen Generating Station | NJ | Bergen | 1301 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | 50399 | BERGEN 18 KV | 112.5 | 0.9 | 115 | 115 | 92 | N |  |  | OP | X | 6 | 1995 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1995 | natural gas combined cycle | TRUE | 15147 | PSEG Fossil LLC | 2398 | Bergen Generating Station | NJ | Bergen | 1401 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | 50400 | BERGEN 18 KV | 112.5 | 0.9 | 115 | 115 | 92 | N |  |  | OP | X | 6 | 1995 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1959 | natural gas combined cycle | TRUE | 15147 | PSEG Fossil LLC | 2398 | Bergen Generating Station | NJ | Bergen | 1501 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X | 50401 | BERGEN 18 KV | 325.2 | 0.85 | 204 | 204 | 92 | N |  |  | OP | X | 5 | 1959 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2002 | natural gas combined cycle | TRUE | 15147 | PSEG Fossil LLC | 2398 | Bergen Generating Station | NJ | Bergen | 2101 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | 5021666 | BERGEN 18 KV | 183.6 | 0.85 | 178.5 | 178.5 | 127 | N |  |  | OP | X | 6 | 2002 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2002 | natural gas combined cycle | TRUE | 15147 | PSEG Fossil LLC | 2398 | Bergen Generating Station | NJ | Bergen | 2201 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | 5021667 | BERGEN 18 KV | 183.6 | 0.85 | 174 | 174 | 127 | N |  |  | OP | X | 6 | 2002 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2002 | natural gas combined cycle | TRUE | 15147 | PSEG Fossil LLC | 2398 | Bergen Generating Station | NJ | Bergen | 2301 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | 5021665 | BERGEN 18 KV | 258.4 | 0.85 | 238.5 | 238.5 | 127 | N |  |  | OP | X | 6 | 2002 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 15147 | PSEG Fossil LLC | 2399 | PSEG Burlington Generating Station | NJ | Burlington | 121 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 93142 | BURLINGT13 KV | 60.5 | 0.85 | 42 | 42 | 42 | N |  |  | OP | X | 6 | 2000 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2000 | natural gas peaker | TRUE | 15147 | PSEG Fossil LLC | 2399 | PSEG Burlington Generating Station | NJ | Burlington | 122 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 93143 | BURLINGT13 KV | 60.5 | 0.85 | 42 | 42 | 42 | N |  |  | OP | X | 6 | 2000 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2000 | natural gas peaker | TRUE | 15147 | PSEG Fossil LLC | 2399 | PSEG Burlington Generating Station | NJ | Burlington | 123 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 93144 | BURLINGT13 KV | 60.5 | 0.85 | 42 | 42 | 42 | N |  |  | OP | X | 6 | 2000 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2000 | natural gas peaker | TRUE | 15147 | PSEG Fossil LLC | 2399 | PSEG Burlington Generating Station | NJ | Burlington | 124 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 93145 | BURLINGT13 KV | 60.5 | 0.85 | 42 | 42 | 42 | N |  |  | OP | X | 6 | 2000 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1990 | natural gas peaker | TRUE | 15147 | PSEG Fossil LLC | 2401 | PSEG Essex Generating Station | NJ | Essex | 9 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 50419 | ESSEX 13 KV | 93.6 | 0.9 | 81 | 81 | 53.3 | N |  |  | OP | X | 7 | 1990 | 6 | 2022 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2012 | natural gas peaker | TRUE | 15147 | PSEG Fossil LLC | 2404 | PSEG Kearny Generating Station | NJ | Hudson | 131 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 123901463 | KEARNY 13 KV | 60.5 | 0.85 | 46.9 | 46.9 | 25 | N |  |  | OP | X | 6 | 2012 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2012 | natural gas peaker | TRUE | 15147 | PSEG Fossil LLC | 2404 | PSEG Kearny Generating Station | NJ | Hudson | 132 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 123901465 | KEARNY 13 KV | 60.5 | 0.85 | 46.9 | 46.9 | 25 | N |  |  | OP | X | 6 | 2012 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2012 | natural gas peaker | TRUE | 15147 | PSEG Fossil LLC | 2404 | PSEG Kearny Generating Station | NJ | Hudson | 133 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 123901467 | KEARNY 13 KV | 60.5 | 0.85 | 46.9 | 46.9 | 25 | N |  |  | OP | X | 6 | 2012 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2012 | natural gas peaker | TRUE | 15147 | PSEG Fossil LLC | 2404 | PSEG Kearny Generating Station | NJ | Hudson | 134 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 1084390238 | KEARNY 13 KV | 60.5 | 0.85 | 46.9 | 46.9 | 25 | N |  |  | OP | X | 6 | 2012 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H |  | N | [21 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2012 | natural gas peaker | TRUE | 15147 | PSEG Fossil LLC | 2404 | PSEG Kearny Generating Station | NJ | Hudson | 141 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 123901459 | KEARNY 13 KV | 60.5 | 0.85 | 46.9 | 46.9 | 25 | N |  |  | OP | X | 6 | 2012 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2012 | natural gas peaker | TRUE | 15147 | PSEG Fossil LLC | 2404 | PSEG Kearny Generating Station | NJ | Hudson | 142 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 123901461 | KEARNY 13 KV | 60.5 | 0.85 | 46.9 | 46.9 | 25 | N |  |  | OP | X | 6 | 2012 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2001 | natural gas peaker | TRUE | 15147 | PSEG Fossil LLC | 2404 | PSEG Kearny Generating Station | NJ | Hudson | N121 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 50436 | KEARNY 13 KV | 60.5 | 0.85 | 43.8 | 43.8 | 25 | N |  |  | OP | X | 8 | 2001 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2001 | natural gas peaker | TRUE | 15147 | PSEG Fossil LLC | 2404 | PSEG Kearny Generating Station | NJ | Hudson | N122 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 50437 | KEARNY 13 KV | 60.5 | 0.85 | 43.7 | 43.7 | 25 | N |  |  | OP | X | 8 | 2001 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2001 | natural gas peaker | TRUE | 15147 | PSEG Fossil LLC | 2404 | PSEG Kearny Generating Station | NJ | Hudson | N123 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 50438 | KEARNY 13 KV | 60.5 | 0.85 | 43.8 | 43.8 | 25 | N |  |  | OP | X | 8 | 2001 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2001 | natural gas peaker | TRUE | 15147 | PSEG Fossil LLC | 2404 | PSEG Kearny Generating Station | NJ | Hudson | N124 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 50439 | KEARNY 13 KV | 60.5 | 0.85 | 43.7 | 43.7 | 25 | N |  |  | OP | X | 8 | 2001 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2006 | natural gas combined cycle | TRUE | 15147 | PSEG Fossil LLC | 2406 | PSEG Linden Generating Station | NJ | Union | 1001 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | 21601782 | LINDEN 18 KV | 315 | 0.85 | 252 | 252 | 155 | N |  |  | OP | X | 4 | 2006 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2006 | natural gas combined cycle | TRUE | 15147 | PSEG Fossil LLC | 2406 | PSEG Linden Generating Station | NJ | Union | 1101 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | 21601783 | LINDEN 18 KV | 181.4 | 0.85 | 199 | 199 | 155 | N |  |  | OP | X | 4 | 2006 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2006 | natural gas combined cycle | TRUE | 15147 | PSEG Fossil LLC | 2406 | PSEG Linden Generating Station | NJ | Union | 1201 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | 21601784 | LINDEN 18 KV | 181.4 | 0.85 | 199 | 199 | 155 | N |  |  | OP | X | 4 | 2006 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2006 | natural gas combined cycle | TRUE | 15147 | PSEG Fossil LLC | 2406 | PSEG Linden Generating Station | NJ | Union | 2001 | Natural Gas Fired Combined Cycle | CA | CC2 | S | Y | X | 21601787 | LINDEN 18 KV | 315 | 0.85 | 252 | 252 | 155 | N |  |  | OP | X | 4 | 2006 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2006 | natural gas combined cycle | TRUE | 15147 | PSEG Fossil LLC | 2406 | PSEG Linden Generating Station | NJ | Union | 2101 | Natural Gas Fired Combined Cycle | CT | CC2 | S | X | N | 21601785 | LINDEN 18 KV | 181.4 | 0.85 | 199 | 199 | 155 | N |  |  | OP | X | 4 | 2006 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2006 | natural gas combined cycle | TRUE | 15147 | PSEG Fossil LLC | 2406 | PSEG Linden Generating Station | NJ | Union | 2201 | Natural Gas Fired Combined Cycle | CT | CC2 | S | X | N | 21601786 | LINDEN 18 KV | 181.4 | 0.85 | 199 | 199 | 155 | N |  |  | OP | X | 4 | 2006 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 15147 | PSEG Fossil LLC | 2406 | PSEG Linden Generating Station | NJ | Union | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 93140 | LINDEN 13 KV | 96.1 | 0.85 | 86 | 86 | 56.6 | N |  |  | OP | X | 6 | 2000 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2000 | natural gas peaker | TRUE | 15147 | PSEG Fossil LLC | 2406 | PSEG Linden Generating Station | NJ | Union | 6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 93141 | LINDEN 13 KV | 96.1 | 0.85 | 86 | 86 | 56.6 | N |  |  | OP | X | 6 | 2000 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1995 | natural gas peaker | TRUE | 15147 | PSEG Fossil LLC | 2406 | PSEG Linden Generating Station | NJ | Union | 7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 71856675 | LINDEN 13 KV | 96.1 | 0.85 | 84 | 84 | 55.3 | N |  |  | OP | X | 6 | 1995 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1995 | natural gas peaker | TRUE | 15147 | PSEG Fossil LLC | 2406 | PSEG Linden Generating Station | NJ | Union | 8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 718566677 | LINDEN 13 KV | 96.1 | 0.85 | 80.2 | 80.2 | 53.3 | N |  |  | OP | X | 6 | 1995 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1977 | nuclear | TRUE | 15478 | PSEG Nuclear LLC | 2410 | PSEG Salem Generating Station | NJ | Salem | 1 | Nuclear | ST |  | J | X | X | 50489 | SALEM 25 KV | 1170 | 0.9 | 1145.8 | 1145.8 | 1145.8 | N |  |  | OP | X | 6 | 1977 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1981 | nuclear | TRUE | 15478 | PSEG Nuclear LLC | 2410 | PSEG Salem Generating Station | NJ | Salem | 2 | Nuclear | ST |  | J | X | X | 50490 | SALEM 25 KV | 1170 | 0.9 | 1138.9 | 1138.9 | 1138.9 | N |  |  | OP | X | 10 | 1981 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1971 | petroleum | TRUE | 15478 | PSEG Nuclear LLC | 2410 | PSEG Salem Generating Station | NJ | Salem | 3 | Petroleum Liquids | GT |  | J | X | X | 50488 | SALEM 13 KV | 41.8 | 0.9 | 38.4 | 38.4 | 38 | N |  |  | SB | N | 6 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2018 | natural gas combined cycle | TRUE | 15147 | PSEG Fossil LLC | 2411 | PSEG Sewaren Generating Station | NJ | Middlesex | 701 | Natural Gas Fired Combined Cycle | CT | CC7 | S | X | N |  |  | 365.5 | 0.85 | 338 | 338 | 225 | N |  |  | OP | X | 6 | 2018 |  |  | N | IPP Non-CHP | 2 | [12 empty] | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2018 | natural gas combined cycle | TRUE | 15147 | PSEG Fossil LLC | 2411 | PSEG Sewaren Generating Station | NJ | Middlesex | 702 | Natural Gas Fired Combined Cycle | CA | CC7 | S | Y | X |  |  | 244 | 0.85 | 200 | 200 | 225 | N |  |  | OP | X | 6 | 2018 |  |  | N | IPP Non-CHP | 2 | [9 empty] | DFO |  | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2012 | natural gas peaker | TRUE | 19856 | City of Vineland - (NJ) | 2434 | Howard Down | NJ | Cumberland | 11 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | VINELAND 13.8KV CTYVINEL |  | 68.2 | 0.85 | 55 | 60 | 55 | N |  |  | OP | X | 6 | 2012 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1969 | hard coal | TRUE | 803 | Arizona Public Service Co | 2442 | Four Corners | NM | San Juan | 4 | Conventional Steam Coal | ST |  | J | X | X |  |  | 818.1 | 0.9 | 770 | 770 | 364 | N |  |  | OP | X | 7 | 1969 | 12 | 2031 | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: NG; DFO DFO DFO: BIT; DFO DFO DFO: NG |  |  | N |  |  | OVER |  | Y |  |  |  | Y | [17 empty] | N
Vintage1970 | hard coal | TRUE | 803 | Arizona Public Service Co | 2442 | Four Corners | NM | San Juan | 5 | Conventional Steam Coal | ST |  | J | X | X |  |  | 818.1 | 0.9 | 770 | 770 | 364 | N |  |  | OP | X | 7 | 1970 | 12 | 2031 | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: NG; DFO DFO DFO: BIT; DFO DFO DFO: NG |  |  | N |  |  | OVER |  | Y |  |  |  | Y | [17 empty] | N
Vintage1957 | natural gas steam turbine | TRUE | 5701 | El Paso Electric Co | 2444 | Rio Grande | NM | Dona Ana | 6 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 50 | 0.85 | 45 | 47 | 18 | N |  |  | OP | X | 6 | 1957 | 12 | 2024 | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1958 | natural gas steam turbine | TRUE | 5701 | El Paso Electric Co | 2444 | Rio Grande | NM | Dona Ana | 7 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 50 | 0.85 | 46 | 48 | 18 | N |  |  | OP | X | 6 | 1958 | 12 | 2023 | N | Electric Utility | 1 | [11 empty] | N |  |  | OVER | [23 empty] | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1972 | natural gas steam turbine | TRUE | 5701 | El Paso Electric Co | 2444 | Rio Grande | NM | Dona Ana | 8 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 166.5 | 0.9 | 144 | 147 | 44 | N |  |  | OP | X | 7 | 1972 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | OVER | [23 empty] | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage2013 | natural gas peaker | TRUE | 5701 | El Paso Electric Co | 2444 | Rio Grande | NM | Dona Ana | 9 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 131.8 | 0.85 | 83 | 93 | 17.9 | N |  |  | OP | X | 5 | 2013 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 10M | [23 empty] | N | N | bar: X X X to DFO RC RC
Vintage1967 | natural gas steam turbine | TRUE | 17718 | Southwestern Public Service Co | 2446 | Maddox | NM | Lea | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | SPS.MADDOX1 | SPS.MADDOX1 | 113.6 | 0.85 | 112 | 112 | 35 | N |  |  | OP | X | 1 | 1967 | 12 | 2028 | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1976 | natural gas peaker | TRUE | 17718 | Southwestern Public Service Co | 2446 | Maddox | NM | Lea | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SPS.MADDOXCT2 | SPS.MADDOXCT2 | 86.9 | 0.9 | 61 | 63 | 48 | N |  |  | OP | X | 1 | 1976 | 12 | 2025 | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1963 | natural gas peaker | TRUE | 17718 | Southwestern Public Service Co | 2446 | Maddox | NM | Lea | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 11.5 | 0.85 | 10 | 10 | 3 | N |  |  | OP | X | 1 | 1963 | 12 | 2025 | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1960 | natural gas steam turbine | TRUE | 15473 | Public Service Co of NM | 2450 | Reeves | NM | Bernalillo | 1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 44 | 0.85 | 42 | 42 | 10 | N |  |  | OP | X | 8 | 1960 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1960 | natural gas steam turbine | TRUE | 15473 | Public Service Co of NM | 2450 | Reeves | NM | Bernalillo | 2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 44 | 0.85 | 41 | 41 | 10 | N |  |  | OP | X | 3 | 1960 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1962 | natural gas steam turbine | TRUE | 15473 | Public Service Co of NM | 2450 | Reeves | NM | Bernalillo | 3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 66 | 0.85 | 63 | 63 | 15 | N |  |  | OP | X | 7 | 1962 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1976 | hard coal | TRUE | 15473 | Public Service Co of NM | 2451 | San Juan | NM | San Juan | 1 | Conventional Steam Coal | ST |  | J | X | X |  |  | 369 | 0.9 | 340 | 340 | 150 | N |  |  | OP | X | 12 | 1976 | 6 | 2022 | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: BIT; DFO DFO DFO: DFO; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1982 | hard coal | TRUE | 15473 | Public Service Co of NM | 2451 | San Juan | NM | San Juan | 4 | Conventional Steam Coal | ST |  | J | X | X |  |  | 555 | 0.9 | 507 | 507 | 150 | N |  |  | OP | X | 4 | 1982 | 9 | 2022 | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: BIT; DFO DFO DFO: DFO; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1957 | natural gas steam turbine | TRUE | 17718 | Southwestern Public Service Co | 2454 | Cunningham | NM | Lea | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | SPS.CUNNGHAM1 | SPS.CUNNGHAM1 | 75 | 0.85 | 71 | 71 | 31 | N |  |  | OP | X | 1 | 1957 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1965 | natural gas steam turbine | TRUE | 17718 | Southwestern Public Service Co | 2454 | Cunningham | NM | Lea | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | SPS.CUNNGHAM2 | SPS.CUNNGHAM2 | 190.4 | 0.85 | 183 | 183 | 59 | N |  |  | OP | X | 1 | 1965 | 12 | 2025 | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1998 | natural gas peaker | TRUE | 17718 | Southwestern Public Service Co | 2454 | Cunningham | NM | Lea | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SPS.CUNNGHAM3 | SPS.CUNNGHAM3 | 126.9 | 0.9 | 106 | 98 | 87 | N |  |  | OP | X | 5 | 1998 | 12 | 2040 | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1998 | natural gas peaker | TRUE | 17718 | Southwestern Public Service Co | 2454 | Cunningham | NM | Lea | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SPS.CUNNGHAM4 | SPS.CUNNGHAM4 | 126.9 | 0.9 | 103 | 98 | 87 | N |  |  | OP | X | 5 | 1998 | 12 | 2040 | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1954 | natural gas steam turbine | TRUE | 15473 | Public Service Co of NM | 2475 | Algodones | NM | Sandoval | 1 | Natural Gas Steam Turbine | ST |  | J | X | X |  |  | 15 | 0.9 | 15 | 15 | 15 | N |  |  | OS | X | 10 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: RFO; DFO DFO DFO: NG |  |  |  | N |  | 12H | [23 empty] | N |  | N
Vintage1954 | natural gas steam turbine | TRUE | 15473 | Public Service Co of NM | 2475 | Algodones | NM | Sandoval | 2 | Natural Gas Steam Turbine | ST |  | J | X | X |  |  | 15 | 0.9 | 15 | 15 | 15 | N |  |  | OS | X | 10 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: RFO; DFO DFO DFO: NG |  |  |  | N |  | 12H | [23 empty] | N |  | N
Vintage1959 | natural gas steam turbine | TRUE | 15473 | Public Service Co of NM | 2475 | Algodones | NM | Sandoval | 3 | Natural Gas Steam Turbine | ST |  | J | X | X |  |  | 15 | 0.9 | 15 | 15 | 15 | N |  |  | OS | X | 3 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: RFO; DFO DFO DFO: NG |  |  |  | N |  | 12H | [23 empty] | N |  | N
Vintage1951 | natural gas steam turbine | TRUE | 58971 | Danskammer Energy | 2480 | Danskammer Generating Station | NY | Orange | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | Zone G | Zone G | 72 | 0.85 | 68 | 68 | 20 | N |  |  | OP | X | 12 | 1951 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: RFO; DFO DFO DFO: NG |  |  | N | N |  | 12H |  |  |  |  | N | N | [17 empty] | Y | Y | Y
Vintage1954 | natural gas steam turbine | TRUE | 58971 | Danskammer Energy | 2480 | Danskammer Generating Station | NY | Orange | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | Zone G | Zone G | 73.5 | 0.85 | 65.7 | 65.5 | 20 | N |  |  | OP | X | 9 | 1954 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: RFO; DFO DFO DFO: NG |  |  | N | N |  | 12H |  |  |  |  | N | [18 empty] | Y | Y | Y
Vintage1959 | natural gas steam turbine | TRUE | 58971 | Danskammer Energy | 2480 | Danskammer Generating Station | NY | Orange | 3 | Natural Gas Steam Turbine | ST |  | S | X | X | Zone G | Zone G | 147.1 | 0.85 | 137.7 | 137.1 | 40 | N |  |  | OP | X | 10 | 1959 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H |  | N |  |  | N | [18 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1967 | natural gas steam turbine | TRUE | 58971 | Danskammer Energy | 2480 | Danskammer Generating Station | NY | Orange | 4 | Natural Gas Steam Turbine | ST |  | S | X | X | zone G | Zone G | 239.4 | 0.85 | 225.9 | 229.5 | 60 | N |  |  | OP | X | 9 | 1967 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H |  | N |  |  | N | [18 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1967 | petroleum | TRUE | 58971 | Danskammer Energy | 2480 | Danskammer Generating Station | NY | Orange | 5 | Petroleum Liquids | IC |  | S | X | X | Zone G | Zone G | 2.7 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | SB | Y | 1 | 1967 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO; DFO DFO DFO: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1967 | petroleum | TRUE | 58971 | Danskammer Energy | 2480 | Danskammer Generating Station | NY | Orange | 6 | Petroleum Liquids | IC |  | S | X | X | Zone G | Zone G | 2.7 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | SB | Y | 1 | 1967 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO; DFO DFO DFO: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1920 | hydro | TRUE | 3249 | Central Hudson Gas & Elec Corp | 2481 | Dashville | NY | Ulster | 1 | Conventional Hydroelectric | HY |  | S | X | X | 23610 | 23610 | 2.4 | 0.8 | 2.4 | 2.4 | 0.3 | N |  |  | OP | X | 1 | 1920 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1920 | hydro | TRUE | 3249 | Central Hudson Gas & Elec Corp | 2481 | Dashville | NY | Ulster | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 2.4 | 2.4 | 0.3 | N |  |  | OP | X | 1 | 1920 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1953 | hydro | TRUE | 15296 | New York Power Authority | 2483 | Neversink | NY | Sullivan | H1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 25 | 1 | 25 | 25 | 1 | N |  |  | OP | X | 12 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1970 | other | TRUE | 3249 | Central Hudson Gas & Elec Corp | 2485 | South Cairo | NY | Greene | GT1 | Petroleum Liquids | GT |  | S | X | X | 23612 | 23612 | 21.3 | 0.86 | 18.1 | 22.9 | 2 | N |  |  | OP | X | 6 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: KER |  |  | N | N |  | 10M | [23 empty] | N
Vintage1924 | hydro | TRUE | 3249 | Central Hudson Gas & Elec Corp | 2486 | Sturgeon | NY | Ulster | H1 | Conventional Hydroelectric | HY |  | S | X | X | 23609 | 23609 | 4.8 | 0.8 | 4.8 | 4.8 | 4 | N |  |  | OP | X | 1 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1924 | hydro | TRUE | 3249 | Central Hudson Gas & Elec Corp | 2486 | Sturgeon | NY | Ulster | H2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.8 | 0.8 | 4.8 | 4.8 | 4 | N |  |  | OP | X | 1 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1924 | hydro | TRUE | 3249 | Central Hudson Gas & Elec Corp | 2486 | Sturgeon | NY | Ulster | H3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.8 | 0.8 | 4.8 | 4.8 | 4 | N |  |  | OP | X | 1 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1969 | natural gas peaker | TRUE | 3249 | Central Hudson Gas & Elec Corp | 2487 | West Coxsackie | NY | Greene | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 23611 | 23611 | 21.3 | 0.86 | 20.2 | 24.8 | 2 | N |  |  | OP | X | 12 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1959 | natural gas steam turbine | TRUE | 13192 | NRG Arthur Kill Operations Inc | 2490 | Arthur Kill Generating Station | NY | Richmond | 2 | Natural Gas Steam Turbine | ST |  | W | X | X |  |  | 342 | 0.8 | 340 | 344.2 | 90 | N |  |  | OP | X | 9 | 1959 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1969 | natural gas steam turbine | TRUE | 13192 | NRG Arthur Kill Operations Inc | 2490 | Arthur Kill Generating Station | NY | Richmond | 3 | Natural Gas Steam Turbine | ST |  | W | X | X |  |  | 535.5 | 0.9 | 520.1 | 523.4 | 150 | N |  |  | OP | X | 6 | 1969 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1970 | natural gas peaker | TRUE | 13192 | NRG Arthur Kill Operations Inc | 2490 | Arthur Kill Generating Station | NY | Richmond | GT1 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 18 | 1 | 12.1 | 15.8 | 1 | N |  |  | OP | X | 1 | 1970 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2005 | natural gas peaker | TRUE | 4226 | Consolidated Edison Co-NY Inc | 2493 | East River | NY | New York | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 180 | 0.85 | 155.8 | 192.5 | 110 | N |  |  | OP | X | 4 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2005 | natural gas peaker | TRUE | 4226 | Consolidated Edison Co-NY Inc | 2493 | East River | NY | New York | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 180 | 0.85 | 152.9 | 195 | 110 | N |  |  | OP | X | 4 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1951 | natural gas steam turbine | TRUE | 4226 | Consolidated Edison Co-NY Inc | 2493 | East River | NY | New York | 6 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 156.2 | 0.8 | 145.3 | 150.2 | 45 | N |  |  | OP | X | 11 | 1951 |  |  | Y | Electric Utility | 1 | X X X: T; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: RFO; DFO DFO DFO: NG |  |  | N | N |  | OVER | [23 empty] | Y | Y | Y
Vintage1955 | natural gas steam turbine | TRUE | 4226 | Consolidated Edison Co-NY Inc | 2493 | East River | NY | New York | 7 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 200 | 0.8 | 184.8 | 188.8 | 65 | N |  |  | OP | X | 6 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: RFO; DFO DFO DFO: NG |  |  | N | N |  | OVER | [23 empty] | Y | Y | Y
Vintage1971 | petroleum | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT11 | Petroleum Liquids | GT |  | S | X | X |  |  | 20 | 1 | 18.6 | 24.7 | 16 | N |  |  | OP | X | 6 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1971 | petroleum | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT12 | Petroleum Liquids | GT |  | S | X | X |  |  | 20 | 1 | 19.5 | 24.2 | 16 | N |  |  | OP | X | 6 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1971 | petroleum | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT13 | Petroleum Liquids | GT |  | S | X | X |  |  | 20 | 1 | 17.9 | 23.2 | 16 | N |  |  | OP | X | 6 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1971 | petroleum | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT14 | Petroleum Liquids | GT |  | S | X | X |  |  | 20 | 1 | 16.4 | 21.2 | 15.6 | N |  |  | OP | X | 6 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1971 | petroleum | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT15 | Petroleum Liquids | GT |  | S | X | X |  |  | 20 | 1 | 17.8 | 22.6 | 15.9 | N |  |  | OP | X | 6 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1971 | petroleum | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT16 | Petroleum Liquids | GT |  | S | X | X |  |  | 20 | 1 | 16.5 | 21.4 | 15.6 | N |  |  | OP | X | 6 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1971 | petroleum | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT17 | Petroleum Liquids | GT |  | S | X | X |  |  | 20 | 1 | 18 | 22.4 | 16 | N |  |  | OP | X | 6 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1971 | petroleum | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT18 | Petroleum Liquids | GT |  | S | X | X |  |  | 20 | 1 | 16 | 21 | 14.6 | N |  |  | OS | X | 6 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1971 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT21 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 20 | 1 | 17.1 | 21.6 | 16 | N |  |  | OP | X | 6 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1971 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT22 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 20 | 1 | 16.9 | 21.5 | 15.2 | N |  |  | OP | X | 6 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1971 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT23 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 20 | 1 | 19.1 | 22.6 | 16 | N |  |  | OP | X | 6 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1971 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT24 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 20 | 1 | 17.1 | 22 | 16 | N |  |  | OP | X | 6 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1971 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT25 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 20 | 1 | 17.8 | 24 | 16 | N |  |  | OP | X | 6 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1971 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT26 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 20 | 1 | 19.7 | 24.9 | 16 | N |  |  | OP | X | 6 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1971 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT27 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 20 | 1 | 19.1 | 24.9 | 16 | N |  |  | OP | X | 6 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO | [5 empty] | 1H | [23 empty] | Y | Y | Y
Vintage1971 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT28 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 20 | 1 | 17.3 | 23.5 | 16 | N |  |  | OP | X | 6 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1971 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT31 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 20 | 1 | 17 | 21.5 | 16 | N |  |  | OP | X | 7 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1971 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT32 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 20 | 1 | 16.9 | 22 | 16 | N |  |  | OP | X | 7 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1971 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT33 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 20 | 1 | 18.3 | 23.7 | 16 | N |  |  | OP | X | 7 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1971 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT34 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 20 | 1 | 15.9 | 21.6 | 15.9 | N |  |  | OP | X | 7 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1971 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT35 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 20 | 1 | 17.3 | 22.5 | 16 | N |  |  | OP | X | 7 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1971 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT36 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 20 | 1 | 15.4 | 20.8 | 15.2 | N |  |  | OP | X | 7 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1971 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT37 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 20 | 1 | 17.9 | 23.6 | 16 | N |  |  | OP | X | 7 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1971 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT38 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 20 | 1 | 17.8 | 23.7 | 16 | N |  |  | OP | X | 7 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1971 | petroleum | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT41 | Petroleum Liquids | GT |  | S | X | X |  |  | 20 | 1 | 18.9 | 24.2 | 16 | N |  |  | OP | X | 7 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1971 | petroleum | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT42 | Petroleum Liquids | GT |  | S | X | X |  |  | 20 | 1 | 18.5 | 23.1 | 16 | N |  |  | OP | X | 7 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1971 | petroleum | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT43 | Petroleum Liquids | GT |  | S | X | X |  |  | 20 | 1 | 18.4 | 21.7 | 16 | N |  |  | OP | X | 7 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1971 | petroleum | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT44 | Petroleum Liquids | GT |  | S | X | X |  |  | 20 | 1 | 16 | 21.6 | 15.8 | N |  |  | OP | X | 7 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1971 | petroleum | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT45 | Petroleum Liquids | GT |  | S | X | X |  |  | 20 | 1 | 16.6 | 22.1 | 15.7 | N |  |  | OP | X | 7 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1971 | petroleum | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT46 | Petroleum Liquids | GT |  | S | X | X |  |  | 20 | 1 | 18.5 | 23.9 | 16 | N |  |  | OP | X | 7 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1971 | petroleum | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT47 | Petroleum Liquids | GT |  | S | X | X |  |  | 20 | 1 | 18.4 | 24.7 | 14 | N |  |  | OP | X | 7 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1971 | petroleum | TRUE | 54863 | U S Power Generating Company LLC | 2494 | Gowanus Gas Turbines Generating | NY | Kings | GT48 | Petroleum Liquids | GT |  | S | X | X |  |  | 20 | 1 | 17.2 | 23.2 | 16 | N |  |  | OP | X | 7 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1970 | other | TRUE | 4226 | Consolidated Edison Co-NY Inc | 2496 | Hudson Avenue | NY | Kings | GT3 | Petroleum Liquids | GT |  | S | X | X |  |  | 16.3 | 0.85 | 13.9 | 15.6 | 11 | N |  |  | OP | X | 7 | 1970 | 11 | 2022 | N | Electric Utility | 1 | X X X: X; DFO RC RC: KER |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1970 | other | TRUE | 4226 | Consolidated Edison Co-NY Inc | 2496 | Hudson Avenue | NY | Kings | GT5 | Petroleum Liquids | GT |  | S | X | X |  |  | 16.3 | 0.85 | 13.9 | 18.6 | 11 | N |  |  | OP | X | 7 | 1970 | 11 | 2022 | N | Electric Utility | 1 | X X X: X; DFO RC RC: KER |  |  |  | N |  | 1H | [23 empty] | N | N
Vintage1972 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2499 | Narrows Gas Turbines Generating | NY | Kings | NT11 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 22 | 1 | 19.4 | 24.4 | 16 | N |  |  | OP | X | 5 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1972 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2499 | Narrows Gas Turbines Generating | NY | Kings | NT12 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 22 | 1 | 17.5 | 22.7 | 16 | N |  |  | OP | X | 5 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1972 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2499 | Narrows Gas Turbines Generating | NY | Kings | NT13 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 22 | 1 | 18.5 | 24.4 | 16 | N |  |  | OP | X | 5 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1972 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2499 | Narrows Gas Turbines Generating | NY | Kings | NT14 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 22 | 1 | 18.7 | 24.9 | 16 | N |  |  | OP | X | 5 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1972 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2499 | Narrows Gas Turbines Generating | NY | Kings | NT15 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 22 | 1 | 20.7 | 24 | 16 | N |  |  | OP | X | 5 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1972 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2499 | Narrows Gas Turbines Generating | NY | Kings | NT16 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 22 | 1 | 16.3 | 21.9 | 15.7 | N |  |  | OP | X | 5 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 10M | [23 empty] | Y | Y | Y
Vintage1972 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2499 | Narrows Gas Turbines Generating | NY | Kings | NT17 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 22 | 1 | 19 | 24.9 | 15.6 | N |  |  | OP | X | 5 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1972 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2499 | Narrows Gas Turbines Generating | NY | Kings | NT18 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 22 | 1 | 17.7 | 23.3 | 16 | N |  |  | OP | X | 5 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1972 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2499 | Narrows Gas Turbines Generating | NY | Kings | NT21 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 22 | 1 | 19.2 | 24.6 | 16 | N |  |  | OP | X | 6 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1972 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2499 | Narrows Gas Turbines Generating | NY | Kings | NT22 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 22 | 1 | 16.4 | 22.4 | 16 | N |  |  | OP | X | 6 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1972 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2499 | Narrows Gas Turbines Generating | NY | Kings | NT23 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 22 | 1 | 17.5 | 23.2 | 16 | N |  |  | OP | X | 6 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1972 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2499 | Narrows Gas Turbines Generating | NY | Kings | NT24 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 22 | 1 | 19.7 | 23.8 | 16 | N |  |  | OP | X | 6 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1972 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2499 | Narrows Gas Turbines Generating | NY | Kings | NT25 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 22 | 1 | 20.2 | 24.4 | 16 | N |  |  | OP | X | 6 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1972 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2499 | Narrows Gas Turbines Generating | NY | Kings | NT26 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 22 | 1 | 15.3 | 21.7 | 15.3 | N |  |  | OP | X | 6 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1972 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2499 | Narrows Gas Turbines Generating | NY | Kings | NT27 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 22 | 1 | 19 | 24.2 | 16 | N |  |  | OP | X | 6 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1972 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 2499 | Narrows Gas Turbines Generating | NY | Kings | NT28 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 22 | 1 | 16.4 | 21.4 | 15.7 | N |  |  | OP | X | 6 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1963 | natural gas steam turbine | TRUE | 61130 | Helix Ravenswood, LLC | 2500 | Ravenswood | NY | Queens | 1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 400 | 0.8 | 368.5 | 375 | 75 | N |  |  | OP | X | 2 | 1963 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | OVER |  |  |  |  | N | [18 empty] | Y | Y | Y
Vintage1963 | natural gas steam turbine | TRUE | 61130 | Helix Ravenswood, LLC | 2500 | Ravenswood | NY | Queens | 2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 400 | 0.8 | 373 | 378 | 75 | N |  |  | OP | X | 5 | 1963 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | OVER | [23 empty] | Y | Y | Y
Vintage1965 | natural gas steam turbine | TRUE | 61130 | Helix Ravenswood, LLC | 2500 | Ravenswood | NY | Queens | 3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 1027 | 0.8 | 990 | 988.7 | 150 | N |  |  | OP | X | 6 | 1965 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | OVER | [23 empty] | Y | Y | Y
Vintage2003 | natural gas combined cycle | TRUE | 61130 | Helix Ravenswood, LLC | 2500 | Ravenswood | NY | Queens | 4 | Natural Gas Fired Combined Cycle | CT | CCR4 | S | X | N |  |  | 181 | 0.85 | 161.8 | 192.1 | 115 | N |  |  | OP | X | 12 | 2003 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | OVER | [23 empty] | Y | N | Y
Vintage2003 | natural gas combined cycle | TRUE | 61130 | Helix Ravenswood, LLC | 2500 | Ravenswood | NY | Queens | 4S | Natural Gas Fired Combined Cycle | CA | CCR4 | S | N | X |  |  | 87.5 | 0.85 | 78.3 | 92.9 | 0 | N |  |  | OP | X | 12 | 2003 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | OVER | [23 empty] | Y | N | Y
Vintage1967 | natural gas peaker | TRUE | 61130 | Helix Ravenswood, LLC | 2500 | Ravenswood | NY | Queens | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 16 | 0.85 | 8.1 | 11.1 | 7 | N |  |  | OP | X | 7 | 1967 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1969 | natural gas peaker | TRUE | 61130 | Helix Ravenswood, LLC | 2500 | Ravenswood | NY | Queens | GT10 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 25 | 0.85 | 16 | 22.3 | 10 | N |  |  | OP | X | 7 | 1969 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1969 | natural gas peaker | TRUE | 61130 | Helix Ravenswood, LLC | 2500 | Ravenswood | NY | Queens | GT11 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 25 | 0.85 | 16.4 | 22.4 | 10 | N |  |  | OP | X | 6 | 1969 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1969 | natural gas peaker | TRUE | 61130 | Helix Ravenswood, LLC | 2500 | Ravenswood | NY | Queens | GT21 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 42.9 | 0.85 | 30.6 | 41.7 | 10 | N |  |  | OS | X | 6 | 1969 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1969 | natural gas peaker | TRUE | 61130 | Helix Ravenswood, LLC | 2500 | Ravenswood | NY | Queens | GT22 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 42.9 | 0.85 | 32 | 41.9 | 10 | N |  |  | OS | X | 6 | 1969 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1969 | natural gas peaker | TRUE | 61130 | Helix Ravenswood, LLC | 2500 | Ravenswood | NY | Queens | GT23 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 42.9 | 0.85 | 30.7 | 37.3 | 10 | N |  |  | OS | X | 6 | 1969 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1969 | natural gas peaker | TRUE | 61130 | Helix Ravenswood, LLC | 2500 | Ravenswood | NY | Queens | GT24 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 42.9 | 0.85 | 30.9 | 41.6 | 10 | N |  |  | OS | X | 6 | 1969 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1969 | natural gas peaker | TRUE | 61130 | Helix Ravenswood, LLC | 2500 | Ravenswood | NY | Queens | GT31 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 42.9 | 0.85 | 30.7 | 40.8 | 10 | N |  |  | OS | X | 6 | 1969 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1969 | natural gas peaker | TRUE | 61130 | Helix Ravenswood, LLC | 2500 | Ravenswood | NY | Queens | GT32 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 42.9 | 0.85 | 29.7 | 40.3 | 10 | N |  |  | OS | X | 6 | 1969 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1969 | natural gas peaker | TRUE | 61130 | Helix Ravenswood, LLC | 2500 | Ravenswood | NY | Queens | GT34 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 42.9 | 0.85 | 29.8 | 40.8 | 10 | N |  |  | OS | X | 6 | 1969 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1969 | natural gas peaker | TRUE | 4226 | Consolidated Edison Co-NY Inc | 2503 | 59th Street | NY | New York | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 17.1 | 0.91 | 13.1 | 18.8 | 3 | N |  |  | OP | X | 6 | 1969 | 4 | 2025 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1968 | other | TRUE | 4226 | Consolidated Edison Co-NY Inc | 2504 | 74th Street | NY | New York | GT1 | Petroleum Liquids | GT |  | S | X | X |  |  | 18.5 | 0.85 | 18.5 | 22.6 | 8 | N |  |  | OP | X | 10 | 1968 | 4 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: KER |  |  | N | N |  | 1H | [23 empty] | N
Vintage1968 | other | TRUE | 4226 | Consolidated Edison Co-NY Inc | 2504 | 74th Street | NY | New York | GT2 | Petroleum Liquids | GT |  | S | X | X |  |  | 18.5 | 0.85 | 19.3 | 22.6 | 8 | N |  |  | OP | X | 10 | 1968 | 4 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: KER |  |  | N | N |  | 1H | [23 empty] | N
Vintage1971 | natural gas peaker | TRUE | 56505 | National Grid Generation LLC | 2511 | E F Barrett | NY | Nassau | 10 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 23701 | 23701 | 41.8 | 0.9 | 40.6 | 50 | 30 | N |  |  | OP | X | 6 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1971 | natural gas peaker | TRUE | 56505 | National Grid Generation LLC | 2511 | E F Barrett | NY | Nassau | 11 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 23702 | 23702 | 41.8 | 0.9 | 40.1 | 50.5 | 30 | N |  |  | OP | X | 6 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1971 | natural gas peaker | TRUE | 56505 | National Grid Generation LLC | 2511 | E F Barrett | NY | Nassau | 12 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 23703 | 23703 | 41.8 | 0.9 | 40.9 | 48.7 | 30 | N |  |  | OP | X | 6 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1970 | natural gas peaker | TRUE | 56505 | National Grid Generation LLC | 2511 | E F Barrett | NY | Nassau | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 23706 | 23706 | 18 | 0.85 | 17.7 | 20.2 | 10.5 | N |  |  | OP | X | 6 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1970 | natural gas peaker | TRUE | 56505 | National Grid Generation LLC | 2511 | E F Barrett | NY | Nassau | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 23707 | 23707 | 18 | 0.85 | 16.8 | 20.5 | 11.4 | N |  |  | OP | X | 7 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1970 | natural gas peaker | TRUE | 56505 | National Grid Generation LLC | 2511 | E F Barrett | NY | Nassau | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 23708 | 23708 | 18 | 0.85 | 17.6 | 20.1 | 11 | N |  |  | OP | X | 7 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  |  | N |  | 1H | [23 empty] | Y | N | Y
Vintage1970 | natural gas peaker | TRUE | 56505 | National Grid Generation LLC | 2511 | E F Barrett | NY | Nassau | 6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 23709 | 23709 | 18 | 0.85 | 16.4 | 19.9 | 11.2 | N |  |  | OP | X | 7 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  |  | N |  | 10M | [23 empty] | Y | N | Y
Vintage1970 | natural gas peaker | TRUE | 56505 | National Grid Generation LLC | 2511 | E F Barrett | NY | Nassau | 8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 23711 | 23711 | 18 | 0.85 | 15.1 | 15.2 | 11.4 | N |  |  | OP | X | 7 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1971 | natural gas peaker | TRUE | 56505 | National Grid Generation LLC | 2511 | E F Barrett | NY | Nassau | 9 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 23700 | 23700 | 41.8 | 0.9 | 41.2 | 49.2 | 29.8 | N |  |  | OP | X | 6 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1970 | natural gas peaker | TRUE | 56505 | National Grid Generation LLC | 2511 | E F Barrett | NY | Nassau | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 23704 | 23704 | 18 | 0.85 | 17.4 | 20.5 | 10.7 | N |  |  | OP | X | 6 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1970 | natural gas peaker | TRUE | 56505 | National Grid Generation LLC | 2511 | E F Barrett | NY | Nassau | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 23705 | 23705 | 18 | 0.85 | 17.6 | 20.4 | 9 | N |  |  | OP | X | 6 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1956 | natural gas steam turbine | TRUE | 56505 | National Grid Generation LLC | 2511 | E F Barrett | NY | Nassau | ST1 | Natural Gas Steam Turbine | ST |  | S | X | X | 23545 | 23545 | 188 | 0.85 | 194.2 | 199.5 | 15 | N |  |  | OP | X | 11 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: RFO; DFO DFO DFO: NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1963 | natural gas steam turbine | TRUE | 56505 | National Grid Generation LLC | 2511 | E F Barrett | NY | Nassau | ST2 | Natural Gas Steam Turbine | ST |  | S | X | X | 23546 | 23546 | 188 | 0.85 | 178 | 190.5 | 15 | N |  |  | OP | X | 10 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: RFO; DFO DFO DFO: NG |  |  |  | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1970 | petroleum | TRUE | 56505 | National Grid Generation LLC | 2512 | East Hampton | NY | Suffolk | 1 | Petroleum Liquids | GT |  | S | X | X | 23717 | 23717 | 21.3 | 0.85 | 19.2 | 24 | 15.4 | N |  |  | OP | X | 12 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1962 | petroleum | TRUE | 56505 | National Grid Generation LLC | 2512 | East Hampton | NY | Suffolk | 2 | Petroleum Liquids | IC |  | S | X | X | 23722 | 23722 | 2 | 0.9 | 2 | 2 | 2 | N |  |  | OP | X | 12 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1962 | petroleum | TRUE | 56505 | National Grid Generation LLC | 2512 | East Hampton | NY | Suffolk | 3 | Petroleum Liquids | IC |  | S | X | X | 23722 | 23722 | 2 | 0.9 | 2 | 2.1 | 2 | N |  |  | OP | X | 12 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1962 | petroleum | TRUE | 56505 | National Grid Generation LLC | 2512 | East Hampton | NY | Suffolk | 4 | Petroleum Liquids | IC |  | S | X | X | 23722 | 23722 | 2 | 0.9 | 2 | 2.1 | 1.9 | N |  |  | OP | X | 12 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N | N | N
Vintage1972 | petroleum | TRUE | 56505 | National Grid Generation LLC | 2514 | Glenwood | NY | Nassau | GT2 | Petroleum Liquids | GT |  | S | X | X | 23688 | 23688 | 55 | 0.9 | 49 | 55.1 | 40 | N |  |  | OP | X | 6 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1972 | petroleum | TRUE | 56505 | National Grid Generation LLC | 2514 | Glenwood | NY | Nassau | GT3 | Petroleum Liquids | GT |  | S | X | X | 23689 | 23689 | 55 | 0.9 | 55.1 | 68.6 | 44.1 | N |  |  | OP | X | 6 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1968 | natural gas steam turbine | TRUE | 56505 | National Grid Generation LLC | 2516 | Northport | NY | Suffolk | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | 23552 | 23552 | 387 | 0.9 | 398 | 399 | 40 | N |  |  | OP | X | 6 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: RFO; DFO DFO DFO: NG |  |  | N |  |  | 12H | [23 empty] | Y | Y | Y
Vintage1972 | natural gas steam turbine | TRUE | 56505 | National Grid Generation LLC | 2516 | Northport | NY | Suffolk | 3 | Natural Gas Steam Turbine | ST |  | S | X | X | 23553 | 23553 | 387 | 0.9 | 398.5 | 394.2 | 30 | N |  |  | OP | X | 7 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: RFO; DFO DFO DFO: NG | [5 empty] | 12H | [23 empty] | Y | Y | Y
Vintage1977 | natural gas steam turbine | TRUE | 56505 | National Grid Generation LLC | 2516 | Northport | NY | Suffolk | 4 | Natural Gas Steam Turbine | ST |  | S | X | X | 23650 | 23650 | 387 | 0.9 | 398 | 396.5 | 40 | N |  |  | OP | X | 12 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: RFO; DFO DFO DFO: NG |  |  | N |  |  | 12H | [23 empty] | Y | Y | Y
Vintage1967 | petroleum | TRUE | 56505 | National Grid Generation LLC | 2516 | Northport | NY | Suffolk | GT1 | Petroleum Liquids | GT |  | S | X | X | 23718 | 23718 | 16 | 0.85 | 11.8 | 15.8 | 10.6 | N |  |  | OP | X | 3 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1967 | natural gas steam turbine | TRUE | 56505 | National Grid Generation LLC | 2516 | Northport | NY | Suffolk | ST1 | Natural Gas Steam Turbine | ST |  | S | X | X | 23551 | 23551 | 387 | 0.9 | 397.7 | 396.2 | 40 | N |  |  | OP | X | 7 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: RFO; DFO DFO DFO: NG |  |  | N |  |  | 12H | [23 empty] | Y | Y | Y
Vintage1958 | natural gas steam turbine | TRUE | 56505 | National Grid Generation LLC | 2517 | Port Jefferson | NY | Suffolk | 3 | Natural Gas Steam Turbine | ST |  | S | X | X | 23555 | 23555 | 188 | 0.9 | 192 | 189.2 | 15 | N |  |  | OP | X | 11 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: RFO; DFO DFO DFO: NG |  |  |  | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1960 | natural gas steam turbine | TRUE | 56505 | National Grid Generation LLC | 2517 | Port Jefferson | NY | Suffolk | 4 | Natural Gas Steam Turbine | ST |  | S | X | X | 23616 | 23616 | 188 | 0.9 | 193 | 194.7 | 15 | N |  |  | OP | X | 11 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: RFO; DFO DFO DFO: NG |  |  |  | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1966 | petroleum | TRUE | 56505 | National Grid Generation LLC | 2517 | Port Jefferson | NY | Suffolk | GT1 | Petroleum Liquids | GT |  | S | X | X | 23713 | 23713 | 16 | 0.85 | 12.9 | 16.6 | 10.6 | N |  |  | OP | X | 12 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  |  | N |  | 1H | [23 empty] | N | N
Vintage2002 | natural gas peaker | TRUE | 56505 | National Grid Generation LLC | 2517 | Port Jefferson | NY | Suffolk | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 24210 | 24210 | 53 | 0.9 | 42.6 | 46.7 | 37 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 56505 | National Grid Generation LLC | 2517 | Port Jefferson | NY | Suffolk | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 24211 | 24211 | 53 | 0.9 | 40.1 | 47.1 | 37 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1971 | petroleum | TRUE | 56505 | National Grid Generation LLC | 2518 | Shoreham | NY | Suffolk | GT1 | Petroleum Liquids | GT |  | S | X | X | 23715 | 23715 | 52.9 | 0.9 | 49.8 | 65 | 39.4 | N |  |  | OP | X | 7 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage1966 | petroleum | TRUE | 56505 | National Grid Generation LLC | 2518 | Shoreham | NY | Suffolk | GT2 | Petroleum Liquids | GT |  | S | X | X | 23716 | 23716 | 18.6 | 0.85 | 15.9 | 19.7 | 12 | N |  |  | OP | X | 4 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage1963 | petroleum | TRUE | 56505 | National Grid Generation LLC | 2519 | South Hampton | NY | Suffolk | 1 | Petroleum Liquids | GT |  | S | X | X | 23720 |  | 11.5 | 0.85 | 8.5 | 10.4 | 6.6 | N |  |  | OP | X | 3 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage1964 | petroleum | TRUE | 56505 | National Grid Generation LLC | 2520 | Southold | NY | Suffolk | 1 | Petroleum Liquids | GT |  | S | X | X | 23719 | 23719 | 14 | 0.85 | 10 | 9 | 7.3 | N |  |  | OP | X | 8 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage1971 | petroleum | TRUE | 56505 | National Grid Generation LLC | 2521 | West Babylon | NY | Suffolk | 4 | Petroleum Liquids | GT |  | S | X | X | 23714 | 23714 | 52.4 | 0.9 | 49.7 | 66.5 | 41.5 | N |  |  | SB | Y | 8 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage1921 | hydro | TRUE | 13511 | New York State Elec & Gas Corp | 2522 | Cadyville | NY | Clinton | 1 | Conventional Hydroelectric | HY |  | S | X | X | 23628 | 23628 | 1.2 | 0.8 | 1.2 | 1.2 | 0 | N |  |  | OS | X | 8 | 1921 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1921 | hydro | TRUE | 13511 | New York State Elec & Gas Corp | 2522 | Cadyville | NY | Clinton | 2 | Conventional Hydroelectric | HY |  | S | X | X | 23628 | 23628 | 1.2 | 0.8 | 1.2 | 1.2 | 0 | N |  |  | OP | X | 8 | 1921 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1986 | hydro | TRUE | 13511 | New York State Elec & Gas Corp | 2522 | Cadyville | NY | Clinton | 3 | Conventional Hydroelectric | HY |  | S | X | X | 23628 | 23628 | 3.1 | 0.95 | 3.1 | 3.1 | 0 | N |  |  | OP | X | 9 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1953 | natural gas steam turbine | TRUE | 25 | Greenidge Generation Holdings LLC | 2527 | Greenidge Generation LLC | NY | Yates | 4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 112 | 0.85 | 104.5 | 106.3 | 32 | N |  |  | OP | X | 12 | 1953 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: WDS; DFO DFO DFO: NG |  |  | N | N |  | OVER |  |  |  |  | N | [18 empty] | Y | Y | N
Vintage1967 | petroleum | TRUE | 13511 | New York State Elec & Gas Corp | 2528 | Harris Lake | NY | Essex | 1 | Petroleum Liquids | IC |  | S | X | X | 5018 | 5018 | 1.7 | 0.8 | 1.7 | 1.7 | 1.7 | N |  |  | OP | X | 9 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage2017 | petroleum | TRUE | 13511 | New York State Elec & Gas Corp | 2528 | Harris Lake | NY | Essex | 2 | Petroleum Liquids | IC |  | S | X | X | 5018 | 5018 | 2.5 | 0.8 | 2.3 | 2.3 | 2.3 | N |  |  | OP | X | 8 | 2017 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1948 | hydro | TRUE | 13511 | New York State Elec & Gas Corp | 2530 | High Falls - Saranac NY | NY | Clinton | 1 | Conventional Hydroelectric | HY |  | S | X | X | 23628 | 23628 | 4 | 0.8 | 4 | 4 | 0 | N |  |  | OP | X | 8 | 1948 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 1H | [23 empty] | N
Vintage1949 | hydro | TRUE | 13511 | New York State Elec & Gas Corp | 2530 | High Falls - Saranac NY | NY | Clinton | 2 | Conventional Hydroelectric | HY |  | S | X | X | 23628 | 23628 | 4 | 0.8 | 4 | 4 | 0 | N |  |  | OS | X | 8 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1956 | hydro | TRUE | 13511 | New York State Elec & Gas Corp | 2530 | High Falls - Saranac NY | NY | Clinton | 3 | Conventional Hydroelectric | HY |  | S | X | X | 23628 | 23628 | 7 | 0.8 | 7 | 7 | 0 | N |  |  | OA | X | 8 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H
Vintage1928 | hydro | TRUE | 13511 | New York State Elec & Gas Corp | 2532 | Kent Falls | NY | Clinton | 1 | Conventional Hydroelectric | HY |  | S | X | X | 23628 | 23628 | 3.2 | 0.8 | 3.8 | 3.8 | 0 | N |  |  | OP | X | 8 | 1928 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1928 | hydro | TRUE | 13511 | New York State Elec & Gas Corp | 2532 | Kent Falls | NY | Clinton | 2 | Conventional Hydroelectric | HY |  | S | X | X | 23628 | 23628 | 3.2 | 0.8 | 3.8 | 3.8 | 0 | N |  |  | OS | X | 8 | 1928 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1985 | hydro | TRUE | 13511 | New York State Elec & Gas Corp | 2532 | Kent Falls | NY | Clinton | 3 | Conventional Hydroelectric | HY |  | S | X | X | 23628 | 23628 | 6 | 0.95 | 6 | 6 | 0 | N |  |  | OP | X | 7 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage2005 | natural gas combined cycle | TRUE | 14294 | PSEG Power New York Inc | 2539 | Bethlehem Energy Center | NY | Albany | 5 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | BETHLEHEM | 323560 | 194.3 | 0.85 | 178.4 | 205.8 | 170 | N |  |  | OP | X | 7 | 2005 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2005 | natural gas combined cycle | TRUE | 14294 | PSEG Power New York Inc | 2539 | Bethlehem Energy Center | NY | Albany | 6 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | BETHLEHEM | 323561 | 194.3 | 0.85 | 179.7 | 205.8 | 170 | N |  |  | OP | X | 7 | 2005 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2005 | natural gas combined cycle | TRUE | 14294 | PSEG Power New York Inc | 2539 | Bethlehem Energy Center | NY | Albany | 7 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | BETHLEHEM | 323562 | 194.3 | 0.85 | 177.9 | 205.8 | 170 | N |  |  | OP | X | 7 | 2005 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2005 | natural gas combined cycle | TRUE | 14294 | PSEG Power New York Inc | 2539 | Bethlehem Energy Center | NY | Albany | 8 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | BETHLEHEM | 352659 | 310.2 | 0.85 | 279.5 | 307.3 | 170 | N |  |  | OP | X | 7 | 2005 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1927 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2540 | Allens Falls | NY | St Lawrence | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24042 | 24042 | 4 | 0.8 | 3.5 | 5 | 3.5 | N |  |  | OP | X | 1 | 1927 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1924 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2543 | Beardslee | NY | Herkimer | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24051 | 24051 | 10 | 0.8 | 8.5 | 8.9 | 4 | N |  |  | OP | X | 1 | 1924 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1924 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2543 | Beardslee | NY | Herkimer | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24051 | 24051 | 10 | 0.8 | 8.1 | 7.8 | 4 | N |  |  | OP | X | 1 | 1924 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1903 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2544 | Belfort | NY | Lewis | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24048 | 24048 | 0.4 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 1 | 1903 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1915 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2544 | Belfort | NY | Lewis | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24048 | 24048 | 0.6 | 0.8 | 0.5 | 0.5 | 0.4 | N |  |  | OP | X | 1 | 1915 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1918 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2544 | Belfort | NY | Lewis | 3 | Conventional Hydroelectric | HY |  | S | X | X | 24048 | 24048 | 1 | 0.8 | 0.9 | 0.9 | 0.7 | N |  |  | OP | X | 1 | 1918 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1932 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2545 | Bennetts Bridge | NY | Oswego | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24043 | 24043 | 9 | 0.8 | 8.4 | 7 | 3 | N |  |  | OP | X | 1 | 1932 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1932 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2545 | Bennetts Bridge | NY | Oswego | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24043 | 24043 | 9 | 0.8 | 8.4 | 7.5 | 3 | N |  |  | OP | X | 1 | 1932 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1966 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2545 | Bennetts Bridge | NY | Oswego | 3 | Conventional Hydroelectric | HY |  | S | X | X | 24043 | 24043 | 9 | 0.8 | 6.3 | 7.3 | 3 | N |  |  | OP | X | 1 | 1966 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1966 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2545 | Bennetts Bridge | NY | Oswego | 4 | Conventional Hydroelectric | HY |  | S | X | X | 24043 | 24043 | 9 | 0.8 | 7.2 | 7.3 | 3 | N |  |  | OP | X | 1 | 1966 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1920 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2546 | Black River | NY | Jefferson | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24047 | 24047 | 2 | 0.8 | 1.5 | 2.3 | 1.5 | N |  |  | OP | X | 1 | 1920 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1920 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2546 | Black River | NY | Jefferson | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24047 | 24047 | 2 | 0.8 | 1.5 | 2.3 | 1.5 | N |  |  | OP | X | 1 | 1920 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1920 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2546 | Black River | NY | Jefferson | 3 | Conventional Hydroelectric | HY |  | S | X | X | 24047 | 24047 | 2 | 0.8 | 1.5 | 2.3 | 1.5 | N |  |  | OP | X | 1 | 1920 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1957 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2547 | Blake | NY | St Lawrence | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24056 | 24056 | 15 | 0.8 | 14.2 | 14.5 | 1 | N |  |  | OP | X | 1 | 1957 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1923 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2548 | Browns Falls | NY | St Lawrence | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24044 | 24044 | 8 | 0.8 | 7.9 | 7.6 | 7 | N |  |  | OP | X | 1 | 1923 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1923 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2548 | Browns Falls | NY | St Lawrence | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24044 | 24044 | 8 | 0.8 | 7.9 | 7.6 | 7 | N |  |  | OP | X | 1 | 1923 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1913 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2550 | Chasm | NY | Franklin | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24042 | 24042 | 1 | 0.8 | 0.5 | 0.6 | 0.5 | N |  |  | OP | X | 1 | 1913 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1913 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2550 | Chasm | NY | Franklin | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24042 | 24042 | 1 | 0.8 | 0.5 | 0.6 | 0.5 | N |  |  | OP | X | 1 | 1913 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1926 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2550 | Chasm | NY | Franklin | 3 | Conventional Hydroelectric | HY |  | S | X | X | 24042 | 24042 | 1 | 0.9 | 0.6 | 0.7 | 0.6 | N |  |  | OP | X | 1 | 1926 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1918 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2551 | Colton | NY | St Lawrence | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24057 | 24057 | 10 | 0.8 | 9.9 | 9.7 | 0.2 | N |  |  | OP | X | 1 | 1918 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1918 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2551 | Colton | NY | St Lawrence | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24057 | 24057 | 10 | 0.8 | 10.3 | 9.9 | 0.2 | N |  |  | OP | X | 1 | 1918 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1928 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2551 | Colton | NY | St Lawrence | 3 | Conventional Hydroelectric | HY |  | S | X | X | 24057 | 24057 | 10 | 0.8 | 9.5 | 11.1 | 0.2 | N |  |  | OP | X | 1 | 1928 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1925 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2552 | Deferiet | NY | Jefferson | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24047 | 24047 | 4 | 0.8 | 3.6 | 3.6 | 2.8 | N |  |  | OP | X | 1 | 1925 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1925 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2552 | Deferiet | NY | Jefferson | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24047 | 24047 | 4 | 0.8 | 3.6 | 3.6 | 2.8 | N |  |  | OP | X | 1 | 1925 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1925 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2552 | Deferiet | NY | Jefferson | 3 | Conventional Hydroelectric | HY |  | S | X | X | 24047 | 24047 | 4 | 0.8 | 3.6 | 3.6 | 2.8 | N |  |  | OP | X | 1 | 1925 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1950 | hard coal | TRUE | 13579 | Dunkirk Power LLC | 2554 | Dunkirk Generating Plant | NY | Chautauqua | 1 | Conventional Steam Coal | ST |  | W | X | X | Zone A - West | Zone A - West | 96 | 0.8 | 75 | 75 | 35 | N |  |  | OS | X | 11 | 1950 | 4 | 2022 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: SUB; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1959 | hard coal | TRUE | 13579 | Dunkirk Power LLC | 2554 | Dunkirk Generating Plant | NY | Chautauqua | 3 | Conventional Steam Coal | ST |  | W | X | X | Zone A - West | Zone A - West | 217.6 | 0.85 | 185 | 185 | 85 | N |  |  | OS | X | 9 | 1959 | 4 | 2022 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1960 | hard coal | TRUE | 13579 | Dunkirk Power LLC | 2554 | Dunkirk Generating Plant | NY | Chautauqua | ST4 | Conventional Steam Coal | ST |  | W | X | X | Zone A - West | Zone A - West | 217.6 | 0.85 | 185 | 185 | 85 | N |  |  | OS | X | 8 | 1960 | 4 | 2022 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1914 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2555 | Eagle | NY | Lewis | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24048 | 24048 | 2 | 0.9 | 1.4 | 1.1 | 1.1 | N |  |  | OP | X | 1 | 1914 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1915 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2555 | Eagle | NY | Lewis | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24048 | 24048 | 1 | 0.9 | 1.2 | 1 | 1 | N |  |  | OP | X | 1 | 1915 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1919 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2555 | Eagle | NY | Lewis | 3 | Conventional Hydroelectric | HY |  | S | X | X | 24048 | 24048 | 1 | 0.9 | 1.2 | 1 | 1 | N |  |  | OP | X | 1 | 1919 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1925 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2555 | Eagle | NY | Lewis | 4 | Conventional Hydroelectric | HY |  | S | X | X | 24048 | 24048 | 2 | 0.8 | 2 | 1.8 | 1.8 | N |  |  | OP | X | 1 | 1925 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1928 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2556 | Eel Weir | NY | St Lawrence | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24044 | 24044 | 0.5 | 0.8 | 0.4 | 0.4 | 0.4 | N |  |  | OP | X | 1 | 1928 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1928 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2556 | Eel Weir | NY | St Lawrence | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24044 | 24044 | 1 | 0.8 | 0.8 | 0.8 | 0.8 | N |  |  | OP | X | 1 | 1928 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1928 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2556 | Eel Weir | NY | St Lawrence | 3 | Conventional Hydroelectric | HY |  | S | X | X | 24044 | 24044 | 1 | 0.8 | 0.8 | 0.8 | 0.8 | N |  |  | OP | X | 1 | 1928 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1902 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2557 | Effley | NY | Lewis | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24048 | 24048 | 0.4 | 1 | 0.4 | 0.4 | 0.4 | N |  |  | OP | X | 1 | 1902 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1907 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2557 | Effley | NY | Lewis | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24048 | 24048 | 0.4 | 1 | 0.4 | 0.4 | 0.4 | N |  |  | OP | X | 1 | 1907 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1910 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2557 | Effley | NY | Lewis | 3 | Conventional Hydroelectric | HY |  | S | X | X | 24048 | 24048 | 0.6 | 0.8 | 0.4 | 0.4 | 0.4 | N |  |  | OP | X | 1 | 1910 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1923 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2557 | Effley | NY | Lewis | 4 | Conventional Hydroelectric | HY |  | S | X | X | 24048 | 24048 | 1.6 | 0.8 | 1.7 | 1.4 | 1.4 | N |  |  | OP | X | 1 | 1923 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1916 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2559 | Elmer | NY | Lewis | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24048 | 24048 | 1 | 0.8 | 1 | 1 | 0.7 | N |  |  | OP | X | 1 | 1916 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1916 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2559 | Elmer | NY | Lewis | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24048 | 24048 | 1 | 0.8 | 1 | 1 | 0.7 | N |  |  | OP | X | 1 | 1916 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1920 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2560 | Ephratah | NY | Fulton | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24051 | 24051 | 1 | 0.8 | 0.9 | 0.9 | 0.2 | N |  |  | OP | X | 1 | 1920 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1911 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2560 | Ephratah | NY | Fulton | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24051 | 24051 | 1 | 0.8 | 0.9 | 1 | 0.2 | N |  |  | OP | X | 1 | 1911 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1911 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2560 | Ephratah | NY | Fulton | 3 | Conventional Hydroelectric | HY |  | S | X | X | 24051 | 24051 | 1 | 0.8 | 0.9 | 1 | 0.2 | N |  |  | OP | X | 1 | 1911 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1911 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2560 | Ephratah | NY | Fulton | 4 | Conventional Hydroelectric | HY |  | S | X | X | 24051 | 24051 | 1 | 0.8 | 1 | 1 | 0.2 | N |  |  | OP | X | 1 | 1911 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1928 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2561 | East Norfolk | NY | St Lawrence | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24057 | 24057 | 4 | 0.8 | 4.1 | 4 | 0.9 | N |  |  | OP | X | 1 | 1928 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1955 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2562 | Five Falls | NY | St Lawrence | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24056 | 24056 | 24 | 0.8 | 22.4 | 23.5 | 1 | N |  |  | OP | X | 1 | 1955 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1924 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2563 | Flat Rock | NY | St Lawrence | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24044 | 24044 | 2 | 0.8 | 2.4 | 2.4 | 1.4 | N |  |  | OP | X | 1 | 1924 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1924 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2563 | Flat Rock | NY | St Lawrence | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24044 | 24044 | 3 | 0.8 | 2.8 | 2.8 | 2.5 | N |  |  | OP | X | 1 | 1924 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1911 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2564 | Franklin (NY) | NY | Franklin | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24042 | 24042 | 1 | 0.8 | 0.9 | 0.9 | 0.8 | N |  |  | OP | X | 1 | 1911 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1926 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2564 | Franklin (NY) | NY | Franklin | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24042 | 24042 | 1 | 0.8 | 1.1 | 1.1 | 1 | N |  |  | OP | X | 1 | 1926 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1924 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2566 | Fulton Hydro | NY | Oswego | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24041 | 24041 | 0.8 | 0.8 | 0.1 | 0.7 | 0.1 | N |  |  | OP | X | 1 | 1924 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1928 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2566 | Fulton Hydro | NY | Oswego | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24041 | 24041 | 0.5 | 0.8 | 0.1 | 0.3 | 0.1 | N |  |  | OP | X | 1 | 1928 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1950 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2568 | Glenwood Hydro | NY | Orleans | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24046 | 24046 | 0.5 | 0.8 | 0.5 | 0.4 | 0.3 | N |  |  | OP | X | 1 | 1950 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1950 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2568 | Glenwood Hydro | NY | Orleans | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24046 | 24046 | 0.5 | 0.8 | 0.5 | 0.4 | 0.3 | N |  |  | OP | X | 1 | 1950 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1950 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2568 | Glenwood Hydro | NY | Orleans | 3 | Conventional Hydroelectric | HY |  | S | X | X | 24046 | 24046 | 0.5 | 0.8 | 0.5 | 0.4 | 0.3 | N |  |  | OP | X | 1 | 1950 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1983 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2569 | Granby | NY | Oswego | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24041 | 24041 | 5 | 0.9 | 5.1 | 5.2 | 2.8 | N |  |  | OP | X | 1 | 1983 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1983 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2569 | Granby | NY | Oswego | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24041 | 24041 | 5 | 0.9 | 5.1 | 5.2 | 2.8 | N |  |  | OP | X | 1 | 1983 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1914 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2571 | Hannawa | NY | St Lawrence | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24057 | 24057 | 3.6 | 0.8 | 3.6 | 3.6 | 0.2 | N |  |  | OP | X | 1 | 1914 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1920 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2571 | Hannawa | NY | St Lawrence | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24057 | 24057 | 3.6 | 0.8 | 3.6 | 3.6 | 0.2 | N |  |  | OP | X | 1 | 1920 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1924 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2572 | Herrings | NY | Jefferson | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24047 | 24047 | 1.8 | 0.8 | 1.5 | 1.5 | 1 | N |  |  | OP | X | 1 | 1924 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1924 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2572 | Herrings | NY | Jefferson | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24047 | 24047 | 1.8 | 0.8 | 1.5 | 1.5 | 1 | N |  |  | OP | X | 1 | 1924 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1924 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2572 | Herrings | NY | Jefferson | 3 | Conventional Hydroelectric | HY |  | S | X | X | 24047 | 24047 | 1.8 | 0.8 | 1.5 | 1.5 | 1 | N |  |  | OP | X | 1 | 1924 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1924 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2573 | Heuvelton | NY | St Lawrence | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24044 | 24044 | 0.5 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 1 | 1924 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1924 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2573 | Heuvelton | NY | St Lawrence | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24044 | 24044 | 0.5 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 1 | 1924 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1928 | hydro | TRUE | 14240 | Oswego City of | 2574 | High Dam | NY | Oswego | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.8 | 1 | 2.2 | 2.2 | 0.7 | N |  |  | OP | X | 8 | 1928 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M | [23 empty] | N
Vintage1928 | hydro | TRUE | 14240 | Oswego City of | 2574 | High Dam | NY | Oswego | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.8 | 1 | 2.2 | 2.2 | 0.7 | N |  |  | OP | X | 8 | 1928 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M | [23 empty] | N
Vintage1928 | hydro | TRUE | 14240 | Oswego City of | 2574 | High Dam | NY | Oswego | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.8 | 1 | 2.2 | 2.2 | 0.7 | N |  |  | OP | X | 8 | 1928 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M | [23 empty] | N
Vintage1949 | hydro | TRUE | 14240 | Oswego City of | 2574 | High Dam | NY | Oswego | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.5 | 1 | 2.2 | 2.2 | 0.7 | N |  |  | OP | X | 8 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M | [23 empty] | N
Vintage1925 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2575 | High Falls - Croghan NY | NY | Lewis | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24048 | 24048 | 2 | 0.8 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 1 | 1925 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1925 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2575 | High Falls - Croghan NY | NY | Lewis | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24048 | 24048 | 2 | 0.8 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 7 | 1925 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1925 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2575 | High Falls - Croghan NY | NY | Lewis | 3 | Conventional Hydroelectric | HY |  | S | X | X | 24048 | 24048 | 2 | 0.8 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 7 | 1925 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage2003 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2576 | Higley | NY | St Lawrence | 1N | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.6 | 0.3 | N |  |  | OP | X | 9 | 2003 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage2003 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2576 | Higley | NY | St Lawrence | 2N | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 0.8 | 1.6 | 1.6 | 0.3 | N |  |  | OP | X | 9 | 2003 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage2003 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2576 | Higley | NY | St Lawrence | 3N | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 0.8 | 1.6 | 1.6 | 0.3 | N |  |  | OP | X | 9 | 2003 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage2003 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2576 | Higley | NY | St Lawrence | 4N | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 0.8 | 1.6 | 1.6 | 0.3 | N |  |  | OP | X | 9 | 2003 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1942 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2578 | Hydraulic Race | NY | Niagara | 1 | Conventional Hydroelectric | HY |  | S | X | X | 23848 | 23848 | 3 | 0.8 | 2.8 | 2.4 | 1.8 | N |  |  | OP | X | 1 | 1942 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1912 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2579 | Inghams | NY | Fulton | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24050 | 24050 | 3 | 0.8 | 2.8 | 2.9 | 1 | N |  |  | OP | X | 1 | 1912 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1912 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2579 | Inghams | NY | Fulton | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24050 | 24050 | 3 | 0.8 | 3.4 | 3.4 | 1 | N |  |  | OP | X | 1 | 1912 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1909 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2580 | Johnsonville Dam | NY | Rensselaer | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24059 | 24059 | 2 | 0.8 | 1.1 | 1.1 | 0.3 | N |  |  | OP | X | 1 | 1909 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1909 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2580 | Johnsonville Dam | NY | Rensselaer | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24059 | 24059 | 2 | 0.8 | 1.4 | 1.2 | 0.3 | N |  |  | OP | X | 1 | 1909 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1921 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2581 | Kamargo | NY | Jefferson | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24047 | 24047 | 2 | 0.8 | 1.3 | 1.7 | 1 | N |  |  | OP | X | 1 | 1921 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1921 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2581 | Kamargo | NY | Jefferson | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24047 | 24047 | 2 | 0.8 | 1.3 | 1.7 | 1 | N |  |  | OP | X | 1 | 1921 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1921 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2581 | Kamargo | NY | Jefferson | 3 | Conventional Hydroelectric | HY |  | S | X | X | 24047 | 24047 | 2 | 0.8 | 1.3 | 1.7 | 1 | N |  |  | OP | X | 1 | 1921 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1930 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2582 | Lighthouse Hill | NY | Oswego | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24043 | 24043 | 4 | 0.8 | 4 | 4 | 0.5 | N |  |  | OP | X | 1 | 1930 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1930 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2582 | Lighthouse Hill | NY | Oswego | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24043 | 24043 | 4 | 0.8 | 3.6 | 4 | 0.5 | N |  |  | OP | X | 1 | 1930 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1940 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2583 | Macomb | NY | Franklin | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24042 | 24042 | 1 | 0.8 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 1 | 1940 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1915 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2586 | Minetto | NY | Oswego | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24041 | 24041 | 2 | 0.8 | 1.4 | 1.4 | 1.2 | N |  |  | OP | X | 1 | 1915 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1915 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2586 | Minetto | NY | Oswego | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24041 | 24041 | 2 | 0.8 | 1.4 | 1.4 | 1.2 | N |  |  | OP | X | 1 | 1915 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1915 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2586 | Minetto | NY | Oswego | 3 | Conventional Hydroelectric | HY |  | S | X | X | 24041 | 24041 | 2 | 0.8 | 1.4 | 1.4 | 1.2 | N |  |  | OP | X | 1 | 1915 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1915 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2586 | Minetto | NY | Oswego | 4 | Conventional Hydroelectric | HY |  | S | X | X | 24041 | 24041 | 2 | 0.8 | 1.4 | 1.4 | 1.2 | N |  |  | OP | X | 1 | 1915 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1915 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2586 | Minetto | NY | Oswego | 5 | Conventional Hydroelectric | HY |  | S | X | X | 24041 | 24041 | 2 | 0.8 | 1.4 | 1.4 | 1.2 | N |  |  | OP | X | 1 | 1915 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1929 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2588 | Moshier | NY | Herkimer | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24048 | 24048 | 4 | 0.8 | 4 | 4 | 2.5 | N |  |  | OP | X | 1 | 1929 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1929 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2588 | Moshier | NY | Herkimer | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24048 | 24048 | 4 | 0.8 | 4 | 4 | 2.5 | N |  |  | OP | X | 1 | 1929 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1969 | nuclear | TRUE | 55951 | Exelon Nuclear | 2589 | Nine Mile Point Nuclear Station | NY | Oswego | 1 | Nuclear | ST |  | S | X | X |  |  | 641.8 | 0.85 | 621.9 | 624.2 | 105 | N |  |  | OP | X | 12 | 1969 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  | N |  |  | OVER | [23 empty] | N
Vintage1987 | nuclear | TRUE | 55951 | Exelon Nuclear | 2589 | Nine Mile Point Nuclear Station | NY | Oswego | 2 | Nuclear | ST |  | J | X | X |  |  | 1259.3 | 0.9 | 1285.2 | 1297.3 | 75 | N |  |  | OP | X | 7 | 1987 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  | N |  |  | OVER | [23 empty] | N
Vintage1928 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2590 | Norfolk | NY | St Lawrence | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24057 | 24057 | 5 | 0.8 | 5.1 | 5 | 1 | N |  |  | OP | X | 1 | 1928 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1928 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2591 | Norwood | NY | St Lawrence | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24057 | 24057 | 2 | 0.8 | 2.2 | 2.1 | 0.3 | N |  |  | OP | X | 1 | 1928 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1975 | petroleum | TRUE | 64701 | Oswego Harbor Power | 2594 | Oswego Harbor Power | NY | Oswego | ST5 | Petroleum Liquids | ST |  | W | X | X |  |  | 901.8 | 0.925 | 811.7 | 822 | 150 | N |  |  | OP | X | 6 | 1975 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: RFO; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1979 | petroleum | TRUE | 64701 | Oswego Harbor Power | 2594 | Oswego Harbor Power | NY | Oswego | ST6 | Petroleum Liquids | ST |  | W | X | X |  |  | 901.8 | 0.925 | 819.5 | 817.7 | 150 | N |  |  | OP | X | 12 | 1979 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: RFO; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N | N |  | OVER | [23 empty] | Y | Y | Y
Vintage1914 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2595 | Oswego Falls East | NY | Oswego | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24041 | 24041 | 2 | 0.8 | 1.4 | 1.5 | 1 | N |  |  | OP | X | 1 | 1914 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1914 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2595 | Oswego Falls East | NY | Oswego | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24041 | 24041 | 2 | 0.8 | 1.4 | 1.5 | 1 | N |  |  | OP | X | 1 | 1914 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1914 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2595 | Oswego Falls East | NY | Oswego | 3 | Conventional Hydroelectric | HY |  | S | X | X | 24041 | 24041 | 2 | 0.8 | 1.4 | 1.5 | 1 | N |  |  | OP | X | 1 | 1914 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1914 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2596 | Oswego Falls West | NY | Oswego | 4 | Conventional Hydroelectric | HY |  | S | X | X | 24041 | 24041 | 1 | 0.8 | 0.9 | 0.9 | 0.7 | N |  |  | OP | X | 1 | 1914 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1914 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2596 | Oswego Falls West | NY | Oswego | 5 | Conventional Hydroelectric | HY |  | S | X | X | 24041 | 24041 | 1 | 0.8 | 0.9 | 0.9 | 0.7 | N |  |  | OP | X | 1 | 1914 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage2008 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2596 | Oswego Falls West | NY | Oswego | 6 | Conventional Hydroelectric | HY |  | S | X | X | 24041 | 24041 | 0.5 | 0.9 | 0.4 | 0.4 | 0.4 | N |  |  | OP | X | 10 | 2008 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage2008 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2596 | Oswego Falls West | NY | Oswego | 7 | Conventional Hydroelectric | HY |  | S | X | X | 24041 | 24041 | 0.5 | 0.9 | 0.4 | 0.4 | 0.4 | N |  |  | OP | X | 10 | 2008 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1925 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2597 | Parishville | NY | St Lawrence | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24042 | 24042 | 3 | 0.8 | 2.3 | 2.4 | 0.8 | N |  |  | OP | X | 1 | 1925 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1957 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2598 | Piercefield | NY | St Lawrence | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24042 | 24042 | 1.5 | 0.8 | 1.6 | 1.6 | 1 | N |  |  | OP | X | 1 | 1957 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1924 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2598 | Piercefield | NY | St Lawrence | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24042 | 24042 | 0.6 | 0.8 | 0.6 | 0.6 | 0.4 | N |  |  | OP | X | 1 | 1924 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1924 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2598 | Piercefield | NY | St Lawrence | 3 | Conventional Hydroelectric | HY |  | S | X | X | 24042 | 24042 | 0.6 | 0.8 | 0.6 | 0.6 | 0.4 | N |  |  | OP | X | 1 | 1924 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1959 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2599 | Prospect | NY | Oneida | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24049 | 24049 | 19 | 0.8 | 18.3 | 18.1 | 4 | N |  |  | OP | X | 1 | 1959 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1956 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2600 | Rainbow Falls Hydro | NY | St Lawrence | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24056 | 24056 | 25 | 0.8 | 24 | 23.8 | 1 | N |  |  | OP | X | 1 | 1956 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1928 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2601 | Raymondville | NY | St Lawrence | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24057 | 24057 | 2 | 0.8 | 2.3 | 2.1 | 0.2 | N |  |  | OP | X | 1 | 1928 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1912 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2604 | South Edwards | NY | St Lawrence | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24044 | 24044 | 1 | 0.8 | 1.2 | 1.1 | 0.9 | N |  |  | OP | X | 1 | 1912 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1912 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2604 | South Edwards | NY | St Lawrence | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24044 | 24044 | 1 | 0.8 | 1.2 | 1.1 | 0.9 | N |  |  | OP | X | 1 | 1912 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1921 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2604 | South Edwards | NY | St Lawrence | 3 | Conventional Hydroelectric | HY |  | S | X | X | 24044 | 24044 | 1 | 0.8 | 0.8 | 0.7 | 0.6 | N |  |  | OP | X | 1 | 1921 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1994 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2604 | South Edwards | NY | St Lawrence | 4 | Conventional Hydroelectric | HY |  | S | X | X | 24044 | 24044 | 1 | 0.8 | 0.2 | 0.2 | 0.2 | N |  |  | OP | X | 1 | 1994 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1915 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2605 | School Street | NY | Albany | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24059 | 24059 | 7.2 | 0.8 | 7.5 | 7.1 | 1 | N |  |  | OP | X | 1 | 1915 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1915 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2605 | School Street | NY | Albany | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24059 | 24059 | 7.2 | 0.8 | 5.9 | 6.3 | 1 | N |  |  | OP | X | 1 | 1915 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1915 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2605 | School Street | NY | Albany | 3 | Conventional Hydroelectric | HY |  | S | X | X | 24059 | 24059 | 7.2 | 0.8 | 6.1 | 6.4 | 1 | N |  |  | OP | X | 1 | 1915 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1922 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2605 | School Street | NY | Albany | 4 | Conventional Hydroelectric | HY |  | S | X | X | 24059 | 24059 | 7.2 | 0.8 | 6.6 | 6.6 | 1 | N |  |  | OP | X | 1 | 1922 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1924 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2605 | School Street | NY | Albany | 5 | Conventional Hydroelectric | HY |  | S | X | X | 24059 | 24059 | 10 | 0.8 | 10.8 | 9.7 | 1 | N |  |  | OP | X | 1 | 1924 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1908 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2606 | Schaghticoke | NY | Rensselaer | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24059 | 24059 | 4 | 0.8 | 4 | 4.3 | 1.5 | N |  |  | OP | X | 1 | 1908 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1908 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2606 | Schaghticoke | NY | Rensselaer | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24059 | 24059 | 4 | 0.8 | 4.1 | 4.1 | 1.5 | N |  |  | OP | X | 1 | 1908 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1908 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2606 | Schaghticoke | NY | Rensselaer | 3 | Conventional Hydroelectric | HY |  | S | X | X | 24059 | 24059 | 4 | 0.8 | 3.8 | 3.9 | 1.5 | N |  |  | OP | X | 1 | 1908 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1908 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2606 | Schaghticoke | NY | Rensselaer | 4 | Conventional Hydroelectric | HY |  | S | X | X | 24059 | 24059 | 4 | 0.8 | 4 | 3.9 | 1.5 | N |  |  | OP | X | 1 | 1908 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1919 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2607 | Schuylerville | NY | Saratoga | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24059 | 24059 | 2 | 0.8 | 1.5 | 1.6 | 0.1 | N |  |  | OP | X | 1 | 1919 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1925 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2608 | Sewalls | NY | Jefferson | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24047 | 24047 | 1 | 0.8 | 1.1 | 1.1 | 0.7 | N |  |  | OP | X | 1 | 1925 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1925 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2608 | Sewalls | NY | Jefferson | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24047 | 24047 | 1 | 0.8 | 1.1 | 1.1 | 0.7 | N |  |  | OP | X | 1 | 1925 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage2009 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2609 | Sherman Island | NY | Saratoga | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24058 | 24058 | 7 | 0.8 | 6.7 | 6.7 | 1 | N |  |  | OP | X | 4 | 2009 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1923 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2609 | Sherman Island | NY | Saratoga | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24058 | 24058 | 7 | 0.8 | 7 | 8.1 | 1 | N |  |  | OP | X | 1 | 1923 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1923 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2609 | Sherman Island | NY | Saratoga | 3 | Conventional Hydroelectric | HY |  | S | X | X | 24058 | 24058 | 7 | 0.8 | 7 | 8.3 | 1 | N |  |  | OP | X | 1 | 1923 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1923 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2609 | Sherman Island | NY | Saratoga | 4 | Conventional Hydroelectric | HY |  | S | X | X | 24058 | 24058 | 7 | 0.8 | 7.2 | 7.4 | 1 | N |  |  | OP | X | 1 | 1923 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1923 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2609 | Sherman Island | NY | Saratoga | 5 | Conventional Hydroelectric | HY |  | S | X | X | 24058 | 24058 | 7 | 0.8 | 7.7 | 8.2 | 1 | N |  |  | OP | X | 1 | 1923 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage2009 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2609 | Sherman Island | NY | Saratoga | 6 | Conventional Hydroelectric | HY |  | S | X | X | 24058 | 24058 | 1.3 | 0.8 | 1.3 | 1.3 | 0.2 | N |  |  | OP | X | 2 | 2009 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1925 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2610 | Soft Maple | NY | Lewis | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24048 | 24048 | 8 | 0.8 | 7.2 | 8.1 | 4 | N |  |  | OP | X | 1 | 1925 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1925 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2610 | Soft Maple | NY | Lewis | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24048 | 24048 | 8 | 0.8 | 7.2 | 8.1 | 4 | N |  |  | OP | X | 1 | 1925 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1954 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2611 | South Colton | NY | St Lawrence | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24056 | 24056 | 21 | 0.8 | 19.8 | 20 | 1 | N |  |  | OP | X | 1 | 1954 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1924 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2612 | Spier Falls | NY | Saratoga | 8 | Conventional Hydroelectric | HY |  | S | X | X | 24058 | 24058 | 9 | 0.8 | 8.5 | 8.6 | 4 | N |  |  | OP | X | 1 | 1924 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1930 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2612 | Spier Falls | NY | Saratoga | 9 | Conventional Hydroelectric | HY |  | S | X | X | 24058 | 24058 | 47 | 0.8 | 46 | 46.3 | 8 | N |  |  | OP | X | 1 | 1930 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1957 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2613 | Stark | NY | St Lawrence | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24056 | 24056 | 26 | 0.8 | 23.3 | 24.5 | 1 | N |  |  | OP | X | 1 | 1957 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1952 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2614 | Stewarts Bridge | NY | Saratoga | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24058 | 24058 | 36 | 0.8 | 37.5 | 37.5 | 15 | N |  |  | OP | X | 1 | 1952 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage2013 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2614 | Stewarts Bridge | NY | Saratoga | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24058 | 24058 | 2.5 | 0.8 | 2.5 | 2.5 | 0.2 | N |  |  | OP | X | 6 | 2013 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1924 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2616 | Sugar Island | NY | St Lawrence | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24057 | 24057 | 2 | 0.8 | 2.1 | 2.1 | 0.2 | N |  |  | OP | X | 1 | 1924 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1924 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2616 | Sugar Island | NY | St Lawrence | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24057 | 24057 | 2 | 0.8 | 2 | 2 | 0.2 | N |  |  | OP | X | 1 | 1924 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1913 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2617 | Taylorville | NY | Lewis | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24048 | 24048 | 1 | 0.8 | 1.1 | 1.1 | 0.9 | N |  |  | OP | X | 1 | 1913 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1913 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2617 | Taylorville | NY | Lewis | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24048 | 24048 | 1 | 0.8 | 0.9 | 0.9 | 0.9 | N |  |  | OP | X | 1 | 1913 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1913 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2617 | Taylorville | NY | Lewis | 3 | Conventional Hydroelectric | HY |  | S | X | X | 24048 | 24048 | 1 | 0.8 | 1.1 | 1.1 | 0.9 | N |  |  | OP | X | 1 | 1913 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1927 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2617 | Taylorville | NY | Lewis | 4 | Conventional Hydroelectric | HY |  | S | X | X | 24048 | 24048 | 1 | 0.8 | 1.3 | 1.3 | 1.1 | N |  |  | OP | X | 1 | 1927 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1919 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2619 | Trenton Falls | NY | Oneida | 5 | Conventional Hydroelectric | HY |  | S | X | X | 24049 | 24049 | 6.8 | 0.8 | 8.1 | 6.8 | 2 | N |  |  | OP | X | 1 | 1919 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1919 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2619 | Trenton Falls | NY | Oneida | 6 | Conventional Hydroelectric | HY |  | S | X | X | 24049 | 24049 | 6.4 | 0.8 | 8.1 | 6.4 | 2 | N |  |  | OP | X | 1 | 1919 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1919 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2619 | Trenton Falls | NY | Oneida | 7 | Conventional Hydroelectric | HY |  | S | X | X | 24049 | 24049 | 8.7 | 0.8 | 9.7 | 8.7 | 2 | N |  |  | OP | X | 1 | 1919 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1926 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2621 | Varick | NY | Oswego | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24041 | 24041 | 2 | 0.8 | 1.4 | 1.4 | 0.9 | N |  |  | OP | X | 1 | 1926 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1926 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2621 | Varick | NY | Oswego | 3 | Conventional Hydroelectric | HY |  | S | X | X | 24041 | 24041 | 2 | 0.8 | 1.4 | 1.4 | 0.9 | N |  |  | OP | X | 1 | 1926 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1926 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2621 | Varick | NY | Oswego | 4 | Conventional Hydroelectric | HY |  | S | X | X | 24041 | 24041 | 2 | 0.8 | 1.4 | 1.4 | 0.9 | N |  |  | OP | X | 1 | 1926 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1926 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2621 | Varick | NY | Oswego | 5 | Conventional Hydroelectric | HY |  | S | X | X | 24041 | 24041 | 2 | 0.8 | 1.4 | 1.4 | 0.9 | N |  |  | OP | X | 1 | 1926 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1921 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2623 | Waterport | NY | Orleans | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24046 | 24046 | 2 | 0.8 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 1 | 1921 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1921 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2623 | Waterport | NY | Orleans | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24046 | 24046 | 2 | 0.8 | 2 | 2 | 1.1 | N |  |  | OP | X | 1 | 1921 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1940 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2624 | Yaleville | NY | St Lawrence | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24057 | 24057 | 1 | 0.8 | 0.4 | 0.4 | 0.3 | N |  |  | OP | X | 1 | 1940 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1940 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 2624 | Yaleville | NY | St Lawrence | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24057 | 24057 | 1 | 0.8 | 0.2 | 0.1 | 0.1 | N |  |  | OP | X | 1 | 1940 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1972 | natural gas steam turbine | TRUE | 64082 | GenOn Bowline, LLC | 2625 | Bowline Point | NY | Rockland | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | 23526 | 23526 | 621 | 0.9 | 586 | 593.2 | 80 | N |  |  | OP | X | 9 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: RFO; DFO DFO DFO: NG |  |  | N | N |  | OVER | [23 empty] | Y | Y | Y
Vintage1974 | natural gas steam turbine | TRUE | 64082 | GenOn Bowline, LLC | 2625 | Bowline Point | NY | Rockland | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | 23595 | 23595 | 621 | 0.9 | 573.6 | 568.8 | 100 | N |  |  | OP | X | 5 | 1974 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: RFO; DFO DFO DFO: NG |  |  | N | N |  | OVER | [23 empty] | Y | Y | Y
Vintage1956 | hydro | TRUE | 15296 | New York Power Authority | 2627 | Grahamsville | NY | Sullivan | GRHM | Conventional Hydroelectric | HY |  | W | X | X |  |  | 18 | 1 | 18 | 18 | 1 | N |  |  | OP | X | 1 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1972 | natural gas peaker | TRUE | 56142 | Alliance NYGT, LLC | 2628 | Hillburn | NY | Rockland | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | Nyiso | Nyiso | 46.5 | 0.9 | 33.1 | 43.8 | 5 | N |  |  | OP | X | 7 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1923 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 2630 | Mongaup Falls | NY | Sullivan | GEN1 | Conventional Hydroelectric | HY |  | W | X | X | 23641 |  | 4 | 0.8 | 4.3 | 4.3 | 0.4 | N |  |  | OP | X | 7 | 1923 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1923 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 2630 | Mongaup Falls | NY | Sullivan | GEN2 | Conventional Hydroelectric | HY |  | W | X | X | 23641 |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.4 | N |  |  | OP | X | 7 | 1923 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1923 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 2630 | Mongaup Falls | NY | Sullivan | GEN3 | Conventional Hydroelectric | HY |  | W | X | X | 23641 |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.4 | N |  |  | OP | X | 7 | 1923 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1923 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 2630 | Mongaup Falls | NY | Sullivan | GEN4 | Conventional Hydroelectric | HY |  | W | X | X | 23641 |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.4 | N |  |  | OP | X | 7 | 1923 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1927 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 2631 | Rio | NY | Sullivan | RIO | Conventional Hydroelectric | HY |  | W | X | X | 23641 |  | 10 | 0.8 | 10.1 | 10.1 | 4 | N |  |  | OP | X | 12 | 1927 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage2013 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 2631 | Rio | NY | Sullivan | RIO2 | Conventional Hydroelectric | HY |  | W | X | X | 23641 |  | 0.8 | 0.9 | 0.8 | 0.8 | 0.4 | N |  |  | OP | X | 12 | 2013 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1972 | natural gas peaker | TRUE | 56142 | Alliance NYGT, LLC | 2632 | Shoemaker | NY | Orange | SHOE | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | NYISO | NYISO | 41.9 | 0.9 | 33 | 40 | 5 | N |  |  | OP | X | 7 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1939 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 2634 | Swinging Bridge 2 | NY | Sullivan | SWI2 | Conventional Hydroelectric | HY |  | W | X | X | 23641 |  | 6.8 | 0.9 | 7.4 | 7.4 | 5 | N |  |  | OP | X | 8 | 1939 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage2019 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 2634 | Swinging Bridge 2 | NY | Sullivan | SWI3 | Conventional Hydroelectric | HY |  | W | X | X | 23641 |  | 1.2 | 0.9 | 1.2 | 1.2 | 0.4 | N |  |  | OP | X | 12 | 2019 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1952 | hydro | TRUE | 16183 | Rochester Gas & Electric Corp | 2638 | Rochester 26 | NY | Monroe | 1 | Conventional Hydroelectric | HY |  | S | X | X | 23604 | 23604 | 3 | 0.8 | 3 | 3 | 0 | N |  |  | OA | X | 8 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1960 | hydro | TRUE | 16183 | Rochester Gas & Electric Corp | 2639 | Rochester 2 | NY | Monroe | 1 | Conventional Hydroelectric | HY |  | S | X | X | 23604 | 23604 | 8.5 | 0.9 | 8.5 | 8.5 | 0 | N |  |  | OS | X | 8 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1918 | hydro | TRUE | 16183 | Rochester Gas & Electric Corp | 2641 | Rochester 5 | NY | Monroe | 2 | Conventional Hydroelectric | HY |  | S | X | X | 23604 | 23604 | 12.8 | 0.9 | 12.9 | 12.9 | 0 | N |  |  | OA | X | 7 | 1918 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1918 | hydro | TRUE | 16183 | Rochester Gas & Electric Corp | 2641 | Rochester 5 | NY | Monroe | HY1 | Conventional Hydroelectric | HY |  | S | X | X | 23604 | 23604 | 12.8 | 0.9 | 12.9 | 12.9 | 0 | N |  |  | OA | X | 7 | 1918 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1927 | hydro | TRUE | 16183 | Rochester Gas & Electric Corp | 2641 | Rochester 5 | NY | Monroe | HY3 | Conventional Hydroelectric | HY |  | S | X | X | 23604 | 23604 | 18 | 0.8 | 18 | 18 | 0 | N |  |  | OS | X | 7 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1922 | hydro | TRUE | 16183 | Rochester Gas & Electric Corp | 2646 | Wiscoy 170 | NY | Allegany | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0 | N |  |  | OS | X | 7 | 1922 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 1H | [23 empty] | N
Vintage1922 | hydro | TRUE | 16183 | Rochester Gas & Electric Corp | 2646 | Wiscoy 170 | NY | Allegany | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0 | N |  |  | OS | X | 7 | 1922 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 1H | [23 empty] | N
Vintage1949 | petroleum | TRUE | 6775 | Village of Freeport - (NY) | 2678 | Plant No 1 Freeport | NY | Nassau | 2 | Petroleum Liquids | IC |  | S | X | X | 1660 | 1660 | 2.9 | 0.8 | 2.2 | 2.2 | 2.2 | N |  |  | OP | X | 1 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1954 | petroleum | TRUE | 6775 | Village of Freeport - (NY) | 2678 | Plant No 1 Freeport | NY | Nassau | 3 | Petroleum Liquids | IC |  | S | X | X | 1660 | 1660 | 3.1 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 1 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1973 | petroleum | TRUE | 6775 | Village of Freeport - (NY) | 2679 | Plant No 2 Freeport | NY | Nassau | 3 | Petroleum Liquids | GT |  | S | X | X | 1660 | 1660 | 18.1 | 0.9 | 16.8 | 18 | 5 | N |  |  | OP | X | 5 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: KER |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2004 | natural gas peaker | TRUE | 6775 | Village of Freeport - (NY) | 2679 | Plant No 2 Freeport | NY | Nassau | CT5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 23818 | 23818 | 60.5 | 1 | 49 | 49 | 25 | N |  |  | OP | X | 4 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1997 | petroleum | TRUE | 7630 | Village of Greenport - (NY) | 2681 | Greenport | NY | Suffolk | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.7 | 0.8 | 1.5 | 1.6 |  | N |  |  | OS | X | 8 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N | [25 empty] | N | N | N
Vintage1957 | petroleum | TRUE | 7630 | Village of Greenport - (NY) | 2681 | Greenport | NY | Suffolk | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 0.3 | N |  |  | OP | X | 6 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1965 | petroleum | TRUE | 7630 | Village of Greenport - (NY) | 2681 | Greenport | NY | Suffolk | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.6 | 1.6 | 0.3 | N |  |  | OP | X | 6 | 1965 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1971 | petroleum | TRUE | 7630 | Village of Greenport - (NY) | 2681 | Greenport | NY | Suffolk | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.8 | 0.8 | 2.6 | 2.6 | 0.4 | N |  |  | OP | X | 6 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1997 | petroleum | TRUE | 7630 | Village of Greenport - (NY) | 2681 | Greenport | NY | Suffolk | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 |  | N |  |  | OS | X | 8 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N | [25 empty] | N | N
Vintage1951 | natural gas steam turbine | TRUE | 9645 | Jamestown Board of Public Util | 2682 | S A Carlson | NY | Chautauqua | 5 | Natural Gas Steam Turbine | ST | 1 | S | X | X |  |  | 24.5 | 0.9 | 22.5 | 22.5 | 5 | N |  |  | OP | X | 8 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | 12H |  | N |  |  | N | [18 empty] | Y | N | Y
Vintage1968 | natural gas steam turbine | TRUE | 9645 | Jamestown Board of Public Util | 2682 | S A Carlson | NY | Chautauqua | 6 | Natural Gas Steam Turbine | ST | 1 | S | X | X |  |  | 24.5 | 0.9 | 22.5 | 22.5 | 5 | N |  |  | OP | X | 8 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | 12H |  | N |  |  | N | [18 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 9645 | Jamestown Board of Public Util | 2682 | S A Carlson | NY | Chautauqua | 7 | Natural Gas Fired Combustion Turbine | GT | 1 | S | X | X |  |  | 47.3 | 0.9 | 42 | 47 | 9 | N |  |  | OP | X | 11 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N |  | N | bar: X X X to DFO RC RC
Vintage1924 | hydro | TRUE | 15296 | New York Power Authority | 2685 | Crescent | NY | Albany | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.8 | 1 | 2.8 | 2.8 | 1 | N |  |  | OP | X | 7 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1924 | hydro | TRUE | 15296 | New York Power Authority | 2685 | Crescent | NY | Albany | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.8 | 1 | 2.8 | 2.8 | 1 | N |  |  | OP | X | 7 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1991 | hydro | TRUE | 15296 | New York Power Authority | 2685 | Crescent | NY | Albany | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 1 | 3 | 3 | 1 | N |  |  | OP | X | 7 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1991 | hydro | TRUE | 15296 | New York Power Authority | 2685 | Crescent | NY | Albany | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 1 | 3 | 3 | 1 | N |  |  | OP | X | 7 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1924 | hydro | TRUE | 15296 | New York Power Authority | 2686 | Vischer Ferry | NY | Saratoga | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.8 | 1 | 2.8 | 2.9 | 1 | N |  |  | OP | X | 7 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1924 | hydro | TRUE | 15296 | New York Power Authority | 2686 | Vischer Ferry | NY | Saratoga | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.8 | 1 | 2.8 | 2.9 | 1 | N |  |  | OP | X | 7 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1991 | hydro | TRUE | 15296 | New York Power Authority | 2686 | Vischer Ferry | NY | Saratoga | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 1 | 3 | 2.9 | 1 | N |  |  | OP | X | 7 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1991 | hydro | TRUE | 15296 | New York Power Authority | 2686 | Vischer Ferry | NY | Saratoga | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 1 | 3 | 2.9 | 1 | N |  |  | OP | X | 7 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1973 | other | TRUE | 15296 | New York Power Authority | 2691 | Blenheim Gilboa | NY | Schoharie | 1 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 250 | 1 | 291.8 | 290.7 | 1 | N |  |  | OP | X | 7 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1973 | other | TRUE | 15296 | New York Power Authority | 2691 | Blenheim Gilboa | NY | Schoharie | 2 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 250 | 1 | 291.3 | 292.7 | 1 | N |  |  | OP | X | 7 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1973 | other | TRUE | 15296 | New York Power Authority | 2691 | Blenheim Gilboa | NY | Schoharie | 3 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 250 | 1 | 291.9 | 290.8 | 1 | N |  |  | OP | X | 7 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1973 | other | TRUE | 15296 | New York Power Authority | 2691 | Blenheim Gilboa | NY | Schoharie | 4 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 250 | 1 | 291.8 | 292.5 | 1 | N |  |  | OP | X | 7 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1961 | other | TRUE | 15296 | New York Power Authority | 2692 | Lewiston Niagara | NY | Niagara | 1 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 20 | 1 | 20 | 20 | 1 | N |  |  | OP | X | 10 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1962 | other | TRUE | 15296 | New York Power Authority | 2692 | Lewiston Niagara | NY | Niagara | 10 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 20 | 1 | 20 | 20 | 1 | N |  |  | OP | X | 7 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1962 | other | TRUE | 15296 | New York Power Authority | 2692 | Lewiston Niagara | NY | Niagara | 11 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 20 | 1 | 20 | 20 | 1 | N |  |  | OP | X | 8 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1962 | other | TRUE | 15296 | New York Power Authority | 2692 | Lewiston Niagara | NY | Niagara | 12 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 20 | 1 | 20 | 20 | 1 | N |  |  | OP | X | 10 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1961 | other | TRUE | 15296 | New York Power Authority | 2692 | Lewiston Niagara | NY | Niagara | 2 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 20 | 1 | 20 | 20 | 1 | N |  |  | OP | X | 11 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1961 | other | TRUE | 15296 | New York Power Authority | 2692 | Lewiston Niagara | NY | Niagara | 3 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 20 | 1 | 20 | 20 | 1 | N |  |  | OP | X | 11 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1962 | other | TRUE | 15296 | New York Power Authority | 2692 | Lewiston Niagara | NY | Niagara | 4 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 20 | 1 | 20 | 20 | 1 | N |  |  | OP | X | 1 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1962 | other | TRUE | 15296 | New York Power Authority | 2692 | Lewiston Niagara | NY | Niagara | 5 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 20 | 1 | 20 | 20 | 1 | N |  |  | OP | X | 2 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1962 | other | TRUE | 15296 | New York Power Authority | 2692 | Lewiston Niagara | NY | Niagara | 6 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 20 | 1 | 20 | 20 | 1 | N |  |  | OP | X | 2 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1962 | other | TRUE | 15296 | New York Power Authority | 2692 | Lewiston Niagara | NY | Niagara | 7 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 20 | 1 | 20 | 20 | 1 | N |  |  | OP | X | 4 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1962 | other | TRUE | 15296 | New York Power Authority | 2692 | Lewiston Niagara | NY | Niagara | 8 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 20 | 1 | 20 | 20 | 1 | N |  |  | OP | X | 5 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1962 | other | TRUE | 15296 | New York Power Authority | 2692 | Lewiston Niagara | NY | Niagara | 9 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 20 | 1 | 20 | 20 | 1 | N |  |  | OP | X | 6 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1961 | hydro | TRUE | 15296 | New York Power Authority | 2693 | Robert Moses Niagara | NY | Niagara | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 193.5 | 1 | 187.3 | 187.3 | 1 | N |  |  | OP | X | 1 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1961 | hydro | TRUE | 15296 | New York Power Authority | 2693 | Robert Moses Niagara | NY | Niagara | 10 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 193.5 | 1 | 187.3 | 187.3 | 1 | N |  |  | OP | X | 12 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1962 | hydro | TRUE | 15296 | New York Power Authority | 2693 | Robert Moses Niagara | NY | Niagara | 11 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 193.5 | 1 | 187.3 | 187.3 | 1 | N |  |  | OP | X | 2 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1962 | hydro | TRUE | 15296 | New York Power Authority | 2693 | Robert Moses Niagara | NY | Niagara | 12 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 193.5 | 1 | 187.3 | 187.3 | 1 | N |  |  | OP | X | 3 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1962 | hydro | TRUE | 15296 | New York Power Authority | 2693 | Robert Moses Niagara | NY | Niagara | 13 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 193.5 | 1 | 187.3 | 187.3 | 1 | N |  |  | OP | X | 5 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1962 | hydro | TRUE | 15296 | New York Power Authority | 2693 | Robert Moses Niagara | NY | Niagara | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 193.5 | 1 | 187.3 | 187.3 | 1 | N |  |  | OP | X | 2 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1961 | hydro | TRUE | 15296 | New York Power Authority | 2693 | Robert Moses Niagara | NY | Niagara | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 193.5 | 1 | 187.3 | 187.3 | 1 | N |  |  | OP | X | 3 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1961 | hydro | TRUE | 15296 | New York Power Authority | 2693 | Robert Moses Niagara | NY | Niagara | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 193.5 | 1 | 187.3 | 187.3 | 1 | N |  |  | OP | X | 4 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1961 | hydro | TRUE | 15296 | New York Power Authority | 2693 | Robert Moses Niagara | NY | Niagara | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 193.5 | 1 | 187.3 | 187.3 | 1 | N |  |  | OP | X | 6 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1961 | hydro | TRUE | 15296 | New York Power Authority | 2693 | Robert Moses Niagara | NY | Niagara | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 193.5 | 1 | 187.3 | 187.3 | 1 | N |  |  | OP | X | 7 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1961 | hydro | TRUE | 15296 | New York Power Authority | 2693 | Robert Moses Niagara | NY | Niagara | 7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 193.5 | 1 | 187.3 | 187.3 | 1 | N |  |  | OP | X | 8 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1961 | hydro | TRUE | 15296 | New York Power Authority | 2693 | Robert Moses Niagara | NY | Niagara | 8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 150.3 | 1 | 187.3 | 187.3 | 1 | N |  |  | OP | X | 9 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1961 | hydro | TRUE | 15296 | New York Power Authority | 2693 | Robert Moses Niagara | NY | Niagara | 9 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 150.3 | 1 | 187.3 | 187.3 | 1 | N |  |  | OP | X | 11 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1959 | hydro | TRUE | 15296 | New York Power Authority | 2694 | Robert Moses Power Dam | NY | St Lawrence | 17 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 57 | 1 | 53.5 | 50.6 | 1 | N |  |  | OP | X | 7 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1959 | hydro | TRUE | 15296 | New York Power Authority | 2694 | Robert Moses Power Dam | NY | St Lawrence | 18 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 57 | 1 | 53.5 | 50.6 | 1 | N |  |  | OP | X | 7 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1959 | hydro | TRUE | 15296 | New York Power Authority | 2694 | Robert Moses Power Dam | NY | St Lawrence | 19 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 57 | 1 | 53.5 | 50.6 | 1 | N |  |  | OP | X | 6 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1959 | hydro | TRUE | 15296 | New York Power Authority | 2694 | Robert Moses Power Dam | NY | St Lawrence | 20 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 57 | 1 | 53.5 | 50.6 | 1 | N |  |  | OP | X | 5 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1959 | hydro | TRUE | 15296 | New York Power Authority | 2694 | Robert Moses Power Dam | NY | St Lawrence | 21 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 57 | 1 | 53.5 | 50.6 | 1 | N |  |  | OP | X | 5 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1959 | hydro | TRUE | 15296 | New York Power Authority | 2694 | Robert Moses Power Dam | NY | St Lawrence | 22 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 57 | 1 | 53.5 | 50.6 | 1 | N |  |  | OP | X | 3 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1959 | hydro | TRUE | 15296 | New York Power Authority | 2694 | Robert Moses Power Dam | NY | St Lawrence | 23 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 57 | 1 | 53.5 | 50.6 | 1 | N |  |  | OP | X | 1 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1958 | hydro | TRUE | 15296 | New York Power Authority | 2694 | Robert Moses Power Dam | NY | St Lawrence | 24 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 57 | 1 | 53.5 | 50.6 | 1 | N |  |  | OP | X | 12 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1958 | hydro | TRUE | 15296 | New York Power Authority | 2694 | Robert Moses Power Dam | NY | St Lawrence | 25 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 57 | 1 | 53.5 | 50.6 | 1 | N |  |  | OP | X | 11 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1958 | hydro | TRUE | 15296 | New York Power Authority | 2694 | Robert Moses Power Dam | NY | St Lawrence | 26 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 57 | 1 | 53.5 | 50.6 | 1 | N |  |  | OP | X | 10 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1958 | hydro | TRUE | 15296 | New York Power Authority | 2694 | Robert Moses Power Dam | NY | St Lawrence | 27 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 57 | 1 | 53.5 | 50.6 | 1 | N |  |  | OP | X | 8 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1958 | hydro | TRUE | 15296 | New York Power Authority | 2694 | Robert Moses Power Dam | NY | St Lawrence | 28 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 57 | 1 | 53.5 | 50.6 | 1 | N |  |  | OP | X | 8 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1958 | hydro | TRUE | 15296 | New York Power Authority | 2694 | Robert Moses Power Dam | NY | St Lawrence | 29 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 57 | 1 | 53.5 | 50.6 | 1 | N |  |  | OP | X | 7 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1958 | hydro | TRUE | 15296 | New York Power Authority | 2694 | Robert Moses Power Dam | NY | St Lawrence | 30 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 57 | 1 | 53.5 | 50.6 | 1 | N |  |  | OP | X | 7 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1958 | hydro | TRUE | 15296 | New York Power Authority | 2694 | Robert Moses Power Dam | NY | St Lawrence | 31 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 57 | 1 | 53.5 | 50.6 | 1 | N |  |  | OP | X | 7 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1958 | hydro | TRUE | 15296 | New York Power Authority | 2694 | Robert Moses Power Dam | NY | St Lawrence | 32 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 57 | 1 | 53.5 | 50.6 | 1 | N |  |  | OP | X | 7 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1954 | petroleum | TRUE | 16217 | Village of Rockville Centre - (NY) | 2695 | Charles P Keller | NY | Nassau | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.5 | 0.8 | 3.2 | 3.2 | 1.6 | N |  |  | OP | X | 1 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1962 | petroleum | TRUE | 16217 | Village of Rockville Centre - (NY) | 2695 | Charles P Keller | NY | Nassau | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 5.2 | 0.8 | 5.2 | 5.2 | 2.6 | N |  |  | OP | X | 1 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1967 | petroleum | TRUE | 16217 | Village of Rockville Centre - (NY) | 2695 | Charles P Keller | NY | Nassau | 12 | Petroleum Liquids | IC |  | S | X | X |  |  | 5.5 | 0.8 | 5.5 | 5.5 | 2.7 | N |  |  | OP | X | 1 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1974 | petroleum | TRUE | 16217 | Village of Rockville Centre - (NY) | 2695 | Charles P Keller | NY | Nassau | 13 | Petroleum Liquids | IC |  | S | X | X |  |  | 5.5 | 0.8 | 5.5 | 5.5 | 2.7 | N |  |  | OP | X | 1 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1994 | petroleum | TRUE | 16217 | Village of Rockville Centre - (NY) | 2695 | Charles P Keller | NY | Nassau | 14 | Petroleum Liquids | IC |  | S | X | X |  |  | 6.2 | 0.85 | 6.2 | 6.2 | 3.1 | N |  |  | OP | X | 9 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1954 | petroleum | TRUE | 16217 | Village of Rockville Centre - (NY) | 2695 | Charles P Keller | NY | Nassau | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.5 | 0.8 | 3.2 | 3.2 | 1.6 | N |  |  | OP | X | 1 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1924 | hydro | TRUE | 20188 | City of Watertown - (NY) | 2700 | Watertown | NY | Jefferson | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.7 | 1 | 2.1 | 2.1 | 0.6 | N |  |  | OP | X | 8 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1924 | hydro | TRUE | 20188 | City of Watertown - (NY) | 2700 | Watertown | NY | Jefferson | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.7 | 1 | 2.1 | 2.1 | 0.6 | N |  |  | OP | X | 8 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1924 | hydro | TRUE | 20188 | City of Watertown - (NY) | 2700 | Watertown | NY | Jefferson | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.7 | 1 | 2.1 | 2.1 | 0.6 | N |  |  | OP | X | 8 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage2019 | natural gas combined cycle | TRUE | 3046 | Duke Energy Progress - (NC) | 2706 | Asheville | NC | Buncombe | CT5 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 191.2 | 0.85 | 153 | 190 | 153 | N |  |  | OP | X | 12 | 2019 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2020 | natural gas combined cycle | TRUE | 3046 | Duke Energy Progress - (NC) | 2706 | Asheville | NC | Buncombe | CT7 | Natural Gas Fired Combined Cycle | CT | CC2 | S | X | Y |  |  | 191.2 | 0.85 | 153 | 190 | 153 | N |  |  | OP | X | 1 | 2020 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1999 | natural gas peaker | TRUE | 3046 | Duke Energy Progress - (NC) | 2706 | Asheville | NC | Buncombe | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 211.7 | 0.85 | 160 | 185 | 70 | N |  |  | OP | X | 6 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2000 | natural gas peaker | TRUE | 3046 | Duke Energy Progress - (NC) | 2706 | Asheville | NC | Buncombe | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 211.8 | 0.85 | 160 | 185 | 70 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2019 | natural gas combined cycle | TRUE | 3046 | Duke Energy Progress - (NC) | 2706 | Asheville | NC | Buncombe | ST6 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X |  |  | 102.8 | 0.85 | 85 | 90 | 85 | N |  |  | OP | X | 12 | 2019 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2020 | natural gas combined cycle | TRUE | 3046 | Duke Energy Progress - (NC) | 2706 | Asheville | NC | Buncombe | ST8 | Natural Gas Fired Combined Cycle | CA | CC2 | S | N | X |  |  | 102.8 | 0.85 | 85 | 90 | 85 | N |  |  | OP | X | 4 | 2020 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO | [5 empty] | 1H | [23 empty] | Y | N | Y
Vintage1912 | hydro | TRUE | 3046 | Duke Energy Progress - (NC) | 2707 | Blewett | NC | Anson | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.2 | 0.8 | 4 | 4 | 3 | N |  |  | OP | X | 6 | 1912 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1912 | hydro | TRUE | 3046 | Duke Energy Progress - (NC) | 2707 | Blewett | NC | Anson | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.2 | 0.8 | 4 | 4 | 3 | N |  |  | OP | X | 6 | 1912 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1912 | hydro | TRUE | 3046 | Duke Energy Progress - (NC) | 2707 | Blewett | NC | Anson | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.2 | 0.8 | 4 | 4 | 3 | N |  |  | OP | X | 6 | 1912 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1912 | hydro | TRUE | 3046 | Duke Energy Progress - (NC) | 2707 | Blewett | NC | Anson | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5 | 0.8 | 5 | 5 | 4 | N |  |  | OP | X | 6 | 1912 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1912 | hydro | TRUE | 3046 | Duke Energy Progress - (NC) | 2707 | Blewett | NC | Anson | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5 | 0.8 | 5 | 5 | 4 | N |  |  | OP | X | 6 | 1912 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1912 | hydro | TRUE | 3046 | Duke Energy Progress - (NC) | 2707 | Blewett | NC | Anson | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5 | 0.8 | 5 | 5 | 4 | N |  |  | OP | X | 6 | 1912 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1971 | petroleum | TRUE | 3046 | Duke Energy Progress - (NC) | 2707 | Blewett | NC | Anson | GT1 | Petroleum Liquids | GT |  | S | X | X |  |  | 17.5 | 0.85 | 13 | 17 | 9 | N |  |  | OP | X | 5 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1971 | petroleum | TRUE | 3046 | Duke Energy Progress - (NC) | 2707 | Blewett | NC | Anson | GT2 | Petroleum Liquids | GT |  | S | X | X |  |  | 17.5 | 0.85 | 13 | 17 | 9 | N |  |  | OP | X | 5 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1971 | petroleum | TRUE | 3046 | Duke Energy Progress - (NC) | 2707 | Blewett | NC | Anson | GT3 | Petroleum Liquids | GT |  | S | X | X |  |  | 17.5 | 0.85 | 13 | 17 | 9 | N |  |  | OP | X | 5 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1971 | petroleum | TRUE | 3046 | Duke Energy Progress - (NC) | 2707 | Blewett | NC | Anson | GT4 | Petroleum Liquids | GT |  | S | X | X |  |  | 17.5 | 0.85 | 13 | 17 | 9 | N |  |  | OP | X | 7 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1985 | hydro | TRUE | 3046 | Duke Energy Progress - (NC) | 2710 | Marshall Dam | NC | Madison | HC1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 1 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 3046 | Duke Energy Progress - (NC) | 2710 | Marshall Dam | NC | Madison | HC2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 1 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1966 | hard coal | TRUE | 3046 | Duke Energy Progress - (NC) | 2712 | Roxboro | NC | Person | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 410.8 | 0.9 | 379 | 380 | 70 | N |  |  | OP | X | 5 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N
Vintage1968 | hard coal | TRUE | 3046 | Duke Energy Progress - (NC) | 2712 | Roxboro | NC | Person | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 657 | 0.9 | 668 | 673 | 150 | N |  |  | OP | X | 5 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N
Vintage1973 | hard coal | TRUE | 3046 | Duke Energy Progress - (NC) | 2712 | Roxboro | NC | Person | 3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 745.2 | 0.9 | 694 | 698 | 68 | N |  |  | OP | X | 7 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N
Vintage1980 | hard coal | TRUE | 3046 | Duke Energy Progress - (NC) | 2712 | Roxboro | NC | Person | 4 | Conventional Steam Coal | ST |  | S | X | X |  |  | 745.2 | 0.9 | 698 | 711 | 125 | N |  |  | OP | X | 9 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N
Vintage1928 | hydro | TRUE | 3046 | Duke Energy Progress - (NC) | 2714 | Tillery | NC | Montgomery | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 22 | 0.8 | 21 | 21 | 21 | N |  |  | OP | X | 8 | 1928 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1928 | hydro | TRUE | 3046 | Duke Energy Progress - (NC) | 2714 | Tillery | NC | Montgomery | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18 | 0.8 | 18 | 18 | 18 | N |  |  | OP | X | 8 | 1928 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1928 | hydro | TRUE | 3046 | Duke Energy Progress - (NC) | 2714 | Tillery | NC | Montgomery | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 22 | 0.8 | 21 | 21 | 21 | N |  |  | OP | X | 8 | 1928 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1960 | hydro | TRUE | 3046 | Duke Energy Progress - (NC) | 2714 | Tillery | NC | Montgomery | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 22 | 0.8 | 25 | 25 | 22 | N |  |  | OP | X | 6 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1930 | hydro | TRUE | 3046 | Duke Energy Progress - (NC) | 2715 | Walters | NC | Haywood | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 36 | 0.8 | 36 | 36 | 36 | N |  |  | OP | X | 7 | 1930 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1930 | hydro | TRUE | 3046 | Duke Energy Progress - (NC) | 2715 | Walters | NC | Haywood | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 36 | 0.8 | 40 | 40 | 36 | N |  |  | OP | X | 7 | 1930 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1930 | hydro | TRUE | 3046 | Duke Energy Progress - (NC) | 2715 | Walters | NC | Haywood | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 36 | 0.8 | 36 | 36 | 36 | N |  |  | OP | X | 11 | 1930 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1970 | petroleum | TRUE | 3046 | Duke Energy Progress - (NC) | 2716 | W H Weatherspoon | NC | Robeson | GT1 | Petroleum Liquids | GT |  | S | X | X |  |  | 39.7 | 0.85 | 31 | 41 | 12 | N |  |  | OP | X | 5 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1970 | petroleum | TRUE | 3046 | Duke Energy Progress - (NC) | 2716 | W H Weatherspoon | NC | Robeson | GT2 | Petroleum Liquids | GT |  | S | X | X |  |  | 39.7 | 0.85 | 31 | 41 | 12 | N |  |  | OP | X | 5 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1971 | petroleum | TRUE | 3046 | Duke Energy Progress - (NC) | 2716 | W H Weatherspoon | NC | Robeson | GT3 | Petroleum Liquids | GT |  | S | X | X |  |  | 41.8 | 0.9 | 32 | 41 | 12 | N |  |  | OP | X | 4 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1971 | petroleum | TRUE | 3046 | Duke Energy Progress - (NC) | 2716 | W H Weatherspoon | NC | Robeson | GT4 | Petroleum Liquids | GT |  | S | X | X |  |  | 41.8 | 0.9 | 30 | 41 | 12 | N |  |  | OP | X | 4 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1957 | hard coal | TRUE | 5416 | Duke Energy Carolinas, LLC | 2718 | G G Allen | NC | Gaston | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 163.2 | 0.85 | 162 | 167 | 85 | N |  |  | OP | X | 6 | 1957 | 12 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N
Vintage1961 | hard coal | TRUE | 5416 | Duke Energy Carolinas, LLC | 2718 | G G Allen | NC | Gaston | 5 | Conventional Steam Coal | ST |  | S | X | X |  |  | 272 | 0.85 | 259 | 259 | 140 | N |  |  | OP | X | 7 | 1961 | 12 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N
Vintage1919 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 2719 | Bridgewater | NC | Burke | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 13 | 0.9 | 15 | 15 | 13 | N |  |  | OP | X | 5 | 1919 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1919 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 2719 | Bridgewater | NC | Burke | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 13 | 0.9 | 15 | 15 | 13 | N |  |  | OP | X | 5 | 1919 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage2011 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 2719 | Bridgewater | NC | Burke | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.7 | 0.8 | 1.5 | 1.5 | 1.5 | N |  |  | OP | X | 11 | 2011 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage2011 | natural gas combined cycle | TRUE | 5416 | Duke Energy Carolinas, LLC | 2720 | Buck | NC | Rowan | CT11 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 185.3 | 0.85 | 182 | 206 | 182 | N |  |  | OP | X | 11 | 2011 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  |  | N |  | 12H | [23 empty] | N | N | N
Vintage2011 | natural gas combined cycle | TRUE | 5416 | Duke Energy Carolinas, LLC | 2720 | Buck | NC | Rowan | CT12 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 185.3 | 0.85 | 182 | 206 | 182 | N |  |  | OP | X | 11 | 2011 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  |  | N |  | 12H | [23 empty] | N | N | N
Vintage2011 | natural gas combined cycle | TRUE | 5416 | Duke Energy Carolinas, LLC | 2720 | Buck | NC | Rowan | ST10 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 327.3 | 0.85 | 304 | 306 | 255 | N |  |  | OP | X | 11 | 2011 |  |  | N | Electric Utility | 1 | [12 empty] | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1972 | hard coal | TRUE | 5416 | Duke Energy Carolinas, LLC | 2721 | James E. Rogers Energy Complex | NC | Cleveland | 5 | Conventional Steam Coal | ST |  | S | X | X |  |  | 621 | 0.9 | 544 | 546 | 126 | N |  |  | OP | X | 6 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: NG; DFO DFO DFO: NG; DFO NG NG: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage2012 | hard coal | TRUE | 5416 | Duke Energy Carolinas, LLC | 2721 | James E. Rogers Energy Complex | NC | Cleveland | 6 | Conventional Steam Coal | ST |  | S | X | X |  |  | 909.5 | 0.85 | 844 | 849 | 310 | N |  |  | OP | X | 12 | 2012 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: NG; DFO DFO DFO: NG; DFO NG NG: DFO |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | Y | N | N
Vintage1963 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 2722 | Cowans Ford | NC | Lincoln | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 87.5 | 0.95 | 81 | 81 | 81 | N |  |  | OP | X | 9 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1963 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 2722 | Cowans Ford | NC | Lincoln | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 87.5 | 0.95 | 81 | 81 | 81 | N |  |  | OP | X | 9 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1963 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 2722 | Cowans Ford | NC | Lincoln | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 87.5 | 0.95 | 81 | 81 | 81 | N |  |  | OP | X | 9 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1967 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 2722 | Cowans Ford | NC | Lincoln | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 87.5 | 0.95 | 81 | 81 | 81 | N |  |  | OP | X | 4 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage2012 | natural gas combined cycle | TRUE | 5416 | Duke Energy Carolinas, LLC | 2723 | Dan River | NC | Rockingham | CT8 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 185.3 | 0.85 | 177 | 206 | 177 | N |  |  | OP | X | 12 | 2012 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2012 | natural gas combined cycle | TRUE | 5416 | Duke Energy Carolinas, LLC | 2723 | Dan River | NC | Rockingham | CT9 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 185.3 | 0.85 | 177 | 206 | 177 | N |  |  | OP | X | 12 | 2012 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2012 | natural gas combined cycle | TRUE | 5416 | Duke Energy Carolinas, LLC | 2723 | Dan River | NC | Rockingham | ST7 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 327.3 | 0.85 | 308 | 306 | 300 | N |  |  | OP | X | 12 | 2012 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1915 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 2726 | Lookout Shoals | NC | Iredell | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8.6 | 1 | 9 | 9 | 8.6 | N |  |  | OP | X | 12 | 1915 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1915 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 2726 | Lookout Shoals | NC | Iredell | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8.6 | 1 | 9 | 9 | 8.6 | N |  |  | OP | X | 12 | 1915 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1915 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 2726 | Lookout Shoals | NC | Iredell | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8.6 | 1 | 9 | 9 | 8.6 | N |  |  | OP | X | 12 | 1915 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1965 | hard coal | TRUE | 5416 | Duke Energy Carolinas, LLC | 2727 | Marshall (NC) | NC | Catawba | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 348.5 | 0.9 | 370 | 380 | 140 | N |  |  | OP | X | 3 | 1965 | 12 | 2034 | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: NG; DFO DFO DFO: DFO |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N | N
Vintage1966 | hard coal | TRUE | 5416 | Duke Energy Carolinas, LLC | 2727 | Marshall (NC) | NC | Catawba | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 348.5 | 0.9 | 370 | 380 | 140 | N |  |  | OP | X | 4 | 1966 | 12 | 2034 | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: NG; DFO DFO DFO: DFO |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N | N
Vintage1969 | hard coal | TRUE | 5416 | Duke Energy Carolinas, LLC | 2727 | Marshall (NC) | NC | Catawba | 3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 711 | 0.9 | 658 | 658 | 270 | N |  |  | OP | X | 5 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: NG; DFO DFO DFO: DFO |  |  | N |  |  | OVER |  | Y |  |  |  | Y | [17 empty] | N | N
Vintage1970 | hard coal | TRUE | 5416 | Duke Energy Carolinas, LLC | 2727 | Marshall (NC) | NC | Catawba | 4 | Conventional Steam Coal | ST |  | S | X | X |  |  | 711 | 0.9 | 660 | 660 | 270 | N |  |  | OP | X | 5 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: NG; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | N | N
Vintage1923 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 2728 | Mountain Island | NC | Gaston | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.8 | 14 | 14 | 14 | N |  |  | OP | X | 12 | 1923 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1923 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 2728 | Mountain Island | NC | Gaston | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.8 | 14 | 14 | 14 | N |  |  | OP | X | 12 | 1923 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1923 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 2728 | Mountain Island | NC | Gaston | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.8 | 17 | 17 | 15 | N |  |  | OP | X | 12 | 1923 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1923 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 2728 | Mountain Island | NC | Gaston | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.8 | 17 | 17 | 15 | N |  |  | OP | X | 12 | 1923 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1928 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 2729 | Oxford Dam | NC | Catawba | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18 | 0.8 | 20 | 20 | 18 | N |  |  | OP | X | 4 | 1928 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1928 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 2729 | Oxford Dam | NC | Catawba | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18 | 0.8 | 20 | 20 | 18 | N |  |  | OP | X | 4 | 1928 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1925 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 2730 | Rhodhiss | NC | Caldwell | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8.5 | 0.95 | 9.5 | 9.5 | 8.5 | N |  |  | OP | X | 2 | 1925 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1925 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 2730 | Rhodhiss | NC | Caldwell | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8.5 | 0.95 | 11.5 | 11.5 | 8.5 | N |  |  | OP | X | 2 | 1925 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1925 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 2730 | Rhodhiss | NC | Caldwell | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8.5 | 0.95 | 12.4 | 12.4 | 8.5 | N |  |  | OP | X | 2 | 1925 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1996 | hydro | TRUE | 13763 | Northbrook Carolina Hydro LLC | 2735 | Turner Shoals | NC | Polk | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.7 | 0.9 | 2.7 | 2.7 | 0.4 | N |  |  | OP | X | 12 | 1996 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1996 | hydro | TRUE | 13763 | Northbrook Carolina Hydro LLC | 2735 | Turner Shoals | NC | Polk | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.7 | 0.9 | 2.7 | 2.7 | 0.4 | N |  |  | OP | X | 12 | 1996 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1920 | hydro | TRUE | 63011 | Northbrook Tuxedo, LLC | 2736 | Tuxedo | NC | Henderson | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 0.8 | 3.2 | 3.2 | 2.5 | N |  |  | OP | X | 6 | 1920 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1920 | hydro | TRUE | 63011 | Northbrook Tuxedo, LLC | 2736 | Tuxedo | NC | Henderson | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 0.8 | 3.2 | 3.2 | 2.5 | N |  |  | OP | X | 6 | 1920 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1954 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 2741 | Bear Creek Dam | NC | Jackson | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9 | 0.9 | 9.5 | 9.5 | 9 | N |  |  | OP | X | 3 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1952 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 2743 | Cedar Cliff | NC | Jackson | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.4 | 0.85 | 6.4 | 6.4 | 6.4 | N |  |  | OP | X | 1 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1925 | hydro | TRUE | 63010 | Northbrook Carolina Hydro II, LLC | 2745 | Franklin (NC) | NC | Macon | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.5 | N |  |  | OP | X | 1 | 1925 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1925 | hydro | TRUE | 63010 | Northbrook Carolina Hydro II, LLC | 2745 | Franklin (NC) | NC | Macon | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.5 | N |  |  | OP | X | 1 | 1925 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  | N |  | 10M | [23 empty] | N
Vintage1924 | hydro | TRUE | 63010 | Northbrook Carolina Hydro II, LLC | 2746 | Mission | NC | Clay | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.6 | N |  |  | OP | X | 12 | 1924 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1924 | hydro | TRUE | 63010 | Northbrook Carolina Hydro II, LLC | 2746 | Mission | NC | Clay | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.6 | N |  |  | OP | X | 12 | 1924 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1943 | hydro | TRUE | 63010 | Northbrook Carolina Hydro II, LLC | 2746 | Mission | NC | Clay | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.6 | N |  |  | OP | X | 1 | 1943 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1942 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 2747 | Nantahala | NC | Macon | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 43.2 | 0.8 | 45 | 45 | 43.2 | N |  |  | OP | X | 7 | 1942 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1955 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 2749 | Tennessee Creek | NC | Jackson | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10.8 | 0.9 | 11.5 | 11.5 | 10.8 | N |  |  | OP | X | 5 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1941 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 2750 | Thorpe | NC | Jackson | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 21.6 | 0.8 | 19.7 | 19.7 | 19.7 | N |  |  | OP | X | 10 | 1941 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1950 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 2751 | Tuckasegee | NC | Jackson | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.9 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 5 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1963 | hydro | TRUE | 19876 | Virginia Electric & Power Co | 2756 | Gaston | NC | Halifax | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 44.4 | 0.8 | 55 | 55 | 0 | N |  |  | OP | X | 3 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 19876 | Virginia Electric & Power Co | 2756 | Gaston | NC | Halifax | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 44.4 | 0.8 | 55 | 55 | 0 | N |  |  | OP | X | 2 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1963 | hydro | TRUE | 19876 | Virginia Electric & Power Co | 2756 | Gaston | NC | Halifax | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 44.4 | 0.8 | 55 | 55 | 0 | N |  |  | OP | X | 2 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1963 | hydro | TRUE | 19876 | Virginia Electric & Power Co | 2756 | Gaston | NC | Halifax | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 44.4 | 0.8 | 55 | 55 | 0 | N |  |  | OP | X | 2 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1955 | hydro | TRUE | 19876 | Virginia Electric & Power Co | 2758 | Roanoke Rapids | NC | Halifax | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 25 | 0.9 | 24 | 24 | 10 | N |  |  | OP | X | 12 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1955 | hydro | TRUE | 19876 | Virginia Electric & Power Co | 2758 | Roanoke Rapids | NC | Halifax | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 25 | 0.9 | 24 | 24 | 10 | N |  |  | OP | X | 10 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1955 | hydro | TRUE | 19876 | Virginia Electric & Power Co | 2758 | Roanoke Rapids | NC | Halifax | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 25 | 0.9 | 24 | 24 | 10 | N |  |  | OP | X | 9 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1955 | hydro | TRUE | 19876 | Virginia Electric & Power Co | 2758 | Roanoke Rapids | NC | Halifax | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 25 | 0.9 | 23 | 23 | 10 | N |  |  | OP | X | 9 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1927 | hydro | TRUE | 10604 | Lake Lure Town of | 2773 | Lake Lure | NC | Rutherford | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 0.6 | N |  |  | OP | X | 1 | 1927 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 12H | [23 empty] | N
Vintage1927 | hydro | TRUE | 10604 | Lake Lure Town of | 2773 | Lake Lure | NC | Rutherford | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 2.4 | 2.4 | 0.6 | N |  |  | OP | X | 1 | 1927 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 12H
Vintage1954 | hydro | TRUE | 18642 | Tennessee Valley Authority | 2778 | Chatuge | NC | Clay | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 13.2 | 0.9 | 13.9 | 13.1 | 7.9 | N |  |  | OP | X | 12 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1945 | hydro | TRUE | 18642 | Tennessee Valley Authority | 2779 | Fontana Dam | NC | Swain | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 81 | 0.95 | 101.4 | 101.4 | 56 | N |  |  | OP | X | 1 | 1945 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1945 | hydro | TRUE | 18642 | Tennessee Valley Authority | 2779 | Fontana Dam | NC | Swain | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 92.7 | 0.95 | 101.4 | 101.4 | 56 | N |  |  | OP | X | 3 | 1945 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1954 | hydro | TRUE | 18642 | Tennessee Valley Authority | 2779 | Fontana Dam | NC | Swain | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 81 | 0.95 | 101.4 | 101.4 | 56 | N |  |  | OP | X | 2 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1940 | hydro | TRUE | 18642 | Tennessee Valley Authority | 2780 | Hiwassee Dam | NC | Cherokee | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 70.6 | 0.9 | 87.7 | 73.8 | 33.3 | N |  |  | OP | X | 5 | 1940 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1956 | other | TRUE | 18642 | Tennessee Valley Authority | 2780 | Hiwassee Dam | NC | Cherokee | 2 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 95 | 0.95 | 86 | 67.5 | 56.7 | N |  |  | OP | X | 5 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1991 | petroleum | TRUE | 13683 | North Carolina El Member Corp | 2783 | Buxton | NC | Dare | 1A | Petroleum Liquids | IC |  | S | X | X | Buxton 34.5 KV GEN12 | Buxton 34.5 KV GEN12 | 3 | 0.8 | 3 | 3 | 3 | N |  |  | OP | X | 4 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1991 | petroleum | TRUE | 13683 | North Carolina El Member Corp | 2783 | Buxton | NC | Dare | 2A | Petroleum Liquids | IC |  | S | X | X | Buxton 34.5 KV GEN12 | Buxton 34.5 KV GEN12 | 3 | 0.8 | 3 | 3 | 3 | N |  |  | OP | X | 4 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1991 | petroleum | TRUE | 13683 | North Carolina El Member Corp | 2783 | Buxton | NC | Dare | 3A | Petroleum Liquids | IC |  | S | X | X | Buxton 34.5 KV GEN34 | Buxton 34.5 KV GEN34 | 3 | 0.8 | 3 | 3 | 3 | N |  |  | OP | X | 4 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1991 | petroleum | TRUE | 13683 | North Carolina El Member Corp | 2783 | Buxton | NC | Dare | 4A | Petroleum Liquids | IC |  | S | X | X | Buxton 34.5 KV GEN34 | Buxton 34.5 KV GEN34 | 3 | 0.8 | 3 | 3 | 3 | N |  |  | OP | X | 4 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1991 | petroleum | TRUE | 13683 | North Carolina El Member Corp | 2783 | Buxton | NC | Dare | 5A | Petroleum Liquids | IC |  | S | X | X | Buxton 34.5 KV GEN5 | Buxton 34.5 KV GEN5 | 3 | 0.8 | 3 | 3 | 3 | N |  |  | OP | X | 4 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1954 | lignite | TRUE | 12199 | Montana-Dakota Utilities Co | 2790 | R M Heskett | ND | Morton | 1 | Conventional Steam Coal | ST |  | S | X | X | MDU.HESKET1 | MDU.HESKET1 | 40 | 1 | 29.5 | 29.5 | 6.5 | N |  |  | OP | X | 11 | 1954 | 2 | 2022 | N | Electric Utility | 1 | X X X: X; DFO RC RC: LIG; DFO SUB SUB: TDF; DFO DFO DFO: SUB; DFO DFO DFO: NG |  |  | N | N |  | 12H | N | N | Y |  | Y | [18 empty] | N
Vintage1963 | lignite | TRUE | 12199 | Montana-Dakota Utilities Co | 2790 | R M Heskett | ND | Morton | 2 | Conventional Steam Coal | ST |  | S | X | X | MDU.HESKET2 | MDU.HESKET2 | 75 | 0.85 | 74.8 | 74.8 | 29.3 | N |  |  | OP | X | 11 | 1963 | 1 | 2022 | N | Electric Utility | 1 | X X X: X; DFO RC RC: LIG; DFO SUB SUB: TDF; DFO DFO DFO: SUB; DFO DFO DFO: NG |  |  | N | N |  | 12H | Y | N |  |  | Y | [18 empty] | N
Vintage2014 | natural gas peaker | TRUE | 12199 | Montana-Dakota Utilities Co | 2790 | R M Heskett | ND | Morton | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MDU.HESKET3 | MDU.HESKET3 | 88 | 0.85 | 88 | 101 | 8 | N |  |  | OP | X | 8 | 2014 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1976 | petroleum | TRUE | 14232 | Otter Tail Power Co | 2801 | Jamestown | ND | Stutsman | 1 | Petroleum Liquids | GT |  | S | X | X | OTP.JMSPK1 | OTP.JMSPK1 | 24.1 | 0.9 | 20.5 | 25.2 | 6 | N |  |  | SB | Y | 5 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1978 | petroleum | TRUE | 14232 | Otter Tail Power Co | 2801 | Jamestown | ND | Stutsman | 2 | Petroleum Liquids | GT |  | S | X | X | OTP.JMSPK2 | OTP.JMSPK2 | 24.1 | 0.9 | 21.2 | 26 | 6 | N |  |  | SB | Y | 12 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1937 | petroleum | TRUE | 7444 | City of Grafton - (ND) | 2811 | Grafton | ND | Walsh | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.3 | N |  |  | SB | Y | 8 | 1937 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H |  |  |  | N | N | [18 empty] | N | N | N
Vintage1949 | petroleum | TRUE | 7444 | City of Grafton - (ND) | 2811 | Grafton | ND | Walsh | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.4 | N |  |  | SB | Y | 8 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H |  |  |  | N | N | [18 empty] | N | N | N
Vintage1956 | petroleum | TRUE | 7444 | City of Grafton - (ND) | 2811 | Grafton | ND | Walsh | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 0.7 | N |  |  | SB | Y | 9 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H |  |  |  | N | N | [18 empty] | N | N | N
Vintage1956 | petroleum | TRUE | 7444 | City of Grafton - (ND) | 2811 | Grafton | ND | Walsh | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 0.7 | N |  |  | SB | Y | 9 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H |  |  |  | N | N | [18 empty] | N | N | N
Vintage1956 | hydro | TRUE | 19635 | USACE-Omaha | 2815 | Garrison | ND | Mercer | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 121.6 | 0.95 | 102 | 102 | 0 | N |  |  | OP | X | 1 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1956 | hydro | TRUE | 19635 | USACE-Omaha | 2815 | Garrison | ND | Mercer | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 121.6 | 0.95 | 102 | 102 | 0 | N |  |  | OP | X | 3 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1956 | hydro | TRUE | 19635 | USACE-Omaha | 2815 | Garrison | ND | Mercer | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 121.6 | 0.95 | 102 | 102 | 0 | N |  |  | OP | X | 8 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1960 | hydro | TRUE | 19635 | USACE-Omaha | 2815 | Garrison | ND | Mercer | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 109.3 | 0.95 | 102 | 102 | 0 | N |  |  | OP | X | 3 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1960 | hydro | TRUE | 19635 | USACE-Omaha | 2815 | Garrison | ND | Mercer | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 109.3 | 0.95 | 102 | 102 | 0 | N |  |  | OP | X | 5 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1966 | hard coal | TRUE | 1307 | Basin Electric Power Coop | 2817 | Leland Olds | ND | Mercer | 1 | Conventional Steam Coal | ST |  | S | X | X | WAUELELANDOUNLELAND_1_UNIT_RA | WAUE.BEPM.LOS1 | 216 | 0.85 | 221 | 221 | 110 | N |  |  | OP | X | 1 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: LIG; DFO DFO DFO: SUB; DFO DFO DFO: DFO |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1975 | hard coal | TRUE | 1307 | Basin Electric Power Coop | 2817 | Leland Olds | ND | Mercer | 2 | Conventional Steam Coal | ST |  | S | X | X | WAUELELANDOUNLELAND_2_UNIT_RA | WAUE.BEPM.LOS2 | 440 | 0.9 | 445 | 445 | 220 | N |  |  | OP | X | 12 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: LIG; DFO DFO DFO: SUB; DFO DFO DFO: DFO |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1970 | hard coal | TRUE | 12658 | Minnkota Power Coop, Inc | 2823 | Milton R Young | ND | Oliver | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 257 | 0.9 | 237 | 237 | 150 | N |  |  | OP | X | 10 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: LIG; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | N |  | Y | Y | N | [17 empty] | N |  | N
Vintage1977 | hard coal | TRUE | 12658 | Minnkota Power Coop, Inc | 2823 | Milton R Young | ND | Oliver | 2 | Conventional Steam Coal | ST |  | W | X | X |  |  | 477 | 0.9 | 447 | 455 | 270 | N |  |  | OP | X | 4 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: LIG; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | N |  | Y | Y | N | [17 empty] | N
Vintage1967 | hard coal | TRUE | 61412 | Cardinal Operating Company | 2828 | Cardinal | OH | Jefferson | 1 | Conventional Steam Coal | ST |  | W | X | X | 40243871 | 40243871 | 615.2 | 0.85 | 585 | 595 | 340 | N |  |  | OP | X | 2 | 1967 | 12 | 2028 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | N | N | N
Vintage1967 | hard coal | TRUE | 61412 | Cardinal Operating Company | 2828 | Cardinal | OH | Jefferson | 2 | Conventional Steam Coal | ST |  | W | X | X | 40243873 | 40243873 | 615.2 | 0.85 | 585 | 595 | 340 | N |  |  | OP | X | 7 | 1967 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | N | N | N
Vintage1977 | hard coal | TRUE | 61412 | Cardinal Operating Company | 2828 | Cardinal | OH | Jefferson | 3 | Conventional Steam Coal | ST |  | W | X | X | 40243869 | 40243869 | 650 | 0.9 | 620 | 620 | 375 | N |  |  | OP | X | 9 | 1977 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | N | N | N
Vintage2015 | other | TRUE | 3542 | Duke Energy Ohio Inc | 2830 | Walter C Beckjord | OH | Clermont | BECK1 | Batteries | BA |  | S | X | X |  |  | 2 |  | 2 | 2 | 0 | N |  |  | OP | X | 1 | 2015 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: MWH | [5 empty] | 10M
Vintage2015 | other | TRUE | 3542 | Duke Energy Ohio Inc | 2830 | Walter C Beckjord | OH | Clermont | BECK2 | Batteries | BA |  | S | X | X |  |  | 2 |  | 2 | 2 | 0 | N |  |  | OP | X | 11 | 2015 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: MWH | [5 empty] | 10M
Vintage1965 | natural gas peaker | TRUE | 59917 | Luminant Dick's Creek | 2831 | Dicks Creek | OH | Butler | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 100 | 0.9 | 92 | 110 | 5 | N |  |  | OP | X | 9 | 1965 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1969 | natural gas peaker | TRUE | 59917 | Luminant Dick's Creek | 2831 | Dicks Creek | OH | Butler | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 16.5 | 0.85 | 14.2 | 19.5 | 3 | N |  |  | OP | X | 6 | 1969 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1969 | natural gas peaker | TRUE | 59917 | Luminant Dick's Creek | 2831 | Dicks Creek | OH | Butler | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 21.3 | 0.8 | 15 | 21.4 | 3 | N |  |  | OP | X | 10 | 1969 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1969 | natural gas peaker | TRUE | 59917 | Luminant Dick's Creek | 2831 | Dicks Creek | OH | Butler | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 21.3 | 0.8 | 15 | 21.4 | 3 | N |  |  | OP | X | 10 | 1969 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1975 | hard coal | TRUE | 59919 | Luminant Miami Fort | 2832 | Miami Fort | OH | Hamilton | 7 | Conventional Steam Coal | ST |  | S | X | X |  |  | 557.1 | 0.85 | 510 | 510 | 200 | N |  |  | OP | X | 5 | 1975 | 12 | 2027 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | N |  |  | N | N | N
Vintage1978 | hard coal | TRUE | 59919 | Luminant Miami Fort | 2832 | Miami Fort | OH | Hamilton | 8 | Conventional Steam Coal | ST |  | S | X | X |  |  | 557.7 | 0.85 | 510 | 510 | 200 | N |  |  | OP | X | 2 | 1978 | 12 | 2027 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | N |  |  | N | N | N
Vintage1971 | petroleum | TRUE | 59919 | Luminant Miami Fort | 2832 | Miami Fort | OH | Hamilton | GT3 | Petroleum Liquids | GT |  | S | X | X |  |  | 16.5 | 0.85 | 14 | 20 | 3 | N |  |  | OP | X | 7 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 12H | [20 empty] | N |  |  | N | N | N
Vintage1971 | petroleum | TRUE | 59919 | Luminant Miami Fort | 2832 | Miami Fort | OH | Hamilton | GT4 | Petroleum Liquids | GT |  | S | X | X |  |  | 16.5 | 0.85 | 14 | 20 | 3 | N |  |  | OP | X | 8 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 12H | [20 empty] | N |  |  | N | N | N
Vintage1971 | petroleum | TRUE | 59919 | Luminant Miami Fort | 2832 | Miami Fort | OH | Hamilton | GT5 | Petroleum Liquids | GT |  | S | X | X |  |  | 16.5 | 0.85 | 14 | 20 | 3 | N |  |  | OP | X | 9 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 12H | [20 empty] | N |  |  | N | N | N
Vintage1971 | petroleum | TRUE | 59919 | Luminant Miami Fort | 2832 | Miami Fort | OH | Hamilton | GT6 | Petroleum Liquids | GT |  | S | X | X |  |  | 16.5 | 0.85 | 14 | 20 | 3 | N |  |  | OP | X | 10 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 12H | [20 empty] | N |  |  | N | N | N
Vintage1968 | petroleum | TRUE | 14165 | GenOn Power Midwest, LP | 2836 | Avon Lake | OH | Lorain | 10 | Petroleum Liquids | GT |  | S | X | X | 106856941 | AVONLAK2 14 KV G10 | 32.1 | 0.85 | 25 | 30 | 25 | N |  |  | SB | Y | 1 | 1968 | 3 | 2022 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [20 empty] | N |  |  | N
Vintage1970 | hard coal | TRUE | 14165 | GenOn Power Midwest, LP | 2836 | Avon Lake | OH | Lorain | 9 | Conventional Steam Coal | ST |  | S | X | X | 87901609 | AVONLAK2 20 KV UN9 | 680 | 0.95 | 627 | 627 | 330 | N |  |  | OP | X | 1 | 1970 | 3 | 2022 | N | IPP Non-CHP | 2 | X | BIT | SUB | NG | DFO |  |  | NG | DFO |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [14 empty] | N |  |  | N |  | N
Vintage1995 | natural gas peaker | TRUE | 61919 | Kimura Power LLC | 2847 | Tait Electric Generating Station | OH | Montgomery | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 40243895 | 40243895 | 103.5 | 0.85 | 88.5 | 111.9 | 41 | N |  |  | OP | X | 6 | 1995 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1996 | natural gas peaker | TRUE | 61919 | Kimura Power LLC | 2847 | Tait Electric Generating Station | OH | Montgomery | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 40243897 | 40243897 | 106.1 | 0.85 | 86.8 | 114.9 | 41 | N |  |  | OP | X | 12 | 1996 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1998 | natural gas peaker | TRUE | 61919 | Kimura Power LLC | 2847 | Tait Electric Generating Station | OH | Montgomery | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 40243889 | 40243889 | 84.2 | 0.85 | 80.8 | 98.9 | 41 | N |  |  | OP | X | 12 | 1998 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 61919 | Kimura Power LLC | 2847 | Tait Electric Generating Station | OH | Montgomery | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 94 | 0.85 | 81 | 108.9 | 42 | N |  |  | OP | X | 5 | 2002 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y |  | N
Vintage2002 | natural gas peaker | TRUE | 61919 | Kimura Power LLC | 2847 | Tait Electric Generating Station | OH | Montgomery | GT5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 94 | 0.85 | 80.2 | 108.1 | 42 | N |  |  | OP | X | 5 | 2002 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y |  | N
Vintage2002 | natural gas peaker | TRUE | 61919 | Kimura Power LLC | 2847 | Tait Electric Generating Station | OH | Montgomery | GT6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 94 | 0.85 | 80.5 | 104 | 42 | N |  |  | OP | X | 4 | 2002 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y |  | N
Vintage2002 | natural gas peaker | TRUE | 61919 | Kimura Power LLC | 2847 | Tait Electric Generating Station | OH | Montgomery | GT7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 94 | 0.85 | 80.5 | 104 | 42 | N |  |  | OP | X | 4 | 2002 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y |  | N
Vintage1967 | petroleum | TRUE | 61919 | Kimura Power LLC | 2847 | Tait Electric Generating Station | OH | Montgomery | IC1 | Petroleum Liquids | IC |  | S | X | X | 1107290033 | 1107290033 | 2.7 | 0.8 | 3 | 3 | 2.5 | N |  |  | OP | X | 5 | 1967 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1967 | petroleum | TRUE | 61919 | Kimura Power LLC | 2847 | Tait Electric Generating Station | OH | Montgomery | IC2 | Petroleum Liquids | IC |  | S | X | X | 1107290033 | 1107290033 | 2.7 | 0.8 | 3 | 3 | 2.5 | N |  |  | OP | X | 5 | 1967 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1967 | petroleum | TRUE | 61919 | Kimura Power LLC | 2847 | Tait Electric Generating Station | OH | Montgomery | IC3 | Petroleum Liquids | IC |  | S | X | X | 1107290033 | 1107290033 | 2.7 | 0.8 | 3 | 3 | 2.5 | N |  |  | OP | X | 5 | 1967 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1967 | petroleum | TRUE | 61919 | Kimura Power LLC | 2847 | Tait Electric Generating Station | OH | Montgomery | IC4 | Petroleum Liquids | IC |  | S | X | X | 1107290033 | 1107290033 | 2.7 | 0.8 | 3 | 3 | 2.5 | N |  |  | OP | X | 5 | 1967 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1968 | natural gas peaker | TRUE | 61919 | Kimura Power LLC | 2848 | O H Hutchings | OH | Montgomery | 7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 40243943 | 40243943 | 32.6 | 0.85 | 25.3 | 29.9 | 25 | N |  |  | OP | X | 11 | 1968 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1968 | petroleum | TRUE | 61919 | Kimura Power LLC | 2851 | Monument | OH | Montgomery | 1 | Petroleum Liquids | IC |  | S | X | X | 32418667 | 32418667 | 2.7 | 0.8 | 2.4 | 2.4 | 2.4 | N |  |  | OP | X | 6 | 1968 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1968 | petroleum | TRUE | 61919 | Kimura Power LLC | 2851 | Monument | OH | Montgomery | 2 | Petroleum Liquids | IC |  | S | X | X | 32418667 | 32418667 | 2.7 | 0.8 | 2.4 | 2.4 | 2.4 | N |  |  | OP | X | 6 | 1968 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1968 | petroleum | TRUE | 61919 | Kimura Power LLC | 2851 | Monument | OH | Montgomery | 3 | Petroleum Liquids | IC |  | S | X | X | 32418667 | 32418667 | 2.7 | 0.8 | 2.4 | 2.4 | 2.4 | N |  |  | OP | X | 6 | 1968 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1968 | petroleum | TRUE | 61919 | Kimura Power LLC | 2851 | Monument | OH | Montgomery | 4 | Petroleum Liquids | IC |  | S | X | X | 32418667 | 32418667 | 2.7 | 0.8 | 2.4 | 2.4 | 2.4 | N |  |  | OP | X | 6 | 1968 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1968 | petroleum | TRUE | 61919 | Kimura Power LLC | 2851 | Monument | OH | Montgomery | 5 | Petroleum Liquids | IC |  | S | X | X | 32418667 | 32418667 | 2.7 | 0.8 | 2.4 | 2.4 | 2.4 | N |  |  | OP | X | 6 | 1968 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1968 | petroleum | TRUE | 61919 | Kimura Power LLC | 2852 | Sidney (OH) | OH | Shelby | 1 | Petroleum Liquids | IC |  | S | X | X | 32418669 | 32418669 | 2.7 | 0.8 | 2.7 | 2.7 | 2.4 | N |  |  | OP | X | 7 | 1968 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1968 | petroleum | TRUE | 61919 | Kimura Power LLC | 2852 | Sidney (OH) | OH | Shelby | 2 | Petroleum Liquids | IC |  | S | X | X | 32418669 | 32418669 | 2.7 | 0.8 | 2.7 | 2.7 | 2.4 | N |  |  | OP | X | 7 | 1968 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1968 | petroleum | TRUE | 61919 | Kimura Power LLC | 2852 | Sidney (OH) | OH | Shelby | 3 | Petroleum Liquids | IC |  | S | X | X | 32418669 | 32418669 | 2.7 | 0.8 | 2.7 | 2.7 | 2.4 | N |  |  | OP | X | 7 | 1968 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1968 | petroleum | TRUE | 61919 | Kimura Power LLC | 2852 | Sidney (OH) | OH | Shelby | 4 | Petroleum Liquids | IC |  | S | X | X | 32418669 | 32418669 | 2.7 | 0.8 | 2.7 | 2.7 | 2.4 | N |  |  | OP | X | 7 | 1968 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1968 | petroleum | TRUE | 61919 | Kimura Power LLC | 2852 | Sidney (OH) | OH | Shelby | 5 | Petroleum Liquids | IC |  | S | X | X | 32418669 | 32418669 | 2.7 | 0.8 | 2.7 | 2.7 | 2.4 | N |  |  | OP | X | 7 | 1968 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1969 | natural gas peaker | TRUE | 61919 | Kimura Power LLC | 2854 | Yankee Street | OH | Montgomery | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 40243905 | 40243905 | 18.5 | 0.85 | 19.9 | 21.8 | 19.5 | N |  |  | OP | X | 7 | 1969 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1969 | natural gas peaker | TRUE | 61919 | Kimura Power LLC | 2854 | Yankee Street | OH | Montgomery | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 40243907 | 40243907 | 18.5 | 0.85 | 20.1 | 21.8 | 18.5 | N |  |  | OP | X | 7 | 1969 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1969 | natural gas peaker | TRUE | 61919 | Kimura Power LLC | 2854 | Yankee Street | OH | Montgomery | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 40243909 | 40243909 | 18.5 | 0.85 | 20.7 | 21.8 | 18.5 | N |  |  | OP | X | 7 | 1969 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1970 | natural gas peaker | TRUE | 61919 | Kimura Power LLC | 2854 | Yankee Street | OH | Montgomery | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 40243911 | 40243911 | 17.5 | 0.85 | 14.9 | 20.2 | 11 | N |  |  | OP | X | 11 | 1970 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1970 | natural gas peaker | TRUE | 61919 | Kimura Power LLC | 2854 | Yankee Street | OH | Montgomery | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 40243913 | 40243913 | 17.5 | 0.85 | 13.7 | 18.6 | 9 | N |  |  | OP | X | 11 | 1970 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1970 | natural gas peaker | TRUE | 61919 | Kimura Power LLC | 2854 | Yankee Street | OH | Montgomery | 6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 40243915 | 40243915 | 17.5 | 0.85 | 14 | 18.1 | 12 | N |  |  | OP | X | 11 | 1970 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1970 | natural gas peaker | TRUE | 61919 | Kimura Power LLC | 2854 | Yankee Street | OH | Montgomery | 7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 40243917 | 40243917 | 17.5 | 0.85 | 13.6 | 18.1 | 11 | N |  |  | OP | X | 11 | 1970 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2010 | solar pv | TRUE | 61919 | Kimura Power LLC | 2854 | Yankee Street | OH | Montgomery | YS1 | Solar Photovoltaic | PV |  | S | X | X | N/A | N/A | 1.1 |  | 1.1 | 1.1 |  | N |  |  | OP | X | 3 | 2010 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: SUN |  |  | N | N | [25 empty] | N
Vintage1972 | petroleum | TRUE | 63030 | Niles Power, LLC | 2861 | Niles Power Plant | OH | Trumbull | GT1 | Petroleum Liquids | GT |  | S | X | X | 98370497 | NILES 14 KV CT | 27 | 0.85 | 26.1 | 30 | 5 | N |  |  | OP | X | 7 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1967 | hard coal | TRUE | 64226 | Energy Harbor Generation LLC | 2866 | W H Sammis | OH | Jefferson | 5 | Conventional Steam Coal | ST |  | S | X | X | SAMMISFE23.4KV SH50 | SAMMISFE23.4KV SH50 | 334 | 0.85 | 290 | 290 | 135 | N |  |  | OP | X | 12 | 1967 | 6 | 2023 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: SUB; DFO DFO DFO: DFO |  |  | N | N |  | 12H |  | Y |  |  | Y | [15 empty] | N |  |  | N
Vintage1969 | hard coal | TRUE | 64226 | Energy Harbor Generation LLC | 2866 | W H Sammis | OH | Jefferson | 6 | Conventional Steam Coal | ST |  | S | X | X | SAMMISFE19KV SH60 | SAMMISFE 19KV SH60 | 680 | 0.85 | 600 | 600 | 410 | N |  |  | OP | X | 4 | 1969 | 6 | 2023 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: SUB; DFO DFO DFO: DFO |  |  | N | N |  | 12H |  | Y |  |  |  | Y | [14 empty] | N |  |  | N
Vintage1971 | hard coal | TRUE | 64226 | Energy Harbor Generation LLC | 2866 | W H Sammis | OH | Jefferson | 7 | Conventional Steam Coal | ST |  | S | X | X | SAMMISFE19 KV SH70 | SAMMISFE19KV SH70 | 680 | 0.85 | 600 | 600 | 410 | N |  |  | OP | X | 9 | 1971 | 6 | 2023 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: SUB; DFO DFO DFO: DFO |  |  | N | N |  | 12H |  | Y |  |  |  | Y | [14 empty] | N |  |  | N
Vintage1972 | petroleum | TRUE | 64226 | Energy Harbor Generation LLC | 2866 | W H Sammis | OH | Jefferson | A1 | Petroleum Liquids | IC |  | S | X | X | SAMMISFE138KV SL91 | SAMMISFE138KV SL91 | 2.5 | 1 | 3 | 3 | 2 | N |  |  | OP | X | 3 | 1972 | 6 | 2023 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1972 | petroleum | TRUE | 64226 | Energy Harbor Generation LLC | 2866 | W H Sammis | OH | Jefferson | B1 | Petroleum Liquids | IC |  | S | X | X | SAMMISFE138KV SL91 | SAMMISFE138KV SL91 | 2.5 | 1 | 3 | 3 | 2 | N |  |  | OP | X | 3 | 1972 | 6 | 2023 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1972 | petroleum | TRUE | 64226 | Energy Harbor Generation LLC | 2866 | W H Sammis | OH | Jefferson | B2 | Petroleum Liquids | IC |  | S | X | X | SAMMISFE138KV SL91 | SAMMISFE138KV SL91 | 2.5 | 1 | 3 | 3 | 2 | N |  |  | OP | X | 3 | 1972 | 6 | 2023 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1972 | petroleum | TRUE | 64226 | Energy Harbor Generation LLC | 2866 | W H Sammis | OH | Jefferson | B3 | Petroleum Liquids | IC |  | S | X | X | SAMMISFE138KV SL91 | SAMMISFE138KV SL91 | 2.5 | 1 | 2 | 2 | 2 | N |  |  | OP | X | 3 | 1972 | 6 | 2023 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1972 | petroleum | TRUE | 64226 | Energy Harbor Generation LLC | 2866 | W H Sammis | OH | Jefferson | B4 | Petroleum Liquids | IC |  | S | X | X | SAMMISFE138KV SL91 | SAMMISFE138KV SL91 | 2.5 | 1 | 2 | 2 | 2 | N |  |  | OP | X | 3 | 1972 | 6 | 2023 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1973 | petroleum | TRUE | 63239 | Vermillion Power LLC | 2869 | West Lorain | OH | Lorain | 1A | Petroleum Liquids | GT |  | S | X | X | Beaver 13.2 KV WL-A | Beaver 13.2 KV WL-A | 65.3 | 0.85 | 49.6 | 52.1 | 20 | N |  |  | OP | X | 6 | 1973 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage1973 | petroleum | TRUE | 63239 | Vermillion Power LLC | 2869 | West Lorain | OH | Lorain | 1B | Petroleum Liquids | GT |  | S | X | X | Beaver 13.2 KV WL-B | Beaver 13.2 KV WL-B | 65.3 | 0.85 | 51.3 | 56.1 | 20 | N |  |  | OP | X | 6 | 1973 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage2001 | natural gas peaker | TRUE | 63239 | Vermillion Power LLC | 2869 | West Lorain | OH | Lorain | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | Beaver 13.2 KV WL20 | Beaver 13.2 KV WL20 | 85 | 0.85 | 79 | 85 | 50 | N |  |  | OP | X | 7 | 2001 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 63239 | Vermillion Power LLC | 2869 | West Lorain | OH | Lorain | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | Beaver 13.2 KV WL30 | Beaver 13.2 KV WL30 | 85 | 0.85 | 80.4 | 85 | 50 | N |  |  | OP | X | 7 | 2001 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 63239 | Vermillion Power LLC | 2869 | West Lorain | OH | Lorain | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | Beaver 13.2 KV WL40 | Beaver 13.2 KV WL40 | 85 | 0.85 | 79.1 | 85 | 50 | N |  |  | OP | X | 7 | 2001 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 63239 | Vermillion Power LLC | 2869 | West Lorain | OH | Lorain | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | Beaver 13.2 KV WL50 | Beaver 13.2 KV WL50 | 85 | 0.85 | 81.5 | 85 | 50 | N |  |  | OP | X | 7 | 2001 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 63239 | Vermillion Power LLC | 2869 | West Lorain | OH | Lorain | 6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | Beaver 13.2 KV WL60 | Beaver 13.2 KV WL60 | 85 | 0.85 | 79.6 | 85 | 50 | N |  |  | OP | X | 7 | 2001 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1955 | hard coal | TRUE | 14015 | Ohio Valley Electric Corp | 2876 | Kyger Creek | OH | Gallia | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 217.3 | 0.83 | 194 | 198.7 | 80 | N |  |  | OP | X | 2 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: SUB; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1955 | hard coal | TRUE | 14015 | Ohio Valley Electric Corp | 2876 | Kyger Creek | OH | Gallia | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 217.3 | 0.83 | 192.2 | 198 | 80 | N |  |  | OP | X | 6 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: SUB; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1955 | hard coal | TRUE | 14015 | Ohio Valley Electric Corp | 2876 | Kyger Creek | OH | Gallia | 3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 217.3 | 0.83 | 192.2 | 198 | 80 | N |  |  | OP | X | 9 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: SUB; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1955 | hard coal | TRUE | 14015 | Ohio Valley Electric Corp | 2876 | Kyger Creek | OH | Gallia | 4 | Conventional Steam Coal | ST |  | S | X | X |  |  | 217.3 | 0.83 | 192.2 | 198 | 80 | N |  |  | OP | X | 11 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: SUB; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1955 | hard coal | TRUE | 14015 | Ohio Valley Electric Corp | 2876 | Kyger Creek | OH | Gallia | 5 | Conventional Steam Coal | ST |  | S | X | X |  |  | 217.3 | 0.83 | 192.2 | 198 | 80 | N |  |  | OP | X | 12 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: SUB; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1955 | petroleum | TRUE | 62031 | Walleye Power, LLC | 2878 | FirstEnergy Bay Shore | OH | Lucas | 1 | Petroleum Coke | ST |  | W | X | X | BAYSHOR218 KV BS10 | BAYSHOR218 KV BS10 | 150.5 | 0.88 | 139 | 136.3 | 90 | N |  |  | OP | X | 8 | 1955 |  |  | Y | IPP CHP | 3 | X X X: T; DFO RC RC: PC; DFO SUB SUB: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER | Y | N |  |  | Y | [18 empty] | Y | Y | N
Vintage1967 | petroleum | TRUE | 62031 | Walleye Power, LLC | 2878 | FirstEnergy Bay Shore | OH | Lucas | CT | Petroleum Liquids | GT |  | W | X | X | BAYSHOR2138 KV BS81 | BAYSHOR2138 KV BS81 | 16 | 0.85 | 13.5 | 14.1 | 5 | N |  |  | OP | X | 8 | 1967 |  |  | N | IPP CHP | 3 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H |  |  |  | N | [19 empty] | N | N | N
Vintage1965 | petroleum | TRUE | 57359 | Richland-Stryker Generation LLC | 2880 | Richland | OH | Defiance | 1 | Petroleum Liquids | GT |  | S | X | X |  |  | 15 | 0.85 | 11 | 14 | 3 | N |  |  | OP | X | 12 | 1965 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1966 | natural gas peaker | TRUE | 57359 | Richland-Stryker Generation LLC | 2880 | Richland | OH | Defiance | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 15 | 0.85 | 11 | 14 | 3 | N |  |  | OP | X | 2 | 1966 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1966 | natural gas peaker | TRUE | 57359 | Richland-Stryker Generation LLC | 2880 | Richland | OH | Defiance | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 15 | 0.85 | 11 | 14 | 3 | N |  |  | OP | X | 2 | 1966 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2001 | natural gas peaker | TRUE | 57359 | Richland-Stryker Generation LLC | 2880 | Richland | OH | Defiance | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 135 | 0.85 | 112 | 130 | 40 | N |  |  | OP | X | 3 | 2001 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO DFO DFO: PG |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2001 | natural gas peaker | TRUE | 57359 | Richland-Stryker Generation LLC | 2880 | Richland | OH | Defiance | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 135 | 0.85 | 112 | 130 | 40 | N |  |  | OP | X | 3 | 2001 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO DFO DFO: PG |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2001 | natural gas peaker | TRUE | 57359 | Richland-Stryker Generation LLC | 2880 | Richland | OH | Defiance | 6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 135 | 0.85 | 112 | 130 | 40 | N |  |  | OP | X | 3 | 2001 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO DFO DFO: PG |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1968 | petroleum | TRUE | 57359 | Richland-Stryker Generation LLC | 2881 | Stryker | OH | Williams | 1 | Petroleum Liquids | GT |  | S | X | X |  |  | 19 | 0.85 | 17 | 18 | 3 | N |  |  | OP | X | 2 | 1968 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 12H | [23 empty] | N | N
Vintage1951 | petroleum | TRUE | 768 | City of Arcanum - (OH) | 2902 | Arcanum | OH | Darke | 1 | Petroleum Liquids | IC |  | S | X | X | N/A | N/A | 0.7 | 0.8 | 0.8 | 0.8 | 0.2 | N |  |  | OP | X | 9 | 1951 | 3 | 2022 | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1946 | petroleum | TRUE | 768 | City of Arcanum - (OH) | 2902 | Arcanum | OH | Darke | 2 | Petroleum Liquids | IC |  | S | X | X | N/A | N/A | 0.5 | 0.8 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 10 | 1946 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1970 | natural gas peaker | TRUE | 2439 | City of Bryan - (OH) | 2903 | Bryan (OH) | OH | Williams | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | PJM AEP Dayton | PJM AEP Dayton | 15.8 | 0.85 | 12.5 | 19.5 | 3 | N |  |  | OP | X | 7 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1988 | natural gas peaker | TRUE | 2439 | City of Bryan - (OH) | 2903 | Bryan (OH) | OH | Williams | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | PJM AEP Dayton | PJM AEP Dayton | 16 | 0.85 | 12.5 | 19.5 | 3 | N |  |  | OP | X | 7 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1948 | petroleum | TRUE | 2439 | City of Bryan - (OH) | 2903 | Bryan (OH) | OH | Williams | 5 | Petroleum Liquids | IC |  | S | X | X | PJM AEP Dayton | PJM AEP Dayton | 2.5 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 5 | 1948 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO DFO DFO: DFO |  |  | N | N |  | 10M |  |  |  | N | [19 empty] | N |  | N
Vintage1963 | natural gas peaker | TRUE | 2439 | City of Bryan - (OH) | 2903 | Bryan (OH) | OH | Williams | 6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | PJM AEP Dayton | PJM AEP Dayton | 5 | 0.8 | 4 | 6 | 1 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | 1H | [23 empty] | Y |  | Y
Vintage1971 | petroleum | TRUE | 3762 | City of Cleveland - (OH) | 2906 | Collinwood | OH | Cuyahoga | 3 | Petroleum Liquids | GT |  | S | X | X |  |  | 16 | 0.85 | 16 | 18 | 5 | N |  |  | OS | X | 2 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG | [5 empty] | 1H | [23 empty] | Y | Y | Y
Vintage1970 | natural gas peaker | TRUE | 3762 | City of Cleveland - (OH) | 2909 | West 41st Street | OH | Cuyahoga | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 16 | 0.85 | 16 | 18 | 5 | N |  |  | OP | X | 3 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO | [5 empty] | 1H | [23 empty] | Y | Y | Y
Vintage1970 | natural gas peaker | TRUE | 3762 | City of Cleveland - (OH) | 2909 | West 41st Street | OH | Cuyahoga | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 16 | 0.85 | 16 | 18 | 5 | N |  |  | OP | X | 3 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO | [5 empty] | 1H | [23 empty] | Y | Y | Y
Vintage1954 | hard coal | TRUE | 5336 | City of Dover - (OH) | 2914 | Dover | OH | Tuscarawas | 3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 8 | 0.89 | 8 | 8 | 4 | N |  |  | SB | N | 1 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: NG |  |  | N | N |  | 12H |  |  | Y |  | Y | [18 empty] | N | N | N
Vintage1968 | hard coal | TRUE | 5336 | City of Dover - (OH) | 2914 | Dover | OH | Tuscarawas | 4 | Conventional Steam Coal | ST |  | S | X | X |  |  | 19.5 | 0.89 | 15.2 | 15.2 | 7 | N |  |  | OP | X | 6 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: NG |  |  | N | N |  | 12H |  |  | Y |  | Y | [18 empty] | N | N
Vintage1966 | petroleum | TRUE | 5336 | City of Dover - (OH) | 2914 | Dover | OH | Tuscarawas | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.6 | 0.85 | 2.4 | 2.4 | 1.2 | N |  |  | OP | X | 6 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H |  |  |  | N | [19 empty] | N | N | N
Vintage1992 | natural gas peaker | TRUE | 5336 | City of Dover - (OH) | 2914 | Dover | OH | Tuscarawas | 6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 19.5 | 0.85 | 15.3 | 15.3 | 8 | N |  |  | OP | X | 9 | 1992 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1971 | natural gas peaker | TRUE | 7977 | City of Hamilton - (OH) | 2917 | Hamilton (OH) | OH | Butler | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 1107290425 |  | 16.3 | 0.85 | 12 | 16 | 5 | N |  |  | OP | X | 6 | 1971 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1948 | petroleum | TRUE | 13949 | City of Oberlin - (OH) | 2933 | Oberlin (OH) | OH | Lorain | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1 | 1 | 0.9 | N |  |  | OP | X | 1 | 1948 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1990 | natural gas peaker | TRUE | 13949 | City of Oberlin - (OH) | 2933 | Oberlin (OH) | OH | Lorain | 10 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.4 | N |  |  | OP | X | 1 | 1990 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2001 | natural gas peaker | TRUE | 13949 | City of Oberlin - (OH) | 2933 | Oberlin (OH) | OH | Lorain | 2A | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.1 | 0.8 | 3.1 | 3.1 | 2.4 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 13949 | City of Oberlin - (OH) | 2933 | Oberlin (OH) | OH | Lorain | 3A | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.1 | 0.8 | 3.1 | 3.1 | 2.4 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1958 | natural gas peaker | TRUE | 13949 | City of Oberlin - (OH) | 2933 | Oberlin (OH) | OH | Lorain | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 1.9 | N |  |  | OP | X | 1 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1961 | natural gas peaker | TRUE | 13949 | City of Oberlin - (OH) | 2933 | Oberlin (OH) | OH | Lorain | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2.7 | 2.7 | 2.2 | N |  |  | OP | X | 1 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1966 | natural gas peaker | TRUE | 13949 | City of Oberlin - (OH) | 2933 | Oberlin (OH) | OH | Lorain | 8 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 2.3 | N |  |  | OP | X | 1 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1990 | natural gas peaker | TRUE | 13949 | City of Oberlin - (OH) | 2933 | Oberlin (OH) | OH | Lorain | 9 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.4 | N |  |  | OP | X | 1 | 1990 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N |  | N | bar: X X X to DFO RC RC
Vintage1996 | natural gas peaker | TRUE | 13949 | City of Oberlin - (OH) | 2933 | Oberlin (OH) | OH | Lorain | IC4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.1 | 0.8 | 2.1 | 2.1 | 1.6 | N |  |  | OP | X | 6 | 1996 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N |  | N | bar: X X X to DFO RC RC
Vintage1971 | hard coal | TRUE | 14194 | City of Orrville - (OH) | 2935 | Orrville | OH | Wayne | 10 | Conventional Steam Coal | ST |  | S | X | X |  |  | 25 | 0.8 | 23 | 23 | 7 | N |  |  | OP | X | 1 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N | N |  | 12H |  | Y |  |  | Y | [15 empty] | N |  |  | Y | N | N
Vintage1971 | natural gas steam turbine | TRUE | 14194 | City of Orrville - (OH) | 2935 | Orrville | OH | Wayne | 11 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 25 | 0.8 | 23 | 23 | 7 | N |  |  | OP | X | 1 | 1971 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1949 | hard coal | TRUE | 14194 | City of Orrville - (OH) | 2935 | Orrville | OH | Wayne | 7 | Conventional Steam Coal | ST |  | S | X | X |  |  | 5 | 0.85 | 5 | 5 | 1 | N |  |  | OS | X | 1 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: WDS |  |  | N | N |  | 12H |  |  | Y |  | Y | [15 empty] | N |  |  | N | N | N
Vintage1955 | hard coal | TRUE | 14194 | City of Orrville - (OH) | 2935 | Orrville | OH | Wayne | 8 | Conventional Steam Coal | ST |  | S | X | X |  |  | 7.5 | 0.85 | 7.5 | 7.5 | 2 | N |  |  | OS | X | 1 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: WDS |  |  | N | N |  | 12H |  |  | Y |  | Y | [18 empty] | N | N | N
Vintage1961 | hard coal | TRUE | 14194 | City of Orrville - (OH) | 2935 | Orrville | OH | Wayne | 9 | Conventional Steam Coal | ST |  | S | X | X |  |  | 22 | 0.85 | 20 | 20 | 7 | N |  |  | OP | X | 1 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1953 | hard coal | TRUE | 14381 | City of Painesville | 2936 | Painesville | OH | Lake | 3 | Conventional Steam Coal | ST |  | S | X | X | Painesville | Painesville | 7.5 | 0.8 | 7 | 7 | 2.5 | N |  |  | SB | Y | 1 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N | N |  | OVER |  |  | Y |  | Y | [18 empty] | Y | Y | N
Vintage1965 | hard coal | TRUE | 14381 | City of Painesville | 2936 | Painesville | OH | Lake | 5 | Conventional Steam Coal | ST |  | S | X | X | Painesville | Painesville | 16.5 | 0.85 | 15.5 | 15.5 | 5.5 | N |  |  | OP | X | 1 | 1965 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1990 | hard coal | TRUE | 14381 | City of Painesville | 2936 | Painesville | OH | Lake | 7 | Conventional Steam Coal | ST |  | S | X | X | Painesville | Painesville | 22 | 1 | 17.5 | 17.5 | 6 | N |  |  | OP | X | 2 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1949 | hard coal | TRUE | 14381 | City of Painesville | 2936 | Painesville | OH | Lake | ST2 | Conventional Steam Coal | ST |  | S | X | X | Painesville | Painesville | 7.5 | 0.8 | 7 | 7 | 2.5 | N |  |  | SB | Y | 1 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N | N |  | OVER |  |  | Y |  | Y | [18 empty] | Y | Y | N
Vintage2010 | petroleum | TRUE | 14381 | City of Painesville | 2936 | Painesville | OH | Lake | WPCP1 | Petroleum Liquids | IC |  | S | X | X | Painesville | Painesville | 2 | 0.8 | 1.8 | 1.8 | 1.4 | N |  |  | OP | X | 2 | 2010 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N |  | N
Vintage1989 | petroleum | TRUE | 15095 | City of Piqua - (OH) | 2937 | Piqua Power Plant | OH | Miami | 11 | Petroleum Liquids | GT |  | S | X | X |  |  | 16.3 | 0.9 | 16.5 | 16.5 | 13 | N |  |  | OP | X | 12 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1972 | petroleum | TRUE | 15095 | City of Piqua - (OH) | 2937 | Piqua Power Plant | OH | Miami | 8 | Petroleum Liquids | GT |  | S | X | X |  |  | 20 | 0.85 | 20 | 20 | 14 | N |  |  | OP | X | 1 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N | 0 | 1H |  |  |  | N | [19 empty] | N
Vintage1992 | petroleum | TRUE | 17891 | City of St Marys - (OH) | 2942 | St Marys | OH | Auglaize | 7 | Petroleum Liquids | GT |  | S | X | X |  |  | 14 | 0.8 | 12 | 12 | 1 | N |  |  | SB | N | 8 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO DFO DFO: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1999 | natural gas peaker | TRUE | 17891 | City of St Marys - (OH) | 2942 | St Marys | OH | Auglaize | GT1 | Natural Gas Fired Combustion Turbine | GT |  | J | X | X |  |  | 11 | 0.85 | 10.4 | 10.4 | 1 | N |  |  | SB | Y | 12 | 1999 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: X X X to DFO RC RC
Vintage1983 | petroleum | TRUE | 20977 | City of Woodsfield - (OH) | 2945 | Anadarko | OH | Monroe | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 1 | N |  |  | SB | N | 1 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage1983 | petroleum | TRUE | 20977 | City of Woodsfield - (OH) | 2945 | Anadarko | OH | Monroe | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 0.4 | N |  |  | SB | N | 1 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage1949 | petroleum | TRUE | 20977 | City of Woodsfield - (OH) | 2945 | Anadarko | OH | Monroe | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.4 | N |  |  | SB | N | 1 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage1957 | petroleum | TRUE | 20977 | City of Woodsfield - (OH) | 2945 | Anadarko | OH | Monroe | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 0.4 | N |  |  | SB | N | 1 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG | [5 empty] | 1H | [23 empty] | N |  | N
Vintage1965 | petroleum | TRUE | 20977 | City of Woodsfield - (OH) | 2945 | Anadarko | OH | Monroe | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.4 | N |  |  | SB | N | 1 | 1965 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG | [5 empty] | 1H | [23 empty] | N |  | N
Vintage1971 | petroleum | TRUE | 20977 | City of Woodsfield - (OH) | 2945 | Anadarko | OH | Monroe | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.1 | 0.8 | 2.1 | 2.1 | 2 | N |  |  | SB | N | 1 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG | [5 empty] | 1H | [23 empty] | N |  | N
Vintage2001 | natural gas peaker | TRUE | 14063 | Oklahoma Gas & Electric Co | 2951 | Horseshoe Lake | OK | Oklahoma | 10 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | OKGEHL910 | OKGEHL910 | 60.5 | 0.9 | 43.1 | 43.1 | 43.1 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1958 | natural gas steam turbine | TRUE | 14063 | Oklahoma Gas & Electric Co | 2951 | Horseshoe Lake | OK | Oklahoma | 6 | Natural Gas Steam Turbine | ST |  | S | X | X | OKGEHL6 | OKGEHL6 | 163 | 0.9 | 168 | 168 | 60 | N |  |  | OP | X | 4 | 1958 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: RFO; DFO DFO DFO: NG |  |  | N | N |  | OVER | [23 empty] | Y | Y | Y
Vintage1969 | natural gas steam turbine | TRUE | 14063 | Oklahoma Gas & Electric Co | 2951 | Horseshoe Lake | OK | Oklahoma | 8 | Natural Gas Steam Turbine | ST |  | S | X | X | OKGEHL8 | OKGEHL8 | 443 | 0.9 | 377 | 377 | 80 | N |  |  | OP | X | 6 | 1969 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage2001 | natural gas peaker | TRUE | 14063 | Oklahoma Gas & Electric Co | 2951 | Horseshoe Lake | OK | Oklahoma | 9 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | OKGEHL910 | OKGEHL910 | 60.5 | 0.9 | 44.9 | 44.9 | 44.9 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1963 | natural gas steam turbine | TRUE | 14063 | Oklahoma Gas & Electric Co | 2951 | Horseshoe Lake | OK | Oklahoma | ST7 | Natural Gas Steam Turbine | ST |  | S | X | X | OKGEHL7 | OKGEHL7 | 220 | 0.9 | 211 | 211 | 75 | N |  |  | OP | X | 6 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: RFO; DFO DFO DFO: NG; DFO NG NG: RFO |  |  | N | N |  | OVER | [23 empty] | Y | Y | Y
Vintage1977 | natural gas steam turbine | TRUE | 14063 | Oklahoma Gas & Electric Co | 2952 | Muskogee | OK | Muskogee | 4 | Natural Gas Steam Turbine | ST |  | S | X | X | OKGEMK4 | OKGEMK4 | 572 | 0.9 | 484 | 484 | 200 | N |  |  | OP | X | 12 | 1977 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER |  | N |  |  | N | [18 empty] | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1978 | natural gas steam turbine | TRUE | 14063 | Oklahoma Gas & Electric Co | 2952 | Muskogee | OK | Muskogee | 5 | Natural Gas Steam Turbine | ST |  | S | X | X | OKGEMK5 | OKGEMK5 | 572 | 0.9 | 488 | 488 | 200 | N |  |  | OP | X | 10 | 1978 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER |  | N |  |  | N | [18 empty] | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1984 | hard coal | TRUE | 14063 | Oklahoma Gas & Electric Co | 2952 | Muskogee | OK | Muskogee | 6 | Conventional Steam Coal | ST |  | S | X | X | OKGEMK6 | OKGEMK6 | 572 | 0.9 | 503 | 503 | 200 | N |  |  | OP | X | 6 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage2017 | natural gas peaker | TRUE | 14063 | Oklahoma Gas & Electric Co | 2953 | Mustang | OK | Canadian | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | OKGEMT6 | OKGEMT6 | 66 | 0.9 | 57 | 57 | 40 | N |  |  | OP | X | 9 | 2017 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2017 | natural gas peaker | TRUE | 14063 | Oklahoma Gas & Electric Co | 2953 | Mustang | OK | Canadian | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | OKGEMT7 | OKGEMT7 | 66 | 0.9 | 57 | 57 | 40 | N |  |  | OP | X | 10 | 2017 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2017 | natural gas peaker | TRUE | 14063 | Oklahoma Gas & Electric Co | 2953 | Mustang | OK | Canadian | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | OKGEMT8 | OKGEMT8 | 66 | 0.9 | 58 | 58 | 40 | N |  |  | OP | X | 10 | 2017 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2017 | natural gas peaker | TRUE | 14063 | Oklahoma Gas & Electric Co | 2953 | Mustang | OK | Canadian | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | OKGEMT9 | OKGEMT9 | 66 | 0.9 | 58 | 58 | 40 | N |  |  | OP | X | 11 | 2017 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2017 | natural gas peaker | TRUE | 14063 | Oklahoma Gas & Electric Co | 2953 | Mustang | OK | Canadian | GT5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | OKGEMT10 | OKGEMT10 | 66 | 0.9 | 57 | 57 | 40 | N |  |  | OP | X | 12 | 2017 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2017 | natural gas peaker | TRUE | 14063 | Oklahoma Gas & Electric Co | 2953 | Mustang | OK | Canadian | GT6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | OKGEMT11 | OKGEMT11 | 66 | 0.9 | 57 | 57 | 40 | N |  |  | OP | X | 12 | 2017 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2017 | natural gas peaker | TRUE | 14063 | Oklahoma Gas & Electric Co | 2953 | Mustang | OK | Canadian | GT7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | OKGEMT12 | OKGEMT12 | 66 | 0.9 | 57 | 57 | 40 | N |  |  | OP | X | 12 | 2017 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2015 | solar pv | TRUE | 14063 | Oklahoma Gas & Electric Co | 2953 | Mustang | OK | Canadian | SLR1 | Solar Photovoltaic | PV |  | S | X | X |  |  | 2.5 |  | 2.5 | 2.5 |  | N |  |  | OP | X | 8 | 2015 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUN | [9 empty] | N | [19 empty] | N
Vintage1971 | natural gas steam turbine | TRUE | 14063 | Oklahoma Gas & Electric Co | 2956 | Seminole | OK | Seminole | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | OKGESM1 | OKGESM1 | 567 | 0.9 | 485 | 485 | 70 | N |  |  | OP | X | 3 | 1971 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1973 | natural gas steam turbine | TRUE | 14063 | Oklahoma Gas & Electric Co | 2956 | Seminole | OK | Seminole | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | OKGESM2 | OKGESM2 | 567 | 0.9 | 500 | 500 | 70 | N |  |  | OP | X | 2 | 1973 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1975 | natural gas steam turbine | TRUE | 14063 | Oklahoma Gas & Electric Co | 2956 | Seminole | OK | Seminole | 3 | Natural Gas Steam Turbine | ST |  | S | X | X | OKGESM3 | OKGESM3 | 567 | 0.9 | 498 | 498 | 70 | N |  |  | OP | X | 6 | 1975 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1961 | natural gas combined cycle | TRUE | 15474 | Public Service Co of Oklahoma | 2963 | Northeastern | OK | Rogers | 1 | Natural Gas Fired Combined Cycle | CA | NE1S | S | N | X |  |  | 170 | 0.85 | 146 | 161 | 140 | N |  |  | OP | X | 4 | 1961 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H |  | N | [21 empty] | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage2001 | natural gas combined cycle | TRUE | 15474 | Public Service Co of Oklahoma | 2963 | Northeastern | OK | Rogers | 1A | Natural Gas Fired Combined Cycle | CT | NE1S | S | X | Y |  |  | 178.5 | 0.85 | 149 | 165 | 95 | N |  |  | OP | X | 8 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage2001 | natural gas combined cycle | TRUE | 15474 | Public Service Co of Oklahoma | 2963 | Northeastern | OK | Rogers | 1B | Natural Gas Fired Combined Cycle | CT | NE1S | S | X | Y |  |  | 178.5 | 0.85 | 149 | 165 | 95 | N |  |  | OP | X | 8 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1970 | natural gas steam turbine | TRUE | 15474 | Public Service Co of Oklahoma | 2963 | Northeastern | OK | Rogers | 2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 473 | 0.9 | 434 | 434 | 150 | N |  |  | OP | X | 5 | 1970 |  |  | N | Electric Utility | 1 | [12 empty] | N |  | OVER | [23 empty] | N |  | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1979 | hard coal | TRUE | 15474 | Public Service Co of Oklahoma | 2963 | Northeastern | OK | Rogers | 3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 473 | 0.9 | 460 | 460 | 250 | N |  |  | OP | X | 12 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | N | Y | [17 empty] | Y | Y | N
Vintage1980 | petroleum | TRUE | 15474 | Public Service Co of Oklahoma | 2963 | Northeastern | OK | Rogers | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.5 | 0.9 | 4 | 4 | 2.5 | N |  |  | OP | X | 12 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1952 | natural gas steam turbine | TRUE | 15474 | Public Service Co of Oklahoma | 2964 | Southwestern | OK | Caddo | 1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 84 | 0.95 | 56 | 56 | 20 | N |  |  | OP | X | 7 | 1952 | 6 | 2023 | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1954 | natural gas steam turbine | TRUE | 15474 | Public Service Co of Oklahoma | 2964 | Southwestern | OK | Caddo | 2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 84 | 0.95 | 78 | 78 | 10 | N |  |  | OP | X | 3 | 1954 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1967 | natural gas steam turbine | TRUE | 15474 | Public Service Co of Oklahoma | 2964 | Southwestern | OK | Caddo | 3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 315 | 0.9 | 295 | 295 | 25 | N |  |  | OP | X | 7 | 1967 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage2008 | natural gas peaker | TRUE | 15474 | Public Service Co of Oklahoma | 2964 | Southwestern | OK | Caddo | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 86.5 | 0.85 | 76 | 85 | 51 | N |  |  | OP | X | 2 | 2008 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2008 | natural gas peaker | TRUE | 15474 | Public Service Co of Oklahoma | 2964 | Southwestern | OK | Caddo | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 86.5 | 0.85 | 76 | 85 | 51 | N |  |  | OP | X | 2 | 2008 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1966 | petroleum | TRUE | 15474 | Public Service Co of Oklahoma | 2964 | Southwestern | OK | Caddo | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1.8 | N |  |  | OS | X | 5 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  |  | N |  | 1H | [23 empty] | N
Vintage1956 | natural gas steam turbine | TRUE | 15474 | Public Service Co of Oklahoma | 2965 | Tulsa | OK | Tulsa | 2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 170 | 0.85 | 164 | 164 | 13 | N |  |  | OP | X | 11 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | OVER | [23 empty] | N |  | N
Vintage1958 | natural gas steam turbine | TRUE | 15474 | Public Service Co of Oklahoma | 2965 | Tulsa | OK | Tulsa | 4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 170 | 0.85 | 158 | 158 | 13 | N |  |  | OP | X | 4 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | OVER | [23 empty] | N |  | N
Vintage1967 | petroleum | TRUE | 15474 | Public Service Co of Oklahoma | 2965 | Tulsa | OK | Tulsa | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 8.2 | 0.8 | 8.3 | 8.3 | 8.3 | N |  |  | OP | X | 4 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | OVER | [23 empty] | N
Vintage1975 | natural gas peaker | TRUE | 15474 | Public Service Co of Oklahoma | 2966 | Weleetka | OK | Okfuskee | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 53 | 0.9 | 55 | 66 | 50 | N |  |  | OP | X | 7 | 1975 | 1 | 2025 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1976 | natural gas peaker | TRUE | 15474 | Public Service Co of Oklahoma | 2966 | Weleetka | OK | Okfuskee | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 53 | 0.9 | 53 | 66 | 50 | N |  |  | OP | X | 9 | 1976 | 1 | 2025 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage1963 | petroleum | TRUE | 15474 | Public Service Co of Oklahoma | 2966 | Weleetka | OK | Okfuskee | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 4 | 0.9 | 4 | 4 | 4 | N |  |  | OP | X | 10 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 12H | [23 empty] | N |  | N
Vintage1956 | petroleum | TRUE | 4667 | City of Cushing - (OK) | 2975 | Cushing | OK | Payne | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 1.8 | 1.8 | 1.6 | N |  |  | OP | X | 6 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 10M | [23 empty] | Y | Y | N
Vintage1972 | petroleum | TRUE | 4667 | City of Cushing - (OK) | 2975 | Cushing | OK | Payne | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.5 | 0.8 | 4 | 4 | 2 | N |  |  | OP | X | 12 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 10M | [23 empty] | Y | Y | N
Vintage1988 | petroleum | TRUE | 4667 | City of Cushing - (OK) | 2975 | Cushing | OK | Payne | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 6.3 | 0.8 | 6.3 | 6.3 | 3.5 | N |  |  | OP | X | 6 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 10M | [23 empty] | Y | Y | N
Vintage1949 | petroleum | TRUE | 4667 | City of Cushing - (OK) | 2975 | Cushing | OK | Payne | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 6 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 10M | [23 empty] | Y | Y | N
Vintage1936 | petroleum | TRUE | 4667 | City of Cushing - (OK) | 2975 | Cushing | OK | Payne | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.4 | 0.4 | 0.3 | N |  |  | OP | X | 6 | 1936 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 10M | [23 empty] | Y | Y | N
Vintage1936 | petroleum | TRUE | 4667 | City of Cushing - (OK) | 2975 | Cushing | OK | Payne | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.4 | 0.4 | 0.3 | N |  |  | OP | X | 8 | 1936 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 10M | [23 empty] | Y | Y | N
Vintage1936 | petroleum | TRUE | 4667 | City of Cushing - (OK) | 2975 | Cushing | OK | Payne | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.4 | 0.4 | 0.3 | N |  |  | OP | X | 6 | 1936 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 10M | [23 empty] | Y | Y | N
Vintage1939 | petroleum | TRUE | 4667 | City of Cushing - (OK) | 2975 | Cushing | OK | Payne | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.6 | 0.6 | 0.6 | N |  |  | OP | X | 7 | 1939 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 10M | [23 empty] | Y | Y | N
Vintage1956 | petroleum | TRUE | 4667 | City of Cushing - (OK) | 2975 | Cushing | OK | Payne | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 1.9 | 1.9 | 1.9 | N |  |  | OP | X | 6 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 10M | [23 empty] | Y | Y | N
Vintage1956 | petroleum | TRUE | 4667 | City of Cushing - (OK) | 2975 | Cushing | OK | Payne | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 1.9 | 1.9 | 1.9 | N |  |  | OP | X | 6 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 10M | [23 empty] | Y | Y | N
Vintage1965 | petroleum | TRUE | 4667 | City of Cushing - (OK) | 2975 | Cushing | OK | Payne | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.8 | 2.7 | 2.7 | 2.2 | N |  |  | OP | X | 2 | 1965 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 10M | [23 empty] | Y | Y | N
Vintage1964 | hydro | TRUE | 7490 | Grand River Dam Authority | 2980 | Markham | OK | Mayes | 1 | Conventional Hydroelectric | HY |  | S | X | X | GRDAKERR_HYDUN1 | GRDAKERR_HYDUN1_RA | 32.1 | 0.93 | 32 | 32 | 18 | N |  |  | OP | X | 5 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1964 | hydro | TRUE | 7490 | Grand River Dam Authority | 2980 | Markham | OK | Mayes | 2 | Conventional Hydroelectric | HY |  | S | X | X | GRDAKERR_HYDUN2 | GRDAKERR_HYDUN2_RA | 32.1 | 0.93 | 32 | 32 | 18 | N |  |  | OP | X | 5 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1964 | hydro | TRUE | 7490 | Grand River Dam Authority | 2980 | Markham | OK | Mayes | 3 | Conventional Hydroelectric | HY |  | S | X | X | GRDAKERR_HYDUN3 | GRDAKERR_HYDUN3_RA | 32.1 | 0.93 | 32 | 32 | 18 | N |  |  | OP | X | 5 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1964 | hydro | TRUE | 7490 | Grand River Dam Authority | 2980 | Markham | OK | Mayes | 4 | Conventional Hydroelectric | HY |  | S | X | X | GRDAKERR_HYDUN4 | GRDAKERR_HYDUN4_RA | 32.1 | 0.93 | 32 | 32 | 18 | N |  |  | OP | X | 5 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1940 | hydro | TRUE | 7490 | Grand River Dam Authority | 2981 | Pensacola | OK | Mayes | 1 | Conventional Hydroelectric | HY |  | S | X | X | GRDAPENSA1UN1 | GRDAPENSA1UN1_RA | 21.6 | 0.9 | 18.6 | 21 | 5 | N |  |  | OP | X | 8 | 1940 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1940 | hydro | TRUE | 7490 | Grand River Dam Authority | 2981 | Pensacola | OK | Mayes | 2 | Conventional Hydroelectric | HY |  | S | X | X | GRDAPENSA1UN2 | GRDAPENSA1UN2_RA | 21.6 | 0.9 | 18.2 | 21 | 5 | N |  |  | OP | X | 8 | 1940 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1940 | hydro | TRUE | 7490 | Grand River Dam Authority | 2981 | Pensacola | OK | Mayes | 3 | Conventional Hydroelectric | HY |  | S | X | X | GRDAPENSA1UN3 | GRDAPENSA1UN3_RA | 21.6 | 0.9 | 18.3 | 21 | 5 | N |  |  | OP | X | 8 | 1940 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1940 | hydro | TRUE | 7490 | Grand River Dam Authority | 2981 | Pensacola | OK | Mayes | 4 | Conventional Hydroelectric | HY |  | S | X | X | GRDAPENSA1UN4 | GRDAPENSA1UN4_RA | 21.6 | 0.9 | 18.6 | 21 | 5 | N |  |  | OP | X | 8 | 1940 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1946 | hydro | TRUE | 7490 | Grand River Dam Authority | 2981 | Pensacola | OK | Mayes | 5 | Conventional Hydroelectric | HY |  | S | X | X | GRDAPENSA1UN5 | GRDAPENSA1UN5_RA | 21.6 | 0.9 | 18.1 | 21 | 5 | N |  |  | OP | X | 8 | 1946 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1946 | hydro | TRUE | 7490 | Grand River Dam Authority | 2981 | Pensacola | OK | Mayes | 6 | Conventional Hydroelectric | HY |  | S | X | X | GRDAPENSA1UN6 | GRDAPENSA1UN6_RA | 21.6 | 0.9 | 18.4 | 21 | 5 | N |  |  | OP | X | 8 | 1946 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1940 | hydro | TRUE | 7490 | Grand River Dam Authority | 2981 | Pensacola | OK | Mayes | A | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.5 | N |  |  | OS | X | 8 | 1940 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1968 | other | TRUE | 7490 | Grand River Dam Authority | 2982 | Salina | OK | Mayes | 1 | Hydroelectric Pumped Storage | PS |  | S | X | X | GRDASALINA1UN1 | GRDASALINA1UN1_RA | 43.2 | 0.9 | 43 | 43 | 14 | N |  |  | OP | X | 5 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [7 empty] | 6 | 6 | 1 | 2025 | [9 empty] | N |  |  | N
Vintage1968 | other | TRUE | 7490 | Grand River Dam Authority | 2982 | Salina | OK | Mayes | 2 | Hydroelectric Pumped Storage | PS |  | S | X | X | GRDASALINA1UN2 | GRDASALINA1UN2_RA | 43.2 | 0.9 | 43 | 43 | 14 | N |  |  | OP | X | 5 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [7 empty] | 6 | 6 | 6 | 2025 | [9 empty] | N |  |  | N
Vintage1968 | other | TRUE | 7490 | Grand River Dam Authority | 2982 | Salina | OK | Mayes | 3 | Hydroelectric Pumped Storage | PS |  | S | X | X | GRDASALINA1UN3 | GRDASALINA1UN3_RA | 43.2 | 0.9 | 43 | 43 | 14 | N |  |  | OP | X | 5 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [7 empty] | 6 | 6 | 1 | 2026 | [9 empty] | N |  |  | N
Vintage1971 | other | TRUE | 7490 | Grand River Dam Authority | 2982 | Salina | OK | Mayes | 4 | Hydroelectric Pumped Storage | PS |  | S | X | X | GRDASALINA1UN4 | GRDASALINA1UN4_RA | 43.2 | 0.9 | 43 | 43 | 14 | N |  |  | OP | X | 5 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [7 empty] | 6 | 6 | 6 | 2026 | [9 empty] | N |  |  | N
Vintage1971 | other | TRUE | 7490 | Grand River Dam Authority | 2982 | Salina | OK | Mayes | 5 | Hydroelectric Pumped Storage | PS |  | S | X | X | GRDASALINA1UN5 | GRDASALINA1UN5_RA | 43.2 | 0.9 | 43 | 43 | 14 | N |  |  | OP | X | 5 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1971 | other | TRUE | 7490 | Grand River Dam Authority | 2982 | Salina | OK | Mayes | 6 | Hydroelectric Pumped Storage | PS |  | S | X | X | GRDASALINA1UN6 | GRDASALINA1UN6_RA | 43.2 | 0.9 | 43 | 43 | 14 | N |  |  | OP | X | 5 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1968 | hydro | TRUE | 27470 | USCE-Tulsa District | 2984 | Keystone Dam | OK | Tulsa | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 35 | 0.95 | 40 | 40 | 25 | N |  |  | OA | X | 5 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1968 | hydro | TRUE | 27470 | USCE-Tulsa District | 2984 | Keystone Dam | OK | Tulsa | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 35 | 0.95 | 40 | 40 | 25 | N |  |  | OP | X | 5 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1971 | hydro | TRUE | 27470 | USCE-Tulsa District | 2985 | Robert S Kerr | OK | Sequoyah | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 27.5 | 0.95 | 28 | 28 | 10 | N |  |  | OP | X | 10 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [7 empty] | 6 | 6 | 12 | 2025
Vintage1971 | hydro | TRUE | 27470 | USCE-Tulsa District | 2985 | Robert S Kerr | OK | Sequoyah | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 27.5 | 0.95 | 26 | 26 | 10 | N |  |  | OP | X | 7 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [7 empty] | 8 | 8 | 12 | 2025
Vintage1971 | hydro | TRUE | 27470 | USCE-Tulsa District | 2985 | Robert S Kerr | OK | Sequoyah | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 27.5 | 0.95 | 31.6 | 31.6 | 10 | N |  |  | OS | X | 9 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [7 empty] | 6 | 6 | 12 | 2025
Vintage1971 | hydro | TRUE | 27470 | USCE-Tulsa District | 2985 | Robert S Kerr | OK | Sequoyah | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 27.5 | 0.95 | 20 | 20 | 10 | N |  |  | OP | X | 11 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [7 empty] | 14 | 14 | 12 | 2025
Vintage1965 | natural gas peaker | TRUE | 10320 | City of Kingfisher - (OK) | 2986 | Kingfisher | OK | Kingfisher | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.8 | 0.8 | 2.9 | 2.9 | 2.5 | N |  |  | OP | X | 1 | 1965 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1959 | natural gas peaker | TRUE | 10320 | City of Kingfisher - (OK) | 2986 | Kingfisher | OK | Kingfisher | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.2 | 1.2 | 1 | N |  |  | OP | X | 1 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1970 | natural gas peaker | TRUE | 10320 | City of Kingfisher - (OK) | 2986 | Kingfisher | OK | Kingfisher | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.1 | 0.8 | 3 | 3 | 2.5 | N |  |  | OP | X | 1 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1954 | natural gas peaker | TRUE | 10320 | City of Kingfisher - (OK) | 2986 | Kingfisher | OK | Kingfisher | IC1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1 | 1 | 1 | N |  |  | OP | X | 1 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1954 | natural gas peaker | TRUE | 10320 | City of Kingfisher - (OK) | 2986 | Kingfisher | OK | Kingfisher | IC2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.6 | 0.6 | 0.6 | N |  |  | OP | X | 1 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1973 | hydro | TRUE | 27470 | USCE-Tulsa District | 2987 | Webbers Falls | OK | Muskogee | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 25 | 0.95 | 25 | 25 | 7 | N |  |  | OS | X | 8 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1973 | hydro | TRUE | 27470 | USCE-Tulsa District | 2987 | Webbers Falls | OK | Muskogee | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 25 | 0.95 | 25 | 25 | 7 | N |  |  | OP | X | 9 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1973 | hydro | TRUE | 27470 | USCE-Tulsa District | 2987 | Webbers Falls | OK | Muskogee | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 25 | 0.95 | 25 | 25 | 7 | N |  |  | OP | X | 11 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1946 | natural gas peaker | TRUE | 11566 | City of Mangum - (OK) | 2991 | Mangum | OK | Greer | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.1 | 0.8 | 0.9 | 0.9 | 0.5 | N |  |  | OS | X | 1 | 1946 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1956 | natural gas peaker | TRUE | 11566 | City of Mangum - (OK) | 2991 | Mangum | OK | Greer | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.2 | 1.2 | 0.6 | N |  |  | OP | X | 1 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1963 | natural gas peaker | TRUE | 11566 | City of Mangum - (OK) | 2991 | Mangum | OK | Greer | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2 | 0.8 | 1.7 | 1.7 | 0.6 | N |  |  | OP | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1969 | natural gas peaker | TRUE | 11566 | City of Mangum - (OK) | 2991 | Mangum | OK | Greer | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.1 | 0.8 | 1.6 | 1.6 | 0.8 | N |  |  | OP | X | 11 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1949 | petroleum | TRUE | 14582 | City of Pawhuska - (OK) | 2995 | Pawhuska | OK | Osage | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.4 | 0.9 | 1.1 | 1.1 | 0.3 | N |  |  | OS | X | 9 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1954 | petroleum | TRUE | 14582 | City of Pawhuska - (OK) | 2995 | Pawhuska | OK | Osage | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.9 | 1.2 | 1.2 | 0.3 | N |  |  | OP | X | 8 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1966 | petroleum | TRUE | 14582 | City of Pawhuska - (OK) | 2995 | Pawhuska | OK | Osage | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.1 | 0.9 | 2.5 | 2.5 | 0.3 | N |  |  | OP | X | 8 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1960 | petroleum | TRUE | 14582 | City of Pawhuska - (OK) | 2995 | Pawhuska | OK | Osage | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.9 | 2 | 2 | 0.3 | N |  |  | OP | X | 9 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2004 | petroleum | TRUE | 18125 | Stillwater Utilities Authority | 3000 | Boomer Lake Station | OK | Payne | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | OP | X | 5 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage2004 | petroleum | TRUE | 18125 | Stillwater Utilities Authority | 3000 | Boomer Lake Station | OK | Payne | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | OP | X | 5 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2004 | petroleum | TRUE | 18125 | Stillwater Utilities Authority | 3000 | Boomer Lake Station | OK | Payne | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | OP | X | 5 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1953 | hydro | TRUE | 27470 | USCE-Tulsa District | 3003 | Fort Gibson | OK | Cherokee | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 11.2 | 0.95 | 12.9 | 12.9 | 4 | N |  |  | OP | X | 3 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H
Vintage1953 | hydro | TRUE | 27470 | USCE-Tulsa District | 3003 | Fort Gibson | OK | Cherokee | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 11.2 | 0.95 | 12.9 | 12.9 | 4 | N |  |  | OP | X | 3 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H
Vintage1953 | hydro | TRUE | 27470 | USCE-Tulsa District | 3003 | Fort Gibson | OK | Cherokee | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 11.2 | 0.95 | 12.9 | 12.9 | 4 | N |  |  | OP | X | 5 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H
Vintage1953 | hydro | TRUE | 27470 | USCE-Tulsa District | 3003 | Fort Gibson | OK | Cherokee | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 11.2 | 0.95 | 12.5 | 12.5 | 4 | N |  |  | OP | X | 9 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H
Vintage1953 | hydro | TRUE | 27470 | USCE-Tulsa District | 3004 | Tenkiller Ferry | OK | Sequoyah | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 19.5 | 0.95 | 21 | 21 | 8 | N |  |  | OP | X | 11 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H
Vintage1953 | hydro | TRUE | 27470 | USCE-Tulsa District | 3004 | Tenkiller Ferry | OK | Sequoyah | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 19.5 | 0.95 | 21 | 21 | 8 | N |  |  | OP | X | 12 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H
Vintage1953 | natural gas steam turbine | TRUE | 20447 | Western Farmers Elec Coop, Inc | 3006 | Anadarko Plant | OK | Caddo | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | WFEC_ANA_STEAM_PLANT1 | WFEC_ANA_STEAM_PLANT1 | 17.3 | 0.85 | 12 | 12 | 6 | N |  |  | SB | Y | 8 | 1953 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage2009 | natural gas peaker | TRUE | 20447 | Western Farmers Elec Coop, Inc | 3006 | Anadarko Plant | OK | Caddo | 10 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | WFEC_ANA_ORME_10 | WFEC_ANA_ORME_10 | 45 | 0.85 | 45 | 45 | 15 | N |  |  | OP | X | 6 | 2009 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage2009 | natural gas peaker | TRUE | 20447 | Western Farmers Elec Coop, Inc | 3006 | Anadarko Plant | OK | Caddo | 11 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | WFEC_ANA_ORME_11 | WFEC_ANA_ORME_11 | 45 | 0.85 | 45 | 45 | 15 | N |  |  | OP | X | 6 | 2009 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1953 | natural gas steam turbine | TRUE | 20447 | Western Farmers Elec Coop, Inc | 3006 | Anadarko Plant | OK | Caddo | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | WFEC_ANA_STEAM_PLANT2 | WFEC_ANA_STEAM_PLANT2 | 17.3 | 0.9 | 12 | 12 | 6 | N |  |  | SB | Y | 8 | 1953 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1959 | natural gas steam turbine | TRUE | 20447 | Western Farmers Elec Coop, Inc | 3006 | Anadarko Plant | OK | Caddo | 3 | Natural Gas Steam Turbine | ST |  | S | X | X | WFEC_ANA_STEAM_PLANT3 | WFEC_ANA_STEAM_PLANT3 | 50 | 0.85 | 44 | 44 | 15 | N |  |  | SB | Y | 8 | 1959 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1977 | natural gas combined cycle | TRUE | 20447 | Western Farmers Elec Coop, Inc | 3006 | Anadarko Plant | OK | Caddo | 4 | Natural Gas Fired Combined Cycle | CS |  | S | N | N | WFEC_ANA_COMB_CYC_4 | WFEC_ANA_COMB_CYC_4 | 105.1 | 0.9 | 94 | 94 | 80 | N |  |  | OP | X | 12 | 1977 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1977 | natural gas combined cycle | TRUE | 20447 | Western Farmers Elec Coop, Inc | 3006 | Anadarko Plant | OK | Caddo | 5 | Natural Gas Fired Combined Cycle | CS |  | S | N | N | WFEC_ANA_COMB_CYC_5 | WFEC_ANA_COMB_CYC_5 | 105.1 | 0.9 | 94 | 94 | 80 | N |  |  | OP | X | 11 | 1977 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1977 | natural gas combined cycle | TRUE | 20447 | Western Farmers Elec Coop, Inc | 3006 | Anadarko Plant | OK | Caddo | 6 | Natural Gas Fired Combined Cycle | CS |  | S | N | N | WFEC_ANA_COMB_CYC_6 | WFEC_ANA_COMB_CYC_6 | 105.1 | 0.9 | 94 | 94 | 80 | N |  |  | OP | X | 12 | 1977 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage2009 | natural gas peaker | TRUE | 20447 | Western Farmers Elec Coop, Inc | 3006 | Anadarko Plant | OK | Caddo | 9 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | WFEC_ANA_ORME_9 | WFEC_ANA_ORME_9 | 45 | 0.85 | 45 | 45 | 15 | N |  |  | OP | X | 6 | 2009 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1964 | natural gas steam turbine | TRUE | 20447 | Western Farmers Elec Coop, Inc | 3008 | Mooreland | OK | Woodward | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | WFEC_MOORELAND_1 | WFEC_MOORELAND_1 | 45 | 0.85 | 50 | 50 | 20 | N |  |  | OP | X | 3 | 1964 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1968 | natural gas steam turbine | TRUE | 20447 | Western Farmers Elec Coop, Inc | 3008 | Mooreland | OK | Woodward | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | WFEC_MOORELAND_2 | WFEC_MOORELAND_2 | 125 | 0.85 | 132 | 132 | 30 | N |  |  | OP | X | 7 | 1968 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1975 | natural gas steam turbine | TRUE | 20447 | Western Farmers Elec Coop, Inc | 3008 | Mooreland | OK | Woodward | 3 | Natural Gas Steam Turbine | ST |  | S | X | X | WFEC_MOORELAND_3 | WFEC_MOORELAND_3 | 135 | 0.85 | 140 | 140 | 30 | N |  |  | OP | X | 7 | 1975 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1967 | hydro | TRUE | 9191 | Idaho Power Co | 3013 | Hells Canyon | OR | Wallowa | 1 | Conventional Hydroelectric | HY |  | S | X | X | HCPR_2_TOT_GEN-APND | HCPR_2_TOT_GEN | 130.5 | 0.9 | 145.5 | 146.6 | 0 | N |  |  | OP | X | 12 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | Y | 1 | 2022 | N
Vintage1967 | hydro | TRUE | 9191 | Idaho Power Co | 3013 | Hells Canyon | OR | Wallowa | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 130.5 | 0.9 | 146.8 | 148.2 | 0 | N |  |  | OP | X | 12 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1967 | hydro | TRUE | 9191 | Idaho Power Co | 3013 | Hells Canyon | OR | Wallowa | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 130.5 | 0.9 | 131.8 | 131.2 | 0 | N |  |  | OA | X | 10 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | Y | 1 | 2023 | N
Vintage1961 | hydro | TRUE | 9191 | Idaho Power Co | 3014 | Oxbow (OR) | OR | Baker | 1 | Conventional Hydroelectric | HY |  | S | X | X | OBPR_GNODE011 | OBPR_2_G011 | 47.5 | 0.9 | 52.9 | 53.4 | 0 | N |  |  | OP | X | 7 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | Y | 7 | 2024 | N
Vintage1961 | hydro | TRUE | 9191 | Idaho Power Co | 3014 | Oxbow (OR) | OR | Baker | 2 | Conventional Hydroelectric | HY |  | S | X | X | OBPR_GNODE012 | OBPR_2_G012 | 47.5 | 0.9 | 52.2 | 53.3 | 0 | N |  |  | OP | X | 7 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | Y | 7 | 2025 | N
Vintage1961 | hydro | TRUE | 9191 | Idaho Power Co | 3014 | Oxbow (OR) | OR | Baker | 3 | Conventional Hydroelectric | HY |  | S | X | X | OBPR_GNODE013 | OBPR_2_G013 | 47.5 | 0.9 | 53 | 53.8 | 0 | N |  |  | OP | X | 9 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | Y | 7 | 2026 | N
Vintage1961 | hydro | TRUE | 9191 | Idaho Power Co | 3014 | Oxbow (OR) | OR | Baker | 4 | Conventional Hydroelectric | HY |  | S | X | X | OBPR_GNODE014 | OBPR_2_G014 | 47.5 | 0.9 | 52 | 53 | 0 | N |  |  | OP | X | 11 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | Y | 7 | 2028 | N
Vintage1953 | hydro | TRUE | 14354 | PacifiCorp | 3020 | Clearwater 1 | OR | Douglas | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.85 | 17.9 | 17.9 | 0 | N |  |  | OP | X | 6 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1953 | hydro | TRUE | 14354 | PacifiCorp | 3021 | Clearwater 2 | OR | Douglas | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 26 | 0.85 | 31 | 31 | 0 | N |  |  | OP | X | 11 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1957 | hydro | TRUE | 14354 | PacifiCorp | 3024 | Eagle Point | OR | Jackson | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.8 | 0.9 | 2.8 | 2.8 | 0 | N |  |  | OP | X | 11 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1924 | hydro | TRUE | 14354 | PacifiCorp | 3025 | East Side | OR | Klamath | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.2 | 1 | 3 | 3 | 0 | N |  |  | OP | X | 8 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1952 | hydro | TRUE | 14354 | PacifiCorp | 3026 | Fish Creek | OR | Douglas | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 11 | 0.85 | 10.4 | 10.4 | 0 | N |  |  | OP | X | 6 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1958 | hydro | TRUE | 14354 | PacifiCorp | 3028 | John C Boyle | OR | Klamath | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 50.3 | 0.95 | 50.4 | 50.4 | 0 | N |  |  | OP | X | 10 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1958 | hydro | TRUE | 14354 | PacifiCorp | 3028 | John C Boyle | OR | Klamath | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 48.4 | 0.95 | 47.6 | 47.6 | 0 | N |  |  | OP | X | 10 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1955 | hydro | TRUE | 14354 | PacifiCorp | 3029 | Lemolo 1 | OR | Douglas | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 32 | 0.95 | 32 | 32 | 0 | N |  |  | OP | X | 7 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1912 | hydro | TRUE | 14354 | PacifiCorp | 3032 | Prospect 1 | OR | Jackson | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.8 | 0.8 | 4.6 | 4.6 | 0 | N |  |  | OP | X | 1 | 1912 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1928 | hydro | TRUE | 14354 | PacifiCorp | 3033 | Prospect 2 | OR | Jackson | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 16 | 0.8 | 18 | 18 | 0 | N |  |  | OP | X | 1 | 1928 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1928 | hydro | TRUE | 14354 | PacifiCorp | 3033 | Prospect 2 | OR | Jackson | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 16 | 0.8 | 18 | 18 | 0 | N |  |  | OP | X | 2 | 1928 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1932 | hydro | TRUE | 14354 | PacifiCorp | 3034 | Prospect 3 | OR | Jackson | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7.2 | 0.8 | 7.7 | 7.7 | 0 | N |  |  | OP | X | 4 | 1932 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1944 | hydro | TRUE | 14354 | PacifiCorp | 3035 | Prospect 4 | OR | Jackson | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.8 | 0.9 | 0.9 | 0 | N |  |  | OP | X | 11 | 1944 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1951 | hydro | TRUE | 14354 | PacifiCorp | 3036 | Slide Creek | OR | Douglas | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18 | 0.85 | 18 | 18 | 0 | N |  |  | OP | X | 7 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1952 | hydro | TRUE | 14354 | PacifiCorp | 3037 | Soda Springs | OR | Douglas | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 11 | 0.85 | 11.6 | 11.6 | 0 | N |  |  | OP | X | 3 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1950 | hydro | TRUE | 14354 | PacifiCorp | 3040 | Toketee Falls | OR | Douglas | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 14.2 | 0.85 | 15 | 15 | 0 | N |  |  | OP | X | 2 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1949 | hydro | TRUE | 14354 | PacifiCorp | 3040 | Toketee Falls | OR | Douglas | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 14.2 | 0.85 | 15 | 15 | 0 | N |  |  | OP | X | 12 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1950 | hydro | TRUE | 14354 | PacifiCorp | 3040 | Toketee Falls | OR | Douglas | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 14.2 | 0.85 | 15 | 15 | 0 | N |  |  | OP | X | 3 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1921 | hydro | TRUE | 14354 | PacifiCorp | 3041 | Wallowa Falls | OR | Wallowa | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0 | N |  |  | OP | X | 7 | 1921 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1958 | hydro | TRUE | 15248 | Portland General Electric Co | 3045 | Faraday | OR | Clackamas | 6 | Conventional Hydroelectric | HY |  | S | X | X | FYP1_7_GNODE1 |  | 19.2 | 0.93 | 23.9 | 23.9 | 5 | N |  |  | OA | X | 9 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1958 | hydro | TRUE | 15248 | Portland General Electric Co | 3047 | North Fork | OR | Clackamas | 1 | Conventional Hydroelectric | HY |  | S | X | X | NFP1_1_GNODE1 |  | 19.2 | 0.8 | 27 | 27 | 4 | N |  |  | OP | X | 12 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1958 | hydro | TRUE | 15248 | Portland General Electric Co | 3047 | North Fork | OR | Clackamas | 2 | Conventional Hydroelectric | HY |  | S | X | X | NFP1_1_GNODE1 |  | 21.6 | 0.9 | 31 | 31 | 4 | N |  |  | OP | X | 11 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1957 | hydro | TRUE | 15248 | Portland General Electric Co | 3048 | Pelton | OR | Jefferson | 1 | Conventional Hydroelectric | HY |  | J | X | X | PNP1_2_GNODE1-3 | PNP-RBP_2_PELRB | 45 | 0.9 | 38 | 38 | 10 | N |  |  | OP | X | 12 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1958 | hydro | TRUE | 15248 | Portland General Electric Co | 3048 | Pelton | OR | Jefferson | 2 | Conventional Hydroelectric | HY |  | J | X | X | PNP1_2_GNODE1-3 | PNP-RBP_2_PELRB | 32.4 | 0.9 | 36 | 36 | 10 | N |  |  | OP | X | 3 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1958 | hydro | TRUE | 15248 | Portland General Electric Co | 3048 | Pelton | OR | Jefferson | 3 | Conventional Hydroelectric | HY |  | J | X | X | PNP1_2_GNODE1-3 | PNP-RBP_2_PELRB | 32.4 | 0.9 | 36 | 36 | 10 | N |  |  | OP | X | 4 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1911 | hydro | TRUE | 15248 | Portland General Electric Co | 3049 | River Mill | OR | Clackamas | 1 | Conventional Hydroelectric | HY |  | S | X | X | RMP1_7_GNODE1 |  | 3.3 | 0.9 | 4.3 | 4.3 | 2 | N |  |  | OP | X | 11 | 1911 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1911 | hydro | TRUE | 15248 | Portland General Electric Co | 3049 | River Mill | OR | Clackamas | 2 | Conventional Hydroelectric | HY |  | S | X | X | RMP1_7_GNODE1 |  | 3.3 | 0.9 | 4.3 | 4.3 | 2 | N |  |  | OP | X | 12 | 1911 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1912 | hydro | TRUE | 15248 | Portland General Electric Co | 3049 | River Mill | OR | Clackamas | 3 | Conventional Hydroelectric | HY |  | S | X | X | RMP1_7_GNODE1 |  | 3.3 | 0.9 | 4.3 | 4.3 | 2 | N |  |  | OP | X | 1 | 1912 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1927 | hydro | TRUE | 15248 | Portland General Electric Co | 3049 | River Mill | OR | Clackamas | 4 | Conventional Hydroelectric | HY |  | S | X | X | RMP1_7_GNODE1 |  | 3.9 | 0.9 | 5.2 | 5.2 | 3 | N |  |  | OP | X | 12 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1952 | hydro | TRUE | 15248 | Portland General Electric Co | 3049 | River Mill | OR | Clackamas | 5 | Conventional Hydroelectric | HY |  | S | X | X | RMP1_7_GNODE1 |  | 5 | 1 | 6.6 | 6.6 | 2.5 | N |  |  | OP | X | 5 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1964 | hydro | TRUE | 15248 | Portland General Electric Co | 3050 | Round Butte | OR | Jefferson | 1 | Conventional Hydroelectric | HY |  | J | X | X | RBP1_2_GNODE1-3 | PNP-RBP_2_PELRB | 112.5 | 0.9 | 110 | 110 | 1 | N |  |  | OP | X | 8 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1964 | hydro | TRUE | 15248 | Portland General Electric Co | 3050 | Round Butte | OR | Jefferson | 2 | Conventional Hydroelectric | HY |  | J | X | X | RBP1_2_GNODE1-3 | PNP-RBP_2_PELRB | 130 | 0.9 | 121.5 | 121.5 | 1 | N |  |  | OP | X | 11 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1964 | hydro | TRUE | 15248 | Portland General Electric Co | 3050 | Round Butte | OR | Jefferson | 3 | Conventional Hydroelectric | HY |  | J | X | X | RBP1_2_GNODE1-3 | PNP-RBP_2_PELRB | 130 | 0.9 | 121.5 | 121.5 | 1 | N |  |  | OP | X | 10 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1952 | hydro | TRUE | 15248 | Portland General Electric Co | 3053 | Sullivan | OR | Clackamas | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.706 | 1.4 | 1.4 | 0 | N |  |  | OP | X | 12 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1952 | hydro | TRUE | 15248 | Portland General Electric Co | 3053 | Sullivan | OR | Clackamas | 10 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.706 | 1.5 | 1.5 | 0.9 | N |  |  | OP | X | 12 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1952 | hydro | TRUE | 15248 | Portland General Electric Co | 3053 | Sullivan | OR | Clackamas | 11 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.706 | 1.4 | 1.4 | 0.9 | N |  |  | OP | X | 12 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1952 | hydro | TRUE | 15248 | Portland General Electric Co | 3053 | Sullivan | OR | Clackamas | 12 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.706 | 1.4 | 1.4 | 0.9 | N |  |  | OP | X | 12 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1952 | hydro | TRUE | 15248 | Portland General Electric Co | 3053 | Sullivan | OR | Clackamas | 13 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.706 | 1.2 | 1.2 | 0 | N |  |  | OP | X | 12 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1952 | hydro | TRUE | 15248 | Portland General Electric Co | 3053 | Sullivan | OR | Clackamas | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.706 | 1.5 | 1.5 | 0.9 | N |  |  | OP | X | 12 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1952 | hydro | TRUE | 15248 | Portland General Electric Co | 3053 | Sullivan | OR | Clackamas | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.706 | 1.5 | 1.5 | 0.9 | N |  |  | OP | X | 12 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1952 | hydro | TRUE | 15248 | Portland General Electric Co | 3053 | Sullivan | OR | Clackamas | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.706 | 1.5 | 1.5 | 0.9 | N |  |  | OP | X | 12 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1952 | hydro | TRUE | 15248 | Portland General Electric Co | 3053 | Sullivan | OR | Clackamas | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.706 | 1.5 | 1.5 | 0.9 | N |  |  | OP | X | 12 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1952 | hydro | TRUE | 15248 | Portland General Electric Co | 3053 | Sullivan | OR | Clackamas | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.706 | 1.5 | 1.5 | 0.9 | N |  |  | OP | X | 12 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1952 | hydro | TRUE | 15248 | Portland General Electric Co | 3053 | Sullivan | OR | Clackamas | 7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.706 | 1.5 | 1.5 | 0.9 | N |  |  | OP | X | 12 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1952 | hydro | TRUE | 15248 | Portland General Electric Co | 3053 | Sullivan | OR | Clackamas | 8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.706 | 1.4 | 1.4 | 0.9 | N |  |  | OP | X | 12 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1924 | hydro | TRUE | 15248 | Portland General Electric Co | 3053 | Sullivan | OR | Clackamas | 9 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.5 | N |  |  | OP | X | 5 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1963 | hydro | TRUE | 6013 | Eugene Water & Electric Board | 3067 | Carmen Smith | OR | Linn | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 52.2 | 0.95 | 50 | 50 | 12 | N |  |  | OP | X | 8 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1963 | hydro | TRUE | 6013 | Eugene Water & Electric Board | 3067 | Carmen Smith | OR | Linn | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 52.2 | 0.95 | 50 | 50 | 12 | N |  |  | OA | X | 8 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1963 | hydro | TRUE | 6013 | Eugene Water & Electric Board | 3067 | Carmen Smith | OR | Linn | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9.9 | 0.95 | 3.8 | 6.5 | 2 | N |  |  | OP | X | 1 | 1963 | 12 | 2026 | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1930 | hydro | TRUE | 6013 | Eugene Water & Electric Board | 3068 | Leaburg | OR | Lane | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8.4 | 0.8 | 4 | 8 | 2 | N |  |  | OS | X | 1 | 1930 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 12H | [23 empty] | N
Vintage1950 | hydro | TRUE | 6013 | Eugene Water & Electric Board | 3068 | Leaburg | OR | Lane | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7.5 | 0.8 | 4 | 7.5 | 2 | N |  |  | OS | X | 1 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 12H | [23 empty] | N
Vintage1949 | hydro | TRUE | 6013 | Eugene Water & Electric Board | 3071 | Walterville | OR | Lane | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8 | 0.85 | 7.5 | 7.5 | 2 | N |  |  | OP | X | 1 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 1H | [23 empty] | N
Vintage1954 | hydro | TRUE | 19400 | USACE Northwestern Division | 3074 | Big Cliff | OR | Marion | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18 | 0.9 | 21 | 21 | 18 | N |  |  | OP | X | 12 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1938 | hydro | TRUE | 19400 | USACE Northwestern Division | 3075 | Bonneville | OR | Multnomah | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 53.5 | 0.9 | 53.5 | 53.5 | 13.2 | N |  |  | OP | X | 7 | 1938 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1944 | hydro | TRUE | 19400 | USACE Northwestern Division | 3075 | Bonneville | OR | Multnomah | 10 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 62.1 | 0.9 | 54 | 54 | 13.2 | N |  |  | OP | X | 1 | 1944 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1982 | hydro | TRUE | 19400 | USACE Northwestern Division | 3075 | Bonneville | OR | Multnomah | 11 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 66.5 | 0.95 | 66.5 | 66.5 | 23.2 | N |  |  | OA | X | 10 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1982 | hydro | TRUE | 19400 | USACE Northwestern Division | 3075 | Bonneville | OR | Multnomah | 12 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 66.5 | 0.95 | 66.5 | 66.5 | 23.2 | N |  |  | OP | X | 10 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1982 | hydro | TRUE | 19400 | USACE Northwestern Division | 3075 | Bonneville | OR | Multnomah | 13 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 66.5 | 0.95 | 66.5 | 66.5 | 23.2 | N |  |  | OP | X | 10 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  | N |  | 10M
Vintage1982 | hydro | TRUE | 19400 | USACE Northwestern Division | 3075 | Bonneville | OR | Multnomah | 14 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 66.5 | 0.95 | 66.5 | 66.5 | 23.2 | N |  |  | OP | X | 6 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  | N |  | 10M
Vintage1982 | hydro | TRUE | 19400 | USACE Northwestern Division | 3075 | Bonneville | OR | Multnomah | 15 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 66.5 | 0.95 | 66.5 | 66.5 | 23.2 | N |  |  | OP | X | 3 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1981 | hydro | TRUE | 19400 | USACE Northwestern Division | 3075 | Bonneville | OR | Multnomah | 16 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 66.5 | 0.95 | 66.5 | 66.5 | 23.2 | N |  |  | OP | X | 12 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1981 | hydro | TRUE | 19400 | USACE Northwestern Division | 3075 | Bonneville | OR | Multnomah | 17 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 66.5 | 0.95 | 66.5 | 66.5 | 23.2 | N |  |  | OP | X | 9 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1981 | hydro | TRUE | 19400 | USACE Northwestern Division | 3075 | Bonneville | OR | Multnomah | 18 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 66.5 | 0.95 | 66.5 | 66.5 | 23.2 | N |  |  | OP | X | 5 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1938 | hydro | TRUE | 19400 | USACE Northwestern Division | 3075 | Bonneville | OR | Multnomah | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 53.5 | 0.9 | 53.5 | 53.5 | 13.2 | N |  |  | OP | X | 8 | 1938 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1941 | hydro | TRUE | 19400 | USACE Northwestern Division | 3075 | Bonneville | OR | Multnomah | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 62.1 | 0.9 | 62.1 | 62.1 | 13.2 | N |  |  | OP | X | 1 | 1941 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1941 | hydro | TRUE | 19400 | USACE Northwestern Division | 3075 | Bonneville | OR | Multnomah | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 62.1 | 0.9 | 62.1 | 62.1 | 13.2 | N |  |  | OP | X | 2 | 1941 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1941 | hydro | TRUE | 19400 | USACE Northwestern Division | 3075 | Bonneville | OR | Multnomah | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 62.1 | 0.9 | 62.1 | 62.1 | 13.2 | N |  |  | OP | X | 10 | 1941 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1942 | hydro | TRUE | 19400 | USACE Northwestern Division | 3075 | Bonneville | OR | Multnomah | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 62.1 | 0.9 | 62.1 | 62.1 | 13.2 | N |  |  | OP | X | 6 | 1942 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1943 | hydro | TRUE | 19400 | USACE Northwestern Division | 3075 | Bonneville | OR | Multnomah | 7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 62.1 | 0.9 | 62.1 | 62.1 | 13.2 | N |  |  | OP | X | 4 | 1943 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1943 | hydro | TRUE | 19400 | USACE Northwestern Division | 3075 | Bonneville | OR | Multnomah | 8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 62.1 | 0.9 | 62.1 | 62.1 | 13.2 | N |  |  | OP | X | 7 | 1943 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1943 | hydro | TRUE | 19400 | USACE Northwestern Division | 3075 | Bonneville | OR | Multnomah | 9 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 62.1 | 0.9 | 62.1 | 62.1 | 13.2 | N |  |  | OP | X | 10 | 1943 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1982 | hydro | TRUE | 19400 | USACE Northwestern Division | 3075 | Bonneville | OR | Multnomah | F1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 13.1 | 0.95 | 13.1 | 13.1 | 13.1 | N |  |  | OP | X | 1 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1981 | hydro | TRUE | 19400 | USACE Northwestern Division | 3075 | Bonneville | OR | Multnomah | F2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 13.1 | 0.95 | 13.1 | 13.1 | 13.1 | N |  |  | OA | X | 11 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1964 | hydro | TRUE | 19400 | USACE Northwestern Division | 3076 | Cougar | OR | Lane | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 13 | 0.95 | 13 | 13 | 12.5 | N |  |  | OP | X | 4 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1964 | hydro | TRUE | 19400 | USACE Northwestern Division | 3076 | Cougar | OR | Lane | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 13 | 0.95 | 13 | 13 | 12.5 | N |  |  | OP | X | 3 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1953 | hydro | TRUE | 19400 | USACE Northwestern Division | 3077 | Detroit | OR | Marion | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 50 | 0.9 | 50 | 50 | 50 | N |  |  | OS | X | 11 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1953 | hydro | TRUE | 19400 | USACE Northwestern Division | 3077 | Detroit | OR | Marion | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 50 | 0.9 | 50 | 50 | 50 | N |  |  | OP | X | 7 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1955 | hydro | TRUE | 19400 | USACE Northwestern Division | 3078 | Dexter | OR | Lane | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 1 | 15 | 15 | 15 | N |  |  | OP | X | 6 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1967 | hydro | TRUE | 19400 | USACE Northwestern Division | 3080 | Green Peter | OR | Linn | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40 | 0.95 | 40 | 40 | 40 | N |  |  | OP | X | 7 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1967 | hydro | TRUE | 19400 | USACE Northwestern Division | 3080 | Green Peter | OR | Linn | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40 | 0.95 | 40 | 40 | 40 | N |  |  | OP | X | 7 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1962 | hydro | TRUE | 19400 | USACE Northwestern Division | 3081 | Hills Creek | OR | Lane | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.95 | 15 | 15 | 15 | N |  |  | OP | X | 2 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1962 | hydro | TRUE | 19400 | USACE Northwestern Division | 3081 | Hills Creek | OR | Lane | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.95 | 15 | 15 | 15 | N |  |  | OP | X | 2 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1968 | hydro | TRUE | 19400 | USACE Northwestern Division | 3082 | John Day | OR | Sherman | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 135 | 135 | 52 | N |  |  | OP | X | 8 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1969 | hydro | TRUE | 19400 | USACE Northwestern Division | 3082 | John Day | OR | Sherman | 10 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 135 | 135 | 52 | N |  |  | OP | X | 9 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1970 | hydro | TRUE | 19400 | USACE Northwestern Division | 3082 | John Day | OR | Sherman | 11 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 118 | 118 | 52 | N |  |  | OP | X | 3 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1970 | hydro | TRUE | 19400 | USACE Northwestern Division | 3082 | John Day | OR | Sherman | 12 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 118 | 118 | 52 | N |  |  | OA | X | 5 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1970 | hydro | TRUE | 19400 | USACE Northwestern Division | 3082 | John Day | OR | Sherman | 13 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 135 | 135 | 52 | N |  |  | OA | X | 12 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1971 | hydro | TRUE | 19400 | USACE Northwestern Division | 3082 | John Day | OR | Sherman | 14 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 118 | 118 | 52 | N |  |  | OP | X | 1 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1971 | hydro | TRUE | 19400 | USACE Northwestern Division | 3082 | John Day | OR | Sherman | 15 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 135 | 135 | 52 | N |  |  | OP | X | 10 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1971 | hydro | TRUE | 19400 | USACE Northwestern Division | 3082 | John Day | OR | Sherman | 16 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 135 | 135 | 52 | N |  |  | OP | X | 12 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1968 | hydro | TRUE | 19400 | USACE Northwestern Division | 3082 | John Day | OR | Sherman | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 135 | 135 | 52 | N |  |  | OP | X | 9 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1968 | hydro | TRUE | 19400 | USACE Northwestern Division | 3082 | John Day | OR | Sherman | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 129 | 129 | 52 | N |  |  | OA | X | 11 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1968 | hydro | TRUE | 19400 | USACE Northwestern Division | 3082 | John Day | OR | Sherman | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 118 | 118 | 52 | N |  |  | OP | X | 12 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1969 | hydro | TRUE | 19400 | USACE Northwestern Division | 3082 | John Day | OR | Sherman | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 135 | 135 | 52 | N |  |  | OP | X | 2 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1969 | hydro | TRUE | 19400 | USACE Northwestern Division | 3082 | John Day | OR | Sherman | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 135 | 135 | 52 | N |  |  | OP | X | 3 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1969 | hydro | TRUE | 19400 | USACE Northwestern Division | 3082 | John Day | OR | Sherman | 7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 135 | 135 | 52 | N |  |  | OS | X | 4 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1969 | hydro | TRUE | 19400 | USACE Northwestern Division | 3082 | John Day | OR | Sherman | 8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 118 | 118 | 52 | N |  |  | OA | X | 6 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1969 | hydro | TRUE | 19400 | USACE Northwestern Division | 3082 | John Day | OR | Sherman | 9 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 118 | 118 | 52 | N |  |  | OP | X | 8 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1955 | hydro | TRUE | 19400 | USACE Northwestern Division | 3083 | Lookout Point | OR | Lane | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40 | 0.95 | 40 | 40 | 40 | N |  |  | OP | X | 5 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1955 | hydro | TRUE | 19400 | USACE Northwestern Division | 3083 | Lookout Point | OR | Lane | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40 | 0.95 | 40 | 40 | 40 | N |  |  | OA | X | 3 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1955 | hydro | TRUE | 19400 | USACE Northwestern Division | 3083 | Lookout Point | OR | Lane | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40 | 0.95 | 40 | 40 | 40 | N |  |  | OP | X | 1 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1953 | hydro | TRUE | 19400 | USACE Northwestern Division | 3084 | McNary | OR | Umatilla | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 70 | 0.95 | 70 | 70 | 23.8 | N |  |  | OP | X | 12 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1955 | hydro | TRUE | 19400 | USACE Northwestern Division | 3084 | McNary | OR | Umatilla | 10 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 70 | 0.95 | 70 | 70 | 23.8 | N |  |  | OP | X | 11 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1956 | hydro | TRUE | 19400 | USACE Northwestern Division | 3084 | McNary | OR | Umatilla | 11 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 70 | 0.95 | 70 | 70 | 23.8 | N |  |  | OP | X | 5 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1956 | hydro | TRUE | 19400 | USACE Northwestern Division | 3084 | McNary | OR | Umatilla | 12 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 70 | 0.95 | 70 | 70 | 23.8 | N |  |  | OP | X | 5 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1957 | hydro | TRUE | 19400 | USACE Northwestern Division | 3084 | McNary | OR | Umatilla | 13 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 70 | 0.95 | 70 | 70 | 23.8 | N |  |  | OP | X | 3 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1957 | hydro | TRUE | 19400 | USACE Northwestern Division | 3084 | McNary | OR | Umatilla | 14 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 80.5 | 0.95 | 80.5 | 80.5 | 23.8 | N |  |  | OP | X | 3 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1954 | hydro | TRUE | 19400 | USACE Northwestern Division | 3084 | McNary | OR | Umatilla | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 70 | 0.95 | 70 | 70 | 23.8 | N |  |  | OP | X | 1 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1954 | hydro | TRUE | 19400 | USACE Northwestern Division | 3084 | McNary | OR | Umatilla | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 70 | 0.95 | 70 | 70 | 23.8 | N |  |  | OP | X | 5 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1954 | hydro | TRUE | 19400 | USACE Northwestern Division | 3084 | McNary | OR | Umatilla | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 70 | 0.95 | 70 | 70 | 23.8 | N |  |  | OA | X | 7 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1954 | hydro | TRUE | 19400 | USACE Northwestern Division | 3084 | McNary | OR | Umatilla | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 70 | 0.95 | 58 | 58 | 23.8 | Y | 8 | 2021 | OP | X | 10 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1955 | hydro | TRUE | 19400 | USACE Northwestern Division | 3084 | McNary | OR | Umatilla | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 70 | 0.95 | 58 | 58 | 23.8 | N |  |  | OP | X | 1 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1955 | hydro | TRUE | 19400 | USACE Northwestern Division | 3084 | McNary | OR | Umatilla | 7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 70 | 0.95 | 70 | 70 | 23.8 | N |  |  | OA | X | 3 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1955 | hydro | TRUE | 19400 | USACE Northwestern Division | 3084 | McNary | OR | Umatilla | 8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 70 | 0.95 | 70 | 70 | 23.8 | N |  |  | OP | X | 6 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1956 | hydro | TRUE | 19400 | USACE Northwestern Division | 3084 | McNary | OR | Umatilla | 9 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 70 | 0.95 | 70 | 70 | 23.8 | N |  |  | OP | X | 9 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1972 | petroleum | TRUE | 63032 | Brunot Island Power, LLC | 3096 | Brunot Island | PA | Allegheny | 1A | Petroleum Liquids | GT |  | S | X | X | 38367979 | BRUNOTIS 13 KV CT1A | 25.5 | 0.85 | 18.1 | 15 | 15 | N |  |  | OP | X | 3 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1973 | natural gas combined cycle | TRUE | 63032 | Brunot Island Power, LLC | 3096 | Brunot Island | PA | Allegheny | 2A | Natural Gas Fired Combined Cycle | CT | BICC | S | X | N | 38367987 | BRUNOTIS 13 KV CT2A | 65.3 | 0.9 | 47.4 | 54 | 30 | N |  |  | OP | X | 6 | 1973 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1973 | natural gas combined cycle | TRUE | 63032 | Brunot Island Power, LLC | 3096 | Brunot Island | PA | Allegheny | 2B | Natural Gas Fired Combined Cycle | CT | BICC | S | X | N | 38367985 | BRUNOTIS 13 KV CT2B | 65.3 | 0.9 | 47 | 56.7 | 30 | N |  |  | OP | X | 6 | 1973 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1973 | natural gas combined cycle | TRUE | 63032 | Brunot Island Power, LLC | 3096 | Brunot Island | PA | Allegheny | 3 | Natural Gas Fired Combined Cycle | CT | BICC | S | X | N | 38367989 | BRUNOT IS 13KV UNIT 3 | 65.3 | 0.9 | 47.5 | 57.7 | 30 | N |  |  | OP | X | 6 | 1973 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1974 | natural gas combined cycle | TRUE | 63032 | Brunot Island Power, LLC | 3096 | Brunot Island | PA | Allegheny | ST4 | Natural Gas Fired Combined Cycle | CA | BICC | S | Y | X | 38367991 | BRUNOTIS 13 KV UNIT4 | 144 | 0.9 | 101.6 | 101 | 32 | N |  |  | OP | X | 7 | 1974 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1971 | petroleum | TRUE | 63035 | Hamilton Power, LLC | 3109 | Hamilton (PA) | PA | Adams | 1 | Petroleum Liquids | GT |  | S | X | X | 50738 | HAMILTON 13 KV HAMLTN | 19.6 | 0.85 | 20.4 | 24 | 18 | N |  |  | OP | X | 6 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1971 | natural gas peaker | TRUE | 63036 | Hunterstown Power, LLC | 3110 | Hunterstown | PA | Adams | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 50739 | HUNTERST 13 KV HUNTR1 | 20 | 0.85 | 21 | 20 | 18 | N |  |  | OP | X | 5 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1971 | natural gas peaker | TRUE | 63036 | Hunterstown Power, LLC | 3110 | Hunterstown | PA | Adams | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 50740 | HUNTERST 13 KV HUNTR2 | 20 | 0.85 | 21.5 | 20 | 17 | N |  |  | OP | X | 5 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1971 | natural gas peaker | TRUE | 63036 | Hunterstown Power, LLC | 3110 | Hunterstown | PA | Adams | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 50741 | HUNTERST 13 KV HUNTR3 | 20 | 0.85 | 21.5 | 20 | 18 | N |  |  | OP | X | 5 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1972 | petroleum | TRUE | 63037 | Mountain Power, LLC | 3111 | Mountain | PA | Cumberland | 1 | Petroleum Liquids | GT |  | S | X | X | 50743 | MOUN ME 13 KV GEN #1 | 27 | 0.85 | 19.5 | 25 | 18 | N |  |  | OP | X | 6 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1972 | petroleum | TRUE | 63037 | Mountain Power, LLC | 3111 | Mountain | PA | Cumberland | 2 | Petroleum Liquids | GT |  | S | X | X | 50744 | MOUN ME 13 KV GEN #2 | 27 | 0.85 | 20.6 | 25 | 18 | N |  |  | OP | X | 6 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1971 | petroleum | TRUE | 63038 | Orrtanna Power, LLC | 3112 | Orrtanna | PA | Adams | 1 | Petroleum Liquids | GT |  | S | X | X | 50745 | ORRTANNA 13KV ORRTAN | 27 | 0.85 | 20.2 | 26 | 18 | N |  |  | OP | X | 5 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1967 | petroleum | TRUE | 63039 | Portland Power, LLC | 3113 | Portland (PA) | PA | Northampton | 3 | Petroleum Liquids | GT |  | S | X | X | 50750 | PORTLAND 13 KV CT 3 | 18 | 0.85 | 16 | 15 | 13 | N |  |  | OP | X | 12 | 1967 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1971 | petroleum | TRUE | 63039 | Portland Power, LLC | 3113 | Portland (PA) | PA | Northampton | 4 | Petroleum Liquids | GT |  | S | X | X | 50751 | PORTLAND 13 KV CT 4 | 20 | 0.85 | 21 | 20 | 17 | N |  |  | OP | X | 5 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1997 | petroleum | TRUE | 63039 | Portland Power, LLC | 3113 | Portland (PA) | PA | Northampton | 5 | Petroleum Liquids | GT |  | S | X | X | 50749 | PORTLAND 13 KV CT 5 | 156 | 0.85 | 140.5 | 155 | 90 | N |  |  | OP | X | 4 | 1997 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1972 | petroleum | TRUE | 63040 | Shawnee Power, LLC | 3114 | Shawnee (PA) | PA | Monroe | 1 | Petroleum Liquids | GT |  | S | X | X | 50753 | SHAWNEE 13 KV SHAWNE | 20 | 0.85 | 20.6 | 24 | 17 | N |  |  | OP | X | 6 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N
Vintage1967 | petroleum | TRUE | 63041 | Titus Power, LLC | 3115 | Titus | PA | Berks | 4 | Petroleum Liquids | GT |  | S | X | X | 50754 | SPREADING 13 KV TITUS4 | 18 | 0.85 | 15 | 17 | 13 | N |  |  | OP | X | 12 | 1967 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1970 | petroleum | TRUE | 63041 | Titus Power, LLC | 3115 | Titus | PA | Berks | 5 | Petroleum Liquids | GT |  | S | X | X | 50755 | SPREADING 13 KV TITUS5 | 18 | 0.85 | 16.1 | 18 | 13 | N |  |  | OP | X | 8 | 1970 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1972 | petroleum | TRUE | 63042 | Tolna Power, LLC | 3116 | Tolna | PA | York | 1 | Petroleum Liquids | GT |  | S | X | X | 50760 | TOLNA 13 KV GEN1 | 27 | 0.85 | 21 | 25 | 18 | N |  |  | OP | X | 6 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1972 | petroleum | TRUE | 63042 | Tolna Power, LLC | 3116 | Tolna | PA | York | 2 | Petroleum Liquids | GT |  | S | X | X | 50761 | TOLNA 13 KV GEN2 | 27 | 0.85 | 20.2 | 25 | 18 | N |  |  | OP | X | 6 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1905 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 3117 | York Haven | PA | York | 1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 19.6 | 0.95 | 19 | 19 | 1 | N |  |  | OP | X | 12 | 1905 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 12H
Vintage1970 | hard coal | TRUE | 63047 | KeyCon Operating LLC | 3118 | Conemaugh | PA | Indiana | 1 | Conventional Steam Coal | ST |  | J | X | X | 50769 | 50769 | 975.5 | 0.9 | 850 | 850 | 325 | N |  |  | OP | X | 5 | 1970 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: RC; DFO SUB SUB: BIT; DFO DFO DFO: NG; DFO DFO DFO: NG |  |  | N |  |  | OVER |  | Y |  |  |  | Y | [17 empty] | Y | Y | N
Vintage1971 | hard coal | TRUE | 63047 | KeyCon Operating LLC | 3118 | Conemaugh | PA | Indiana | 2 | Conventional Steam Coal | ST |  | J | X | X | 50770 | 50770 | 975.5 | 0.9 | 850 | 850 | 325 | N |  |  | OP | X | 5 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: RC; DFO SUB SUB: BIT; DFO DFO DFO: NG; DFO DFO DFO: NG |  |  | N |  |  | OVER |  | Y |  |  |  | Y | [17 empty] | Y | Y | N
Vintage1970 | petroleum | TRUE | 63047 | KeyCon Operating LLC | 3118 | Conemaugh | PA | Indiana | A | Petroleum Liquids | IC |  | J | X | X |  |  | 3 | 0.8 | 2.8 | 2.8 | 2.8 | N |  |  | OP | X | 2 | 1970 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1970 | petroleum | TRUE | 63047 | KeyCon Operating LLC | 3118 | Conemaugh | PA | Indiana | B | Petroleum Liquids | IC |  | J | X | X |  |  | 3 | 0.8 | 2.8 | 2.8 | 2.8 | N |  |  | SB | Y | 2 | 1970 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1970 | petroleum | TRUE | 63047 | KeyCon Operating LLC | 3118 | Conemaugh | PA | Indiana | C | Petroleum Liquids | IC |  | J | X | X |  |  | 3 | 0.8 | 2.8 | 2.8 | 2.8 | N |  |  | SB | Y | 2 | 1970 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1970 | petroleum | TRUE | 63047 | KeyCon Operating LLC | 3118 | Conemaugh | PA | Indiana | D | Petroleum Liquids | IC |  | J | X | X |  |  | 3 | 0.8 | 2.8 | 2.8 | 2.8 | N |  |  | SB | Y | 2 | 1970 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1971 | natural gas peaker | TRUE | 63043 | Blossburg Power, LLC | 3120 | Blossburg | PA | Tioga | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 50765 | bLOSSBUR 13 KV UNITCT | 24 | 0.85 | 20.9 | 19 | 16 | N |  |  | OP | X | 5 | 1971 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1969 | hard coal | TRUE | 58615 | NRG Homer City Services LLC | 3122 | Homer City Generating Station | PA | Indiana | 1 | Conventional Steam Coal | ST |  | J | X | X | 51230 |  | 660 | 0.9 | 626.1 | 631.2 | 285 | N |  |  | OP | X | 6 | 1969 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | N | N | N
Vintage1969 | hard coal | TRUE | 58615 | NRG Homer City Services LLC | 3122 | Homer City Generating Station | PA | Indiana | 2 | Conventional Steam Coal | ST |  | J | X | X | 51231 |  | 660 | 0.9 | 613.3 | 618.5 | 290 | N |  |  | OP | X | 8 | 1969 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | N | N | N
Vintage1977 | hard coal | TRUE | 58615 | NRG Homer City Services LLC | 3122 | Homer City Generating Station | PA | Indiana | 3 | Conventional Steam Coal | ST |  | J | X | X | 51232 |  | 692 | 0.95 | 648.9 | 665.4 | 300 | N |  |  | OP | X | 11 | 1977 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | N | [17 empty] | N | N | N
Vintage1924 | hydro | TRUE | 54679 | BP Piney & Deep Creek LLC | 3124 | Piney | PA | Clarion | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 0.8 | 11.8 | 11.8 | 4 | N |  |  | OP | X | 6 | 1924 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1924 | hydro | TRUE | 54679 | BP Piney & Deep Creek LLC | 3124 | Piney | PA | Clarion | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 0.8 | 11.8 | 11.8 | 4 | N |  |  | OP | X | 7 | 1924 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1928 | hydro | TRUE | 54679 | BP Piney & Deep Creek LLC | 3124 | Piney | PA | Clarion | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 0.8 | 9.6 | 9.6 | 3 | N |  |  | OP | X | 2 | 1928 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage2004 | hard coal | TRUE | 61781 | Seward Generating LLC | 3130 | Seward (PA) | PA | Indiana | FB1 | Conventional Steam Coal | ST |  | W | X | X | 21601799 | 21601799 | 585 | 0.9 | 521 | 521 | 200 | N |  |  | OP | X | 11 | 2004 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WC; DFO SUB SUB: DFO; DFO DFO DFO: DFO |  |  | N | N |  | OVER | Y |  |  |  | Y | [18 empty] | Y | N | N
Vintage1954 | natural gas steam turbine | TRUE | 63044 | Shawville Power, LLC | 3131 | Shawville | PA | Clearfield | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | 50796 | SHAWVILLE 18 KV UNIT 1 | 125 | 0.8 | 122.3 | 122 | 30 | N |  |  | OP | X | 8 | 1954 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO DFO DFO: NG; DFO NG NG: DFO |  |  | N | N |  | OVER | [20 empty] | N |  |  | N |  | N
Vintage1954 | natural gas steam turbine | TRUE | 63044 | Shawville Power, LLC | 3131 | Shawville | PA | Clearfield | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | 50797 | SHAWVILLE 18 KV UNIT 2 | 125 | 0.8 | 124.7 | 124.7 | 31 | N |  |  | OP | X | 3 | 1954 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO DFO DFO: NG; DFO NG NG: DFO |  |  | N | N |  | OVER | [20 empty] | N |  |  | N |  | N
Vintage1959 | natural gas steam turbine | TRUE | 63044 | Shawville Power, LLC | 3131 | Shawville | PA | Clearfield | 3 | Natural Gas Steam Turbine | ST |  | S | X | X | 50798 | SHAWVILLE 18 KV UNIT 3 | 188 | 0.85 | 174 | 172 | 59 | N |  |  | OP | X | 12 | 1959 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO DFO DFO: NG; DFO NG NG: DFO |  |  | N | N |  | OVER | [20 empty] | N |  |  | N |  | N
Vintage1960 | natural gas steam turbine | TRUE | 63044 | Shawville Power, LLC | 3131 | Shawville | PA | Clearfield | 4 | Natural Gas Steam Turbine | ST |  | S | X | X | 50799 | SHAWVILLE 18 KV UNIT 4 | 188 | 0.85 | 175 | 171 | 59 | N |  |  | OP | X | 4 | 1960 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO DFO DFO: NG; DFO NG NG: DFO |  |  | N | N |  | OVER | [20 empty] | N |  |  | N |  | N
Vintage1960 | petroleum | TRUE | 63044 | Shawville Power, LLC | 3131 | Shawville | PA | Clearfield | 5 | Petroleum Liquids | IC |  | S | X | X | 50795 | 50795 | 2 | 0.8 | 2 | 2 | 2 | N |  |  | SB | Y | 4 | 1960 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N |  | N
Vintage1966 | petroleum | TRUE | 63044 | Shawville Power, LLC | 3131 | Shawville | PA | Clearfield | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | SB | Y | 4 | 1966 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N |  | N
Vintage1960 | petroleum | TRUE | 63044 | Shawville Power, LLC | 3131 | Shawville | PA | Clearfield | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | SB | Y | 4 | 1960 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N |  | N
Vintage1972 | natural gas peaker | TRUE | 63045 | Warren Generation, LLC | 3132 | Warren | PA | Warren | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 50803 | 50803 | 53.1 | 0.85 | 62 | 50.1 | 5 | N |  |  | OP | X | 9 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1967 | hard coal | TRUE | 63047 | KeyCon Operating LLC | 3136 | Keystone | PA | Armstrong | 1 | Conventional Steam Coal | ST |  | J | X | X | 50781 | 50781 | 936 | 0.9 | 850 | 850 | 350 | N |  |  | OP | X | 8 | 1967 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: RC; DFO SUB SUB: BIT; DFO DFO DFO: DFO; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | Y | Y | N
Vintage1968 | hard coal | TRUE | 63047 | KeyCon Operating LLC | 3136 | Keystone | PA | Armstrong | 2 | Conventional Steam Coal | ST |  | J | X | X | 50782 | 50782 | 936 | 0.9 | 850 | 850 | 350 | N |  |  | OP | X | 7 | 1968 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: RC; DFO SUB SUB: BIT; DFO DFO DFO: DFO; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | Y | Y | N
Vintage1968 | petroleum | TRUE | 63047 | KeyCon Operating LLC | 3136 | Keystone | PA | Armstrong | 3 | Petroleum Liquids | IC |  | J | X | X | 50783 | 50783 | 2.5 | 0.8 | 2.8 | 2.8 | 2.8 | N |  |  | OP | X | 11 | 1968 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1968 | petroleum | TRUE | 63047 | KeyCon Operating LLC | 3136 | Keystone | PA | Armstrong | 4 | Petroleum Liquids | IC |  | J | X | X |  |  | 2.9 | 0.8 | 2.8 | 2.8 | 2.8 | N |  |  | OP | X | 11 | 1968 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1968 | petroleum | TRUE | 63047 | KeyCon Operating LLC | 3136 | Keystone | PA | Armstrong | 5 | Petroleum Liquids | IC |  | J | X | X |  |  | 2.9 | 0.8 | 2.8 | 2.8 | 2.8 | N |  |  | OP | X | 11 | 1968 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1968 | petroleum | TRUE | 63047 | KeyCon Operating LLC | 3136 | Keystone | PA | Armstrong | 6 | Petroleum Liquids | IC |  | J | X | X |  |  | 2.9 | 0.8 | 2.8 | 2.8 | 2.8 | N |  |  | OP | X | 11 | 1968 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1952 | natural gas steam turbine | TRUE | 63031 | New Castle Power, LLC | 3138 | New Castle Plant | PA | Lawrence | 3 | Natural Gas Steam Turbine | ST |  | S | X | X | 98370489 | NEWCASOE 14 KV G3 | 98 | 0.85 | 92.3 | 93 | 20 | N |  |  | OP | X | 9 | 1952 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: SUB; DFO DFO DFO: NG |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N
Vintage1958 | natural gas steam turbine | TRUE | 63031 | New Castle Power, LLC | 3138 | New Castle Plant | PA | Lawrence | 4 | Natural Gas Steam Turbine | ST |  | S | X | X | 98370491 | NEWCASOE 14 KV G4 | 114 | 0.85 | 93 | 92 | 25 | N |  |  | OP | X | 8 | 1958 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: SUB; DFO DFO DFO: NG |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N
Vintage1964 | natural gas steam turbine | TRUE | 63031 | New Castle Power, LLC | 3138 | New Castle Plant | PA | Lawrence | 5 | Natural Gas Steam Turbine | ST |  | S | X | X | 98370487 | NEWCASOE 14 KV G5 | 136 | 0.85 | 141 | 135 | 35 | N |  |  | OP | X | 6 | 1964 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: SUB; DFO DFO DFO: NG |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N
Vintage1968 | petroleum | TRUE | 63031 | New Castle Power, LLC | 3138 | New Castle Plant | PA | Lawrence | EMDA | Petroleum Liquids | IC |  | S | X | X | 98370491 | NEWCASOE 23KV EMDS-A | 3.2 | 0.8 | 2.5 | 2.5 | 1 | N |  |  | OP | X | 12 | 1968 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1968 | petroleum | TRUE | 63031 | New Castle Power, LLC | 3138 | New Castle Plant | PA | Lawrence | EMDB | Petroleum Liquids | IC |  | S | X | X | 98370487 | NEWCASOE 23KV EMDS-B | 3.2 | 0.8 | 2.5 | 2.5 | 1 | N |  |  | OS | X | 12 | 1968 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1967 | petroleum | TRUE | 15276 | TalenEnergy Martins Creek LLC | 3139 | TalenEnergy Martin Creek LLC Allentown | PA | Lehigh | CTG1 | Petroleum Liquids | GT |  | S | X | X | 48934141 | 48934141 | 16 | 0.85 | 14 | 14 | 14 | N |  |  | OP | X | 7 | 1967 | 6 | 2022 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1967 | petroleum | TRUE | 15276 | TalenEnergy Martins Creek LLC | 3139 | TalenEnergy Martin Creek LLC Allentown | PA | Lehigh | CTG2 | Petroleum Liquids | GT |  | S | X | X | 48934143 | 48934143 | 16 | 0.85 | 14 | 14 | 14 | N |  |  | OP | X | 7 | 1967 | 6 | 2022 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1967 | petroleum | TRUE | 15276 | TalenEnergy Martins Creek LLC | 3139 | TalenEnergy Martin Creek LLC Allentown | PA | Lehigh | CTG3 | Petroleum Liquids | GT |  | S | X | X | 48934145 | 48934145 | 16 | 0.85 | 14 | 14 | 14 | N |  |  | OP | X | 7 | 1967 | 6 | 2022 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1967 | petroleum | TRUE | 15276 | TalenEnergy Martins Creek LLC | 3139 | TalenEnergy Martin Creek LLC Allentown | PA | Lehigh | CTG4 | Petroleum Liquids | GT |  | S | X | X | 48934147 | 48934147 | 16 | 0.85 | 14 | 14 | 14 | N |  |  | OP | X | 7 | 1967 | 6 | 2022 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1961 | hard coal | TRUE | 15537 | Brunner Island LLC | 3140 | Brunner Island | PA | York | 1 | Conventional Steam Coal | ST |  | S | X | X | 50578 | 50578 | 363.3 | 0.9 | 306 | 306 | 122 | N |  |  | OP | X | 5 | 1961 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: NG; DFO DFO DFO: DFO; DFO NG NG: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | N |  |  | Y | Y | N
Vintage1965 | hard coal | TRUE | 15537 | Brunner Island LLC | 3140 | Brunner Island | PA | York | 2 | Conventional Steam Coal | ST |  | S | X | X | 50579 | 50579 | 405 | 0.9 | 363 | 363 | 126 | N |  |  | OP | X | 9 | 1965 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: NG; DFO DFO DFO: DFO; DFO NG NG: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | N |  |  | Y | Y | N
Vintage1969 | hard coal | TRUE | 15537 | Brunner Island LLC | 3140 | Brunner Island | PA | York | 3 | Conventional Steam Coal | ST |  | S | X | X | 50581 | 50581 | 847.8 | 0.97 | 742 | 742 | 365 | N |  |  | OP | X | 6 | 1969 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: NG; DFO DFO DFO: DFO; DFO NG NG: NG |  |  | N | N |  | OVER |  | Y |  |  | N | Y | [14 empty] | N |  |  | Y | Y | N
Vintage1969 | petroleum | TRUE | 15276 | TalenEnergy Martins Creek LLC | 3142 | TalenEnergy Martins Creek LLC Fishbach | PA | Schuylkill | UNT1 | Petroleum Liquids | GT |  | S | X | X | 50598 | 50598 | 18.5 | 0.85 | 14 | 14 | 14 | N |  |  | OP | X | 8 | 1969 | 4 | 2022 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1969 | petroleum | TRUE | 15276 | TalenEnergy Martins Creek LLC | 3142 | TalenEnergy Martins Creek LLC Fishbach | PA | Schuylkill | UNT2 | Petroleum Liquids | GT |  | S | X | X | 50599 | 50599 | 18.5 | 0.85 | 14 | 14 | 14 | N |  |  | OP | X | 8 | 1969 | 4 | 2022 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1967 | petroleum | TRUE | 15276 | TalenEnergy Martins Creek LLC | 3143 | TalenEnergy Martins Creek LLC Harrisburg | PA | Dauphin | CTG1 | Petroleum Liquids | GT |  | S | X | X | 48934149 | 48934149 | 16 | 0.85 | 13.4 | 13.4 | 13.4 | N |  |  | OP | X | 3 | 1967 | 6 | 2022 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1967 | petroleum | TRUE | 15276 | TalenEnergy Martins Creek LLC | 3143 | TalenEnergy Martins Creek LLC Harrisburg | PA | Dauphin | CTG2 | Petroleum Liquids | GT |  | S | X | X | 48934151 | 48934151 | 16 | 0.85 | 13.9 | 13.9 | 13.9 | N |  |  | OP | X | 3 | 1967 | 6 | 2022 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1967 | petroleum | TRUE | 15276 | TalenEnergy Martins Creek LLC | 3143 | TalenEnergy Martins Creek LLC Harrisburg | PA | Dauphin | CTG3 | Petroleum Liquids | GT |  | S | X | X | 48934153 | 48934153 | 16 | 0.85 | 13.8 | 13.8 | 13.8 | N |  |  | OP | X | 3 | 1967 | 6 | 2022 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1967 | petroleum | TRUE | 15276 | TalenEnergy Martins Creek LLC | 3144 | TalenEnergy Martins Creek LLC Harwood | PA | Luzerne | CTG1 | Petroleum Liquids | GT |  | S | X | X | 50609 | 50609 | 16 | 0.85 | 12.9 | 12.9 | 12.9 | N |  |  | OP | X | 7 | 1967 | 5 | 2022 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1967 | petroleum | TRUE | 15276 | TalenEnergy Martins Creek LLC | 3144 | TalenEnergy Martins Creek LLC Harwood | PA | Luzerne | CTG2 | Petroleum Liquids | GT |  | S | X | X | 50610 | 50610 | 16 | 0.85 | 12.3 | 12.3 | 12.3 | N |  |  | OP | X | 7 | 1967 | 5 | 2022 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1910 | hydro | TRUE | 60416 | BIF III Holtwood LLC | 3145 | Holtwood | PA | Lancaster | HW1 | Conventional Hydroelectric | HY |  | S | X | X | 50593 | 50593 | 10.4 | 1 | 10 | 10 | 3 | N |  |  | OP | X | 10 | 1910 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1924 | hydro | TRUE | 60416 | BIF III Holtwood LLC | 3145 | Holtwood | PA | Lancaster | HW10 | Conventional Hydroelectric | HY |  | S | X | X | 50592 | 50592 | 12 | 1 | 13.2 | 13.2 | 4 | N |  |  | OP | X | 3 | 1924 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage2011 | hydro | TRUE | 60416 | BIF III Holtwood LLC | 3145 | Holtwood | PA | Lancaster | HW11 | Conventional Hydroelectric | HY |  | S | X | X | 123901489 | 123901489 | 1.4 | 1 | 1.2 | 1.2 | 1 | N |  |  | OP | X | 6 | 2011 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage2011 | hydro | TRUE | 60416 | BIF III Holtwood LLC | 3145 | Holtwood | PA | Lancaster | HW13 | Conventional Hydroelectric | HY |  | S | X | X | 123901487 | 123901487 | 1.4 | 1 | 1.2 | 1.2 | 1 | N |  |  | OP | X | 6 | 2011 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage2013 | hydro | TRUE | 60416 | BIF III Holtwood LLC | 3145 | Holtwood | PA | Lancaster | HW18 | Conventional Hydroelectric | HY |  | S | X | X | 123901483 | 123901483 | 66 | 1 | 64.6 | 64.6 | 25 | N |  |  | OP | X | 11 | 2013 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage2013 | hydro | TRUE | 60416 | BIF III Holtwood LLC | 3145 | Holtwood | PA | Lancaster | HW19 | Conventional Hydroelectric | HY |  | S | X | X | 123901485 | 123901485 | 66 | 1 | 64.6 | 64.6 | 25 | N |  |  | OP | X | 11 | 2013 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1911 | hydro | TRUE | 60416 | BIF III Holtwood LLC | 3145 | Holtwood | PA | Lancaster | HW2 | Conventional Hydroelectric | HY |  | S | X | X | 50594 | 50594 | 10.4 | 1 | 11.7 | 11.7 | 4 | N |  |  | OP | X | 2 | 1911 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1911 | hydro | TRUE | 60416 | BIF III Holtwood LLC | 3145 | Holtwood | PA | Lancaster | HW3 | Conventional Hydroelectric | HY |  | S | X | X | 50595 | 50595 | 13.5 | 1 | 12.7 | 12.7 | 4 | N |  |  | OP | X | 2 | 1911 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1911 | hydro | TRUE | 60416 | BIF III Holtwood LLC | 3145 | Holtwood | PA | Lancaster | HW4 | Conventional Hydroelectric | HY |  | S | X | X | 50596 | 50596 | 10.4 | 1 | 11.2 | 11.2 | 7 | N |  |  | OP | X | 5 | 1911 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1911 | hydro | TRUE | 60416 | BIF III Holtwood LLC | 3145 | Holtwood | PA | Lancaster | HW5 | Conventional Hydroelectric | HY |  | S | X | X | 50597 | 50597 | 10.4 | 1 | 12.1 | 12.1 | 7 | N |  |  | OP | X | 7 | 1911 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1911 | hydro | TRUE | 60416 | BIF III Holtwood LLC | 3145 | Holtwood | PA | Lancaster | HW6 | Conventional Hydroelectric | HY |  | S | X | X | 50588 | 50588 | 10.4 | 1 | 12.5 | 12.5 | 4 | N |  |  | OP | X | 12 | 1911 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1913 | hydro | TRUE | 60416 | BIF III Holtwood LLC | 3145 | Holtwood | PA | Lancaster | HW7 | Conventional Hydroelectric | HY |  | S | X | X | 50589 | 50589 | 10.4 | 1 | 10.3 | 10.3 | 7 | N |  |  | OP | X | 10 | 1913 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1914 | hydro | TRUE | 60416 | BIF III Holtwood LLC | 3145 | Holtwood | PA | Lancaster | HW8 | Conventional Hydroelectric | HY |  | S | X | X | 50590 | 50590 | 11.4 | 1 | 10.5 | 10.5 | 4 | N |  |  | OP | X | 12 | 1914 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1914 | hydro | TRUE | 60416 | BIF III Holtwood LLC | 3145 | Holtwood | PA | Lancaster | HW9 | Conventional Hydroelectric | HY |  | S | X | X | 50591 | 50591 | 13.2 | 1 | 13.2 | 13.2 | 4 | N |  |  | OP | X | 2 | 1914 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1969 | petroleum | TRUE | 15276 | TalenEnergy Martins Creek LLC | 3146 | TalenEnergy Martins Creek LLC Jenkins | PA | Luzerne | CTG1 | Petroleum Liquids | GT |  | S | X | X | 50613 | 50613 | 16 | 0.85 | 13.8 | 13.8 | 13.8 | N |  |  | OP | X | 8 | 1969 | 4 | 2022 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1969 | petroleum | TRUE | 15276 | TalenEnergy Martins Creek LLC | 3146 | TalenEnergy Martins Creek LLC Jenkins | PA | Luzerne | CTG2 | Petroleum Liquids | GT |  | S | X | X | 50614 | 50614 | 16 | 0.85 | 13.8 | 13.8 | 13.8 | N |  |  | OP | X | 7 | 1969 | 4 | 2022 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1969 | petroleum | TRUE | 15276 | TalenEnergy Martins Creek LLC | 3147 | TalenEnergy Martins Creek LLC Lock Haven | PA | Lycoming | CTG | Petroleum Liquids | GT |  | S | X | X | 50616 | 50616 | 18.5 | 0.85 | 14 | 14 | 14 | N |  |  | OP | X | 11 | 1969 | 4 | 2022 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1975 | natural gas steam turbine | TRUE | 15276 | TalenEnergy Martins Creek LLC | 3148 | TalenEnergy Martins Creek | PA | Northampton | 3 | Natural Gas Steam Turbine | ST |  | W | X | X | 50621 | 50621 | 850.5 | 0.9 | 850 | 850 | 165 | N |  |  | OP | X | 10 | 1975 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: RFO; DFO DFO DFO: DFO; DFO DFO DFO: NG |  |  | N | N |  | OVER | [20 empty] | N |  |  | Y | Y | Y
Vintage1977 | natural gas steam turbine | TRUE | 15276 | TalenEnergy Martins Creek LLC | 3148 | TalenEnergy Martins Creek | PA | Northampton | 4 | Natural Gas Steam Turbine | ST |  | W | X | X | 50622 | 50622 | 850.5 | 0.9 | 850 | 850 | 165 | N |  |  | OP | X | 3 | 1977 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: RFO; DFO DFO DFO: DFO; DFO DFO DFO: NG |  |  | N | N |  | OVER | [20 empty] | N |  |  | Y | Y | Y
Vintage1971 | natural gas peaker | TRUE | 15276 | TalenEnergy Martins Creek LLC | 3148 | TalenEnergy Martins Creek | PA | Northampton | CTG1 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X | 48934161 | 48934161 | 23.6 | 0.9 | 18 | 18 | 18 | N |  |  | OP | X | 6 | 1971 | 5 | 2023 | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1971 | natural gas peaker | TRUE | 15276 | TalenEnergy Martins Creek LLC | 3148 | TalenEnergy Martins Creek | PA | Northampton | CTG2 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X | 48934163 | 48934163 | 23.6 | 0.9 | 17.3 | 17.3 | 17.3 | N |  |  | OP | X | 6 | 1971 | 5 | 2023 | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1971 | natural gas peaker | TRUE | 15276 | TalenEnergy Martins Creek LLC | 3148 | TalenEnergy Martins Creek | PA | Northampton | CTG3 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X | 48934165 | 48934165 | 22.3 | 0.85 | 18 | 18 | 18 | N |  |  | OP | X | 6 | 1971 | 6 | 2022 | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1971 | natural gas peaker | TRUE | 15276 | TalenEnergy Martins Creek LLC | 3148 | TalenEnergy Martins Creek | PA | Northampton | CTG4 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X | 48934167 | 48934167 | 23.6 | 0.9 | 17.2 | 17.2 | 17.2 | N |  |  | OP | X | 6 | 1971 | 5 | 2023 | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1972 | hard coal | TRUE | 15534 | TalenEnergy Montour LLC | 3149 | TalenEnergy Montour | PA | Montour | 1 | Conventional Steam Coal | ST |  | S | X | X | 50628 | 50628 | 864.9 | 0.93 | 752 | 752 | 338 | N |  |  | OP | X | 3 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: DFO; DFO DFO DFO: RC; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [14 empty] | N |  |  | Y | Y | N
Vintage1973 | hard coal | TRUE | 15534 | TalenEnergy Montour LLC | 3149 | TalenEnergy Montour | PA | Montour | 2 | Conventional Steam Coal | ST |  | S | X | X | 50629 | 50629 | 893 | 0.94 | 752 | 752 | 342 | N |  |  | OP | X | 4 | 1973 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: DFO; DFO DFO DFO: RC; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [14 empty] | N |  |  | Y | Y | N
Vintage1971 | petroleum | TRUE | 22001 | Sunbury Generation LP | 3152 | Sunbury Generation LP | PA | Snyder | CTG1 | Petroleum Liquids | GT |  | S | X | X | SUNBURY | SUNBURY | 23.6 | 0.85 | 18 | 18 | 2 | N |  |  | SB | Y | 11 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1971 | petroleum | TRUE | 22001 | Sunbury Generation LP | 3152 | Sunbury Generation LP | PA | Snyder | CTG2 | Petroleum Liquids | GT |  | S | X | X | SUNBURY | SUNBURY | 23.6 | 0.85 | 18 | 18 | 2 | N |  |  | SB | Y | 11 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1967 | petroleum | TRUE | 22001 | Sunbury Generation LP | 3152 | Sunbury Generation LP | PA | Snyder | DI2 | Petroleum Liquids | IC |  | S | X | X | SUNBURY | SUNBURY | 5.5 | 0.8 | 5 | 5 | 2.5 | N |  |  | SB | Y | 4 | 1967 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1926 | hydro | TRUE | 60417 | Wallenpuapack Hydro | 3153 | Wallenpaupack | PA | Wayne | WP1 | Conventional Hydroelectric | HY |  | S | X | X | 50577 | 50577 | 20 | 1 | 22 | 22 | 2 | N |  |  | OP | X | 6 | 1926 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1926 | hydro | TRUE | 60417 | Wallenpuapack Hydro | 3153 | Wallenpaupack | PA | Wayne | WP2 | Conventional Hydroelectric | HY |  | S | X | X | 50577 | 50577 | 20 | 1 | 22 | 22 | 2 | N |  |  | OP | X | 6 | 1926 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1969 | petroleum | TRUE | 15276 | TalenEnergy Martins Creek LLC | 3154 | TalenEnergy Martins Creek LLC West Shore | PA | Cumberland | CTG1 | Petroleum Liquids | GT |  | S | X | X | 50656 | 50656 | 18.5 | 0.85 | 14 | 14 | 14 | N |  |  | OP | X | 8 | 1969 | 4 | 2022 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1969 | petroleum | TRUE | 15276 | TalenEnergy Martins Creek LLC | 3154 | TalenEnergy Martins Creek LLC West Shore | PA | Cumberland | CTG2 | Petroleum Liquids | GT |  | S | X | X | 50657 | 50657 | 18.5 | 0.85 | 14 | 14 | 14 | N |  |  | OP | X | 8 | 1969 | 4 | 2022 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1967 | petroleum | TRUE | 15276 | TalenEnergy Martins Creek LLC | 3155 | TalenEnergy Martins Creek LLC Williamsport | PA | Lycoming | CTG1 | Petroleum Liquids | GT |  | S | X | X | 1048046 | 1048046 | 16 | 0.85 | 13.2 | 13.2 | 13.2 | N |  |  | OP | X | 8 | 1967 | 4 | 2022 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1967 | petroleum | TRUE | 15276 | TalenEnergy Martins Creek LLC | 3155 | TalenEnergy Martins Creek LLC Williamsport | PA | Lycoming | CTG2 | Petroleum Liquids | GT |  | S | X | X | 1048046 | 1048046 | 16 | 0.85 | 13.4 | 13.4 | 13.4 | N |  |  | OP | X | 8 | 1967 | 4 | 2022 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1969 | petroleum | TRUE | 6035 | Exelon Power | 3157 | Chester Generating Station | PA | Chester | 7 | Petroleum Liquids | GT |  | S | X | X | CHESTER 13 KV UNIT 7 | CHESTER 13 KV UNIT 7 | 18.6 | 0.85 | 13 | 18 | 5 | N |  |  | OP | X | 2 | 1969 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1969 | petroleum | TRUE | 6035 | Exelon Power | 3157 | Chester Generating Station | PA | Chester | 8 | Petroleum Liquids | GT |  | S | X | X | CHESTER 13 KV UNIT 8 | CHESTER 13 KV UNIT 8 | 18.6 | 0.85 | 13 | 18 | 5 | N |  |  | OP | X | 5 | 1969 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1969 | petroleum | TRUE | 6035 | Exelon Power | 3157 | Chester Generating Station | PA | Chester | 9 | Petroleum Liquids | GT |  | S | X | X | CHESTER 13 KV UNIT 9 | CHESTER 13 KV UNIT 9 | 18.6 | 0.85 | 13 | 18 | 5 | N |  |  | OP | X | 3 | 1969 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1969 | petroleum | TRUE | 6035 | Exelon Power | 3160 | Delaware Generating Station | PA | Philadelphia | 10 | Petroleum Liquids | GT |  | S | X | X | DELA PE 13 KV UNIT10 | DELA PE 13 KV UNIT10 | 18.6 | 0.85 | 13 | 18 | 5 | N |  |  | OP | X | 5 | 1969 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1969 | petroleum | TRUE | 6035 | Exelon Power | 3160 | Delaware Generating Station | PA | Philadelphia | 11 | Petroleum Liquids | GT |  | S | X | X | DELA PE 13 KV UNIT11 | DELA PE 13 KV UNIT11 | 18.6 | 0.85 | 13 | 18 | 5 | N |  |  | OP | X | 4 | 1969 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1969 | petroleum | TRUE | 6035 | Exelon Power | 3160 | Delaware Generating Station | PA | Philadelphia | 12 | Petroleum Liquids | GT |  | S | X | X | DELA PE 13 KV UNIT12 | DELA PE 13 KV UNIT12 | 18.6 | 0.85 | 13 | 18 | 5 | N |  |  | OP | X | 5 | 1969 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1970 | petroleum | TRUE | 6035 | Exelon Power | 3160 | Delaware Generating Station | PA | Philadelphia | 9 | Petroleum Liquids | GT |  | S | X | X | DELA PE 13 KV UNIT09 | DELA PE 13 KV UNIT09 | 21.2 | 0.85 | 17 | 20 | 5 | N |  |  | OP | X | 7 | 1970 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1967 | petroleum | TRUE | 6035 | Exelon Power | 3161 | Eddystone Generating Station | PA | Delaware | 10 | Petroleum Liquids | GT |  | S | X | X | EDDYSTON13 KV UNIT10 | EDDYSTON13 KV UNIT10 | 18.6 | 0.85 | 13 | 18 | 5 | N |  |  | OP | X | 5 | 1967 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1967 | petroleum | TRUE | 6035 | Exelon Power | 3161 | Eddystone Generating Station | PA | Delaware | 20 | Petroleum Liquids | GT |  | S | X | X | EDDYSTON13 KV UNIT20 | EDDYSTON13 KV UNIT20 | 18.6 | 0.85 | 13 | 18 | 5 | N |  |  | OP | X | 10 | 1967 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1974 | natural gas steam turbine | TRUE | 6035 | Exelon Power | 3161 | Eddystone Generating Station | PA | Delaware | 3 | Natural Gas Steam Turbine | ST |  | S | X | X | EDDYSTON20 KV UNIT03 | EDDYSTON20 KV UNIT03 | 391 | 0.85 | 380 | 380 | 50 | N |  |  | OP | X | 9 | 1974 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: DFO; DFO NG NG: NG |  |  | N | N |  | OVER | [20 empty] | N |  |  | Y | Y | Y
Vintage1970 | petroleum | TRUE | 6035 | Exelon Power | 3161 | Eddystone Generating Station | PA | Delaware | 30 | Petroleum Liquids | GT |  | S | X | X | EDDYSTON13 KV UNIT30 | EDDYSTON13 KV UNIT30 | 21.2 | 0.85 | 17 | 20 | 5 | N |  |  | OP | X | 3 | 1970 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1976 | natural gas steam turbine | TRUE | 6035 | Exelon Power | 3161 | Eddystone Generating Station | PA | Delaware | 4 | Natural Gas Steam Turbine | ST |  | S | X | X | EDDYSTON20 KV UNIT04 | EDDYSTON20 KV UNIT04 | 391 | 0.85 | 380 | 380 | 50 | N |  |  | OP | X | 6 | 1976 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: DFO; DFO NG NG: NG |  |  | N | N |  | OVER | [20 empty] | N |  |  | Y | Y | Y
Vintage1970 | petroleum | TRUE | 6035 | Exelon Power | 3161 | Eddystone Generating Station | PA | Delaware | 40 | Petroleum Liquids | GT |  | S | X | X | EDDYSTON13 KV UNIT40 | EDDYSTON13 KV UNIT40 | 21.2 | 0.85 | 17 | 20 | 5 | N |  |  | OP | X | 6 | 1970 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1970 | petroleum | TRUE | 6035 | Exelon Power | 3162 | Falls | PA | Bucks | 1 | Petroleum Liquids | GT |  | S | X | X | FALLS 13 KV UNIT01 | FALLS 13 KV UNIT01 | 21.2 | 0.85 | 17 | 20 | 5 | N |  |  | OP | X | 5 | 1970 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1970 | petroleum | TRUE | 6035 | Exelon Power | 3162 | Falls | PA | Bucks | 2 | Petroleum Liquids | GT |  | S | X | X | FALLS 13 KV UNIT02 | FALLS 13 KV UNIT02 | 21.2 | 0.85 | 17 | 20 | 5 | N |  |  | OP | X | 5 | 1970 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1970 | petroleum | TRUE | 6035 | Exelon Power | 3162 | Falls | PA | Bucks | 3 | Petroleum Liquids | GT |  | S | X | X | FALLS 13 KV UNIT03 | FALLS 13 KV UNIT03 | 21.2 | 0.85 | 17 | 20 | 5 | N |  |  | OP | X | 6 | 1970 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1970 | petroleum | TRUE | 6035 | Exelon Power | 3163 | Moser Generating Station | PA | Montgomery | 1 | Petroleum Liquids | GT |  | S | X | X | MOSER 13 KV UNIT1 | MOSER 13 KV UNIT1 | 21.2 | 0.85 | 17 | 20 | 5 | N |  |  | OP | X | 6 | 1970 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1970 | petroleum | TRUE | 6035 | Exelon Power | 3163 | Moser Generating Station | PA | Montgomery | 2 | Petroleum Liquids | GT |  | S | X | X | MOSER 13 KV UNIT2 | MOSER 13 KV UNIT2 | 21.2 | 0.85 | 17 | 20 | 5 | N |  |  | OP | X | 5 | 1970 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1970 | petroleum | TRUE | 6035 | Exelon Power | 3163 | Moser Generating Station | PA | Montgomery | 3 | Petroleum Liquids | GT |  | S | X | X | MOSER 13 KV UNIT3 | MOSER 13 KV UNIT3 | 21.2 | 0.85 | 17 | 20 | 5 | N |  |  | OP | X | 6 | 1970 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1967 | other | TRUE | 6035 | Exelon Power | 3164 | Muddy Run | PA | Lancaster | 1 | Hydroelectric Pumped Storage | PS |  | S | X | X | MUDDYRN 13 KV UNIT1 | MUDDYRN 13 KV UNIT1 | 134 | 0.9 | 134 | 134 | 50 | N |  |  | OP | X | 4 | 1967 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1967 | other | TRUE | 6035 | Exelon Power | 3164 | Muddy Run | PA | Lancaster | 2 | Hydroelectric Pumped Storage | PS |  | S | X | X | MUDDYRN 13 KV UNIT2 | MUDDYRN 13 KV UNIT2 | 134 | 0.9 | 133 | 133 | 50 | N |  |  | OP | X | 4 | 1967 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1967 | other | TRUE | 6035 | Exelon Power | 3164 | Muddy Run | PA | Lancaster | 3 | Hydroelectric Pumped Storage | PS |  | S | X | X | MUDDYRN 13 KV UNIT3 | MUDDYRN 13 KV UNIT3 | 134 | 0.9 | 134 | 134 | 50 | N |  |  | OP | X | 4 | 1967 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1967 | other | TRUE | 6035 | Exelon Power | 3164 | Muddy Run | PA | Lancaster | 4 | Hydroelectric Pumped Storage | PS |  | S | X | X | MUDDYRN 13 KV UNIT4 | MUDDYRN 13 KV UNIT4 | 134 | 0.9 | 134 | 134 | 50 | N |  |  | OP | X | 6 | 1967 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1967 | other | TRUE | 6035 | Exelon Power | 3164 | Muddy Run | PA | Lancaster | 5 | Hydroelectric Pumped Storage | PS |  | S | X | X | MUDDYRN 13 KV UNIT5 | MUDDYRN 13 KV UNIT5 | 134 | 0.9 | 134 | 134 | 50 | N |  |  | OP | X | 10 | 1967 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1967 | other | TRUE | 6035 | Exelon Power | 3164 | Muddy Run | PA | Lancaster | 6 | Hydroelectric Pumped Storage | PS |  | S | X | X | MUDDYRN 13 KV UNIT6 | MUDDYRN 13 KV UNIT6 | 134 | 0.9 | 133 | 133 | 50 | N |  |  | OP | X | 10 | 1967 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1968 | other | TRUE | 6035 | Exelon Power | 3164 | Muddy Run | PA | Lancaster | 7 | Hydroelectric Pumped Storage | PS |  | S | X | X | MUDDYRN 13 KV UNIT7 | MUDDYRN 13 KV UNIT7 | 134 | 0.9 | 134 | 134 | 50 | N |  |  | OP | X | 2 | 1968 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1968 | other | TRUE | 6035 | Exelon Power | 3164 | Muddy Run | PA | Lancaster | 8 | Hydroelectric Pumped Storage | PS |  | S | X | X | MUDDYRN 13 KV UNIT8 | MUDDYRN 13 KV UNIT8 | 134 | 0.9 | 134 | 134 | 50 | N |  |  | OP | X | 2 | 1968 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1974 | nuclear | TRUE | 55951 | Exelon Nuclear | 3166 | Peach Bottom | PA | York | 2 | Nuclear | ST |  | J | X | X | 20141102 | 20141102 | 1499.4 | 0.98 | 1264.7 | 1345.1 | 115.8 | N |  |  | OP | X | 7 | 1974 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N
Vintage1974 | nuclear | TRUE | 55951 | Exelon Nuclear | 3166 | Peach Bottom | PA | York | 3 | Nuclear | ST |  | J | X | X | 20141103 | 20141103 | 1377 | 0.9 | 1284.7 | 1349.7 | 117.3 | N |  |  | OP | X | 12 | 1974 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N
Vintage1973 | petroleum | TRUE | 6035 | Exelon Power | 3168 | Richmond Generating Station | PA | Philadelphia | 91 | Petroleum Liquids | GT |  | S | X | X | RICH PE 13 KV UNIT91 | RICH PE 13 KV UNIT91 | 65.8 | 0.9 | 49 | 66 | 20 | N |  |  | OP | X | 6 | 1973 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1973 | petroleum | TRUE | 6035 | Exelon Power | 3168 | Richmond Generating Station | PA | Philadelphia | 92 | Petroleum Liquids | GT |  | S | X | X | RICH PE 13 KV UNIT92 | RICH PE 13 KV UNIT92 | 65.8 | 0.9 | 49 | 66 | 20 | N |  |  | OP | X | 6 | 1973 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1969 | petroleum | TRUE | 6035 | Exelon Power | 3169 | Schuylkill Generating Station | PA | Philadelphia | 10 | Petroleum Liquids | GT |  | S | X | X | SCHUYLKI13 KV UNIT10 | SCHUYLKI13 KV UNIT10 | 18.6 | 0.85 | 13 | 18 | 5 | N |  |  | OP | X | 5 | 1969 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1971 | petroleum | TRUE | 6035 | Exelon Power | 3169 | Schuylkill Generating Station | PA | Philadelphia | 11 | Petroleum Liquids | GT |  | S | X | X | SCHUYLKI13 KV UNIT11 | SCHUYLKI13 KV UNIT11 | 21.2 | 0.85 | 17 | 20 | 5 | N |  |  | OP | X | 6 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1967 | petroleum | TRUE | 6035 | Exelon Power | 3170 | Southwark | PA | Philadelphia | 3 | Petroleum Liquids | GT |  | S | X | X | SWARK 13 KV UNIT3 | SWARK 13 KV UNIT3 | 18.6 | 0.85 | 13 | 18 | 5 | N |  |  | OP | X | 6 | 1967 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N
Vintage1967 | petroleum | TRUE | 6035 | Exelon Power | 3170 | Southwark | PA | Philadelphia | 4 | Petroleum Liquids | GT |  | S | X | X | SWARK 13 KV UNIT4 | SWARK 13 KV UNIT4 | 18.6 | 0.85 | 13 | 18 | 5 | N |  |  | OP | X | 10 | 1967 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N
Vintage1967 | petroleum | TRUE | 6035 | Exelon Power | 3170 | Southwark | PA | Philadelphia | 5 | Petroleum Liquids | GT |  | S | X | X | SWARK 13 KV UNIT5 | SWARK 13 KV UNIT5 | 18.6 | 0.85 | 13 | 18 | 5 | N |  |  | OP | X | 7 | 1967 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N
Vintage1968 | petroleum | TRUE | 6035 | Exelon Power | 3170 | Southwark | PA | Philadelphia | 6 | Petroleum Liquids | GT |  | S | X | X | SWARK 13 KV UNIT6 | SWARK 13 KV UNIT6 | 18.6 | 0.85 | 13 | 18 | 5 | N |  |  | OP | X | 11 | 1968 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1940 | hydro | TRUE | 59364 | Safe Harbor | 3175 | Safe Harbor | PA | Lancaster | 1 | Conventional Hydroelectric | HY |  | S | X | X | 50639 | 50639 | 33 | 1 | 33 | 33 | 10 | N |  |  | OP | X | 10 | 1940 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1985 | hydro | TRUE | 59364 | Safe Harbor | 3175 | Safe Harbor | PA | Lancaster | 10 | Conventional Hydroelectric | HY |  | S | X | X | 50636 | 50636 | 37.5 | 1 | 37.5 | 37.5 | 33 | N |  |  | OP | X | 6 | 1985 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1986 | hydro | TRUE | 59364 | Safe Harbor | 3175 | Safe Harbor | PA | Lancaster | 11 | Conventional Hydroelectric | HY |  | S | X | X | 50637 | 50637 | 37.5 | 1 | 37.5 | 37.5 | 33 | N |  |  | OP | X | 4 | 1986 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1985 | hydro | TRUE | 59364 | Safe Harbor | 3175 | Safe Harbor | PA | Lancaster | 12 | Conventional Hydroelectric | HY |  | S | X | X | 50638 | 50638 | 37.5 | 1 | 37.5 | 37.5 | 33 | N |  |  | OP | X | 9 | 1985 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1934 | hydro | TRUE | 59364 | Safe Harbor | 3175 | Safe Harbor | PA | Lancaster | 2 | Conventional Hydroelectric | HY |  | S | X | X | 50640 | 50640 | 33 | 1 | 33 | 33 | 10 | N |  |  | OP | X | 11 | 1934 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1931 | hydro | TRUE | 59364 | Safe Harbor | 3175 | Safe Harbor | PA | Lancaster | 3 | Conventional Hydroelectric | HY |  | S | X | X | 50641 | 50641 | 32 | 1 | 32 | 32 | 10 | N |  |  | OP | X | 12 | 1931 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1931 | hydro | TRUE | 59364 | Safe Harbor | 3175 | Safe Harbor | PA | Lancaster | 4 | Conventional Hydroelectric | HY |  | S | X | X | 50642 | 50642 | 32 | 1 | 32 | 32 | 10 | N |  |  | OP | X | 12 | 1931 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1931 | hydro | TRUE | 59364 | Safe Harbor | 3175 | Safe Harbor | PA | Lancaster | 41 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0 | N |  |  | OP | X | 12 | 1931 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 1H
Vintage1931 | hydro | TRUE | 59364 | Safe Harbor | 3175 | Safe Harbor | PA | Lancaster | 42 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0 | N |  |  | OP | X | 12 | 1931 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1932 | hydro | TRUE | 59364 | Safe Harbor | 3175 | Safe Harbor | PA | Lancaster | 5 | Conventional Hydroelectric | HY |  | S | X | X | 50643 | 50643 | 32 | 1 | 32 | 32 | 10 | N |  |  | OP | X | 1 | 1932 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1932 | hydro | TRUE | 59364 | Safe Harbor | 3175 | Safe Harbor | PA | Lancaster | 6 | Conventional Hydroelectric | HY |  | S | X | X | 50644 | 50644 | 32 | 1 | 32 | 32 | 10 | N |  |  | OP | X | 1 | 1932 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1933 | hydro | TRUE | 59364 | Safe Harbor | 3175 | Safe Harbor | PA | Lancaster | 7 | Conventional Hydroelectric | HY |  | S | X | X | 50645 | 50645 | 32 | 1 | 32 | 32 | 10 | N |  |  | OP | X | 10 | 1933 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1985 | hydro | TRUE | 59364 | Safe Harbor | 3175 | Safe Harbor | PA | Lancaster | 8 | Conventional Hydroelectric | HY |  | S | X | X | 50634 | 50634 | 37.5 | 1 | 37.5 | 37.5 | 33 | N |  |  | OP | X | 4 | 1985 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1986 | hydro | TRUE | 59364 | Safe Harbor | 3175 | Safe Harbor | PA | Lancaster | 9 | Conventional Hydroelectric | HY |  | S | X | X | 50635 | 50635 | 37.5 | 1 | 37.5 | 37.5 | 33 | N |  |  | OP | X | 2 | 1986 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1959 | natural gas combined cycle | TRUE | 19391 | UGI Development Co | 3176 | Hunlock Power Station | PA | Luzerne | 3 | Natural Gas Fired Combined Cycle | CA | HUN1 | S | Y | X |  |  | 49.9 | 0.85 | 29.1 | 30.3 | 4 | N |  |  | OP | X | 9 | 1959 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H |  | N | [21 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2011 | natural gas combined cycle | TRUE | 19391 | UGI Development Co | 3176 | Hunlock Power Station | PA | Luzerne | 5 | Natural Gas Fired Combined Cycle | CT | HUN1 | S | X | N |  |  | 48 | 0.85 | 48 | 50.3 | 30 | N |  |  | OP | X | 7 | 2011 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2011 | natural gas combined cycle | TRUE | 19391 | UGI Development Co | 3176 | Hunlock Power Station | PA | Luzerne | 6 | Natural Gas Fired Combined Cycle | CT | HUN1 | S | X | N |  |  | 48 | 0.85 | 48.4 | 48.3 | 30 | N |  |  | OP | X | 7 | 2011 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1995 | natural gas combined cycle | TRUE | 63350 | Manchester Street, LLC. | 3236 | Manchester Street | RI | Providence | G10A | Natural Gas Fired Combined Cycle | CT | 321 | S | X | N |  |  | 125 | 0.85 | 110.1 | 115.6 | 70 | N |  |  | OP | X | 11 | 1995 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1995 | natural gas combined cycle | TRUE | 63350 | Manchester Street, LLC. | 3236 | Manchester Street | RI | Providence | G11A | Natural Gas Fired Combined Cycle | CT | 322 | S | X | N |  |  | 125 | 0.85 | 110.2 | 115.6 | 70 | N |  |  | OP | X | 9 | 1995 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1995 | natural gas combined cycle | TRUE | 63350 | Manchester Street, LLC. | 3236 | Manchester Street | RI | Providence | GE10 | Natural Gas Fired Combined Cycle | CA | 321 | S | N | X |  |  | 48 | 0.8 | 46.9 | 54.4 | 40 | N |  |  | OP | X | 11 | 1995 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1995 | natural gas combined cycle | TRUE | 63350 | Manchester Street, LLC. | 3236 | Manchester Street | RI | Providence | GE11 | Natural Gas Fired Combined Cycle | CA | 322 | S | N | X |  |  | 46 | 0.8 | 46.8 | 54.4 | 40 | N |  |  | OP | X | 9 | 1995 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1995 | natural gas combined cycle | TRUE | 63350 | Manchester Street, LLC. | 3236 | Manchester Street | RI | Providence | GE9A | Natural Gas Fired Combined Cycle | CT | 323 | S | X | N |  |  | 125 | 0.85 | 110.1 | 115.6 | 70 | N |  |  | OP | X | 11 | 1995 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1995 | natural gas combined cycle | TRUE | 63350 | Manchester Street, LLC. | 3236 | Manchester Street | RI | Providence | GEN9 | Natural Gas Fired Combined Cycle | CA | 323 | S | N | X |  |  | 46 | 0.8 | 46.9 | 54.5 | 40 | N |  |  | OP | X | 11 | 1995 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1997 | natural gas peaker | TRUE | 3046 | Duke Energy Progress - (NC) | 3250 | Darlington County | SC | Darlington | 12 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 158 | 0.9 | 118 | 131 | 40 | N |  |  | OP | X | 5 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1997 | natural gas peaker | TRUE | 3046 | Duke Energy Progress - (NC) | 3250 | Darlington County | SC | Darlington | 13 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 158 | 0.9 | 116 | 133 | 40 | N |  |  | OP | X | 6 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1971 | nuclear | TRUE | 3046 | Duke Energy Progress - (NC) | 3251 | H B Robinson | SC | Darlington | 2 | Nuclear | ST |  | S | X | X |  |  | 768.6 | 0.925 | 759 | 792.9 | 759 | N |  |  | OP | X | 3 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N | N
Vintage1996 | hydro | TRUE | 13763 | Northbrook Carolina Hydro LLC | 3253 | Boyds Mill Hydro | SC | Greenville | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.9 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 12 | 1996 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1996 | hydro | TRUE | 13763 | Northbrook Carolina Hydro LLC | 3253 | Boyds Mill Hydro | SC | Greenville | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.9 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 12 | 1996 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1940 | hydro | TRUE | 17543 | South Carolina Public Service Authority | 3254 | Buzzard Roost | SC | Greenwood | HC1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 5 | 0.8 | 2.3 | 2.3 | 1 | N |  |  | OP | X | 8 | 1940 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1940 | hydro | TRUE | 17543 | South Carolina Public Service Authority | 3254 | Buzzard Roost | SC | Greenwood | HC2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 5 | 0.8 | 2.3 | 2.3 | 1 | N |  |  | OP | X | 8 | 1940 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1940 | hydro | TRUE | 17543 | South Carolina Public Service Authority | 3254 | Buzzard Roost | SC | Greenwood | HC3 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 5 | 0.8 | 2.3 | 2.3 | 1 | N |  |  | OP | X | 8 | 1940 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1926 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 3255 | Cedar Creek | SC | Lancaster | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.8 | 15 | 15 | 15 | N |  |  | OP | X | 8 | 1926 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1926 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 3255 | Cedar Creek | SC | Lancaster | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.9 | 15 | 15 | 15 | N |  |  | OP | X | 8 | 1926 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1926 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 3255 | Cedar Creek | SC | Lancaster | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.9 | 15 | 15 | 15 | N |  |  | OP | X | 8 | 1926 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1923 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 3256 | Dearborn | SC | Chester | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.8 | 14 | 14 | 14 | N |  |  | OP | X | 3 | 1923 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1923 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 3256 | Dearborn | SC | Chester | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.8 | 14 | 14 | 14 | N |  |  | OP | X | 3 | 1923 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1923 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 3256 | Dearborn | SC | Chester | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.8 | 14 | 14 | 14 | N |  |  | OP | X | 3 | 1923 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1916 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 3257 | Fishing Creek | SC | Chester | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9.3 | 0.9 | 11 | 11 | 9.3 | N |  |  | OP | X | 11 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1916 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 3257 | Fishing Creek | SC | Chester | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8.8 | 0.9 | 10 | 10 | 8.8 | N |  |  | OP | X | 11 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1916 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 3257 | Fishing Creek | SC | Chester | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8.8 | 0.9 | 10 | 10 | 8.8 | N |  |  | OP | X | 11 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1916 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 3257 | Fishing Creek | SC | Chester | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9.4 | 0.9 | 11 | 11 | 9.4 | N |  |  | OP | X | 11 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1916 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 3257 | Fishing Creek | SC | Chester | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6 | 0.9 | 9 | 9 | 6 | N |  |  | OP | X | 11 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1908 | hydro | TRUE | 63010 | Northbrook Carolina Hydro II, LLC | 3258 | Gaston Shoals | SC | Cherokee | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.4 | 0.8 | 1 | 1 | 1 | N |  |  | OP | X | 8 | 1908 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1908 | hydro | TRUE | 63010 | Northbrook Carolina Hydro II, LLC | 3258 | Gaston Shoals | SC | Cherokee | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.4 | 0.8 | 2 | 2 | 1 | N |  |  | OP | X | 8 | 1908 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1908 | hydro | TRUE | 63010 | Northbrook Carolina Hydro II, LLC | 3258 | Gaston Shoals | SC | Cherokee | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.4 | 0.8 | 2 | 2 | 1 | N |  |  | OP | X | 5 | 1908 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1927 | hydro | TRUE | 63010 | Northbrook Carolina Hydro II, LLC | 3258 | Gaston Shoals | SC | Cherokee | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 2 | N |  |  | OP | X | 8 | 1927 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1907 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 3259 | Great Falls (SC) | SC | Chester | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 3 | N |  |  | OP | X | 4 | 1907 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1907 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 3259 | Great Falls (SC) | SC | Chester | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 3 | N |  |  | OP | X | 4 | 1907 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1907 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 3259 | Great Falls (SC) | SC | Chester | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 3 | N |  |  | OP | X | 4 | 1907 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1907 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 3259 | Great Falls (SC) | SC | Chester | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 3 | N |  |  | OP | X | 4 | 1907 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1996 | hydro | TRUE | 13763 | Northbrook Carolina Hydro LLC | 3261 | Hollidays Bridge Hydro | SC | Anderson | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.9 | 1.2 | 1.2 | 0.1 | N |  |  | OP | X | 12 | 1996 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1996 | hydro | TRUE | 13763 | Northbrook Carolina Hydro LLC | 3261 | Hollidays Bridge Hydro | SC | Anderson | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.9 | 1.2 | 1.2 | 0.1 | N |  |  | OP | X | 12 | 1996 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1996 | hydro | TRUE | 13763 | Northbrook Carolina Hydro LLC | 3261 | Hollidays Bridge Hydro | SC | Anderson | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.9 | 1.2 | 1.2 | 0.1 | N |  |  | OP | X | 12 | 1996 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1996 | hydro | TRUE | 13763 | Northbrook Carolina Hydro LLC | 3261 | Hollidays Bridge Hydro | SC | Anderson | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.9 | 1.2 | 1.2 | 0.1 | N |  |  | OP | X | 12 | 1996 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1973 | other | TRUE | 5416 | Duke Energy Carolinas, LLC | 3262 | Jocassee | SC | Pickens | 1 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 193.5 | 0.9 | 195 | 195 | 155 | N |  |  | OP | X | 12 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1973 | other | TRUE | 5416 | Duke Energy Carolinas, LLC | 3262 | Jocassee | SC | Pickens | 2 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 193.5 | 0.9 | 195 | 195 | 155 | N |  |  | OP | X | 12 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1975 | other | TRUE | 5416 | Duke Energy Carolinas, LLC | 3262 | Jocassee | SC | Pickens | 3 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 193.5 | 0.9 | 195 | 195 | 155 | N |  |  | OP | X | 5 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1975 | other | TRUE | 5416 | Duke Energy Carolinas, LLC | 3262 | Jocassee | SC | Pickens | 4 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 193.5 | 0.9 | 195 | 195 | 155 | N |  |  | OP | X | 5 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1958 | natural gas steam turbine | TRUE | 5416 | Duke Energy Carolinas, LLC | 3264 | W S Lee | SC | Anderson | 3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 163.2 | 0.85 | 170 | 173 | 45 | N |  |  | OP | X | 12 | 1958 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER |  | N |  |  | N | [18 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage2007 | natural gas peaker | TRUE | 5416 | Duke Energy Carolinas, LLC | 3264 | W S Lee | SC | Anderson | 7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 54 | 0.9 | 42 | 48 | 42 | N |  |  | OP | X | 1 | 2007 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO | [5 empty] | 10M | [23 empty] | Y | N | Y
Vintage2007 | natural gas peaker | TRUE | 5416 | Duke Energy Carolinas, LLC | 3264 | W S Lee | SC | Anderson | 8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 54 | 0.9 | 42 | 48 | 42 | N |  |  | OP | X | 1 | 2007 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO | [5 empty] | 10M | [23 empty] | Y | N | Y
Vintage2018 | natural gas combined cycle | TRUE | 5416 | Duke Energy Carolinas, LLC | 3264 | W S Lee | SC | Anderson | CT11 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 242.3 | 0.85 | 237 | 248 | 237 | N |  |  | OP | X | 4 | 2018 |  |  | N | Electric Utility | 1 | [14 empty] | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2018 | natural gas combined cycle | TRUE | 5416 | Duke Energy Carolinas, LLC | 3264 | W S Lee | SC | Anderson | CT12 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 242.3 | 0.85 | 236 | 248 | 236 | N |  |  | OP | X | 4 | 2018 |  |  | N | Electric Utility | 1 | [14 empty] | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2018 | natural gas combined cycle | TRUE | 5416 | Duke Energy Carolinas, LLC | 3264 | W S Lee | SC | Anderson | ST10 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 362.1 | 0.85 | 313 | 313 | 313 | N |  |  | OP | X | 4 | 2018 |  |  | N | Electric Utility | 1 | [14 empty] | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1973 | nuclear | TRUE | 5416 | Duke Energy Carolinas, LLC | 3265 | Oconee | SC | Oconee | 1 | Nuclear | ST |  | S | X | X |  |  | 886.7 | 0.9 | 847 | 865 | 847 | N |  |  | OP | X | 7 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [7 empty] | 15 | 15 | 1 | 2024 | [12 empty] | N | N
Vintage1974 | nuclear | TRUE | 5416 | Duke Energy Carolinas, LLC | 3265 | Oconee | SC | Oconee | 2 | Nuclear | ST |  | S | X | X |  |  | 886.7 | 0.9 | 848 | 872 | 848 | N |  |  | OP | X | 9 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [7 empty] | 15 | 15 | 1 | 2024 | [12 empty] | N | N
Vintage1974 | nuclear | TRUE | 5416 | Duke Energy Carolinas, LLC | 3265 | Oconee | SC | Oconee | 3 | Nuclear | ST |  | S | X | X |  |  | 893.3 | 0.9 | 859 | 881 | 859 | N |  |  | OP | X | 12 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [7 empty] | 15 | 15 | 1 | 2024 | [12 empty] | N | N
Vintage1996 | hydro | TRUE | 13763 | Northbrook Carolina Hydro LLC | 3267 | Saluda Dam | SC | Greenville | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.9 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 12 | 1996 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1996 | hydro | TRUE | 13763 | Northbrook Carolina Hydro LLC | 3267 | Saluda Dam | SC | Greenville | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.9 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 12 | 1996 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M | [23 empty] | N
Vintage1996 | hydro | TRUE | 13763 | Northbrook Carolina Hydro LLC | 3267 | Saluda Dam | SC | Greenville | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.9 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 12 | 1996 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M | [23 empty] | N
Vintage1996 | hydro | TRUE | 13763 | Northbrook Carolina Hydro LLC | 3267 | Saluda Dam | SC | Greenville | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.9 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 12 | 1996 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M | [23 empty] | N
Vintage1919 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 3270 | Wateree Hydro | SC | Kershaw | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18.1 | 0.95 | 17 | 17 | 11.2 | N |  |  | OP | X | 10 | 1919 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M
Vintage1919 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 3270 | Wateree Hydro | SC | Kershaw | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18.1 | 0.95 | 17 | 17 | 11.2 | N |  |  | OP | X | 10 | 1919 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M
Vintage1919 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 3270 | Wateree Hydro | SC | Kershaw | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18.1 | 0.95 | 17 | 17 | 11.2 | N |  |  | OP | X | 10 | 1919 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M
Vintage1919 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 3270 | Wateree Hydro | SC | Kershaw | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18.1 | 0.95 | 17 | 17 | 11.2 | N |  |  | OP | X | 10 | 1919 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M
Vintage1919 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 3270 | Wateree Hydro | SC | Kershaw | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18.1 | 0.95 | 17 | 17 | 11.2 | N |  |  | OP | X | 10 | 1919 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M
Vintage1925 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 3271 | Wylie | SC | York | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.9 | 18 | 18 | 15 | N |  |  | OP | X | 8 | 1925 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M
Vintage1925 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 3271 | Wylie | SC | York | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.9 | 18 | 18 | 15 | N |  |  | OP | X | 8 | 1925 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M
Vintage1925 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 3271 | Wylie | SC | York | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.9 | 18 | 18 | 15 | N |  |  | OP | X | 8 | 1925 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M
Vintage1925 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 3271 | Wylie | SC | York | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.9 | 6 | 6 | 6 | N |  |  | OP | X | 8 | 1925 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M
Vintage1910 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 3272 | 99 Islands | SC | Cherokee | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.8 | 4.2 | 4.2 | 1.6 | N |  |  | OP | X | 5 | 1910 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M
Vintage1910 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 3272 | 99 Islands | SC | Cherokee | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 1 | 3.4 | 3.4 | 1.6 | N |  |  | OP | X | 5 | 1910 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M
Vintage1910 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 3272 | 99 Islands | SC | Cherokee | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.8 | 4.2 | 4.2 | 1.6 | N |  |  | OP | X | 5 | 1910 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M
Vintage1910 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 3272 | 99 Islands | SC | Cherokee | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 1 | 3.4 | 3.4 | 1.6 | N |  |  | OP | X | 5 | 1910 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M
Vintage1921 | hydro | TRUE | 11118 | Lockhart Power Co | 3275 | Lockhart | SC | Union | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.2 | 0.8 | 4.2 | 4.2 | 1 | N |  |  | OP | X | 1 | 1921 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1921 | hydro | TRUE | 11118 | Lockhart Power Co | 3275 | Lockhart | SC | Union | HY1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.2 | 0.8 | 4.2 | 4.2 | 1 | N |  |  | OP | X | 1 | 1921 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1921 | hydro | TRUE | 11118 | Lockhart Power Co | 3275 | Lockhart | SC | Union | HY3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.2 | 0.8 | 4.2 | 4.2 | 1 | N |  |  | OP | X | 1 | 1921 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1921 | hydro | TRUE | 11118 | Lockhart Power Co | 3275 | Lockhart | SC | Union | HY4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.2 | 0.8 | 4.2 | 4.2 | 1 | N |  |  | OP | X | 1 | 1921 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1921 | hydro | TRUE | 11118 | Lockhart Power Co | 3275 | Lockhart | SC | Union | HY5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 0.8 | N |  |  | OP | X | 1 | 1921 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1969 | natural gas peaker | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3281 | Coit GT | SC | Richland | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 19.6 | 0.85 | 14 | 18 | 1 | N |  |  | OP | X | 7 | 1969 | 9 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1969 | natural gas peaker | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3281 | Coit GT | SC | Richland | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 19.6 | 0.85 | 12 | 18 | 1 | N |  |  | OP | X | 5 | 1969 | 9 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1929 | hydro | TRUE | 57221 | City of Columbia SC | 3283 | Columbia Canal Hydro | SC | Richland | 1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.6 | 0.8 | 1.3 | 1.3 | 1 | N |  |  | OS | X | 6 | 1929 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1929 | hydro | TRUE | 57221 | City of Columbia SC | 3283 | Columbia Canal Hydro | SC | Richland | 2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.6 | 0.8 | 1.7 | 1.7 | 1 | N |  |  | OS | X | 6 | 1929 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1929 | hydro | TRUE | 57221 | City of Columbia SC | 3283 | Columbia Canal Hydro | SC | Richland | 3 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.6 | 0.8 | 1.3 | 1.3 | 1 | N |  |  | OS | X | 6 | 1929 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1953 | hydro | TRUE | 57221 | City of Columbia SC | 3283 | Columbia Canal Hydro | SC | Richland | 4 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 1 | N |  |  | OS | X | 6 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1953 | hydro | TRUE | 57221 | City of Columbia SC | 3283 | Columbia Canal Hydro | SC | Richland | 5 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.3 | 0.8 | 1.7 | 1.7 | 1 | N |  |  | OS | X | 6 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1928 | hydro | TRUE | 57221 | City of Columbia SC | 3283 | Columbia Canal Hydro | SC | Richland | 6 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.6 | 0.8 | 1.3 | 1.3 | 1 | N |  |  | OS | X | 6 | 1928 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1927 | hydro | TRUE | 57221 | City of Columbia SC | 3283 | Columbia Canal Hydro | SC | Richland | 7 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.6 | 0.8 | 1.3 | 1.3 | 1 | N |  |  | OS | X | 6 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1991 | natural gas peaker | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3285 | Hagood | SC | Charleston | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 122 | 0.85 | 88 | 99 | 40 | N |  |  | OP | X | 6 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2009 | natural gas peaker | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3285 | Hagood | SC | Charleston | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 27.4 | 0.85 | 18 | 21 | 2.5 | N |  |  | OP | X | 12 | 2009 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2010 | natural gas peaker | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3285 | Hagood | SC | Charleston | 6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 27.9 | 0.85 | 20 | 21 | 2.5 | N |  |  | OP | X | 2 | 2010 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1968 | petroleum | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3286 | Hardeeville | SC | Jasper | 1 | Petroleum Liquids | GT |  | S | X | X |  |  | 16.3 | 0.8 | 9 | 9 | 3 | N |  |  | OS | X | 4 | 1968 | 3 | 2022 | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1958 | natural gas steam turbine | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3287 | McMeekin | SC | Lexington | 1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 146.8 | 0.85 | 125 | 125 | 35 | N |  |  | OP | X | 7 | 1958 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER |  | N |  |  | N | [18 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1958 | natural gas steam turbine | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3287 | McMeekin | SC | Lexington | 2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 146.8 | 0.85 | 125 | 125 | 35 | N |  |  | OP | X | 12 | 1958 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER |  | N |  |  | N | [18 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1905 | hydro | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3289 | Neal Shoals | SC | Union | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.1 | 0.85 | 1.1 | 1.1 | 0.3 | N |  |  | OP | X | 6 | 1905 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1905 | hydro | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3289 | Neal Shoals | SC | Union | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.1 | 0.85 | 1.1 | 1.1 | 0.3 | N |  |  | OP | X | 6 | 1905 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1905 | hydro | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3289 | Neal Shoals | SC | Union | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.1 | 0.85 | 1.1 | 1.1 | 0.3 | N |  |  | OP | X | 6 | 1905 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1905 | hydro | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3289 | Neal Shoals | SC | Union | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.1 | 0.85 | 1.1 | 1.1 | 0.3 | N |  |  | OP | X | 6 | 1905 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1914 | hydro | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3290 | Parr Hydro | SC | Fairfield | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 0.2 | N |  |  | OP | X | 8 | 1914 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [7 empty] | 2.2 | 2.2 | 9 | 2023 | [12 empty] | N
Vintage1914 | hydro | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3290 | Parr Hydro | SC | Fairfield | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 0.2 | N |  |  | OP | X | 8 | 1914 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [7 empty] | 2.2 | 2.2 | 9 | 2026 | [12 empty] | N
Vintage1914 | hydro | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3290 | Parr Hydro | SC | Fairfield | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 0.2 | N |  |  | OA | X | 8 | 1914 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [7 empty] | 0.5 | 0.5 | 10 | 2022 | [12 empty] | N
Vintage1914 | hydro | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3290 | Parr Hydro | SC | Fairfield | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 0.2 | N |  |  | OP | X | 8 | 1914 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [7 empty] | 2.2 | 2.2 | 9 | 2028 | [12 empty] | N
Vintage1914 | hydro | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3290 | Parr Hydro | SC | Fairfield | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 0.2 | N |  |  | OP | X | 8 | 1914 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [7 empty] | 2.2 | 2.2 | 9 | 2029 | [12 empty] | N
Vintage1921 | hydro | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3290 | Parr Hydro | SC | Fairfield | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 0.2 | N |  |  | OP | X | 8 | 1921 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [7 empty] | 2.2 | 2.2 | 9 | 2027 | [12 empty] | N
Vintage1970 | natural gas peaker | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3291 | Parr GT | SC | Fairfield | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 19.6 | 0.85 | 13.5 | 17 | 1 | N |  |  | OS | X | 7 | 1970 | 4 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1970 | natural gas peaker | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3291 | Parr GT | SC | Fairfield | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 19.6 | 0.85 | 13.5 | 17 | 1 | N |  |  | OP | X | 7 | 1970 | 4 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1971 | natural gas peaker | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3291 | Parr GT | SC | Fairfield | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 22.3 | 0.85 | 16.5 | 19.5 | 1 | N |  |  | OP | X | 6 | 1971 | 4 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1971 | natural gas peaker | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3291 | Parr GT | SC | Fairfield | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 22.3 | 0.85 | 16.5 | 19.5 | 1 | N |  |  | OP | X | 6 | 1971 | 4 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1930 | hydro | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3293 | Saluda Lexington | SC | Lexington | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 32.5 | 0.8 | 32.5 | 32.5 | 1.5 | N |  |  | OP | X | 8 | 1930 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [7 empty] | 8 | 8 | 9 | 2031 | [12 empty] | N
Vintage1930 | hydro | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3293 | Saluda Lexington | SC | Lexington | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 32.5 | 0.8 | 32.5 | 32.5 | 1.5 | N |  |  | OP | X | 8 | 1930 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [7 empty] | 8 | 8 | 9 | 2033 | [12 empty] | N
Vintage1930 | hydro | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3293 | Saluda Lexington | SC | Lexington | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 42.3 | 0.9 | 35 | 35 | 2 | N |  |  | OP | X | 8 | 1930 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [7 empty] | 8 | 8 | 9 | 2027 | [12 empty] | N
Vintage1930 | hydro | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3293 | Saluda Lexington | SC | Lexington | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 32.5 | 0.8 | 32.5 | 32.5 | 1.5 | N |  |  | OP | X | 8 | 1930 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [7 empty] | 8 | 8 | 9 | 2029 | [12 empty] | N
Vintage1971 | hydro | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3293 | Saluda Lexington | SC | Lexington | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 67.5 | 0.9 | 66 | 66 | 4 | N |  |  | OP | X | 7 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [7 empty] | 16 | 17 | 9 | 2025 | [12 empty] | N
Vintage1953 | natural gas combined cycle | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3295 | Urquhart | SC | Aiken | 1 | Natural Gas Fired Combined Cycle | CA | UR15 | S | N | X |  |  | 75 | 0.8 | 64 | 65 | 50 | N |  |  | OP | X | 12 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1954 | natural gas combined cycle | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3295 | Urquhart | SC | Aiken | 2 | Natural Gas Fired Combined Cycle | CA | UR26 | S | N | X |  |  | 75 | 0.8 | 64 | 66 | 50 | N |  |  | OP | X | 2 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1955 | natural gas steam turbine | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3295 | Urquhart | SC | Aiken | 3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 100 | 0.8 | 95 | 96 | 30 | N |  |  | OP | X | 11 | 1955 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER |  | N | [21 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage2002 | natural gas combined cycle | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3295 | Urquhart | SC | Aiken | CT1 | Natural Gas Fired Combined Cycle | CT | UR15 | S | X | N |  |  | 198.9 | 0.8 | 162 | 177 | 75 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2002 | natural gas combined cycle | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3295 | Urquhart | SC | Aiken | CT2 | Natural Gas Fired Combined Cycle | CT | UR26 | S | X | N |  |  | 198.9 | 0.85 | 168 | 176 | 75 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1969 | natural gas peaker | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3295 | Urquhart | SC | Aiken | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 19.6 | 0.85 | 13 | 16 | 5 | N |  |  | OP | X | 10 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1969 | natural gas peaker | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3295 | Urquhart | SC | Aiken | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 16.3 | 0.85 | 14 | 17 | 5 | N |  |  | OP | X | 8 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1969 | natural gas peaker | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3295 | Urquhart | SC | Aiken | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 16.3 | 0.85 | 12 | 15 | 5 | N |  |  | OP | X | 7 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1999 | natural gas peaker | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3295 | Urquhart | SC | Aiken | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 58.9 | 0.85 | 48 | 49 | 15 | N |  |  | OP | X | 6 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1970 | hard coal | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3297 | Wateree | SC | Richland | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 385.9 | 0.85 | 342 | 342 | 220 | N |  |  | OP | X | 9 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | N | N | N
Vintage1971 | hard coal | TRUE | 17539 | Dominion Energy South Carolina, Inc | 3297 | Wateree | SC | Richland | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 385.9 | 0.85 | 342 | 342 | 220 | N |  |  | OP | X | 12 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | N | N | N
Vintage1972 | natural gas peaker | TRUE | 17554 | South Carolina Genertg Co, Inc | 3298 | Williams | SC | Berkeley | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 26.9 | 0.85 | 20 | 26 | 5 | N |  |  | OS | X | 6 | 1972 | 12 | 2022 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1972 | natural gas peaker | TRUE | 17554 | South Carolina Genertg Co, Inc | 3298 | Williams | SC | Berkeley | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 26.9 | 0.85 | 20 | 26 | 5 | N |  |  | OP | X | 6 | 1972 | 12 | 2022 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1973 | hard coal | TRUE | 17554 | South Carolina Genertg Co, Inc | 3298 | Williams | SC | Berkeley | ST1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 659.7 | 0.9 | 605 | 610 | 270 | N |  |  | OP | X | 7 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: RC; DFO DFO DFO: DFO; DFO NG NG: NG |  |  | N | N |  | OVER |  | Y |  |  | N | Y | [17 empty] | N | N | N
Vintage1941 | hydro | TRUE | 34 | City of Abbeville - (SC) | 3305 | Rocky River (SC) | SC | Anderson | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.2 | N |  |  | OA | X | 1 | 1941 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1941 | hydro | TRUE | 34 | City of Abbeville - (SC) | 3305 | Rocky River (SC) | SC | Anderson | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.2 | N |  |  | OA | X | 1 | 1941 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage2013 | petroleum | TRUE | 34 | City of Abbeville - (SC) | 3305 | Rocky River (SC) | SC | Anderson | IC2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1 | 1 | 0.2 | N |  |  | OP | X | 5 | 2013 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1973 | petroleum | TRUE | 17543 | South Carolina Public Service Authority | 3318 | Hilton Head | SC | Beaufort | 1 | Petroleum Liquids | GT |  | S | X | X |  |  | 26.6 | 0.9 | 16 | 20 | 2 | N |  |  | OP | X | 8 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1974 | petroleum | TRUE | 17543 | South Carolina Public Service Authority | 3318 | Hilton Head | SC | Beaufort | 2 | Petroleum Liquids | GT |  | S | X | X |  |  | 26.6 | 0.9 | 16 | 20 | 2 | N |  |  | OP | X | 8 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1979 | petroleum | TRUE | 17543 | South Carolina Public Service Authority | 3318 | Hilton Head | SC | Beaufort | 3 | Petroleum Liquids | GT |  | S | X | X |  |  | 64.7 | 0.9 | 52 | 60 | 7 | N |  |  | OP | X | 4 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1942 | hydro | TRUE | 17543 | South Carolina Public Service Authority | 3319 | Jefferies | SC | Berkeley | H1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 30.6 | 0.9 | 31 | 31 | 18 | N |  |  | OP | X | 12 | 1942 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1942 | hydro | TRUE | 17543 | South Carolina Public Service Authority | 3319 | Jefferies | SC | Berkeley | H2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 36.9 | 0.9 | 36 | 36 | 13 | N |  |  | OP | X | 12 | 1942 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1942 | hydro | TRUE | 17543 | South Carolina Public Service Authority | 3319 | Jefferies | SC | Berkeley | H3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 30.6 | 0.9 | 29 | 29 | 18 | N |  |  | OP | X | 12 | 1942 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1942 | hydro | TRUE | 17543 | South Carolina Public Service Authority | 3319 | Jefferies | SC | Berkeley | H4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 36.9 | 0.9 | 36 | 36 | 13 | N |  |  | OP | X | 12 | 1942 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1942 | hydro | TRUE | 17543 | South Carolina Public Service Authority | 3319 | Jefferies | SC | Berkeley | H6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10.2 | 0.9 | 8 | 8 | 8 | N |  |  | OP | X | 12 | 1942 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1972 | petroleum | TRUE | 17543 | South Carolina Public Service Authority | 3320 | Myrtle Beach | SC | Horry | 1 | Petroleum Liquids | GT |  | S | X | X |  |  | 11.5 | 0.85 | 8 | 10 | 3 | N |  |  | OP | X | 8 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H |  | N | [21 empty] | N | N | N
Vintage1962 | petroleum | TRUE | 17543 | South Carolina Public Service Authority | 3320 | Myrtle Beach | SC | Horry | 2 | Petroleum Liquids | GT |  | S | X | X |  |  | 11.5 | 0.85 | 8 | 10 | 3 | N |  |  | OP | X | 5 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H |  | N | [21 empty] | N | N | N
Vintage1962 | petroleum | TRUE | 17543 | South Carolina Public Service Authority | 3320 | Myrtle Beach | SC | Horry | 3 | Petroleum Liquids | GT |  | S | X | X |  |  | 26.6 | 0.9 | 19 | 20 | 4 | N |  |  | OP | X | 5 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H |  | N | [21 empty] | N | N | N
Vintage1972 | petroleum | TRUE | 17543 | South Carolina Public Service Authority | 3320 | Myrtle Beach | SC | Horry | 4 | Petroleum Liquids | GT |  | S | X | X |  |  | 26.6 | 0.9 | 19 | 20 | 4 | N |  |  | OP | X | 8 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1976 | petroleum | TRUE | 17543 | South Carolina Public Service Authority | 3320 | Myrtle Beach | SC | Horry | 5 | Petroleum Liquids | GT |  | S | X | X |  |  | 35.3 | 0.9 | 21 | 25 | 10 | N |  |  | OP | X | 6 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1950 | hydro | TRUE | 17543 | South Carolina Public Service Authority | 3321 | Spillway | SC | Berkeley | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1.5 | N |  |  | OP | X | 8 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1953 | hydro | TRUE | 19375 | USCE-Savannah District | 3323 | J Strom Thurmond | SC | McCormick | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 51.7 | 0.9 | 48 | 48 | 25 | N |  |  | OP | X | 1 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage1953 | hydro | TRUE | 19375 | USCE-Savannah District | 3323 | J Strom Thurmond | SC | McCormick | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 51.7 | 0.9 | 48 | 48 | 25 | N |  |  | OP | X | 1 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage1953 | hydro | TRUE | 19375 | USCE-Savannah District | 3323 | J Strom Thurmond | SC | McCormick | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 51.7 | 0.9 | 48 | 48 | 25 | N |  |  | OP | X | 1 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage1953 | hydro | TRUE | 19375 | USCE-Savannah District | 3323 | J Strom Thurmond | SC | McCormick | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 51.7 | 0.9 | 48 | 48 | 25 | N |  |  | OP | X | 1 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage1954 | hydro | TRUE | 19375 | USCE-Savannah District | 3323 | J Strom Thurmond | SC | McCormick | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 51.7 | 0.9 | 48 | 48 | 25 | N |  |  | OP | X | 1 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage1954 | hydro | TRUE | 19375 | USCE-Savannah District | 3323 | J Strom Thurmond | SC | McCormick | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 51.7 | 0.9 | 48 | 48 | 25 | N |  |  | OP | X | 1 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage1954 | hydro | TRUE | 19375 | USCE-Savannah District | 3323 | J Strom Thurmond | SC | McCormick | 7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 51.7 | 0.9 | 48 | 48 | 25 | N |  |  | OP | X | 1 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M | [23 empty] | N
Vintage1965 | petroleum | TRUE | 19545 | Black Hills Power, Inc. | 3325 | Ben French | SD | Pennington | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 7 | 1965 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1965 | petroleum | TRUE | 19545 | Black Hills Power, Inc. | 3325 | Ben French | SD | Pennington | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 7 | 1965 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1965 | petroleum | TRUE | 19545 | Black Hills Power, Inc. | 3325 | Ben French | SD | Pennington | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 7 | 1965 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1965 | petroleum | TRUE | 19545 | Black Hills Power, Inc. | 3325 | Ben French | SD | Pennington | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 7 | 1965 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1965 | petroleum | TRUE | 19545 | Black Hills Power, Inc. | 3325 | Ben French | SD | Pennington | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 7 | 1965 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1977 | natural gas peaker | TRUE | 19545 | Black Hills Power, Inc. | 3325 | Ben French | SD | Pennington | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 25 | 0.9 | 17 | 25 | 2 | N |  |  | OP | X | 7 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | Y | N | Y
Vintage1977 | natural gas peaker | TRUE | 19545 | Black Hills Power, Inc. | 3325 | Ben French | SD | Pennington | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 25 | 0.9 | 17 | 25 | 2 | N |  |  | OP | X | 8 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | Y | N | Y
Vintage1978 | natural gas peaker | TRUE | 19545 | Black Hills Power, Inc. | 3325 | Ben French | SD | Pennington | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 25 | 0.9 | 17 | 25 | 2 | N |  |  | OP | X | 6 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M |  |  |  |  | N | [15 empty] | N |  |  | Y | N | Y
Vintage1979 | natural gas peaker | TRUE | 19545 | Black Hills Power, Inc. | 3325 | Ben French | SD | Pennington | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 25 | 0.9 | 17 | 25 | 2 | N |  |  | OP | X | 6 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [20 empty] | N |  |  | Y | N | Y
Vintage2013 | natural gas peaker | TRUE | 13809 | NorthWestern Energy - (SD) | 3338 | Aberdeen CT | SD | Brown | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  | WAUE.NWPS.AB2 | 82.2 | 0.85 | 52 | 60 | 15 | N |  |  | OP | X | 4 | 2013 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y |  | Y
Vintage1978 | petroleum | TRUE | 13809 | NorthWestern Energy - (SD) | 3338 | Aberdeen CT | SD | Brown | GT1 | Petroleum Liquids | GT |  | S | X | X |  | WAUE.NWPS.AB1 | 28.8 | 0.9 | 20.5 | 28 | 1.7 | N |  |  | OP | X | 5 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage1970 | petroleum | TRUE | 13809 | NorthWestern Energy - (SD) | 3341 | Clark (SD) | SD | Clark | 1 | Petroleum Liquids | IC |  | S | X | X |  | WAUE_NWPS_NTWK | 2.7 | 0.8 | 2.6 | 2.7 | 1.2 | N |  |  | SB | Y | 1 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1969 | petroleum | TRUE | 13809 | NorthWestern Energy - (SD) | 3342 | Faulkton | SD | Faulk | 1 | Petroleum Liquids | IC |  | S | X | X |  | WAUE_NWPS_NTWK | 2.7 | 0.8 | 2.5 | 2.5 | 1.2 | N |  |  | SB | Y | 3 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1961 | natural gas peaker | TRUE | 13809 | NorthWestern Energy - (SD) | 3344 | Huron | SD | Beadle | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  | WAUE.NWPS.HURON1 | 15 | 0.85 | 11 | 14.5 | 0.5 | N |  |  | SB | Y | 1 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1978 | petroleum | TRUE | 14232 | Otter Tail Power Co | 3352 | Lake Preston | SD | Kingsbury | 1A | Petroleum Liquids | GT |  | S | X | X | OTP.HETLA | OTP.HETLA | 24.1 | 0.9 | 19.9 | 24.1 | 6 | N |  |  | SB | Y | 6 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1962 | hydro | TRUE | 19635 | USACE-Omaha | 3356 | Oahe | SD | Hughes | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 112.3 | 0.95 | 102 | 102 | 0 | N |  |  | OP | X | 4 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1962 | hydro | TRUE | 19635 | USACE-Omaha | 3356 | Oahe | SD | Hughes | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 112.3 | 0.95 | 102 | 102 | 0 | N |  |  | OP | X | 12 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1962 | hydro | TRUE | 19635 | USACE-Omaha | 3356 | Oahe | SD | Hughes | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 112.3 | 0.95 | 102 | 102 | 0 | N |  |  | OP | X | 7 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1962 | hydro | TRUE | 19635 | USACE-Omaha | 3356 | Oahe | SD | Hughes | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 112.3 | 0.95 | 102 | 102 | 0 | N |  |  | OP | X | 10 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1963 | hydro | TRUE | 19635 | USACE-Omaha | 3356 | Oahe | SD | Hughes | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 112.3 | 0.95 | 102 | 102 | 0 | N |  |  | OP | X | 3 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1963 | hydro | TRUE | 19635 | USACE-Omaha | 3356 | Oahe | SD | Hughes | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 112.3 | 0.95 | 102 | 102 | 0 | N |  |  | OP | X | 5 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1963 | hydro | TRUE | 19635 | USACE-Omaha | 3356 | Oahe | SD | Hughes | 7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 112.3 | 0.95 | 102 | 102 | 0 | N |  |  | OP | X | 6 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1954 | hydro | TRUE | 19635 | USACE-Omaha | 3373 | Fort Randall | SD | Charles Mix | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40 | 0.95 | 45 | 45 | 0 | N |  |  | OP | X | 3 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1954 | hydro | TRUE | 19635 | USACE-Omaha | 3373 | Fort Randall | SD | Charles Mix | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40 | 0.95 | 45 | 45 | 0 | N |  |  | OP | X | 5 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1954 | hydro | TRUE | 19635 | USACE-Omaha | 3373 | Fort Randall | SD | Charles Mix | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40 | 0.95 | 45 | 45 | 0 | N |  |  | OP | X | 10 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1954 | hydro | TRUE | 19635 | USACE-Omaha | 3373 | Fort Randall | SD | Charles Mix | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40 | 0.95 | 45 | 45 | 0 | N |  |  | OP | X | 10 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1955 | hydro | TRUE | 19635 | USACE-Omaha | 3373 | Fort Randall | SD | Charles Mix | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40 | 0.95 | 45 | 45 | 0 | N |  |  | OP | X | 2 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1955 | hydro | TRUE | 19635 | USACE-Omaha | 3373 | Fort Randall | SD | Charles Mix | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40 | 0.95 | 45 | 45 | 0 | N |  |  | OP | X | 6 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1955 | hydro | TRUE | 19635 | USACE-Omaha | 3373 | Fort Randall | SD | Charles Mix | 7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40 | 0.95 | 45 | 45 | 0 | N |  |  | OP | X | 10 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1956 | hydro | TRUE | 19635 | USACE-Omaha | 3373 | Fort Randall | SD | Charles Mix | 8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40 | 0.95 | 45 | 45 | 0 | N |  |  | OP | X | 1 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1964 | hydro | TRUE | 19635 | USACE-Omaha | 3375 | Big Bend Dam | SD | Buffalo | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 67.3 | 0.95 | 65 | 65 | 0 | N |  |  | OP | X | 9 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1964 | hydro | TRUE | 19635 | USACE-Omaha | 3375 | Big Bend Dam | SD | Buffalo | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 67.3 | 0.95 | 65 | 65 | 0 | N |  |  | OP | X | 11 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1965 | hydro | TRUE | 19635 | USACE-Omaha | 3375 | Big Bend Dam | SD | Buffalo | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 67.2 | 0.95 | 65 | 65 | 0 | N |  |  | OP | X | 2 | 1965 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1965 | hydro | TRUE | 19635 | USACE-Omaha | 3375 | Big Bend Dam | SD | Buffalo | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 67.3 | 0.95 | 65 | 65 | 0 | N |  |  | OP | X | 5 | 1965 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1965 | hydro | TRUE | 19635 | USACE-Omaha | 3375 | Big Bend Dam | SD | Buffalo | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 67.3 | 0.95 | 65 | 65 | 0 | N |  |  | OP | X | 9 | 1965 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1965 | hydro | TRUE | 19635 | USACE-Omaha | 3375 | Big Bend Dam | SD | Buffalo | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 67.3 | 0.95 | 65 | 65 | 0 | N |  |  | OP | X | 12 | 1965 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1966 | hydro | TRUE | 19635 | USACE-Omaha | 3375 | Big Bend Dam | SD | Buffalo | 7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 67.3 | 0.95 | 65 | 65 | 0 | N |  |  | OP | X | 5 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1966 | hydro | TRUE | 19635 | USACE-Omaha | 3375 | Big Bend Dam | SD | Buffalo | 8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 67.3 | 0.95 | 65 | 65 | 0 | N |  |  | OP | X | 7 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage2018 | natural gas combined cycle | TRUE | 18642 | Tennessee Valley Authority | 3393 | Allen | TN | Shelby | CTG1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 347 | 0.85 | 311.9 | 330.3 |  | N |  |  | OP | X | 4 | 2018 | 12 | 2023 | N | Electric Utility | 1 | [14 empty] | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2018 | natural gas combined cycle | TRUE | 18642 | Tennessee Valley Authority | 3393 | Allen | TN | Shelby | CTG2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 347 | 0.85 | 311.9 | 330.3 |  | N |  |  | OP | X | 4 | 2018 | 12 | 2023 | N | Electric Utility | 1 | [14 empty] | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1971 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3393 | Allen | TN | Shelby | G10 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 23.9 | 0.9 | 15.1 | 20.4 | 5 | N |  |  | OP | X | 6 | 1971 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1971 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3393 | Allen | TN | Shelby | G11 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 23.9 | 0.9 | 15.1 | 20.4 | 5 | N |  |  | OP | X | 6 | 1971 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1971 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3393 | Allen | TN | Shelby | G12 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 23.9 | 0.9 | 15.1 | 20.4 | 5 | N |  |  | OP | X | 6 | 1971 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1971 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3393 | Allen | TN | Shelby | G13 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 23.9 | 0.9 | 15.1 | 20.4 | 5 | N |  |  | OP | X | 6 | 1971 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1971 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3393 | Allen | TN | Shelby | G14 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 23.9 | 0.9 | 15.1 | 20.4 | 5 | N |  |  | OP | X | 6 | 1971 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1971 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3393 | Allen | TN | Shelby | G15 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 23.9 | 0.9 | 15.1 | 20.4 | 5 | N |  |  | OP | X | 6 | 1971 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1971 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3393 | Allen | TN | Shelby | G16 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 23.9 | 0.9 | 15.1 | 20.4 | 5 | N |  |  | OP | X | 6 | 1971 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1972 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3393 | Allen | TN | Shelby | G17 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 59.6 | 0.9 | 46.4 | 62.2 | 10 | N |  |  | OP | X | 9 | 1972 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1972 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3393 | Allen | TN | Shelby | G18 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 59.6 | 0.9 | 46.4 | 62.2 | 10 | N |  |  | OP | X | 9 | 1972 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1972 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3393 | Allen | TN | Shelby | G19 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 59.6 | 0.9 | 46.4 | 62.2 | 10 | N |  |  | OP | X | 9 | 1972 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1972 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3393 | Allen | TN | Shelby | G20 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 59.6 | 0.9 | 46.4 | 62.2 | 10 | N |  |  | OP | X | 9 | 1972 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1971 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3393 | Allen | TN | Shelby | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 23.9 | 0.9 | 15.1 | 20.4 | 5 | N |  |  | OP | X | 6 | 1971 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1971 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3393 | Allen | TN | Shelby | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 23.9 | 0.9 | 15.1 | 20.4 | 5 | N |  |  | OP | X | 6 | 1971 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1971 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3393 | Allen | TN | Shelby | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 23.9 | 0.9 | 15.1 | 20.4 | 5 | N |  |  | OP | X | 6 | 1971 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1971 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3393 | Allen | TN | Shelby | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 23.9 | 0.9 | 15.1 | 20.4 | 5 | N |  |  | OP | X | 6 | 1971 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1971 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3393 | Allen | TN | Shelby | GT5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 23.9 | 0.9 | 15.1 | 20.4 | 5 | N |  |  | OP | X | 6 | 1971 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1971 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3393 | Allen | TN | Shelby | GT6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 23.9 | 0.9 | 15.1 | 20.4 | 5 | N |  |  | OP | X | 6 | 1971 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1971 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3393 | Allen | TN | Shelby | GT7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 23.9 | 0.9 | 15.1 | 20.4 | 5 | N |  |  | OP | X | 6 | 1971 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1971 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3393 | Allen | TN | Shelby | GT8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 23.9 | 0.9 | 15.1 | 20.4 | 5 | N |  |  | OP | X | 6 | 1971 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1971 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3393 | Allen | TN | Shelby | GT9 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 23.9 | 0.9 | 15.1 | 20.4 | 5 | N |  |  | OP | X | 6 | 1971 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2018 | natural gas combined cycle | TRUE | 18642 | Tennessee Valley Authority | 3393 | Allen | TN | Shelby | STG1 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 476.9 | 0.85 | 428.3 | 453.5 |  | N |  |  | OP | X | 4 | 2018 | 12 | 2023 | N | Electric Utility | 1 | [14 empty] | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1943 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3394 | Apalachia | TN | Polk | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 52.2 | 0.9 | 41.2 | 41.2 | 13.1 | N |  |  | OP | X | 11 | 1943 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1943 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3394 | Apalachia | TN | Polk | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 41.4 | 0.9 | 41.2 | 41.2 | 13.1 | N |  |  | OP | X | 9 | 1943 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1953 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3395 | Boone Dam | TN | Sullivan | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 38 | 0.95 | 37.8 | 29.8 | 19.7 | N |  |  | OP | X | 9 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1953 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3395 | Boone Dam | TN | Sullivan | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 38.3 | 0.95 | 37.8 | 29.8 | 19.7 | N |  |  | OP | X | 6 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1953 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3395 | Boone Dam | TN | Sullivan | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 29.6 | 0.95 | 37.8 | 29.8 | 19.7 | N |  |  | OP | X | 3 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1967 | hard coal | TRUE | 18642 | Tennessee Valley Authority | 3396 | Bull Run | TN | Anderson | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 950 | 0.94 | 865 | 872 | 572 | N |  |  | OP | X | 6 | 1967 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | N | Y | [17 empty] | N
Vintage1942 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3397 | Cherokee Dam | TN | Jefferson | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 33.4 | 0.9 | 37 | 37 | 14.5 | N |  |  | OP | X | 4 | 1942 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1953 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3397 | Cherokee Dam | TN | Jefferson | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 34.6 | 0.9 | 39.8 | 36.1 | 14.5 | N |  |  | OP | X | 1 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1942 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3397 | Cherokee Dam | TN | Jefferson | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 34.6 | 0.9 | 39.8 | 37.5 | 14.5 | N |  |  | OP | X | 6 | 1942 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1953 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3397 | Cherokee Dam | TN | Jefferson | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 32.4 | 0.9 | 25 | 25 | 14.5 | N |  |  | OP | X | 10 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1940 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3398 | Chickamauga | TN | Hamilton | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 39.9 | 0.95 | 35.4 | 29.8 | 11.3 | N |  |  | OP | X | 7 | 1940 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1940 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3398 | Chickamauga | TN | Hamilton | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 39.9 | 0.95 | 35.4 | 29.8 | 11.3 | N |  |  | OP | X | 5 | 1940 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1940 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3398 | Chickamauga | TN | Hamilton | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 39.9 | 0.95 | 35.4 | 29.8 | 11.3 | N |  |  | OP | X | 3 | 1940 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1952 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3398 | Chickamauga | TN | Hamilton | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 39.9 | 0.95 | 35.4 | 29.8 | 11.3 | N |  |  | OP | X | 3 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1973 | hard coal | TRUE | 18642 | Tennessee Valley Authority | 3399 | Cumberland (TN) | TN | Stewart | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 1300 | 0.9 | 1239 | 1265 | 650 | N |  |  | OP | X | 3 | 1973 | 12 | 2028 | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | N
Vintage1973 | hard coal | TRUE | 18642 | Tennessee Valley Authority | 3399 | Cumberland (TN) | TN | Stewart | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 1300 | 0.9 | 1231 | 1257 | 650 | N |  |  | OP | X | 11 | 1973 | 12 | 2026 | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | N
Vintage1944 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3400 | Douglas Dam | TN | Sevier | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 36.5 | 0.9 | 44.2 | 27 | 14.2 | N |  |  | OP | X | 1 | 1944 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1949 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3400 | Douglas Dam | TN | Sevier | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 41.4 | 0.9 | 44.7 | 27.5 | 13 | N |  |  | OP | X | 5 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1943 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3400 | Douglas Dam | TN | Sevier | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 31.5 | 0.9 | 44.5 | 27.6 | 14.2 | N |  |  | OP | X | 3 | 1943 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1954 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3400 | Douglas Dam | TN | Sevier | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 41.4 | 0.9 | 44.5 | 29.1 | 13 | N |  |  | OP | X | 8 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1954 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3401 | Fort Patrick Henry | TN | Sullivan | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 29.7 | 0.9 | 20.4 | 20.4 | 11.8 | N |  |  | OP | X | 2 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1953 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3401 | Fort Patrick Henry | TN | Sullivan | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 29.7 | 0.9 | 20.3 | 20.3 | 11.8 | N |  |  | OP | X | 12 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1944 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3402 | Fort Loudoun | TN | Loudon | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 35.5 | 0.9 | 39.9 | 38.4 | 10.6 | N |  |  | OP | X | 1 | 1944 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1943 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3402 | Fort Loudoun | TN | Loudon | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 34.2 | 0.9 | 37.7 | 37.7 | 10.6 | N |  |  | OP | X | 11 | 1943 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1948 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3402 | Fort Loudoun | TN | Loudon | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 43 | 0.95 | 45.3 | 42.8 | 24.1 | N |  |  | OP | X | 10 | 1948 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1949 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3402 | Fort Loudoun | TN | Loudon | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40.6 | 0.95 | 45.3 | 42.8 | 24.1 | N |  |  | OP | X | 1 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1956 | hard coal | TRUE | 18642 | Tennessee Valley Authority | 3403 | Gallatin (TN) | TN | Sumner | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 300 | 0.9 | 225 | 228 | 108 | N |  |  | OP | X | 11 | 1956 | 12 | 2031 | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: SUB; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1957 | hard coal | TRUE | 18642 | Tennessee Valley Authority | 3403 | Gallatin (TN) | TN | Sumner | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 300 | 0.9 | 225 | 228 | 108 | N |  |  | OP | X | 6 | 1957 | 12 | 2031 | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: SUB; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1959 | hard coal | TRUE | 18642 | Tennessee Valley Authority | 3403 | Gallatin (TN) | TN | Sumner | 3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 327.6 | 0.9 | 263 | 266 | 130 | N |  |  | OP | X | 5 | 1959 | 12 | 2031 | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: SUB; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1959 | hard coal | TRUE | 18642 | Tennessee Valley Authority | 3403 | Gallatin (TN) | TN | Sumner | 4 | Conventional Steam Coal | ST |  | S | X | X |  |  | 327.6 | 0.9 | 263 | 266 | 130 | N |  |  | OP | X | 8 | 1959 | 12 | 2031 | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: SUB; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1975 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3403 | Gallatin (TN) | TN | Sumner | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 81.3 | 0.9 | 71.5 | 88.7 | 10 | N |  |  | OP | X | 7 | 1975 | 12 | 2031 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1975 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3403 | Gallatin (TN) | TN | Sumner | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 81.3 | 0.9 | 71.5 | 88.7 | 10 | N |  |  | OP | X | 7 | 1975 | 12 | 2031 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1975 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3403 | Gallatin (TN) | TN | Sumner | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 81.3 | 0.9 | 71.5 | 88.7 | 10 | N |  |  | OP | X | 7 | 1975 | 12 | 2031 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1975 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3403 | Gallatin (TN) | TN | Sumner | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 81.3 | 0.9 | 71.5 | 88.7 | 10 | N |  |  | OP | X | 7 | 1975 | 12 | 2031 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3403 | Gallatin (TN) | TN | Sumner | GT5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 84.5 | 0.9 | 73.4 | 93.7 | 57 | N |  |  | OP | X | 7 | 2000 | 12 | 2031 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3403 | Gallatin (TN) | TN | Sumner | GT6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 84.5 | 0.9 | 73.4 | 93.7 | 57 | N |  |  | OP | X | 7 | 2000 | 12 | 2031 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3403 | Gallatin (TN) | TN | Sumner | GT7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 84.5 | 0.9 | 73.4 | 93.7 | 57 | N |  |  | OP | X | 7 | 2000 | 12 | 2031 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3403 | Gallatin (TN) | TN | Sumner | GT8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 84.5 | 0.9 | 73.4 | 93.7 | 57 | N |  |  | OP | X | 7 | 2000 | 12 | 2031 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1916 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3404 | Great Falls (TN) | TN | Warren | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15.3 | 0.96 | 15.9 | 16 | 9 | N |  |  | OP | X | 12 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  | N | 0 | 1H | [23 empty] | N
Vintage1924 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3404 | Great Falls (TN) | TN | Warren | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18.4 | 0.8 | 19.5 | 19.6 | 9 | N |  |  | OP | X | 10 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  | N | 0 | 1H | [23 empty] | N
Vintage2012 | natural gas combined cycle | TRUE | 18642 | Tennessee Valley Authority | 3405 | John Sevier | TN | Hawkins | CTG1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 191.3 | 0.9 | 165 | 188 | 44.8 | N |  |  | OP | X | 4 | 2012 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2012 | natural gas combined cycle | TRUE | 18642 | Tennessee Valley Authority | 3405 | John Sevier | TN | Hawkins | CTG2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 191.3 | 0.9 | 165 | 188 | 44.8 | N |  |  | OP | X | 4 | 2012 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2012 | natural gas combined cycle | TRUE | 18642 | Tennessee Valley Authority | 3405 | John Sevier | TN | Hawkins | CTG3 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 191.3 | 0.9 | 165 | 188 | 44.8 | N |  |  | OP | X | 4 | 2012 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2012 | natural gas combined cycle | TRUE | 18642 | Tennessee Valley Authority | 3405 | John Sevier | TN | Hawkins | STG1 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 423 | 0.9 | 383 | 376 | 90.2 | N |  |  | OP | X | 4 | 2012 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1975 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3406 | Johnsonville | TN | Humphreys | G10 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 68 | 0.9 | 47.1 | 62.5 | 25 | N |  |  | OP | X | 6 | 1975 | 6 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1975 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3406 | Johnsonville | TN | Humphreys | G11 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 68 | 0.9 | 47.1 | 62.5 | 25 | N |  |  | OP | X | 6 | 1975 | 6 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1975 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3406 | Johnsonville | TN | Humphreys | G12 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 68 | 0.9 | 47.1 | 62.5 | 25 | N |  |  | OP | X | 6 | 1975 | 6 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1975 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3406 | Johnsonville | TN | Humphreys | G13 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 68 | 0.9 | 47.1 | 62.5 | 25 | N |  |  | OP | X | 6 | 1975 | 6 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1975 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3406 | Johnsonville | TN | Humphreys | G14 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 68 | 0.9 | 47.1 | 62.5 | 25 | N |  |  | OP | X | 6 | 1975 | 6 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1975 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3406 | Johnsonville | TN | Humphreys | G15 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 68 | 0.9 | 47.1 | 62.5 | 25 | N |  |  | OP | X | 6 | 1975 | 6 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1975 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3406 | Johnsonville | TN | Humphreys | G16 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 68 | 0.9 | 47.1 | 62.5 | 25 | N |  |  | OP | X | 6 | 1975 | 6 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3406 | Johnsonville | TN | Humphreys | G17 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 84.5 | 0.9 | 72.8 | 93 | 56 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3406 | Johnsonville | TN | Humphreys | G18 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 84.5 | 0.9 | 72.8 | 93 | 56 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3406 | Johnsonville | TN | Humphreys | G19 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 84.5 | 0.9 | 72.8 | 93 | 56 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3406 | Johnsonville | TN | Humphreys | G20 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 84.5 | 0.9 | 72.8 | 93 | 56 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1975 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3406 | Johnsonville | TN | Humphreys | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 68 | 0.9 | 47.1 | 62.5 | 25 | N |  |  | OP | X | 6 | 1975 | 6 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1975 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3406 | Johnsonville | TN | Humphreys | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 68 | 0.9 | 47.1 | 62.5 | 25 | N |  |  | OP | X | 6 | 1975 | 6 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1975 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3406 | Johnsonville | TN | Humphreys | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 68 | 0.9 | 47.1 | 62.5 | 25 | N |  |  | OP | X | 6 | 1975 | 6 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1975 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3406 | Johnsonville | TN | Humphreys | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 68 | 0.9 | 47.1 | 62.5 | 25 | N |  |  | OP | X | 6 | 1975 | 6 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1975 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3406 | Johnsonville | TN | Humphreys | GT5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 68 | 0.9 | 47.1 | 62.5 | 25 | N |  |  | OP | X | 6 | 1975 | 6 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1975 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3406 | Johnsonville | TN | Humphreys | GT6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 68 | 0.9 | 47.1 | 62.5 | 25 | N |  |  | OP | X | 6 | 1975 | 6 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1975 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3406 | Johnsonville | TN | Humphreys | GT7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 68 | 0.9 | 47.1 | 62.5 | 25 | N |  |  | OP | X | 6 | 1975 | 6 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1975 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3406 | Johnsonville | TN | Humphreys | GT8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 68 | 0.9 | 47.1 | 62.5 | 25 | N |  |  | OP | X | 6 | 1975 | 6 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1975 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 3406 | Johnsonville | TN | Humphreys | GT9 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 68 | 0.9 | 47.1 | 62.5 | 25 | N |  |  | OP | X | 6 | 1975 | 6 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  |  | N |  | 10M | [23 empty] | Y | N | Y
Vintage1954 | hard coal | TRUE | 18642 | Tennessee Valley Authority | 3407 | Kingston | TN | Roane | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 175 | 0.9 | 132 | 135 | 55 | N |  |  | OP | X | 2 | 1954 | 12 | 2027 | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1954 | hard coal | TRUE | 18642 | Tennessee Valley Authority | 3407 | Kingston | TN | Roane | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 175 | 0.9 | 132 | 135 | 55 | N |  |  | OP | X | 4 | 1954 | 12 | 2027 | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1954 | hard coal | TRUE | 18642 | Tennessee Valley Authority | 3407 | Kingston | TN | Roane | 3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 175 | 0.9 | 132 | 135 | 55 | N |  |  | OP | X | 6 | 1954 | 12 | 2027 | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1954 | hard coal | TRUE | 18642 | Tennessee Valley Authority | 3407 | Kingston | TN | Roane | 4 | Conventional Steam Coal | ST |  | S | X | X |  |  | 175 | 0.9 | 132 | 135 | 55 | N |  |  | OP | X | 7 | 1954 | 12 | 2027 | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1955 | hard coal | TRUE | 18642 | Tennessee Valley Authority | 3407 | Kingston | TN | Roane | 5 | Conventional Steam Coal | ST |  | S | X | X |  |  | 200 | 0.9 | 174 | 176 | 73 | N |  |  | OP | X | 1 | 1955 | 12 | 2027 | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1955 | hard coal | TRUE | 18642 | Tennessee Valley Authority | 3407 | Kingston | TN | Roane | 6 | Conventional Steam Coal | ST |  | S | X | X |  |  | 200 | 0.9 | 174 | 176 | 73 | N |  |  | OP | X | 3 | 1955 | 12 | 2027 | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1955 | hard coal | TRUE | 18642 | Tennessee Valley Authority | 3407 | Kingston | TN | Roane | 7 | Conventional Steam Coal | ST |  | S | X | X |  |  | 200 | 0.9 | 174 | 176 | 73 | N |  |  | OP | X | 5 | 1955 | 12 | 2026 | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1955 | hard coal | TRUE | 18642 | Tennessee Valley Authority | 3407 | Kingston | TN | Roane | 8 | Conventional Steam Coal | ST |  | S | X | X |  |  | 200 | 0.9 | 174 | 176 | 73 | N |  |  | OP | X | 8 | 1955 | 12 | 2026 | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1955 | hard coal | TRUE | 18642 | Tennessee Valley Authority | 3407 | Kingston | TN | Roane | 9 | Conventional Steam Coal | ST |  | S | X | X |  |  | 200 | 0.9 | 174 | 176 | 73 | N |  |  | OP | X | 12 | 1955 | 12 | 2026 | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1964 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3408 | Melton Hill | TN | Loudon | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 36 | 0.9 | 39.5 | 39.7 | 9.3 | N |  |  | OP | X | 7 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1964 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3408 | Melton Hill | TN | Loudon | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 36 | 0.9 | 39.7 | 39.7 | 9.3 | N |  |  | OP | X | 11 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1968 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3409 | Nickajack | TN | Marion | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 27.4 | 0.9 | 28.3 | 28.8 | 13.7 | N |  |  | OP | X | 4 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1968 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3409 | Nickajack | TN | Marion | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 27.9 | 0.9 | 27.3 | 28 | 13.7 | N |  |  | OP | X | 4 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1968 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3409 | Nickajack | TN | Marion | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 24.3 | 0.9 | 25 | 25.6 | 12.8 | N |  |  | OP | X | 2 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1968 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3409 | Nickajack | TN | Marion | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 24.3 | 0.9 | 25 | 25.6 | 12.8 | N |  |  | OP | X | 2 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1936 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3411 | Norris Dam | TN | Anderson | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 65.7 | 0.9 | 63.5 | 54.8 | 25.8 | N |  |  | OP | X | 9 | 1936 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1936 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3411 | Norris Dam | TN | Anderson | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 65.7 | 0.9 | 63.5 | 54.8 | 25.8 | N |  |  | OP | X | 7 | 1936 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1912 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3412 | Ocoee 1 | TN | Polk | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.8 | 0.8 | 4.8 | 4.8 | 2.2 | N |  |  | OP | X | 1 | 1912 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1912 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3412 | Ocoee 1 | TN | Polk | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.8 | 0.8 | 4.8 | 4.8 | 2.2 | N |  |  | OP | X | 1 | 1912 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1912 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3412 | Ocoee 1 | TN | Polk | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.8 | 0.8 | 4.8 | 4.8 | 2.2 | N |  |  | OP | X | 5 | 1912 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1912 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3412 | Ocoee 1 | TN | Polk | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.8 | 0.8 | 4.8 | 4.8 | 2.2 | N |  |  | OP | X | 5 | 1912 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1914 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3412 | Ocoee 1 | TN | Polk | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.8 | 0.8 | 4.8 | 4.8 | 2.2 | N |  |  | OP | X | 12 | 1914 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1913 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3413 | Ocoee 2 | TN | Polk | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 11.5 | 0.8 | 10.8 | 10.8 | 6 | N |  |  | OP | X | 10 | 1913 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1913 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3413 | Ocoee 2 | TN | Polk | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 11.5 | 0.8 | 12.6 | 12.6 | 6 | N |  |  | OP | X | 10 | 1913 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1943 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3414 | Ocoee 3 | TN | Polk | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 28.8 | 0.9 | 28.6 | 28.6 | 10.8 | N |  |  | OP | X | 4 | 1943 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1938 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3415 | Pickwick Landing Dam | TN | Hardin | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40 | 0.91 | 37.7 | 34.4 | 32.7 | N |  |  | OP | X | 8 | 1938 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1938 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3415 | Pickwick Landing Dam | TN | Hardin | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40 | 0.91 | 37.6 | 34.3 | 32.7 | N |  |  | OP | X | 6 | 1938 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1942 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3415 | Pickwick Landing Dam | TN | Hardin | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40 | 0.91 | 38.5 | 35.2 | 32.7 | N |  |  | OP | X | 8 | 1942 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1942 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3415 | Pickwick Landing Dam | TN | Hardin | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40 | 0.91 | 43.6 | 39.4 | 32.7 | N |  |  | OP | X | 6 | 1942 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1952 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3415 | Pickwick Landing Dam | TN | Hardin | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40 | 0.91 | 43.7 | 38.4 | 30.8 | N |  |  | OP | X | 10 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1952 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3415 | Pickwick Landing Dam | TN | Hardin | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40 | 0.91 | 43.2 | 37.9 | 30.8 | N |  |  | OP | X | 12 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1951 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3416 | South Holston | TN | Sullivan | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 38.5 | 0.9 | 44.4 | 44.4 | 14.6 | N |  |  | OP | X | 2 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  | N | 0 | 1H | [23 empty] | N
Vintage1972 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3417 | Tims Ford | TN | Franklin | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 45 | 0.9 | 39.7 | 36.2 | 18.7 | N |  |  | OP | X | 3 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1987 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3417 | Tims Ford | TN | Franklin | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.9 | 0.5 | 0.5 | 0.3 | N |  |  | OP | X | 3 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1949 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3418 | Watauga | TN | Carter | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 28.8 | 0.9 | 37.9 | 37.1 | 20.6 | N |  |  | OP | X | 9 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1949 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3418 | Watauga | TN | Carter | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 28.8 | 0.9 | 29.1 | 28.5 | 15.7 | N |  |  | OP | X | 8 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1942 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3420 | Watts Bar Hydro | TN | Rhea | HY1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 41 | 0.94 | 39.3 | 36.9 | 16 | N |  |  | OP | X | 7 | 1942 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1942 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3420 | Watts Bar Hydro | TN | Rhea | HY2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 33.4 | 0.94 | 39.3 | 36.9 | 16 | N |  |  | OP | X | 4 | 1942 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1942 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3420 | Watts Bar Hydro | TN | Rhea | HY3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 33.4 | 0.94 | 39.3 | 36.9 | 16 | N |  |  | OP | X | 3 | 1942 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1944 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3420 | Watts Bar Hydro | TN | Rhea | HY4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 33.4 | 0.94 | 39.2 | 36.7 | 30 | N |  |  | OP | X | 4 | 1944 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1944 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3420 | Watts Bar Hydro | TN | Rhea | HY5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 33.4 | 0.94 | 39.3 | 36.9 | 16 | N |  |  | OP | X | 3 | 1944 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1912 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3421 | Wilbur | TN | Carter | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.8 | 1.4 | 1.4 | 1.3 | N |  |  | OP | X | 12 | 1912 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1912 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3421 | Wilbur | TN | Carter | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.8 | 1.4 | 1.4 | 1.3 | N |  |  | OP | X | 12 | 1912 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1926 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3421 | Wilbur | TN | Carter | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.8 | 1.3 | 1.3 | 1.2 | N |  |  | OP | X | 1 | 1926 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1950 | hydro | TRUE | 18642 | Tennessee Valley Authority | 3421 | Wilbur | TN | Carter | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7 | 0.9 | 7 | 7 | 1.6 | N |  |  | OP | X | 7 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1973 | hydro | TRUE | 19462 | USCE-Nashville District | 3423 | Cordell Hull | TN | Smith | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 33.3 | 0.9 | 38 | 38 | 33.3 | N |  |  | OP | X | 8 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1973 | hydro | TRUE | 19462 | USCE-Nashville District | 3423 | Cordell Hull | TN | Smith | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 33.3 | 0.9 | 30 | 30 | 30 | N |  |  | OP | X | 10 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1974 | hydro | TRUE | 19462 | USCE-Nashville District | 3423 | Cordell Hull | TN | Smith | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 33.3 | 0.9 | 38 | 38 | 33.3 | N |  |  | OP | X | 2 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1948 | hydro | TRUE | 19462 | USCE-Nashville District | 3424 | Dale Hollow | TN | Clay | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18 | 0.9 | 20.7 | 20.7 | 18 | N |  |  | OP | X | 12 | 1948 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1949 | hydro | TRUE | 19462 | USCE-Nashville District | 3424 | Dale Hollow | TN | Clay | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18 | 0.9 | 20.7 | 20.7 | 18 | N |  |  | OP | X | 1 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1953 | hydro | TRUE | 19462 | USCE-Nashville District | 3424 | Dale Hollow | TN | Clay | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18 | 0.9 | 20.7 | 20.7 | 18 | N |  |  | OP | X | 11 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1957 | hydro | TRUE | 19462 | USCE-Nashville District | 3426 | Old Hickory | TN | Sumner | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 28.7 | 0.85 | 28.7 | 28.7 | 25 | N |  |  | OP | X | 4 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1957 | hydro | TRUE | 19462 | USCE-Nashville District | 3426 | Old Hickory | TN | Sumner | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 25 | 0.85 | 29 | 29 | 25 | N |  |  | OP | X | 7 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1957 | hydro | TRUE | 19462 | USCE-Nashville District | 3426 | Old Hickory | TN | Sumner | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 25 | 0.85 | 29 | 29 | 25 | N |  |  | OP | X | 9 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1957 | hydro | TRUE | 19462 | USCE-Nashville District | 3426 | Old Hickory | TN | Sumner | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 25 | 0.85 | 29 | 29 | 25 | N |  |  | OA | X | 12 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M
Vintage1970 | hydro | TRUE | 19462 | USCE-Nashville District | 3428 | J P Priest | TN | Davidson | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 28 | 0.9 | 30 | 30 | 28 | N |  |  | OP | X | 2 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1932 | hydro | TRUE | 54683 | Maverick Cty Water Control & Improvement | 3437 | Eagle Pass | TX | Maverick | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.2 | 1 | 2 | 2 | 0.1 | N |  |  | OP | X | 8 | 1932 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1932 | hydro | TRUE | 54683 | Maverick Cty Water Control & Improvement | 3437 | Eagle Pass | TX | Maverick | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.2 | 1 | 2 | 2 | 0.1 | N |  |  | OP | X | 8 | 1932 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1932 | hydro | TRUE | 54683 | Maverick Cty Water Control & Improvement | 3437 | Eagle Pass | TX | Maverick | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.2 | 1 | 2 | 2 | 0.1 | N |  |  | OP | X | 8 | 1932 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage2008 | natural gas peaker | TRUE | 49979 | Talen Texas, LLC | 3439 | Laredo | TX | Webb | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 131.8 | 0.85 | 90.1 | 97.4 | 35 | N |  |  | OP | X | 8 | 2008 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2008 | natural gas peaker | TRUE | 49979 | Talen Texas, LLC | 3439 | Laredo | TX | Webb | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 131.8 | 0.85 | 87.3 | 94.4 | 35 | N |  |  | OP | X | 9 | 2008 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1972 | natural gas combined cycle | TRUE | 49979 | Talen Texas, LLC | 3441 | Nueces Bay | TX | Nueces | 7 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 351 | 0.9 | 319 | 325 | 100 | N |  |  | OP | X | 7 | 1972 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2010 | natural gas combined cycle | TRUE | 49979 | Talen Texas, LLC | 3441 | Nueces Bay | TX | Nueces | 8 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 189.6 | 0.9 | 157 | 165 | 60 | N |  |  | OP | X | 3 | 2010 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2010 | natural gas combined cycle | TRUE | 49979 | Talen Texas, LLC | 3441 | Nueces Bay | TX | Nueces | 9 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 189.6 | 0.9 | 157 | 165 | 60 | N |  |  | OP | X | 3 | 2010 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1963 | natural gas combined cycle | TRUE | 60638 | Victoria WLE, LP | 3443 | Victoria | TX | Victoria | 5 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | VIC_VICTORG5 |  | 180 | 0.85 | 112 | 112 | 55 | N |  |  | OP | X | 3 | 1963 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | bar: X X X to DFO RC RC
Vintage2009 | natural gas combined cycle | TRUE | 60638 | Victoria WLE, LP | 3443 | Victoria | TX | Victoria | 7 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | VIC_VICTORG6 |  | 196.9 | 0.9 | 176 | 176 | 115 | N |  |  | OP | X | 5 | 2009 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | bar: X X X to DFO RC RC
Vintage1970 | natural gas steam turbine | TRUE | 55983 | Luminant Generation Company LLC | 3452 | Lake Hubbard | TX | Dallas | 1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 396.5 | 0.9 | 392 | 392 | 56 | N |  |  | OP | X | 6 | 1970 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1973 | natural gas steam turbine | TRUE | 55983 | Luminant Generation Company LLC | 3452 | Lake Hubbard | TX | Dallas | 2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 531 | 0.9 | 523 | 523 | 40 | N |  |  | OP | X | 11 | 1973 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1956 | natural gas steam turbine | TRUE | 62026 | Mountain Creek Power, LLC | 3453 | Mountain Creek | TX | Dallas | 6 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 135.7 | 0.85 | 122 | 122 | 15 | N |  |  | OP | X | 2 | 1956 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1958 | natural gas steam turbine | TRUE | 62026 | Mountain Creek Power, LLC | 3453 | Mountain Creek | TX | Dallas | 7 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 136 | 0.85 | 122 | 122 | 15 | N |  |  | OP | X | 3 | 1958 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N |  |  | OVER | [23 empty] | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1967 | natural gas steam turbine | TRUE | 62026 | Mountain Creek Power, LLC | 3453 | Mountain Creek | TX | Dallas | 8 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 580.5 | 0.9 | 582 | 582 | 100 | N |  |  | OP | X | 7 | 1967 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N |  |  | 12H | [5 empty] | N | [17 empty] | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1960 | natural gas steam turbine | TRUE | 5701 | El Paso Electric Co | 3456 | Newman | TX | El Paso | 1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 81.6 | 0.85 | 76 | 78 | 21 | N |  |  | OP | X | 5 | 1960 | 12 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N |  |  | OVER | [23 empty] | Y | Y | Y
Vintage1963 | natural gas steam turbine | TRUE | 5701 | El Paso Electric Co | 3456 | Newman | TX | El Paso | 2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 81.6 | 0.85 | 76 | 78 | 21 | N |  |  | OP | X | 6 | 1963 | 12 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N |  |  | 12H | [23 empty] | Y | Y | Y
Vintage1966 | natural gas steam turbine | TRUE | 5701 | El Paso Electric Co | 3456 | Newman | TX | El Paso | 3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 121.8 | 0.85 | 95 | 98 | 20 | N |  |  | OP | X | 3 | 1966 | 12 | 2031 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N |  |  | 12H | [23 empty] | Y | Y | Y
Vintage1975 | natural gas combined cycle | TRUE | 5701 | El Paso Electric Co | 3456 | Newman | TX | El Paso | 4 | Natural Gas Fired Combined Cycle | CA | 4CC | S | Y | X |  |  | 120 | 0.9 | 89 | 89 | 24 | N |  |  | OP | X | 8 | 1975 | 12 | 2031 | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | bar: X X X to DFO RC RC
Vintage2011 | natural gas combined cycle | TRUE | 5701 | El Paso Electric Co | 3456 | Newman | TX | El Paso | 5CA1 | Natural Gas Fired Combined Cycle | CA | 5CC | S | Y | X |  |  | 134 | 0.85 | 128 | 128 | 51 | N |  |  | OP | X | 2 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | bar: X X X to DFO RC RC
Vintage2009 | natural gas combined cycle | TRUE | 5701 | El Paso Electric Co | 3456 | Newman | TX | El Paso | 5CT1 | Natural Gas Fired Combined Cycle | CT | 5CC | S | X | Y |  |  | 86.5 | 0.85 | 67 | 72 | 44 | N |  |  | OP | X | 6 | 2009 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | bar: X X X to DFO RC RC
Vintage2009 | natural gas combined cycle | TRUE | 5701 | El Paso Electric Co | 3456 | Newman | TX | El Paso | 5CT2 | Natural Gas Fired Combined Cycle | CT | 5CC | S | X | Y |  |  | 86.5 | 0.85 | 67 | 72 | 44 | N |  |  | OP | X | 6 | 2009 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | bar: X X X to DFO RC RC
Vintage1975 | natural gas combined cycle | TRUE | 5701 | El Paso Electric Co | 3456 | Newman | TX | El Paso | CT1 | Natural Gas Fired Combined Cycle | CT | 4CC | S | X | N |  |  | 85 | 0.9 | 69 | 72 | 29 | N |  |  | OP | X | 8 | 1975 | 12 | 2026 | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | bar: X X X to DFO RC RC
Vintage1975 | natural gas combined cycle | TRUE | 5701 | El Paso Electric Co | 3456 | Newman | TX | El Paso | CT2 | Natural Gas Fired Combined Cycle | CT | 4CC | S | X | N |  |  | 85 | 0.9 | 69 | 72 | 29 | N |  |  | OP | X | 8 | 1975 | 12 | 2026 | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | bar: X X X to DFO RC RC
Vintage1970 | natural gas steam turbine | TRUE | 55937 | Entergy Texas Inc. | 3457 | Lewis Creek | TX | Montgomery | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | EES.L_CREEK1 |  | 271.4 | 0.87 | 250 | 252.7 | 50 | N |  |  | OP | X | 12 | 1970 | 6 | 2034 | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1971 | natural gas steam turbine | TRUE | 55937 | Entergy Texas Inc. | 3457 | Lewis Creek | TX | Montgomery | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | EES.L_CREEK2 |  | 271.4 | 0.87 | 250 | 254.2 | 50 | N |  |  | OP | X | 5 | 1971 | 6 | 2034 | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1962 | natural gas steam turbine | TRUE | 55937 | Entergy Texas Inc. | 3459 | Sabine | TX | Orange | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | EES.SABINE1 | EES.SABINE1 | 239.4 | 0.85 | 211.6 | 206.6 | 50 | N |  |  | OP | X | 1 | 1962 | 6 | 2023 | N | Electric Utility | 1 | [11 empty] | N |  |  | OVER | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1966 | natural gas steam turbine | TRUE | 55937 | Entergy Texas Inc. | 3459 | Sabine | TX | Orange | 3 | Natural Gas Steam Turbine | ST |  | S | X | X | EES.SABINE3 | EES.SABINE3 | 473.4 | 0.87 | 367.9 | 373.2 | 55 | N |  |  | OP | X | 12 | 1966 | 6 | 2026 | N | Electric Utility | 1 | [11 empty] | N |  |  | OVER | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1974 | natural gas steam turbine | TRUE | 55937 | Entergy Texas Inc. | 3459 | Sabine | TX | Orange | 4 | Natural Gas Steam Turbine | ST |  | S | X | X | EES.SABINE4 | EES.SABINE4 | 591.6 | 0.87 | 495 | 497.7 | 185 | N |  |  | OP | X | 8 | 1974 | 6 | 2026 | N | Electric Utility | 1 | [11 empty] | N |  |  | OVER | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1979 | natural gas steam turbine | TRUE | 55937 | Entergy Texas Inc. | 3459 | Sabine | TX | Orange | 5 | Natural Gas Steam Turbine | ST |  | S | X | X | EES.SABINE5 | EES.SABINE5 | 507.4 | 0.87 | 436.6 | 443.2 | 55 | N |  |  | OP | X | 12 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO DFO DFO: DFO |  |  | N |  |  | OVER | [23 empty] | N | N | N
Vintage1970 | natural gas steam turbine | TRUE | 54888 | NRG Texas Power LLC | 3460 | Cedar Bayou | TX | Chambers | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | CBY_CBY_G1 | CBY_CBY_G1 | 765 | 0.9 | 746 | 746 | 65 | N |  |  | OP | X | 12 | 1970 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | OVER | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1972 | natural gas steam turbine | TRUE | 54888 | NRG Texas Power LLC | 3460 | Cedar Bayou | TX | Chambers | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | CBY_CBY_G2 | CBY_CBY_G2 | 765 | 0.9 | 749 | 749 | 65 | N |  |  | OP | X | 3 | 1972 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | OVER | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1976 | natural gas peaker | TRUE | 54888 | NRG Texas Power LLC | 3464 | Greens Bayou | TX | Harris | 73 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | GBY_GT | GBY_GT | 72 | 0.9 | 54 | 54 | 30 | N |  |  | OP | X | 12 | 1976 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1976 | natural gas peaker | TRUE | 54888 | NRG Texas Power LLC | 3464 | Greens Bayou | TX | Harris | 74 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | GBY_GT | GBY_GT | 72 | 0.9 | 54 | 54 | 30 | N |  |  | OP | X | 12 | 1976 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1976 | natural gas peaker | TRUE | 54888 | NRG Texas Power LLC | 3464 | Greens Bayou | TX | Harris | 81 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | GBY_GT | GBY_GT | 72 | 0.9 | 54 | 54 | 30 | N |  |  | OP | X | 12 | 1976 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1976 | natural gas peaker | TRUE | 54888 | NRG Texas Power LLC | 3464 | Greens Bayou | TX | Harris | 82 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | GBY_GT | GBY_GT | 72 | 0.9 | 50 | 50 | 30 | N |  |  | OP | X | 12 | 1976 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1976 | natural gas peaker | TRUE | 54888 | NRG Texas Power LLC | 3464 | Greens Bayou | TX | Harris | 83 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | GBY_GT | GBY_GT | 72 | 0.9 | 64 | 64 | 30 | N |  |  | OP | X | 12 | 1976 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1976 | natural gas peaker | TRUE | 54888 | NRG Texas Power LLC | 3464 | Greens Bayou | TX | Harris | 84 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | GBY_GT | GBY_GT | 72 | 0.9 | 54 | 54 | 30 | N |  |  | OP | X | 12 | 1976 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1974 | natural gas combined cycle | TRUE | 54888 | NRG Texas Power LLC | 3469 | T H Wharton | TX | Harris | 3 | Natural Gas Fired Combined Cycle | CA | THW3 | S | N | X | THW_CC1 | THW_CC1 | 113.1 | 0.85 | 104 | 104 | 27 | N |  |  | OP | X | 8 | 1974 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1972 | natural gas combined cycle | TRUE | 54888 | NRG Texas Power LLC | 3469 | T H Wharton | TX | Harris | 31 | Natural Gas Fired Combined Cycle | CT | THW3 | S | X | Y | THW_CC1 | THW_CC1 | 54 | 0.85 | 57 | 57 | 53 | N |  |  | OP | X | 7 | 1972 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1972 | natural gas combined cycle | TRUE | 54888 | NRG Texas Power LLC | 3469 | T H Wharton | TX | Harris | 32 | Natural Gas Fired Combined Cycle | CT | THW3 | S | X | Y | THW_CC1 | THW_CC1 | 54 | 0.9 | 57 | 57 | 53 | N |  |  | OP | X | 7 | 1972 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1972 | natural gas combined cycle | TRUE | 54888 | NRG Texas Power LLC | 3469 | T H Wharton | TX | Harris | 33 | Natural Gas Fired Combined Cycle | CT | THW3 | S | X | Y | THW_CC1 | THW_CC1 | 54 | 0.9 | 57 | 57 | 53 | N |  |  | OP | X | 7 | 1972 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1972 | natural gas combined cycle | TRUE | 54888 | NRG Texas Power LLC | 3469 | T H Wharton | TX | Harris | 34 | Natural Gas Fired Combined Cycle | CT | THW3 | S | X | Y | THW_CC1 | THW_CC1 | 54 | 0.9 | 57 | 57 | 53 | N |  |  | OP | X | 7 | 1972 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1974 | natural gas combined cycle | TRUE | 54888 | NRG Texas Power LLC | 3469 | T H Wharton | TX | Harris | 4 | Natural Gas Fired Combined Cycle | CA | THW4 | S | N | X | THW_CC2 | THW_CC2 | 113.1 | 0.85 | 104 | 104 | 27 | N |  |  | OP | X | 8 | 1974 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1972 | natural gas combined cycle | TRUE | 54888 | NRG Texas Power LLC | 3469 | T H Wharton | TX | Harris | 41 | Natural Gas Fired Combined Cycle | CT | THW4 | S | X | Y | THW_CC2 | THW_CC2 | 54 | 0.9 | 57 | 57 | 53 | N |  |  | OP | X | 7 | 1972 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1972 | natural gas combined cycle | TRUE | 54888 | NRG Texas Power LLC | 3469 | T H Wharton | TX | Harris | 42 | Natural Gas Fired Combined Cycle | CT | THW4 | S | X | Y | THW_CC2 | THW_CC2 | 54 | 0.9 | 57 | 57 | 53 | N |  |  | OP | X | 7 | 1972 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1974 | natural gas combined cycle | TRUE | 54888 | NRG Texas Power LLC | 3469 | T H Wharton | TX | Harris | 43 | Natural Gas Fired Combined Cycle | CT | THW4 | S | X | Y | THW_CC2 | THW_CC2 | 56.7 | 0.9 | 57 | 57 | 53 | N |  |  | OP | X | 8 | 1974 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1974 | natural gas combined cycle | TRUE | 54888 | NRG Texas Power LLC | 3469 | T H Wharton | TX | Harris | 44 | Natural Gas Fired Combined Cycle | CT | THW4 | S | X | Y | THW_CC2 | THW_CC2 | 56.7 | 0.9 | 57 | 57 | 53 | N |  |  | OP | X | 8 | 1974 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1975 | natural gas peaker | TRUE | 54888 | NRG Texas Power LLC | 3469 | T H Wharton | TX | Harris | 51 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | THW_THWGT5X | THW_THWGT5X | 85 | 0.9 | 58 | 58 | 40 | N |  |  | OP | X | 11 | 1975 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1975 | natural gas peaker | TRUE | 54888 | NRG Texas Power LLC | 3469 | T H Wharton | TX | Harris | 52 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | THW_THWGT5X | THW_THWGT5X | 85 | 0.9 | 58 | 58 | 38 | N |  |  | OP | X | 11 | 1975 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1975 | natural gas peaker | TRUE | 54888 | NRG Texas Power LLC | 3469 | T H Wharton | TX | Harris | 53 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | THW_THWGT5X | THW_THWGT5X | 85 | 0.9 | 58 | 58 | 42 | N |  |  | OP | X | 11 | 1975 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1975 | natural gas peaker | TRUE | 54888 | NRG Texas Power LLC | 3469 | T H Wharton | TX | Harris | 54 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | THW_THWGT5X | THW_THWGT5X | 85 | 0.9 | 58 | 58 | 48 | N |  |  | OP | X | 11 | 1975 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1975 | natural gas peaker | TRUE | 54888 | NRG Texas Power LLC | 3469 | T H Wharton | TX | Harris | 55 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | THW_THWGT5X | THW_THWGT5X | 85 | 0.9 | 58 | 58 | 42 | N |  |  | OP | X | 11 | 1975 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1975 | natural gas peaker | TRUE | 54888 | NRG Texas Power LLC | 3469 | T H Wharton | TX | Harris | 56 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | THW_THWGT5X | THW_THWGT5X | 85 | 0.9 | 58 | 58 | 38 | N |  |  | OP | X | 11 | 1975 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1967 | natural gas peaker | TRUE | 54888 | NRG Texas Power LLC | 3469 | T H Wharton | TX | Harris | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | THW_THWGT_1 | THW_THWGT_1 | 16.3 | 0.85 | 13 | 13 | 5 | N |  |  | OP | X | 7 | 1967 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1958 | natural gas steam turbine | TRUE | 54888 | NRG Texas Power LLC | 3470 | W A Parish | TX | Fort Bend | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | WAP_WAP_G1 | WAP_WAP_G1 | 187.8 | 0.85 | 169 | 169 | 30 | N |  |  | OP | X | 6 | 1958 | 12 | 2026 | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1958 | natural gas steam turbine | TRUE | 54888 | NRG Texas Power LLC | 3470 | W A Parish | TX | Fort Bend | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | WAP_WAP_G2 | WAP_WAP_G2 | 187.8 | 0.85 | 169 | 169 | 30 | N |  |  | OP | X | 12 | 1958 | 12 | 2026 | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1961 | natural gas steam turbine | TRUE | 54888 | NRG Texas Power LLC | 3470 | W A Parish | TX | Fort Bend | 3 | Natural Gas Steam Turbine | ST |  | S | X | X | WAP_WAP_G3 | WAP_WAP_G3 | 299.2 | 0.85 | 273 | 273 | 60 | N |  |  | OP | X | 3 | 1961 | 12 | 2026 | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1968 | natural gas steam turbine | TRUE | 54888 | NRG Texas Power LLC | 3470 | W A Parish | TX | Fort Bend | 4 | Natural Gas Steam Turbine | ST |  | S | X | X | WAP_WAP_G4 | WAP_WAP_G4 | 580.5 | 0.9 | 552 | 552 | 60 | N |  |  | OP | X | 6 | 1968 | 12 | 2026 | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1977 | hard coal | TRUE | 54888 | NRG Texas Power LLC | 3470 | W A Parish | TX | Fort Bend | 5 | Conventional Steam Coal | ST |  | S | X | X | WAP_WAP_G5 | WAP_WAP_G5 | 734.1 | 0.9 | 664 | 664 | 175 | N |  |  | OP | X | 12 | 1977 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1978 | hard coal | TRUE | 54888 | NRG Texas Power LLC | 3470 | W A Parish | TX | Fort Bend | 6 | Conventional Steam Coal | ST |  | S | X | X | WAP_WAP_G6 | WAP_WAP_G6 | 734.1 | 0.9 | 663 | 663 | 175 | N |  |  | OP | X | 12 | 1978 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1980 | hard coal | TRUE | 54888 | NRG Texas Power LLC | 3470 | W A Parish | TX | Fort Bend | 7 | Conventional Steam Coal | ST |  | S | X | X | WAP_WAP_G7 | WAP_WAP_G7 | 614.6 | 0.87 | 577 | 577 | 175 | N |  |  | OP | X | 6 | 1980 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1982 | hard coal | TRUE | 54888 | NRG Texas Power LLC | 3470 | W A Parish | TX | Fort Bend | 8 | Conventional Steam Coal | ST |  | S | X | X | WAP_WAP_G8 | WAP_WAP_G8 | 654 | 0.87 | 610 | 610 | 175 | N |  |  | OP | X | 12 | 1982 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1967 | natural gas peaker | TRUE | 54888 | NRG Texas Power LLC | 3470 | W A Parish | TX | Fort Bend | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | WAP_WAP_GT_1 | WAP_WAP_GT_1 | 16.3 | 0.85 | 13 | 13 | 3 | N |  |  | OP | X | 7 | 1967 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1974 | natural gas steam turbine | TRUE | 17698 | Southwestern Electric Power Co | 3476 | Knox Lee | TX | Gregg | 5 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 351 | 0.9 | 342 | 348 | 75 | N |  |  | OP | X | 4 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1964 | natural gas steam turbine | TRUE | 17698 | Southwestern Electric Power Co | 3478 | Wilkes | TX | Marion | 1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 180 | 0.85 | 174 | 174 | 30 | N |  |  | OP | X | 5 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: RFO; DFO DFO DFO: NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1970 | natural gas steam turbine | TRUE | 17698 | Southwestern Electric Power Co | 3478 | Wilkes | TX | Marion | 2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 351 | 0.9 | 355 | 365 | 40 | N |  |  | OP | X | 5 | 1970 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1971 | natural gas steam turbine | TRUE | 17698 | Southwestern Electric Power Co | 3478 | Wilkes | TX | Marion | 3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 351 | 0.9 | 354 | 362 | 40 | N |  |  | OP | X | 12 | 1971 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1971 | natural gas steam turbine | TRUE | 17718 | Southwestern Public Service Co | 3482 | Jones | TX | Lubbock | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | SPS.JONES1 | SPS.JONES1 | 247.5 | 0.9 | 243 | 243 | 56 | N |  |  | OP | X | 1 | 1971 | 12 | 2031 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | OVER | [23 empty] | Y | Y | Y
Vintage1974 | natural gas steam turbine | TRUE | 17718 | Southwestern Public Service Co | 3482 | Jones | TX | Lubbock | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | SPS.JONES2 | SPS.JONES2 | 247.5 | 0.9 | 243 | 243 | 56 | N |  |  | OP | X | 1 | 1974 | 12 | 2034 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | OVER | [23 empty] | Y | Y | Y
Vintage2011 | natural gas peaker | TRUE | 17718 | Southwestern Public Service Co | 3482 | Jones | TX | Lubbock | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SPS.JONES3 | SPS.JONES3 | 182.7 | 0.9 | 166 | 183 | 114 | N |  |  | OP | X | 6 | 2011 | 12 | 2056 | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage2013 | natural gas peaker | TRUE | 17718 | Southwestern Public Service Co | 3482 | Jones | TX | Lubbock | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SPS.JONES4 | SPS.JONES4 | 182.7 | 0.9 | 168 | 183 | 116 | N |  |  | OP | X | 5 | 2013 | 12 | 2058 | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1960 | natural gas steam turbine | TRUE | 17718 | Southwestern Public Service Co | 3484 | Nichols | TX | Potter | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | SPS.NICHOLS1 | SPS.NICHOLS1 | 113.6 | 0.85 | 107 | 107 | 25 | N |  |  | OP | X | 1 | 1960 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1962 | natural gas steam turbine | TRUE | 17718 | Southwestern Public Service Co | 3484 | Nichols | TX | Potter | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | SPS.NICHOLS2 | SPS.NICHOLS2 | 113.6 | 0.85 | 106 | 106 | 18 | N |  |  | OP | X | 1 | 1962 | 12 | 2023 | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1968 | natural gas steam turbine | TRUE | 17718 | Southwestern Public Service Co | 3484 | Nichols | TX | Potter | 3 | Natural Gas Steam Turbine | ST |  | S | X | X | SPS.NICHOLS3 | SPS.NICHOLS3 | 247.5 | 0.9 | 244 | 244 | 25 | N |  |  | OP | X | 1 | 1968 | 12 | 2030 | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1952 | natural gas steam turbine | TRUE | 17718 | Southwestern Public Service Co | 3485 | Plant X | TX | Lamb | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | SPS.PLANTX1 | SPS.PLANTX1 | 48 | 0.8 | 38 | 38 | 21 | N |  |  | OP | X | 1 | 1952 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1953 | natural gas steam turbine | TRUE | 17718 | Southwestern Public Service Co | 3485 | Plant X | TX | Lamb | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | SPS.PLANTX2 | SPS.PLANTX2 | 98 | 0.8 | 90 | 90 | 40 | N |  |  | OP | X | 1 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | OVER | [23 empty] | Y | Y | Y
Vintage1955 | natural gas steam turbine | TRUE | 17718 | Southwestern Public Service Co | 3485 | Plant X | TX | Lamb | 3 | Natural Gas Steam Turbine | ST |  | S | X | X | SPS.PLANTX3 | SPS.PLANTX3 | 98 | 0.8 | 93 | 93 | 35 | N |  |  | OP | X | 1 | 1955 | 12 | 2022 | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1964 | natural gas steam turbine | TRUE | 17718 | Southwestern Public Service Co | 3485 | Plant X | TX | Lamb | 4 | Natural Gas Steam Turbine | ST |  | S | X | X | SPS.PLANTX4 | SPS.PLANTX4 | 190.4 | 0.85 | 190 | 190 | 55 | N |  |  | OP | X | 1 | 1964 | 12 | 2027 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | OVER | [23 empty] | Y | Y | Y
Vintage1960 | natural gas steam turbine | TRUE | 55983 | Luminant Generation Company LLC | 3490 | Graham | TX | Young | 1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 247.7 | 0.85 | 239 | 239 | 46 | N |  |  | OP | X | 12 | 1960 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1969 | natural gas steam turbine | TRUE | 55983 | Luminant Generation Company LLC | 3490 | Graham | TX | Young | 2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 387 | 0.9 | 390 | 390 | 26 | N |  |  | OP | X | 6 | 1969 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1963 | natural gas steam turbine | TRUE | 6035 | Exelon Power | 3491 | Handley | TX | Tarrant | 3 | Natural Gas Steam Turbine | ST |  | S | X | X | HLSES_UNIT3 | HLSES_UNIT3 | 404.8 | 0.8 | 395 | 395 | 50 | N |  |  | OP | X | 7 | 1963 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N | 0 | 12H | [20 empty] | N |  |  | N |  | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1976 | natural gas steam turbine | TRUE | 6035 | Exelon Power | 3491 | Handley | TX | Tarrant | 4 | Natural Gas Steam Turbine | ST |  | S | X | X | HLSES_UNIT4 | HLSES_UNIT4 | 455 | 0.91 | 435 | 435 | 120 | N |  |  | OP | X | 10 | 1976 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1977 | natural gas steam turbine | TRUE | 6035 | Exelon Power | 3491 | Handley | TX | Tarrant | 5 | Natural Gas Steam Turbine | ST |  | S | X | X | HLSES_UNIT5 | HLSES_UNIT5 | 455 | 0.91 | 435 | 435 | 120 | N |  |  | OP | X | 10 | 1977 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1988 | natural gas peaker | TRUE | 55983 | Luminant Generation Company LLC | 3492 | Morgan Creek | TX | Mitchell | CT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 89.4 | 0.9 | 66 | 82 | 30 | N |  |  | OP | X | 7 | 1988 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1988 | natural gas peaker | TRUE | 55983 | Luminant Generation Company LLC | 3492 | Morgan Creek | TX | Mitchell | CT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 89.4 | 0.9 | 65 | 80 | 30 | N |  |  | OP | X | 7 | 1988 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1988 | natural gas peaker | TRUE | 55983 | Luminant Generation Company LLC | 3492 | Morgan Creek | TX | Mitchell | CT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 89.4 | 0.9 | 65 | 80 | 30 | N |  |  | OP | X | 8 | 1988 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1988 | natural gas peaker | TRUE | 55983 | Luminant Generation Company LLC | 3492 | Morgan Creek | TX | Mitchell | CT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 89.4 | 0.9 | 67 | 81 | 30 | N |  |  | OP | X | 7 | 1988 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1988 | natural gas peaker | TRUE | 55983 | Luminant Generation Company LLC | 3492 | Morgan Creek | TX | Mitchell | CT5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 89.4 | 0.9 | 67 | 80 | 30 | N |  |  | OP | X | 7 | 1988 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1988 | natural gas peaker | TRUE | 55983 | Luminant Generation Company LLC | 3492 | Morgan Creek | TX | Mitchell | CT6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 89.4 | 0.9 | 67 | 82 | 30 | N |  |  | OP | X | 7 | 1988 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1988 | natural gas peaker | TRUE | 55983 | Luminant Generation Company LLC | 3494 | Permian Basin | TX | Ward | CT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 89.4 | 0.9 | 63 | 79 | 41 | N |  |  | OP | X | 5 | 1988 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1988 | natural gas peaker | TRUE | 55983 | Luminant Generation Company LLC | 3494 | Permian Basin | TX | Ward | CT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 89.4 | 0.9 | 64 | 76 | 41 | N |  |  | OP | X | 5 | 1988 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1988 | natural gas peaker | TRUE | 55983 | Luminant Generation Company LLC | 3494 | Permian Basin | TX | Ward | CT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 89.4 | 0.9 | 64 | 78 | 41 | N |  |  | OP | X | 5 | 1988 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1990 | natural gas peaker | TRUE | 55983 | Luminant Generation Company LLC | 3494 | Permian Basin | TX | Ward | CT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 89.4 | 0.9 | 64 | 75 | 41 | N |  |  | OP | X | 2 | 1990 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1990 | natural gas peaker | TRUE | 55983 | Luminant Generation Company LLC | 3494 | Permian Basin | TX | Ward | CT5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 89.4 | 0.9 | 65 | 79 | 41 | N |  |  | OP | X | 2 | 1990 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1966 | petroleum | TRUE | 55983 | Luminant Generation Company LLC | 3504 | Stryker Creek | TX | Cherokee | D1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 7 | 1966 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1966 | petroleum | TRUE | 55983 | Luminant Generation Company LLC | 3504 | Stryker Creek | TX | Cherokee | D2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 7 | 1966 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1966 | petroleum | TRUE | 55983 | Luminant Generation Company LLC | 3504 | Stryker Creek | TX | Cherokee | D3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 7 | 1966 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1966 | petroleum | TRUE | 55983 | Luminant Generation Company LLC | 3504 | Stryker Creek | TX | Cherokee | D4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 7 | 1966 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1966 | petroleum | TRUE | 55983 | Luminant Generation Company LLC | 3504 | Stryker Creek | TX | Cherokee | D5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 7 | 1966 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1958 | natural gas steam turbine | TRUE | 55983 | Luminant Generation Company LLC | 3504 | Stryker Creek | TX | Cherokee | ST1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 176.8 | 0.8 | 167 | 167 | 20 | N |  |  | OP | X | 6 | 1958 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1965 | natural gas steam turbine | TRUE | 55983 | Luminant Generation Company LLC | 3504 | Stryker Creek | TX | Cherokee | ST2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 526.6 | 0.9 | 502 | 502 | 35 | N |  |  | OP | X | 12 | 1965 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1965 | natural gas steam turbine | TRUE | 55983 | Luminant Generation Company LLC | 3507 | Trinidad (TX) | TX | Henderson | 6 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 239.3 | 0.85 | 235 | 235 | 50 | N |  |  | OP | X | 5 | 1965 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1966 | petroleum | TRUE | 55983 | Luminant Generation Company LLC | 3507 | Trinidad (TX) | TX | Henderson | D1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 8 | 1966 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1966 | petroleum | TRUE | 55983 | Luminant Generation Company LLC | 3507 | Trinidad (TX) | TX | Henderson | D2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 8 | 1966 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1978 | natural gas steam turbine | TRUE | 1015 | Austin Energy | 3548 | Decker Creek | TX | Travis | 2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 405 | 0.9 | 404 | 448 | 50 | N |  |  | OP | X | 1 | 1978 | 3 | 2022 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO DFO DFO: DFO | [5 empty] | 12H | [23 empty] | N | N | N
Vintage1988 | natural gas peaker | TRUE | 1015 | Austin Energy | 3548 | Decker Creek | TX | Travis | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 51.5 | 0.9 | 52 | 60 | 49 | N |  |  | OP | X | 9 | 1988 |  |  | N | Electric Utility | 1 | [14 empty] | 10M | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1988 | natural gas peaker | TRUE | 1015 | Austin Energy | 3548 | Decker Creek | TX | Travis | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 51.5 | 0.9 | 52 | 60 | 49 | N |  |  | OP | X | 9 | 1988 |  |  | N | Electric Utility | 1 | [14 empty] | 10M | [23 empty] | N |  | N | bar: X X X to DFO RC RC
Vintage1988 | natural gas peaker | TRUE | 1015 | Austin Energy | 3548 | Decker Creek | TX | Travis | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 51.5 | 0.9 | 52 | 60 | 49 | N |  |  | OP | X | 9 | 1988 |  |  | N | Electric Utility | 1 | [14 empty] | 10M | [23 empty] | N |  | N | bar: X X X to DFO RC RC
Vintage1988 | natural gas peaker | TRUE | 1015 | Austin Energy | 3548 | Decker Creek | TX | Travis | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 51.5 | 0.9 | 52 | 60 | 49 | N |  |  | OP | X | 9 | 1988 |  |  | N | Electric Utility | 1 | [14 empty] | 10M | [23 empty] | N |  | N | bar: X X X to DFO RC RC
Vintage2004 | natural gas peaker | TRUE | 2409 | Brownsville Public Utilities Board | 3559 | Silas Ray | TX | Cameron | 10 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SILASRAY_SILAS_10 | SILASRAY_SILAS_10 | 61 | 0.85 | 45 | 48 | 15 | N |  |  | OP | X | 12 | 2004 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1959 | natural gas combined cycle | TRUE | 2409 | Brownsville Public Utilities Board | 3559 | Silas Ray | TX | Cameron | 6 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | SILASRAY_SILAS_CC1_2 | SILASRAY_SILAS_CC1_2 | 25 | 0.85 | 20 | 20 | 15 | N |  |  | OP | X | 5 | 1959 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N |  | N | bar: X X X to DFO RC RC
Vintage1996 | natural gas combined cycle | TRUE | 2409 | Brownsville Public Utilities Board | 3559 | Silas Ray | TX | Cameron | 9 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y | SILASRAY_SILAS_CC1_1 | SILASRAY_SILAS_CC1_1 | 50 | 0.85 | 42 | 52 | 32 | N |  |  | OP | X | 6 | 1996 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2001 | petroleum | TRUE | 2409 | Brownsville Public Utilities Board | 3559 | Silas Ray | TX | Cameron | DG-3a | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1 | 1 | 1 | N |  |  | SB | Y | 11 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage2001 | petroleum | TRUE | 2409 | Brownsville Public Utilities Board | 3559 | Silas Ray | TX | Cameron | DG-3b | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1 | 1 | 1 | N |  |  | SB | Y | 11 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage2001 | petroleum | TRUE | 2409 | Brownsville Public Utilities Board | 3559 | Silas Ray | TX | Cameron | DG-4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1 | 1 | 1 | N |  |  | SB | Y | 11 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage2001 | petroleum | TRUE | 2409 | Brownsville Public Utilities Board | 3559 | Silas Ray | TX | Cameron | DG-6a | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1 | 1 | 1 | N |  |  | SB | N | 11 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage2001 | petroleum | TRUE | 2409 | Brownsville Public Utilities Board | 3559 | Silas Ray | TX | Cameron | DG-6b | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1 | 1 | 1 | N |  |  | SB | N | 11 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1975 | natural gas peaker | TRUE | 2442 | City of Bryan - (TX) | 3561 | Bryan (TX) | TX | Brazos | 7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | ATK ATKG |  | 22 | 0.9 | 21 | 21 | 5 | N |  |  | OP | X | 5 | 1975 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H |  |  |  |  | N | [18 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1967 | natural gas steam turbine | TRUE | 6958 | City of Garland - (TX) | 3576 | Ray Olinger | TX | Collin | 1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 75 | 0.85 | 75 | 75 | 10 | N |  |  | OP | X | 7 | 1967 |  |  | N | Electric Utility | 1 | [14 empty] | OVER | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1971 | natural gas steam turbine | TRUE | 6958 | City of Garland - (TX) | 3576 | Ray Olinger | TX | Collin | 2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 113.4 | 0.85 | 107 | 107 | 20 | N |  |  | OP | X | 1 | 1971 |  |  | N | Electric Utility | 1 | [14 empty] | OVER | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1976 | natural gas steam turbine | TRUE | 6958 | City of Garland - (TX) | 3576 | Ray Olinger | TX | Collin | 3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 156.6 | 0.9 | 138 | 138 | 25 | N |  |  | OP | X | 6 | 1976 |  |  | N | Electric Utility | 1 | [14 empty] | OVER | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage2001 | natural gas peaker | TRUE | 6958 | City of Garland - (TX) | 3576 | Ray Olinger | TX | Collin | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 82.7 | 0.85 | 75 | 81 | 55 | N |  |  | OP | X | 7 | 2001 |  |  | N | Electric Utility | 1 | [14 empty] | 1H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1927 | hydro | TRUE | 7751 | Guadalupe Blanco River Authority | 3581 | Abbott TP 3 | TX | Guadalupe | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.4 | 0.8 | 1.4 | 1.4 | 1.1 | N |  |  | OP | X | 1 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1927 | hydro | TRUE | 7751 | Guadalupe Blanco River Authority | 3581 | Abbott TP 3 | TX | Guadalupe | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.4 | 0.8 | 1.4 | 1.4 | 1.1 | N |  |  | OP | X | 1 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1927 | hydro | TRUE | 7751 | Guadalupe Blanco River Authority | 3582 | Dunlap TP 1 | TX | Guadalupe | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.7 | N |  |  | OS | X | 1 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1927 | hydro | TRUE | 7751 | Guadalupe Blanco River Authority | 3582 | Dunlap TP 1 | TX | Guadalupe | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.7 | N |  |  | OS | X | 1 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1931 | hydro | TRUE | 7751 | Guadalupe Blanco River Authority | 3583 | H 4 | TX | Gonzales | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 2.4 | 2.4 | 0.5 | N |  |  | OP | X | 1 | 1931 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1931 | hydro | TRUE | 7751 | Guadalupe Blanco River Authority | 3584 | H 5 | TX | Gonzales | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 2.4 | 2.4 | 0.5 | N |  |  | OS | X | 1 | 1931 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1927 | hydro | TRUE | 7751 | Guadalupe Blanco River Authority | 3585 | Nolte | TX | Guadalupe | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 0.6 | N |  |  | OP | X | 1 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1927 | hydro | TRUE | 7751 | Guadalupe Blanco River Authority | 3585 | Nolte | TX | Guadalupe | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 0.6 | N |  |  | OP | X | 1 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1932 | hydro | TRUE | 7751 | Guadalupe Blanco River Authority | 3586 | TP 4 | TX | Guadalupe | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 2.4 | 2.4 | 0.5 | N |  |  | OP | X | 1 | 1932 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 1H | [23 empty] | N
Vintage1940 | hydro | TRUE | 11269 | Lower Colorado River Authority | 3594 | Austin | TX | Travis | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9 | 1 | 8.2 | 8.2 | 7 | N |  |  | OP | X | 4 | 1940 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1940 | hydro | TRUE | 11269 | Lower Colorado River Authority | 3594 | Austin | TX | Travis | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9 | 1 | 8.8 | 8.8 | 7 | N |  |  | OP | X | 4 | 1940 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1938 | hydro | TRUE | 11269 | Lower Colorado River Authority | 3595 | Buchanan Dam (TX) | TX | Llano | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18.3 | 1 | 18.3 | 18.3 | 11 | N |  |  | OP | X | 1 | 1938 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1938 | hydro | TRUE | 11269 | Lower Colorado River Authority | 3595 | Buchanan Dam (TX) | TX | Llano | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18.3 | 1 | 18.3 | 18.3 | 11 | N |  |  | OP | X | 1 | 1938 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1950 | hydro | TRUE | 11269 | Lower Colorado River Authority | 3595 | Buchanan Dam (TX) | TX | Llano | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18.3 | 1 | 18.3 | 18.3 | 11 | N |  |  | OP | X | 5 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1951 | hydro | TRUE | 11269 | Lower Colorado River Authority | 3597 | Granite Shoals | TX | Burnet | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 27 | 0.9 | 27 | 27 | 23 | N |  |  | OP | X | 6 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1951 | hydro | TRUE | 11269 | Lower Colorado River Authority | 3597 | Granite Shoals | TX | Burnet | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 27 | 0.9 | 27 | 27 | 23 | N |  |  | OP | X | 8 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1938 | hydro | TRUE | 11269 | Lower Colorado River Authority | 3598 | Inks | TX | Burnet | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 1 | 13.8 | 13.8 | 7 | N |  |  | OP | X | 1 | 1938 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1951 | hydro | TRUE | 11269 | Lower Colorado River Authority | 3599 | Marble Falls | TX | Burnet | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 19.8 | 0.9 | 19.8 | 19.8 | 9 | N |  |  | OP | X | 10 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1951 | hydro | TRUE | 11269 | Lower Colorado River Authority | 3599 | Marble Falls | TX | Burnet | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 19.8 | 0.9 | 19.8 | 19.8 | 9 | N |  |  | OP | X | 9 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1941 | hydro | TRUE | 11269 | Lower Colorado River Authority | 3600 | Marshall Ford | TX | Travis | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 36 | 1 | 36 | 36 | 15 | N |  |  | OP | X | 1 | 1941 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1941 | hydro | TRUE | 11269 | Lower Colorado River Authority | 3600 | Marshall Ford | TX | Travis | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 36 | 1 | 36 | 36 | 20 | N |  |  | OP | X | 1 | 1941 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1941 | hydro | TRUE | 11269 | Lower Colorado River Authority | 3600 | Marshall Ford | TX | Travis | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 36 | 1 | 36 | 36 | 15 | N |  |  | OP | X | 1 | 1941 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1965 | natural gas steam turbine | TRUE | 11269 | Lower Colorado River Authority | 3601 | Sim Gideon | TX | Bastrop | 1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 136 | 0.85 | 136 | 140 | 19 | N |  |  | OP | X | 5 | 1965 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1968 | natural gas steam turbine | TRUE | 11269 | Lower Colorado River Authority | 3601 | Sim Gideon | TX | Bastrop | 2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 136 | 0.85 | 136 | 140 | 19 | N |  |  | OP | X | 3 | 1968 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1972 | natural gas steam turbine | TRUE | 11269 | Lower Colorado River Authority | 3601 | Sim Gideon | TX | Bastrop | 3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 351 | 0.9 | 335 | 340 | 57 | N |  |  | OP | X | 5 | 1972 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1965 | natural gas steam turbine | TRUE | 11292 | City of Lubbock - (TX) | 3602 | Ty Cooke | TX | Lubbock | 1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 44 | 0.9 | 42 | 42 | 25 | N |  |  | OA | X | 6 | 1965 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1978 | natural gas steam turbine | TRUE | 11292 | City of Lubbock - (TX) | 3602 | Ty Cooke | TX | Lubbock | 2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 53.6 | 0.9 | 46 | 46 | 25 | N |  |  | OA | X | 6 | 1978 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1971 | natural gas peaker | TRUE | 11292 | City of Lubbock - (TX) | 3602 | Ty Cooke | TX | Lubbock | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 18.5 | 0.9 | 16 | 18.5 | 16 | N |  |  | OP | X | 6 | 1971 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1974 | natural gas peaker | TRUE | 11292 | City of Lubbock - (TX) | 3602 | Ty Cooke | TX | Lubbock | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 22 | 0.9 | 16 | 18 | 16 | N |  |  | OA | X | 7 | 1974 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1957 | natural gas combined cycle | TRUE | 11292 | City of Lubbock - (TX) | 3604 | J Robert Massengale | TX | Lubbock | 6A | Natural Gas Fired Combined Cycle | CA | MGL8 | S | Y | X |  |  | 22 | 0.9 | 18 | 18 | 10 | N |  |  | OP | X | 6 | 1957 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1959 | natural gas combined cycle | TRUE | 11292 | City of Lubbock - (TX) | 3604 | J Robert Massengale | TX | Lubbock | 7 | Natural Gas Fired Combined Cycle | CA | MGL8 | S | Y | X |  |  | 22 | 0.9 | 18 | 18 | 10 | N |  |  | OP | X | 3 | 1959 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2000 | natural gas combined cycle | TRUE | 11292 | City of Lubbock - (TX) | 3604 | J Robert Massengale | TX | Lubbock | 8 | Natural Gas Fired Combined Cycle | CT | MGL8 | S | X | N |  |  | 40 | 0.9 | 38 | 42 | 30 | N |  |  | OP | X | 9 | 2000 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2004 | natural gas peaker | TRUE | 16604 | City of San Antonio - (TX) | 3609 | Leon Creek | TX | Bexar | CGT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | LEONLCPCT1_2 | LEONLCPCT1_2 | 57.4 | 0.85 | 46 | 46 | 20 | N |  |  | OP | X | 6 | 2004 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N |  | N | bar: X X X to DFO RC RC
Vintage2004 | natural gas peaker | TRUE | 16604 | City of San Antonio - (TX) | 3609 | Leon Creek | TX | Bexar | CGT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | LEONLCPCT1_2 | LEONLCPCT1_2 | 57.4 | 0.85 | 46 | 46 | 20 | N |  |  | OP | X | 6 | 2004 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N |  | N | bar: X X X to DFO RC RC
Vintage2004 | natural gas peaker | TRUE | 16604 | City of San Antonio - (TX) | 3609 | Leon Creek | TX | Bexar | CGT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | LEONLCPCT3_4 | LEONLCPCT3_4 | 57.4 | 0.85 | 46 | 46 | 20 | N |  |  | OP | X | 6 | 2004 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N |  | N | bar: X X X to DFO RC RC
Vintage2004 | natural gas peaker | TRUE | 16604 | City of San Antonio - (TX) | 3609 | Leon Creek | TX | Bexar | CGT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | LEONLCPCT3_4 | LEONLCPCT3_4 | 57.4 | 0.85 | 46 | 46 | 20 | N |  |  | OP | X | 6 | 2004 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N |  | N | bar: X X X to DFO RC RC
Vintage1972 | natural gas steam turbine | TRUE | 16604 | City of San Antonio - (TX) | 3611 | O W Sommers | TX | Bexar | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | CALAVER_OWS1 | CALAVER_OWS1 | 446 | 0.9 | 420 | 420 | 70 | N |  |  | OP | X | 4 | 1972 | 12 | 2026 | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1974 | natural gas steam turbine | TRUE | 16604 | City of San Antonio - (TX) | 3611 | O W Sommers | TX | Bexar | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | CALAVER_OWS2 | CALAVER_OWS2 | 446 | 0.9 | 410 | 410 | 70 | N |  |  | OP | X | 1 | 1974 | 12 | 2028 | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1966 | natural gas steam turbine | TRUE | 16604 | City of San Antonio - (TX) | 3612 | V H Braunig | TX | Bexar | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | BRAUNIG_VHB1 | BRAUNIG_VHB1 | 225 | 0.85 | 217 | 217 | 60 | N |  |  | OP | X | 3 | 1966 | 12 | 2024 | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1968 | natural gas steam turbine | TRUE | 16604 | City of San Antonio - (TX) | 3612 | V H Braunig | TX | Bexar | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | BRAUNIG_VHB2 | BRAUNIG_VHB2 | 252 | 0.85 | 230 | 230 | 60 | N |  |  | OP | X | 4 | 1968 | 12 | 2024 | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1970 | natural gas steam turbine | TRUE | 16604 | City of San Antonio - (TX) | 3612 | V H Braunig | TX | Bexar | 3 | Natural Gas Steam Turbine | ST |  | S | X | X | BRAUNIG_VHB3 | BRAUNIG_VHB3 | 417 | 0.85 | 412 | 412 | 70 | N |  |  | OP | X | 5 | 1970 | 12 | 2024 | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage2010 | natural gas peaker | TRUE | 16604 | City of San Antonio - (TX) | 3612 | V H Braunig | TX | Bexar | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | BR_VHB6CT5_6 | BR_VHB6CT5_6 | 61 | 0.85 | 48 | 48 | 20 | N |  |  | OP | X | 12 | 2010 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2010 | natural gas peaker | TRUE | 16604 | City of San Antonio - (TX) | 3612 | V H Braunig | TX | Bexar | 6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | BR_VHB6CT5_6 | BR_VHB6CT5_6 | 61 | 0.85 | 48 | 48 | 20 | N |  |  | OP | X | 12 | 2010 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2010 | natural gas peaker | TRUE | 16604 | City of San Antonio - (TX) | 3612 | V H Braunig | TX | Bexar | 7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | BR_VHB6CT7_8 | BR_VHB6CT7_8 | 61 | 0.85 | 48 | 48 | 20 | N |  |  | OP | X | 12 | 2010 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2010 | natural gas peaker | TRUE | 16604 | City of San Antonio - (TX) | 3612 | V H Braunig | TX | Bexar | 8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | BR_VHB6CT7_8 | BR_VHB6CT7_8 | 61 | 0.85 | 47 | 47 | 20 | N |  |  | OP | X | 12 | 2010 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1968 | natural gas steam turbine | TRUE | 2172 | Brazos Electric Power Coop Inc | 3628 | R W Miller | TX | Palo Pinto | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | MIL_MILG1_2 | MIL_MILG1_2 | 66 | 0.85 | 66 | 66 | 20 | N |  |  | OS | X | 10 | 1968 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H |  |  |  |  | N | [18 empty] | N |  | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1972 | natural gas steam turbine | TRUE | 2172 | Brazos Electric Power Coop Inc | 3628 | R W Miller | TX | Palo Pinto | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | MIL_MILG1_2 | MIL_MILG1_2 | 100 | 0.85 | 100 | 100 | 38 | N |  |  | OP | X | 7 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | 12H |  |  |  |  | N | [18 empty] | Y | Y | Y
Vintage1975 | natural gas steam turbine | TRUE | 2172 | Brazos Electric Power Coop Inc | 3628 | R W Miller | TX | Palo Pinto | 3 | Natural Gas Steam Turbine | ST |  | S | X | X | MIL_MILG345 | MIL_MILG345 | 200 | 0.9 | 200 | 200 | 40 | N |  |  | OP | X | 8 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | 12H |  |  |  |  | N | [18 empty] | Y | Y | Y
Vintage1994 | natural gas peaker | TRUE | 2172 | Brazos Electric Power Coop Inc | 3628 | R W Miller | TX | Palo Pinto | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MIL_MILG345 | MIL_MILG345 | 118.8 | 0.9 | 104 | 104 | 35 | N |  |  | OP | X | 7 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H |  |  |  |  | N | [18 empty] | Y | Y | Y
Vintage1994 | natural gas peaker | TRUE | 2172 | Brazos Electric Power Coop Inc | 3628 | R W Miller | TX | Palo Pinto | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MIL_MILG345 | MIL_MILG345 | 118.8 | 0.9 | 104 | 104 | 35 | N |  |  | OP | X | 7 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H |  |  |  |  | N | [18 empty] | Y | Y | Y
Vintage2010 | natural gas peaker | TRUE | 17583 | South Texas Electric Coop, Inc | 3630 | Pearsall | TX | Frio | 10A | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PEARSA_1_24 |  | 8.4 | 0.8 | 8.4 | 8.4 | 4 | N |  |  | OP | X | 3 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2010 | natural gas peaker | TRUE | 17583 | South Texas Electric Coop, Inc | 3630 | Pearsall | TX | Frio | 11A | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PEARSA_1_24 |  | 8.4 | 0.8 | 8.4 | 8.4 | 4 | N |  |  | OP | X | 3 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2010 | natural gas peaker | TRUE | 17583 | South Texas Electric Coop, Inc | 3630 | Pearsall | TX | Frio | 12A | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PEARSA_1_24 |  | 8.4 | 0.8 | 8.4 | 8.4 | 4 | N |  |  | OP | X | 3 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2010 | natural gas peaker | TRUE | 17583 | South Texas Electric Coop, Inc | 3630 | Pearsall | TX | Frio | 13A | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PEARSA_1_24 |  | 8.4 | 0.8 | 8.4 | 8.4 | 4 | N |  |  | OP | X | 3 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2010 | natural gas peaker | TRUE | 17583 | South Texas Electric Coop, Inc | 3630 | Pearsall | TX | Frio | 14A | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PEARSA_1_24 |  | 8.4 | 0.8 | 8.4 | 8.4 | 4 | N |  |  | OP | X | 3 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2010 | natural gas peaker | TRUE | 17583 | South Texas Electric Coop, Inc | 3630 | Pearsall | TX | Frio | 15A | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PEARSA_1_24 |  | 8.4 | 0.8 | 8.4 | 8.4 | 4 | N |  |  | OP | X | 3 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2010 | natural gas peaker | TRUE | 17583 | South Texas Electric Coop, Inc | 3630 | Pearsall | TX | Frio | 16A | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PEARSA_1_24 |  | 8.4 | 0.8 | 8.4 | 8.4 | 4 | N |  |  | OP | X | 3 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2010 | natural gas peaker | TRUE | 17583 | South Texas Electric Coop, Inc | 3630 | Pearsall | TX | Frio | 17A | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PEARSA_1_24 |  | 8.4 | 0.8 | 8.4 | 8.4 | 4 | N |  |  | OP | X | 4 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2010 | natural gas peaker | TRUE | 17583 | South Texas Electric Coop, Inc | 3630 | Pearsall | TX | Frio | 18A | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PEARSA_1_24 |  | 8.4 | 0.8 | 8.4 | 8.4 | 4 | N |  |  | OP | X | 3 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2010 | natural gas peaker | TRUE | 17583 | South Texas Electric Coop, Inc | 3630 | Pearsall | TX | Frio | 19A | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PEARSA_1_24 |  | 8.4 | 0.8 | 8.4 | 8.4 | 4 | N |  |  | OP | X | 4 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2010 | natural gas peaker | TRUE | 17583 | South Texas Electric Coop, Inc | 3630 | Pearsall | TX | Frio | 1A | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PEARSA_1_24 |  | 8.4 | 0.8 | 8.4 | 8.4 | 4 | N |  |  | OP | X | 3 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2010 | natural gas peaker | TRUE | 17583 | South Texas Electric Coop, Inc | 3630 | Pearsall | TX | Frio | 20A | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PEARSA_1_24 |  | 8.4 | 0.8 | 8.4 | 8.4 | 4 | N |  |  | OP | X | 4 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2010 | natural gas peaker | TRUE | 17583 | South Texas Electric Coop, Inc | 3630 | Pearsall | TX | Frio | 21A | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PEARSA_1_24 |  | 8.4 | 0.8 | 8.4 | 8.4 | 4 | N |  |  | OP | X | 4 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2010 | natural gas peaker | TRUE | 17583 | South Texas Electric Coop, Inc | 3630 | Pearsall | TX | Frio | 22A | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PEARSA_1_24 |  | 8.4 | 0.8 | 8.4 | 8.4 | 4 | N |  |  | OP | X | 4 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2010 | natural gas peaker | TRUE | 17583 | South Texas Electric Coop, Inc | 3630 | Pearsall | TX | Frio | 23A | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PEARSA_1_24 |  | 8.4 | 0.8 | 8.4 | 8.4 | 4 | N |  |  | OP | X | 4 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2010 | natural gas peaker | TRUE | 17583 | South Texas Electric Coop, Inc | 3630 | Pearsall | TX | Frio | 24A | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PEARSA_1_24 |  | 8.4 | 0.8 | 8.4 | 8.4 | 4 | N |  |  | OP | X | 4 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2010 | natural gas peaker | TRUE | 17583 | South Texas Electric Coop, Inc | 3630 | Pearsall | TX | Frio | 2A | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PEARSA_1_24 |  | 8.4 | 0.8 | 8.4 | 8.4 | 4 | N |  |  | OP | X | 3 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2010 | natural gas peaker | TRUE | 17583 | South Texas Electric Coop, Inc | 3630 | Pearsall | TX | Frio | 3A | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PEARSA_1_24 |  | 8.4 | 0.8 | 8.4 | 8.4 | 4 | N |  |  | OP | X | 3 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2010 | natural gas peaker | TRUE | 17583 | South Texas Electric Coop, Inc | 3630 | Pearsall | TX | Frio | 4A | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PEARSA_1_24 |  | 8.4 | 0.8 | 8.4 | 8.4 | 4 | N |  |  | OP | X | 3 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2010 | natural gas peaker | TRUE | 17583 | South Texas Electric Coop, Inc | 3630 | Pearsall | TX | Frio | 5A | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PEARSA_1_24 |  | 8.4 | 0.8 | 8.4 | 8.4 | 4 | N |  |  | OP | X | 3 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2010 | natural gas peaker | TRUE | 17583 | South Texas Electric Coop, Inc | 3630 | Pearsall | TX | Frio | 6A | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PEARSA_1_24 |  | 8.4 | 0.8 | 8.4 | 8.4 | 4 | N |  |  | OP | X | 3 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2010 | natural gas peaker | TRUE | 17583 | South Texas Electric Coop, Inc | 3630 | Pearsall | TX | Frio | 7A | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PEARSA_1_24 |  | 8.4 | 0.8 | 8.4 | 8.4 | 4 | N |  |  | OP | X | 3 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2010 | natural gas peaker | TRUE | 17583 | South Texas Electric Coop, Inc | 3630 | Pearsall | TX | Frio | 8A | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PEARSA_1_24 |  | 8.4 | 0.8 | 8.4 | 8.4 | 4 | N |  |  | OP | X | 3 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2010 | natural gas peaker | TRUE | 17583 | South Texas Electric Coop, Inc | 3630 | Pearsall | TX | Frio | 9A | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PEARSA_1_24 |  | 8.4 | 0.8 | 8.4 | 8.4 | 4 | N |  |  | OP | X | 3 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2003 | natural gas combined cycle | TRUE | 17583 | South Texas Electric Coop, Inc | 3631 | Sam Rayburn | TX | Victoria | 10 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X | RAYBURN_CC1 |  | 42 | 0.9 | 37 | 37 | 7 | N |  |  | OP | X | 10 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1991 | petroleum | TRUE | 17583 | South Texas Electric Coop, Inc | 3631 | Sam Rayburn | TX | Victoria | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 0.9 | 0.9 | 0.5 | N |  |  | OP | X | 7 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO DFO DFO: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1991 | petroleum | TRUE | 17583 | South Texas Electric Coop, Inc | 3631 | Sam Rayburn | TX | Victoria | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 0.9 | 0.9 | 0.5 | N |  |  | OP | X | 10 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO DFO DFO: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage2003 | natural gas combined cycle | TRUE | 17583 | South Texas Electric Coop, Inc | 3631 | Sam Rayburn | TX | Victoria | 7 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | RAYBURN_CC1 |  | 49.2 | 0.85 | 49 | 49 | 8 | N |  |  | OP | X | 10 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2003 | natural gas combined cycle | TRUE | 17583 | South Texas Electric Coop, Inc | 3631 | Sam Rayburn | TX | Victoria | 8 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | RAYBURN_CC1 |  | 49.2 | 0.85 | 49 | 49 | 8 | N |  |  | OP | X | 10 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2003 | natural gas combined cycle | TRUE | 17583 | South Texas Electric Coop, Inc | 3631 | Sam Rayburn | TX | Victoria | 9 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | RAYBURN_CC1 |  | 49.2 | 0.85 | 48 | 48 | 8 | N |  |  | OP | X | 10 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1907 | hydro | TRUE | 1434 | Beaver City Corporation | 3643 | Upper Beaver | UT | Beaver | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 1 | 1.3 | 1.3 | 0.1 | N |  |  | OP | X | 8 | 1907 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1907 | hydro | TRUE | 1434 | Beaver City Corporation | 3643 | Upper Beaver | UT | Beaver | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 1 | 1.2 | 1.2 | 0.1 | N |  |  | OP | X | 8 | 1907 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1927 | hydro | TRUE | 14354 | PacifiCorp | 3646 | Cutler Hydro | UT | Box Elder | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.8 | 15 | 15 | 0 | N |  |  | OP | X | 7 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1927 | hydro | TRUE | 14354 | PacifiCorp | 3646 | Cutler Hydro | UT | Box Elder | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.8 | 15 | 15 | 0 | N |  |  | OP | X | 7 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1951 | natural gas steam turbine | TRUE | 14354 | PacifiCorp | 3648 | Gadsby | UT | Salt Lake | 1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 69 | 0.85 | 64 | 64 | 25 | N |  |  | OP | X | 9 | 1951 | 12 | 2032 | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H |  |  |  |  | N | [18 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1952 | natural gas steam turbine | TRUE | 14354 | PacifiCorp | 3648 | Gadsby | UT | Salt Lake | 2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 69 | 0.8 | 69 | 69 | 20 | N |  |  | OP | X | 12 | 1952 | 12 | 2032 | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1955 | natural gas steam turbine | TRUE | 14354 | PacifiCorp | 3648 | Gadsby | UT | Salt Lake | 3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 133.6 | 0.85 | 104.5 | 104.5 | 25 | N |  |  | OP | X | 6 | 1955 | 12 | 2032 | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage2002 | natural gas peaker | TRUE | 14354 | PacifiCorp | 3648 | Gadsby | UT | Salt Lake | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 71 | 0.85 | 39.6 | 40.7 | 10 | N |  |  | OP | X | 7 | 2002 | 12 | 2032 | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2002 | natural gas peaker | TRUE | 14354 | PacifiCorp | 3648 | Gadsby | UT | Salt Lake | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 71 | 0.85 | 39.6 | 40.7 | 10 | N |  |  | OP | X | 7 | 2002 | 12 | 2032 | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2002 | natural gas peaker | TRUE | 14354 | PacifiCorp | 3648 | Gadsby | UT | Salt Lake | 6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 71 | 0.85 | 36.9 | 40.7 | 10 | N |  |  | OP | X | 8 | 2002 | 12 | 2032 | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1896 | hydro | TRUE | 14354 | PacifiCorp | 3651 | Granite | UT | Salt Lake | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 1 | 1.2 | 1.2 | 0 | N |  |  | OP | X | 8 | 1896 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1910 | hydro | TRUE | 14354 | PacifiCorp | 3656 | Pioneer | UT | Weber | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 1 | 2 | 2 | 0 | N |  |  | OP | X | 6 | 1910 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1910 | hydro | TRUE | 14354 | PacifiCorp | 3656 | Pioneer | UT | Weber | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 1 | 2 | 2 | 0 | N |  |  | OP | X | 6 | 1910 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1910 | hydro | TRUE | 8366 | Heber Light & Power Company | 3658 | Snake Creek | UT | Wasatch | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 1 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 7 | 1910 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1910 | hydro | TRUE | 8366 | Heber Light & Power Company | 3658 | Snake Creek | UT | Wasatch | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 1 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 7 | 1910 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1912 | hydro | TRUE | 14354 | PacifiCorp | 3659 | Stairs | UT | Salt Lake | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 1 | 1.2 | 1.2 | 0 | N |  |  | OP | X | 7 | 1912 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1911 | hydro | TRUE | 14354 | PacifiCorp | 3661 | Weber | UT | Weber | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.8 | 1 | 2 | 2 | 0 | N |  |  | OP | X | 7 | 1911 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage2001 | natural gas peaker | TRUE | 2010 | City of Bountiful | 3665 | Bountiful City | UT | Davis | 1A | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 5.2 | 0.8 | 3.5 | 5.1 | 3 | N |  |  | OP | X | 7 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2012 | natural gas peaker | TRUE | 2010 | City of Bountiful | 3665 | Bountiful City | UT | Davis | 2A | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 12.6 | 0.8 | 10.5 | 13.5 | 7 | N |  |  | OP | X | 6 | 2012 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2012 | natural gas peaker | TRUE | 2010 | City of Bountiful | 3665 | Bountiful City | UT | Davis | 3A | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 12.6 | 0.8 | 10.5 | 13.5 | 7 | N |  |  | OP | X | 6 | 2012 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1921 | hydro | TRUE | 2220 | Brigham City Corporation | 3666 | Brigham City | UT | Box Elder | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.9 | 0.5 | 0.5 | 0.2 | N |  |  | OP | X | 1 | 1921 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1921 | hydro | TRUE | 2220 | Brigham City Corporation | 3666 | Brigham City | UT | Box Elder | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.9 | 0.5 | 0.5 | 0.2 | N |  |  | OP | X | 1 | 1921 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1964 | hydro | TRUE | 2220 | Brigham City Corporation | 3666 | Brigham City | UT | Box Elder | 8182 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.9 | 0.5 | 0.5 | 0.2 | N |  |  | OP | X | 1 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1925 | hydro | TRUE | 11135 | City of Logan - (UT) | 3675 | Hydro III | UT | Cache | HY1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.8 | 0.7 | 0.2 | 0.1 | N |  |  | OP | X | 12 | 1925 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1925 | hydro | TRUE | 11135 | City of Logan - (UT) | 3675 | Hydro III | UT | Cache | HY2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.8 | 0.7 | 0.2 | 0.1 | N |  |  | OP | X | 12 | 1925 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1939 | hydro | TRUE | 11588 | City of Manti - (UT) | 3676 | Manti Upper | UT | Sanpete | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 1 | 0.4 | 0.1 | 0.1 | N |  |  | OP | X | 1 | 1939 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1988 | hydro | TRUE | 11588 | City of Manti - (UT) | 3676 | Manti Upper | UT | Sanpete | HC2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.8 | 0.8 | 0.1 | 0.1 | N |  |  | OP | X | 1 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1988 | hydro | TRUE | 17845 | City of Springville - (UT) | 3688 | Bartholomew | UT | Utah | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.85 | 1 | 1 | 0.1 | N |  |  | OP | X | 4 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1983 | hydro | TRUE | 18205 | Strawberry Water Users Assn | 3691 | Spanish Fork | UT | Utah | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.7 | 0.9 | 1.7 | 1.7 | 0.1 | N |  |  | OP | X | 10 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1983 | hydro | TRUE | 18205 | Strawberry Water Users Assn | 3691 | Spanish Fork | UT | Utah | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.7 | 0.9 | 1.7 | 1.7 | 0.1 | N |  |  | OP | X | 10 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1937 | hydro | TRUE | 18205 | Strawberry Water Users Assn | 3691 | Spanish Fork | UT | Utah | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 10 | 1937 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1958 | hydro | TRUE | 20255 | Weber Basin Water Conserv Dist | 3697 | Gateway | UT | Morgan | 1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 2 | 0.9 | 2 | 2 | 0.3 | N |  |  | OP | X | 8 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [20 empty] | N
Vintage1958 | hydro | TRUE | 20255 | Weber Basin Water Conserv Dist | 3697 | Gateway | UT | Morgan | 2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 2 | 0.9 | 2 | 2 | 0.3 | N |  |  | OP | X | 8 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [20 empty] | N
Vintage1958 | hydro | TRUE | 20255 | Weber Basin Water Conserv Dist | 3698 | Wanship | UT | Summit | 1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.9 | 0.9 | 1.9 | 1.9 | 0.3 | N |  |  | OP | X | 8 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [20 empty] | N
Vintage1958 | hydro | TRUE | 6957 | Garkane Energy Coop, Inc | 3699 | Boulder | UT | Garfield | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.4 | 0.9 | 1.4 | 1.4 | 0.5 | N |  |  | OP | X | 8 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1958 | hydro | TRUE | 6957 | Garkane Energy Coop, Inc | 3699 | Boulder | UT | Garfield | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.4 | 0.9 | 1.4 | 1.4 | 0.5 | N |  |  | OP | X | 8 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1961 | hydro | TRUE | 6957 | Garkane Energy Coop, Inc | 3699 | Boulder | UT | Garfield | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.4 | 0.9 | 1.4 | 1.4 | 0.5 | N |  |  | OP | X | 9 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1920 | hydro | TRUE | 12866 | Moon Lake Electric Assn Inc | 3704 | Uintah | UT | Duchesne | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.3 | N |  |  | OP | X | 7 | 1920 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M |  |  |  | N | [19 empty] | N
Vintage1940 | hydro | TRUE | 12866 | Moon Lake Electric Assn Inc | 3704 | Uintah | UT | Duchesne | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.3 | N |  |  | OP | X | 9 | 1940 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1961 | petroleum | TRUE | 7601 | Green Mountain Power Corp | 3708 | Ascutney | VT | Windsor | GT4 | Petroleum Liquids | GT |  | S | X | X |  |  | 13.2 | 0.8 | 9 | 13.4 | 7 | N |  |  | OP | X | 8 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage1982 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3709 | Smith (VT) | VT | Orange | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.8 | 0.7 | 0.9 | 0.2 | N |  |  | OP | X | 12 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1982 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3709 | Smith (VT) | VT | Orange | HC2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.2 | 0.4 | 0.2 | N |  |  | OP | X | 12 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1907 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3710 | Cavendish | VT | Windsor | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.4 | 0.5 | 0.2 | N |  |  | OP | X | 2 | 1907 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1907 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3710 | Cavendish | VT | Windsor | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.4 | 0.5 | 0.2 | N |  |  | OP | X | 2 | 1907 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1907 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3710 | Cavendish | VT | Windsor | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.3 | 0.4 | 0.2 | N |  |  | OP | X | 2 | 1907 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1937 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3711 | Clark Falls | VT | Chittenden | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 0.5 | N |  |  | OP | X | 2 | 1937 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1919 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3712 | Fairfax Falls | VT | Franklin | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.4 | 0.8 | 1.4 | 1.4 | 0.2 | N |  |  | OP | X | 2 | 1919 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1919 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3712 | Fairfax Falls | VT | Franklin | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.1 | 0.8 | 2 | 2 | 0.2 | N |  |  | OP | X | 2 | 1919 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1920 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3714 | Glen | VT | Rutland | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.2 | N |  |  | OP | X | 8 | 1920 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1920 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3714 | Glen | VT | Rutland | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.2 | N |  |  | OP | X | 8 | 1920 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1917 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3716 | Lower Middlebury | VT | Addison | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 8 | 1917 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1917 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3716 | Lower Middlebury | VT | Addison | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 8 | 1917 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1917 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3716 | Lower Middlebury | VT | Addison | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.2 | N |  |  | OP | X | 8 | 1917 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1929 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3717 | Milton | VT | Chittenden | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.7 | 0.8 | 3.5 | 3.5 | 0.5 | N |  |  | OP | X | 2 | 1929 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1929 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3717 | Milton | VT | Chittenden | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.7 | 0.8 | 3.5 | 3.5 | 0.5 | N |  |  | OP | X | 8 | 1929 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1948 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3720 | Peterson | VT | Chittenden | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.3 | 0.8 | 5.8 | 6.3 | 0.2 | N |  |  | OP | X | 2 | 1948 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1914 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3722 | Pittsford | VT | Rutland | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.4 | 0.2 | N |  |  | OP | X | 2 | 1914 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1914 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3722 | Pittsford | VT | Rutland | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.4 | 0.2 | N |  |  | OP | X | 2 | 1914 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1914 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3722 | Pittsford | VT | Rutland | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.8 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 2 | 1914 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1962 | petroleum | TRUE | 7601 | Green Mountain Power Corp | 3723 | Rutland | VT | Rutland | GT5 | Petroleum Liquids | GT |  | S | X | X |  |  | 13.2 | 0.8 | 8.4 | 12.8 | 7 | N |  |  | OP | X | 12 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage1917 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3724 | Salisbury | VT | Addison | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 0.8 | 1.2 | 1.2 | 0.2 | N |  |  | OP | X | 2 | 1917 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1917 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3725 | Silver Lake (VT) | VT | Addison | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 0.8 | 2.2 | 2.2 | 0.2 | N |  |  | OP | X | 2 | 1917 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1951 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3728 | Weybridge | VT | Addison | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.8 | 3.4 | 3.4 | 0.5 | N |  |  | OP | X | 2 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1940 | hydro | TRUE | 49852 | Great Bay Hydro Corp | 3731 | Newport | VT | Orleans | 1 | Conventional Hydroelectric | HY |  | S | X | X | node #4447 | node #4447 | 1.7 | 0.8 | 1.7 | 1.7 | 0.1 | N |  |  | OP | X | 1 | 1940 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1944 | hydro | TRUE | 49852 | Great Bay Hydro Corp | 3731 | Newport | VT | Orleans | 2 | Conventional Hydroelectric | HY |  | S | X | X | node #4447 | node #4447 | 1.7 | 0.8 | 1.7 | 1.7 | 0.1 | N |  |  | OP | X | 1 | 1944 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1936 | hydro | TRUE | 49852 | Great Bay Hydro Corp | 3731 | Newport | VT | Orleans | 3 | Conventional Hydroelectric | HY |  | S | X | X | node #4447 | node #4447 | 0.6 | 0.8 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 1 | 1936 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1972 | other | TRUE | 7601 | Green Mountain Power Corp | 3734 | Berlin 5 | VT | Washington | GT1 | Petroleum Liquids | GT |  | S | X | X |  |  | 41.8 | 0.8 | 35 | 45.7 | 24 | N |  |  | OP | X | 6 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: KER |  |  | N |  |  | 10M | [23 empty] | N | N
Vintage1965 | petroleum | TRUE | 7601 | Green Mountain Power Corp | 3735 | Colchester 16 | VT | Chittenden | GT1 | Petroleum Liquids | GT |  | S | X | X |  |  | 18 | 0.8 | 8.7 | 13.9 | 3 | N |  |  | OP | X | 10 | 1965 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage1917 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3737 | Essex Junction 19 | VT | Chittenden | H1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.3 | N |  |  | OP | X | 1 | 1917 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1917 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3737 | Essex Junction 19 | VT | Chittenden | H2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.3 | N |  |  | OP | X | 1 | 1917 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1917 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3737 | Essex Junction 19 | VT | Chittenden | H3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.3 | N |  |  | OP | X | 1 | 1917 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1917 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3737 | Essex Junction 19 | VT | Chittenden | H4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.3 | N |  |  | OP | X | 1 | 1917 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage2008 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3737 | Essex Junction 19 | VT | Chittenden | H9 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 3 | 2008 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M | [23 empty] | N
Vintage2007 | petroleum | TRUE | 7601 | Green Mountain Power Corp | 3737 | Essex Junction 19 | VT | Chittenden | IC-5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 10 | 2007 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 10M | [23 empty] | N
Vintage2007 | petroleum | TRUE | 7601 | Green Mountain Power Corp | 3737 | Essex Junction 19 | VT | Chittenden | IC-6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 10 | 2007 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 10M | [23 empty] | N
Vintage2007 | petroleum | TRUE | 7601 | Green Mountain Power Corp | 3737 | Essex Junction 19 | VT | Chittenden | IC-7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 10 | 2007 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 10M | [23 empty] | N
Vintage2007 | petroleum | TRUE | 7601 | Green Mountain Power Corp | 3737 | Essex Junction 19 | VT | Chittenden | IC-8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 10 | 2007 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 10M | [23 empty] | N
Vintage1927 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3739 | Marshfield 6 | VT | Washington | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5 | 0.8 | 5 | 5 | 2.5 | N |  |  | OP | X | 1 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1928 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3740 | Middlesex 2 | VT | Washington | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.2 | N |  |  | OP | X | 1 | 1928 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1928 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3740 | Middlesex 2 | VT | Washington | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.2 | N |  |  | OP | X | 1 | 1928 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1917 | hydro | TRUE | 7601 | Green Mountain Power Corp | 3743 | West Danville 15 | VT | Caledonia | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.2 | N |  |  | OP | X | 1 | 1917 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1928 | hydro | TRUE | 61122 | Great River Hydro, LLC | 3745 | Bellows Falls | VT | Windham | GEN1 | Conventional Hydroelectric | HY |  | S | X | X | 335 |  | 13.6 | 0.8 | 15.7 | 15.7 | 4 | N |  |  | OP | X | 3 | 1928 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1928 | hydro | TRUE | 61122 | Great River Hydro, LLC | 3745 | Bellows Falls | VT | Windham | GEN2 | Conventional Hydroelectric | HY |  | S | X | X | 335 |  | 13.6 | 0.8 | 15.7 | 15.7 | 4 | N |  |  | OP | X | 3 | 1928 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1928 | hydro | TRUE | 61122 | Great River Hydro, LLC | 3745 | Bellows Falls | VT | Windham | GEN3 | Conventional Hydroelectric | HY |  | S | X | X | 335 |  | 13.6 | 0.8 | 15.7 | 15.7 | 4 | N |  |  | OP | X | 4 | 1928 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1924 | hydro | TRUE | 61122 | Great River Hydro, LLC | 3746 | Harriman | VT | Windham | GEN1 | Conventional Hydroelectric | HY |  | S | X | X | 435 |  | 11.2 | 0.8 | 13.6 | 12.8 | 8 | N |  |  | OP | X | 5 | 1924 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1924 | hydro | TRUE | 61122 | Great River Hydro, LLC | 3746 | Harriman | VT | Windham | GEN2 | Conventional Hydroelectric | HY |  | S | X | X | 435 |  | 11.2 | 0.8 | 13.6 | 12.8 | 8 | N |  |  | OP | X | 6 | 1924 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1924 | hydro | TRUE | 61122 | Great River Hydro, LLC | 3746 | Harriman | VT | Windham | GEN3 | Conventional Hydroelectric | HY |  | S | X | X | 435 |  | 11.2 | 0.8 | 13.6 | 12.8 | 8 | N |  |  | OP | X | 11 | 1924 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1927 | hydro | TRUE | 62775 | Central Rivers Power NH, LLC | 3750 | Canaan | VT | Essex | 1 | Conventional Hydroelectric | HY |  | S | X | X | 4002 Z_NewHampshire |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.1 | N |  |  | OP | X | 8 | 1927 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1931 | hydro | TRUE | 1299 | Barton Village, Inc | 3753 | West Charleston | VT | Orleans | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.8 | 0.7 | 0.7 | 0 | N |  |  | OP | X | 7 | 1931 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1948 | hydro | TRUE | 1299 | Barton Village, Inc | 3753 | West Charleston | VT | Orleans | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.8 | 0.6 | 0.6 | 0 | N |  |  | OP | X | 10 | 1948 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1971 | petroleum | TRUE | 2548 | City of Burlington Electric - (VT) | 3754 | Burlington GT | VT | Chittenden | GT1 | Petroleum Liquids | GT |  | S | X | X | 363 | 363 | 25.5 | 0.85 | 19.7 | 23.4 | 5 | N |  |  | OP | X | 9 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO DFO DFO: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1915 | hydro | TRUE | 11359 | Village of Lyndonville - (VT) | 3762 | Great Falls (VT) | VT | Caledonia | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.85 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 8 | 1915 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1915 | hydro | TRUE | 11359 | Village of Lyndonville - (VT) | 3762 | Great Falls (VT) | VT | Caledonia | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.85 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 8 | 1915 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1979 | hydro | TRUE | 11359 | Village of Lyndonville - (VT) | 3762 | Great Falls (VT) | VT | Caledonia | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 0.85 | 1.3 | 1.3 | 0.1 | N |  |  | OP | X | 2 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1924 | hydro | TRUE | 12989 | Village of Morrisville - (VT) | 3764 | Morrisville | VT | Lamoille | 1 | Conventional Hydroelectric | HY |  | S | X | X | 4466 |  | 0.6 | 0.8 | 0.5 | 0.6 | 0.1 | N |  |  | OP | X | 8 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H
Vintage1924 | hydro | TRUE | 12989 | Village of Morrisville - (VT) | 3764 | Morrisville | VT | Lamoille | 2 | Conventional Hydroelectric | HY |  | S | X | X | 4466 |  | 1.2 | 0.8 | 1 | 1.2 | 0.1 | N |  |  | OP | X | 8 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H
Vintage1914 | hydro | TRUE | 12989 | Village of Morrisville - (VT) | 3765 | Cadys Falls | VT | Lamoille | 1 | Conventional Hydroelectric | HY |  | S | X | X | 4466 |  | 0.8 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 8 | 1914 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H
Vintage1947 | hydro | TRUE | 12989 | Village of Morrisville - (VT) | 3765 | Cadys Falls | VT | Lamoille | 2 | Conventional Hydroelectric | HY |  | S | X | X | 4466 |  | 0.8 | 0.8 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 8 | 1947 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H
Vintage1912 | hydro | TRUE | 733 | Appalachian Power Co | 3772 | Buck Hydro | VA | Carroll | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.8 | 0.9 | 3 | 5.3 | 0.2 | N |  |  | OP | X | 1 | 1912 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 12H
Vintage1912 | hydro | TRUE | 733 | Appalachian Power Co | 3772 | Buck Hydro | VA | Carroll | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.8 | 0.9 | 3 | 5.3 | 0.2 | N |  |  | OP | X | 1 | 1912 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 12H
Vintage1912 | hydro | TRUE | 733 | Appalachian Power Co | 3772 | Buck Hydro | VA | Carroll | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.8 | 0.9 | 3 | 5.3 | 0.2 | N |  |  | OP | X | 1 | 1912 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 12H
Vintage1912 | hydro | TRUE | 733 | Appalachian Power Co | 3773 | Byllesby 2 | VA | Carroll | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.4 | 0.9 | 7.9 | 4.4 | 1 | N |  |  | OP | X | 1 | 1912 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 12H
Vintage1912 | hydro | TRUE | 733 | Appalachian Power Co | 3773 | Byllesby 2 | VA | Carroll | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.4 | 0.9 | 7.9 | 4.4 | 1 | N |  |  | OP | X | 1 | 1912 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 12H
Vintage1912 | hydro | TRUE | 733 | Appalachian Power Co | 3773 | Byllesby 2 | VA | Carroll | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.4 | 0.9 | 7.9 | 4.4 | 1 | N |  |  | OP | X | 1 | 1912 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 12H
Vintage1912 | hydro | TRUE | 733 | Appalachian Power Co | 3773 | Byllesby 2 | VA | Carroll | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.4 | 0.9 | 7.9 | 4.4 | 1 | N |  |  | OP | X | 1 | 1912 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 12H
Vintage1939 | hydro | TRUE | 733 | Appalachian Power Co | 3774 | Claytor | VA | Pulaski | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18.7 | 0.9 | 14.7 | 28.2 | 14 | N |  |  | OP | X | 8 | 1939 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 12H
Vintage1939 | hydro | TRUE | 733 | Appalachian Power Co | 3774 | Claytor | VA | Pulaski | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18.7 | 0.9 | 14.7 | 28.2 | 14 | N |  |  | OP | X | 8 | 1939 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 12H
Vintage1939 | hydro | TRUE | 733 | Appalachian Power Co | 3774 | Claytor | VA | Pulaski | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18.7 | 0.9 | 14.7 | 28.2 | 14 | N |  |  | OP | X | 8 | 1939 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 12H
Vintage1939 | hydro | TRUE | 733 | Appalachian Power Co | 3774 | Claytor | VA | Pulaski | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18.7 | 0.9 | 14.7 | 28.2 | 14 | N |  |  | OP | X | 8 | 1939 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 12H
Vintage1958 | natural gas steam turbine | TRUE | 733 | Appalachian Power Co | 3775 | Clinch River | VA | Russell | 1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 237.5 | 0.8 | 230 | 235 | 60 | N |  |  | OP | X | 9 | 1958 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H |  | N |  |  | N | [18 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1958 | natural gas steam turbine | TRUE | 733 | Appalachian Power Co | 3775 | Clinch River | VA | Russell | 2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 237.5 | 0.8 | 230 | 235 | 60 | N |  |  | OP | X | 12 | 1958 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H |  | N |  |  | N | [18 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1964 | hydro | TRUE | 733 | Appalachian Power Co | 3777 | Leesville | VA | Pittsylvania | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 20 | 0.8 | 25 | 25 | 23 | N |  |  | OP | X | 2 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 12H
Vintage1964 | hydro | TRUE | 733 | Appalachian Power Co | 3777 | Leesville | VA | Pittsylvania | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 20 | 0.8 | 25 | 25 | 23 | N |  |  | OP | X | 3 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 12H
Vintage1954 | hydro | TRUE | 733 | Appalachian Power Co | 3778 | Niagara | VA | Roanoke | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 0.6 | 1.4 | 0.3 | N |  |  | OP | X | 6 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 12H
Vintage1954 | hydro | TRUE | 733 | Appalachian Power Co | 3778 | Niagara | VA | Roanoke | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 0.3 | N |  |  | OP | X | 6 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 12H
Vintage1903 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 3779 | Reusens | VA | Campbell | 1 | Conventional Hydroelectric | HY |  | W | X | X | 32418507 |  | 2.5 | 0.8 | 2.5 | 2.5 | 1 | N |  |  | OP | X | 1 | 1903 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1903 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 3779 | Reusens | VA | Campbell | 2 | Conventional Hydroelectric | HY |  | W | X | X | 32418507 |  | 2.5 | 0.8 | 2.5 | 2.5 | 1 | N |  |  | OP | X | 1 | 1903 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1903 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 3779 | Reusens | VA | Campbell | 3 | Conventional Hydroelectric | HY |  | W | X | X | 32418507 |  | 2.5 | 0.8 | 2.5 | 2.5 | 1 | N |  |  | OP | X | 1 | 1903 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1903 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 3779 | Reusens | VA | Campbell | 4 | Conventional Hydroelectric | HY |  | W | X | X | 32418507 |  | 2.5 | 0.8 | 2.5 | 2.5 | 1 | N |  |  | OS | X | 1 | 1903 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1903 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 3779 | Reusens | VA | Campbell | 5 | Conventional Hydroelectric | HY |  | W | X | X | 32418507 |  | 2.5 | 0.8 | 2.5 | 2.5 | 1 | N |  |  | OP | X | 1 | 1903 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H
Vintage1965 | other | TRUE | 733 | Appalachian Power Co | 3780 | Smith Mountain | VA | Pittsylvania | 1 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 66 | 0.95 | 66 | 66 | 65 | N |  |  | OP | X | 12 | 1965 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 12H
Vintage1965 | hydro | TRUE | 733 | Appalachian Power Co | 3780 | Smith Mountain | VA | Pittsylvania | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 150.1 | 0.95 | 174 | 174 | 160 | N |  |  | OP | X | 12 | 1965 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 12H
Vintage1980 | other | TRUE | 733 | Appalachian Power Co | 3780 | Smith Mountain | VA | Pittsylvania | 3 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 115.3 | 0.95 | 106 | 106 | 105 | N |  |  | OP | X | 6 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 12H
Vintage1966 | hydro | TRUE | 733 | Appalachian Power Co | 3780 | Smith Mountain | VA | Pittsylvania | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 150.1 | 0.95 | 174 | 174 | 160 | N |  |  | OP | X | 2 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 12H
Vintage1966 | other | TRUE | 733 | Appalachian Power Co | 3780 | Smith Mountain | VA | Pittsylvania | 5 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 66 | 0.95 | 66 | 66 | 65 | N |  |  | OP | X | 2 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 12H
Vintage1963 | petroleum | TRUE | 56609 | Calpine Mid-Atlantic Generation LLC | 3782 | Bayview | VA | Northampton | BAYV | Petroleum Liquids | IC |  | S | X | X | 50872 | 50872 | 2 | 0.8 | 2.1 | 2.1 | 2 | N |  |  | SB | Y | 10 | 1963 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1963 | petroleum | TRUE | 56609 | Calpine Mid-Atlantic Generation LLC | 3782 | Bayview | VA | Northampton | BYV2 | Petroleum Liquids | IC |  | S | X | X | 50873 | 50873 | 2 | 0.8 | 2.1 | 2.1 | 2 | N |  |  | SB | Y | 10 | 1963 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1963 | petroleum | TRUE | 56609 | Calpine Mid-Atlantic Generation LLC | 3782 | Bayview | VA | Northampton | BYV3 | Petroleum Liquids | IC |  | S | X | X | 50874 | 50874 | 2 | 0.8 | 2.1 | 2.1 | 2 | N |  |  | SB | Y | 10 | 1963 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1963 | petroleum | TRUE | 56609 | Calpine Mid-Atlantic Generation LLC | 3782 | Bayview | VA | Northampton | BYV4 | Petroleum Liquids | IC |  | S | X | X | 50875 | 50875 | 2 | 0.8 | 2.1 | 2.1 | 2 | N |  |  | SB | Y | 10 | 1963 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1963 | petroleum | TRUE | 56609 | Calpine Mid-Atlantic Generation LLC | 3782 | Bayview | VA | Northampton | BYV5 | Petroleum Liquids | IC |  | S | X | X | 50876 | 50876 | 2 | 0.8 | 2.1 | 2.1 | 2 | N |  |  | SB | Y | 10 | 1963 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1963 | petroleum | TRUE | 56609 | Calpine Mid-Atlantic Generation LLC | 3782 | Bayview | VA | Northampton | BYV6 | Petroleum Liquids | IC |  | S | X | X | 50877 | 50877 | 2 | 0.8 | 2.1 | 2.1 | 2 | N |  |  | SB | Y | 10 | 1963 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1972 | petroleum | TRUE | 56609 | Calpine Mid-Atlantic Generation LLC | 3785 | Tasley | VA | Accomack | TAS | Petroleum Liquids | GT |  | S | X | X | 50924 | 50924 | 27 | 0.8 | 29.9 | 40.3 | 26.9 | N |  |  | SB | Y | 6 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1927 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 3789 | Luray Hydro Station | VA | Page | 1 | Conventional Hydroelectric | HY |  | W | X | X | RIVERTON138KV DUM HYD | IVERTON138 DUM HYD | 0.6 | 1 | 0.4 | 0.6 | 0.2 | N |  |  | OP | X | 1 | 1927 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1927 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 3789 | Luray Hydro Station | VA | Page | 2 | Conventional Hydroelectric | HY |  | W | X | X | RIVERTON138KV DUM HYD | RIVERTON138KV DUM HYD | 0.4 | 1 | 0.3 | 0.4 | 0.2 | N |  |  | OP | X | 1 | 1927 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1927 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 3789 | Luray Hydro Station | VA | Page | 3 | Conventional Hydroelectric | HY |  | W | X | X | RIVERTON138KV DUM HYD | RIVERTON138KV DUM HYD | 0.6 | 1 | 0.4 | 0.6 | 0.2 | N |  |  | OP | X | 1 | 1927 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1923 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 3790 | Newport Hydro Station | VA | Page | 1 | Conventional Hydroelectric | HY |  | W | X | X | RIVERTON138KV DUM HYD | RIVERTON138KV DUM HYD | 0.4 | 1 | 0.3 | 0.4 | 0.2 | N |  |  | OP | X | 1 | 1923 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M
Vintage1923 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 3790 | Newport Hydro Station | VA | Page | 2 | Conventional Hydroelectric | HY |  | W | X | X | RIVERTON138KV DUM HYD | RIVERTON138KV DUM HYD | 0.4 | 1 | 0.5 | 0.5 | 0.2 | N |  |  | OP | X | 1 | 1923 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M
Vintage1923 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 3790 | Newport Hydro Station | VA | Page | 3 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.6 | 1 | 0.5 | 0.6 | 0.2 | N |  |  | OP | X | 1 | 1923 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M
Vintage1964 | hard coal | TRUE | 19876 | Virginia Electric & Power Co | 3797 | Chesterfield | VA | Chesterfield | 5 | Conventional Steam Coal | ST |  | S | X | X |  |  | 359 | 0.85 | 336 | 342 | 186 | N |  |  | OP | X | 8 | 1964 | 5 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: DFO; DFO DFO DFO: DFO |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1969 | hard coal | TRUE | 19876 | Virginia Electric & Power Co | 3797 | Chesterfield | VA | Chesterfield | 6 | Conventional Steam Coal | ST |  | S | X | X |  |  | 693.9 | 0.9 | 670 | 690 | 400 | N |  |  | OP | X | 12 | 1969 | 5 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: DFO; DFO DFO DFO: DFO |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1990 | natural gas combined cycle | TRUE | 19876 | Virginia Electric & Power Co | 3797 | Chesterfield | VA | Chesterfield | CT7 | Natural Gas Fired Combined Cycle | CT | CH7 | S | X | N |  |  | 145 | 0.9 | 142 | 166 | 68 | N |  |  | OP | X | 6 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 12H | [23 empty] | Y | Y | Y
Vintage1992 | natural gas combined cycle | TRUE | 19876 | Virginia Electric & Power Co | 3797 | Chesterfield | VA | Chesterfield | CT8 | Natural Gas Fired Combined Cycle | CT | CH8 | S | X | N |  |  | 148 | 0.9 | 140 | 175 | 63 | N |  |  | OP | X | 5 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 12H | [23 empty] | Y | Y | Y
Vintage1990 | natural gas combined cycle | TRUE | 19876 | Virginia Electric & Power Co | 3797 | Chesterfield | VA | Chesterfield | CW7 | Natural Gas Fired Combined Cycle | CA | CH7 | S | N | X |  |  | 74.4 | 0.9 | 55 | 60 | 32 | N |  |  | OP | X | 6 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 12H | [23 empty] | Y |  | N
Vintage1992 | natural gas combined cycle | TRUE | 19876 | Virginia Electric & Power Co | 3797 | Chesterfield | VA | Chesterfield | CW8 | Natural Gas Fired Combined Cycle | CA | CH8 | S | N | X |  |  | 79.2 | 0.9 | 55 | 61 | 37 | N |  |  | OP | X | 5 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 12H | [23 empty] | Y |  | N
Vintage1930 | hydro | TRUE | 61891 | Cushaw Hydro LLC | 3798 | Cushaw | VA | Amherst | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 0.8 | 0.4 | 0.4 | 0.4 | N |  |  | OP | X | 1 | 1930 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1930 | hydro | TRUE | 61891 | Cushaw Hydro LLC | 3798 | Cushaw | VA | Amherst | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 0.8 | 0.4 | 0.4 | 0.4 | N |  |  | OP | X | 1 | 1930 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1930 | hydro | TRUE | 61891 | Cushaw Hydro LLC | 3798 | Cushaw | VA | Amherst | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 0.8 | 0.4 | 0.4 | 0.4 | N |  |  | OP | X | 1 | 1930 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1930 | hydro | TRUE | 61891 | Cushaw Hydro LLC | 3798 | Cushaw | VA | Amherst | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 0.8 | 0.4 | 0.4 | 0.4 | N |  |  | OP | X | 1 | 1930 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M
Vintage1930 | hydro | TRUE | 61891 | Cushaw Hydro LLC | 3798 | Cushaw | VA | Amherst | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 0.8 | 0.4 | 0.4 | 0.4 | N |  |  | OP | X | 1 | 1930 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1971 | petroleum | TRUE | 19876 | Virginia Electric & Power Co | 3799 | Low Moor | VA | Alleghany | GT1 | Petroleum Liquids | GT |  | S | X | X |  |  | 20.7 | 0.85 | 12 | 17 | 3 | N |  |  | OP | X | 7 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N
Vintage1971 | petroleum | TRUE | 19876 | Virginia Electric & Power Co | 3799 | Low Moor | VA | Alleghany | GT2 | Petroleum Liquids | GT |  | S | X | X |  |  | 20.7 | 0.85 | 12 | 16 | 3 | N |  |  | OP | X | 7 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N
Vintage1971 | petroleum | TRUE | 19876 | Virginia Electric & Power Co | 3799 | Low Moor | VA | Alleghany | GT3 | Petroleum Liquids | GT |  | S | X | X |  |  | 20.7 | 0.85 | 12 | 15 | 3 | N |  |  | OP | X | 8 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N
Vintage1971 | petroleum | TRUE | 19876 | Virginia Electric & Power Co | 3799 | Low Moor | VA | Alleghany | GT4 | Petroleum Liquids | GT |  | S | X | X |  |  | 20.7 | 0.85 | 12 | 17 | 3 | N |  |  | OP | X | 8 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N
Vintage1971 | petroleum | TRUE | 19876 | Virginia Electric & Power Co | 3800 | Northern Neck | VA | Richmond | GT1 | Petroleum Liquids | GT |  | S | X | X |  |  | 20.7 | 0.85 | 12 | 18 | 3 | N |  |  | OP | X | 7 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N
Vintage1971 | petroleum | TRUE | 19876 | Virginia Electric & Power Co | 3800 | Northern Neck | VA | Richmond | GT2 | Petroleum Liquids | GT |  | S | X | X |  |  | 20.7 | 0.85 | 11 | 17 | 3 | N |  |  | OP | X | 8 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N
Vintage1971 | petroleum | TRUE | 19876 | Virginia Electric & Power Co | 3800 | Northern Neck | VA | Richmond | GT3 | Petroleum Liquids | GT |  | S | X | X |  |  | 20.7 | 0.85 | 12 | 17 | 3 | N |  |  | OP | X | 7 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N
Vintage1971 | petroleum | TRUE | 19876 | Virginia Electric & Power Co | 3800 | Northern Neck | VA | Richmond | GT4 | Petroleum Liquids | GT |  | S | X | X |  |  | 20.7 | 0.85 | 12 | 18 | 3 | N |  |  | OP | X | 8 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N
Vintage1969 | petroleum | TRUE | 19876 | Virginia Electric & Power Co | 3803 | Chesapeake | VA | Chesapeake City | 6 | Petroleum Liquids | GT |  | S | X | X |  |  | 16.3 | 0.85 | 12 | 16 | 3 | N |  |  | OP | X | 7 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1967 | petroleum | TRUE | 19876 | Virginia Electric & Power Co | 3803 | Chesapeake | VA | Chesapeake City | GT1 | Petroleum Liquids | GT |  | S | X | X |  |  | 18.5 | 0.85 | 15 | 20 | 3 | N |  |  | OP | X | 12 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1969 | petroleum | TRUE | 19876 | Virginia Electric & Power Co | 3803 | Chesapeake | VA | Chesapeake City | GT2 | Petroleum Liquids | GT |  | S | X | X |  |  | 16.3 | 0.85 | 12 | 17 | 3 | N |  |  | OP | X | 3 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1969 | petroleum | TRUE | 19876 | Virginia Electric & Power Co | 3803 | Chesapeake | VA | Chesapeake City | GT4 | Petroleum Liquids | GT |  | S | X | X |  |  | 16.3 | 0.85 | 12 | 16 | 3 | N |  |  | OP | X | 5 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage2003 | natural gas combined cycle | TRUE | 19876 | Virginia Electric & Power Co | 3804 | Possum Point | VA | Prince William | 6A | Natural Gas Fired Combined Cycle | CT | G784 | S | X | N |  |  | 174 | 0.85 | 170 | 176.5 | 87 | N |  |  | OP | X | 7 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage2003 | natural gas combined cycle | TRUE | 19876 | Virginia Electric & Power Co | 3804 | Possum Point | VA | Prince William | 6B | Natural Gas Fired Combined Cycle | CT | G784 | S | X | N |  |  | 174 | 0.85 | 170 | 176.5 | 87 | N |  |  | OP | X | 7 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage2003 | natural gas combined cycle | TRUE | 19876 | Virginia Electric & Power Co | 3804 | Possum Point | VA | Prince William | 6ST | Natural Gas Fired Combined Cycle | CA | G784 | S | Y | X |  |  | 265 | 0.85 | 233 | 262 | 116 | N |  |  | OP | X | 7 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 12H | [23 empty] | Y |  | N
Vintage1968 | petroleum | TRUE | 19876 | Virginia Electric & Power Co | 3804 | Possum Point | VA | Prince William | GT1 | Petroleum Liquids | GT |  | S | X | X |  |  | 16 | 0.85 | 12 | 19 | 3 | N |  |  | OP | X | 5 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N
Vintage1968 | petroleum | TRUE | 19876 | Virginia Electric & Power Co | 3804 | Possum Point | VA | Prince William | GT2 | Petroleum Liquids | GT |  | S | X | X |  |  | 16 | 0.85 | 12 | 17 | 3 | N |  |  | OP | X | 5 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N
Vintage1968 | petroleum | TRUE | 19876 | Virginia Electric & Power Co | 3804 | Possum Point | VA | Prince William | GT3 | Petroleum Liquids | GT |  | S | X | X |  |  | 16 | 0.85 | 12 | 16 | 3 | N |  |  | OP | X | 5 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N
Vintage1968 | petroleum | TRUE | 19876 | Virginia Electric & Power Co | 3804 | Possum Point | VA | Prince William | GT4 | Petroleum Liquids | GT |  | S | X | X |  |  | 16 | 0.85 | 12 | 18 | 3 | N |  |  | OP | X | 5 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N
Vintage1968 | petroleum | TRUE | 19876 | Virginia Electric & Power Co | 3804 | Possum Point | VA | Prince William | GT5 | Petroleum Liquids | GT |  | S | X | X |  |  | 16 | 0.85 | 12 | 17 | 3 | N |  |  | OP | X | 5 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N
Vintage1968 | petroleum | TRUE | 19876 | Virginia Electric & Power Co | 3804 | Possum Point | VA | Prince William | GT6 | Petroleum Liquids | GT |  | S | X | X |  |  | 16 | 0.85 | 12 | 19 | 3 | N |  |  | OP | X | 5 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N
Vintage1972 | nuclear | TRUE | 19876 | Virginia Electric & Power Co | 3806 | Surry | VA | Surry | 1 | Nuclear | ST |  | S | X | X |  |  | 847.5 | 0.9 | 838 | 875 | 189 | N |  |  | OP | X | 12 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC |  |  | N |  |  | OVER | [23 empty] | N
Vintage1973 | nuclear | TRUE | 19876 | Virginia Electric & Power Co | 3806 | Surry | VA | Surry | 2 | Nuclear | ST |  | S | X | X |  |  | 847.5 | 0.9 | 838 | 875 | 189 | N |  |  | OP | X | 5 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC |  |  | N |  |  | OVER | [23 empty] | N
Vintage1974 | petroleum | TRUE | 19876 | Virginia Electric & Power Co | 3809 | Yorktown | VA | York | 3 | Petroleum Liquids | ST |  | S | X | X |  |  | 882 | 0.9 | 790 | 792 | 190 | N |  |  | OP | X | 12 | 1974 | 5 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: RFO; DFO DFO DFO: NG; DFO NG NG: DFO | [5 empty] | OVER | [23 empty] | N |  | N
Vintage1987 | hydro | TRUE | 1456 | Town of Bedford - (VA) | 3821 | Snowden | VA | Bedford | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 0.84 | 2.5 | 2.5 | 0.6 | N |  |  | OP | X | 8 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1987 | hydro | TRUE | 1456 | Town of Bedford - (VA) | 3821 | Snowden | VA | Bedford | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 0.84 | 2.5 | 2.5 | 0.6 | N |  |  | OP | X | 8 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1938 | hydro | TRUE | 64642 | Northbrook Virginia Hydro, LLC | 3825 | Pinnacles | VA | Patrick | 1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 3.7 | 0.93 | 3.5 | 3.5 | 0.1 | N |  |  | OP | X | 6 | 1938 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1938 | hydro | TRUE | 64642 | Northbrook Virginia Hydro, LLC | 3825 | Pinnacles | VA | Patrick | 2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 3.7 | 0.93 | 3.5 | 3.5 | 0.1 | N |  |  | OP | X | 6 | 1938 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1938 | hydro | TRUE | 64642 | Northbrook Virginia Hydro, LLC | 3825 | Pinnacles | VA | Patrick | 3 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 3.7 | 0.93 | 3.5 | 3.5 | 0.1 | N |  |  | OP | X | 6 | 1938 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1932 | hydro | TRUE | 11770 | City of Martinsville - (VA) | 3826 | Martinsville | VA | Henry | 1 | Conventional Hydroelectric | HY |  | S | X | X | BLUE RIDGE |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 5 | 1932 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1932 | hydro | TRUE | 11770 | City of Martinsville - (VA) | 3826 | Martinsville | VA | Henry | 2 | Conventional Hydroelectric | HY |  | S | X | X | BLUE RIDGE |  | 1 | 0.8 | 0.9 | 0.9 | 0.3 | N |  |  | OP | X | 5 | 1932 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1934 | hydro | TRUE | 15619 | City of Radford - (VA) | 3827 | Radford | VA | Pulaski | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.3 | N |  |  | OP | X | 10 | 1934 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1952 | hydro | TRUE | 18574 | USCE-Wilmington District | 3833 | John H Kerr | VA | Mecklenburg | 1 | Conventional Hydroelectric | HY |  | S | X | X | KERRDP 115KV TX1 |  | 13.8 | 0.9 | 13.8 | 13.8 | 13 | N |  |  | OP | X | 12 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1952 | hydro | TRUE | 18574 | USCE-Wilmington District | 3833 | John H Kerr | VA | Mecklenburg | 2 | Conventional Hydroelectric | HY |  | S | X | X | KERRDP 115KV TX1 |  | 46.8 | 0.9 | 46.8 | 46.8 | 32 | N |  |  | OP | X | 11 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1953 | hydro | TRUE | 18574 | USCE-Wilmington District | 3833 | John H Kerr | VA | Mecklenburg | 3 | Conventional Hydroelectric | HY |  | S | X | X | KERRDP 115KV TX1 |  | 46.8 | 0.9 | 46.8 | 46.8 | 32 | N |  |  | OP | X | 1 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1953 | hydro | TRUE | 18574 | USCE-Wilmington District | 3833 | John H Kerr | VA | Mecklenburg | 4 | Conventional Hydroelectric | HY |  | S | X | X | KERRDP 115KV TX1 |  | 46.8 | 0.9 | 46.8 | 46.8 | 32 | N |  |  | OP | X | 3 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1953 | hydro | TRUE | 18574 | USCE-Wilmington District | 3833 | John H Kerr | VA | Mecklenburg | 5 | Conventional Hydroelectric | HY |  | S | X | X | KERRDP 115KV TX1 |  | 46.8 | 0.9 | 46.8 | 46.8 | 32 | N |  |  | OP | X | 9 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1953 | hydro | TRUE | 18574 | USCE-Wilmington District | 3833 | John H Kerr | VA | Mecklenburg | 6 | Conventional Hydroelectric | HY |  | S | X | X | KERRDP 115KV TX1 |  | 46.8 | 0.9 | 46.8 | 46.8 | 32 | N |  |  | OP | X | 10 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1953 | hydro | TRUE | 18574 | USCE-Wilmington District | 3833 | John H Kerr | VA | Mecklenburg | 7 | Conventional Hydroelectric | HY |  | S | X | X | KERRDP 115KV TX1 |  | 46.8 | 0.9 | 46.8 | 46.8 | 32 | N |  |  | OP | X | 12 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage2008 | hydro | TRUE | 18574 | USCE-Wilmington District | 3833 | John H Kerr | VA | Mecklenburg | A | Conventional Hydroelectric | HY |  | S | X | X | KERRDP 115KV TX1 |  | 1.1 | 0.8 | 1 | 1 | 0 | N |  |  | OP | X | 12 | 2008 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage2008 | hydro | TRUE | 18574 | USCE-Wilmington District | 3833 | John H Kerr | VA | Mecklenburg | B | Conventional Hydroelectric | HY |  | S | X | X | KERRDP 115KV TX1 |  | 1.1 | 0.8 | 1 | 1 | 0 | N |  |  | OP | X | 8 | 2008 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1953 | hydro | TRUE | 18574 | USCE-Wilmington District | 3834 | Philpott Lake | VA | Henry | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.7 | 0.9 | 7.5 | 7.5 | 6 | N |  |  | OS | X | 8 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [7 empty] | 3.2 | 3.2 | 6 | 2024 | [12 empty] | N
Vintage1953 | hydro | TRUE | 18574 | USCE-Wilmington District | 3834 | Philpott Lake | VA | Henry | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.7 | 0.9 | 7.5 | 7.5 | 6 | N |  |  | OS | X | 8 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [7 empty] | 3.2 | 3.2 | 6 | 2024 | [12 empty] | N
Vintage1953 | hydro | TRUE | 18574 | USCE-Wilmington District | 3834 | Philpott Lake | VA | Henry | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0 | N |  |  | OS | X | 8 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1973 | hard coal | TRUE | 19099 | TransAlta Centralia Gen LLC | 3845 | Transalta Centralia Generation | WA | Lewis | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 729.9 | 0.94 | 670 | 670 | 250 | N |  |  | OP | X | 7 | 1973 | 12 | 2025 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: RC; DFO SUB SUB: WC; DFO DFO DFO: SUB; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1932 | hydro | TRUE | 14354 | PacifiCorp | 3847 | Merwin | WA | Cowlitz | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 45 | 0.8 | 50 | 50 | 0 | N |  |  | OP | X | 1 | 1932 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1949 | hydro | TRUE | 14354 | PacifiCorp | 3847 | Merwin | WA | Cowlitz | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 45 | 0.8 | 50 | 50 | 0 | N |  |  | OP | X | 12 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1958 | hydro | TRUE | 14354 | PacifiCorp | 3847 | Merwin | WA | Cowlitz | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 45 | 0.8 | 50 | 50 | 0 | N |  |  | OP | X | 9 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1931 | hydro | TRUE | 14354 | PacifiCorp | 3847 | Merwin | WA | Cowlitz | House | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0 | N |  |  | OP | X | 7 | 1931 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1958 | hydro | TRUE | 14354 | PacifiCorp | 3850 | Swift 1 | WA | Skamania | HY11 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 80 | 1 | 87.9 | 87.9 | 0 | N |  |  | OP | X | 12 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1958 | hydro | TRUE | 14354 | PacifiCorp | 3850 | Swift 1 | WA | Skamania | HY12 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 80 | 1 | 87.9 | 87.9 | 0 | N |  |  | OP | X | 12 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1958 | hydro | TRUE | 14354 | PacifiCorp | 3850 | Swift 1 | WA | Skamania | HY13 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 80 | 1 | 87.9 | 87.9 | 0 | N |  |  | OP | X | 12 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1953 | hydro | TRUE | 14354 | PacifiCorp | 3852 | Yale | WA | Cowlitz | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 67 | 1 | 81.8 | 81.8 | 0 | N |  |  | OP | X | 9 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1953 | hydro | TRUE | 14354 | PacifiCorp | 3852 | Yale | WA | Cowlitz | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 67 | 1 | 81.8 | 81.8 | 0 | N |  |  | OP | X | 11 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1969 | petroleum | TRUE | 15500 | Puget Sound Energy Inc | 3853 | Crystal Mountain | WA | Pierce | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2.5 | 2.5 | 0.2 | N |  |  | SB | Y | 12 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1904 | hydro | TRUE | 59866 | Electron Hydro LLC | 3854 | Electron | WA | Pierce | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.1 | 0.92 | 5.7 | 5.7 | 0.1 | N |  |  | OP | X | 4 | 1904 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1904 | hydro | TRUE | 59866 | Electron Hydro LLC | 3854 | Electron | WA | Pierce | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.1 | 0.92 | 5.9 | 5.9 | 0.1 | N |  |  | OP | X | 4 | 1904 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1904 | hydro | TRUE | 59866 | Electron Hydro LLC | 3854 | Electron | WA | Pierce | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.1 | 0.92 | 6.3 | 6.3 | 0.1 | N |  |  | OP | X | 4 | 1904 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1929 | hydro | TRUE | 59866 | Electron Hydro LLC | 3854 | Electron | WA | Pierce | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7.5 | 0.8 | 7.9 | 7.9 | 1 | N |  |  | OP | X | 4 | 1929 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1960 | hydro | TRUE | 15500 | Puget Sound Energy Inc | 3855 | Lower Baker | WA | Skagit | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 80.8 | 0.95 | 74.8 | 74.8 | 2 | N |  |  | OP | X | 3 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage2013 | hydro | TRUE | 15500 | Puget Sound Energy Inc | 3855 | Lower Baker | WA | Skagit | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 30.4 | 0.95 | 30.4 | 30.4 | 2 | N |  |  | OP | X | 7 | 2013 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1898 | hydro | TRUE | 15500 | Puget Sound Energy Inc | 3860 | Snoqualmie | WA | King | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 1 | 1.5 | 1.5 | 0.5 | N |  |  | OP | X | 1 | 1898 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1898 | hydro | TRUE | 15500 | Puget Sound Energy Inc | 3860 | Snoqualmie | WA | King | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 1 | 1.5 | 1.5 | 0.5 | N |  |  | OP | X | 1 | 1898 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1898 | hydro | TRUE | 15500 | Puget Sound Energy Inc | 3860 | Snoqualmie | WA | King | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 1 | 1.5 | 1.5 | 0.5 | N |  |  | OP | X | 1 | 1898 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1898 | hydro | TRUE | 15500 | Puget Sound Energy Inc | 3860 | Snoqualmie | WA | King | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 1 | 1.5 | 1.5 | 0.5 | N |  |  | OP | X | 1 | 1898 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage2013 | hydro | TRUE | 15500 | Puget Sound Energy Inc | 3860 | Snoqualmie | WA | King | 5A | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.8 | 0.95 | 6.1 | 6.1 | 3.7 | N |  |  | OP | X | 8 | 2013 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1959 | hydro | TRUE | 15500 | Puget Sound Energy Inc | 3861 | Upper Baker | WA | Whatcom | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 52.4 | 1 | 52.5 | 52.5 | 0.3 | N |  |  | OP | X | 1 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1959 | hydro | TRUE | 15500 | Puget Sound Energy Inc | 3861 | Upper Baker | WA | Whatcom | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 52.4 | 1 | 52.5 | 52.5 | 0.3 | N |  |  | OP | X | 1 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [7 empty] | 5 | 5 | 7 | 2022
Vintage1910 | hydro | TRUE | 20169 | Avista Corp | 3866 | Little Falls (WA) | WA | Lincoln | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10.8 | 0.9 | 10.8 | 10.8 | 2 | N |  |  | OP | X | 7 | 1910 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1910 | hydro | TRUE | 20169 | Avista Corp | 3866 | Little Falls (WA) | WA | Lincoln | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10.8 | 0.9 | 10.8 | 10.8 | 2 | N |  |  | OP | X | 9 | 1910 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1910 | hydro | TRUE | 20169 | Avista Corp | 3866 | Little Falls (WA) | WA | Lincoln | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10.8 | 0.9 | 10.8 | 10.8 | 2 | N |  |  | OP | X | 12 | 1910 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1911 | hydro | TRUE | 20169 | Avista Corp | 3866 | Little Falls (WA) | WA | Lincoln | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10.8 | 0.9 | 10.8 | 10.8 | 2 | N |  |  | OP | X | 11 | 1911 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1915 | hydro | TRUE | 20169 | Avista Corp | 3867 | Long Lake | WA | Lincoln | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 17.5 | 0.9 | 22.4 | 22.4 | 3 | N |  |  | OP | X | 10 | 1915 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1915 | hydro | TRUE | 20169 | Avista Corp | 3867 | Long Lake | WA | Lincoln | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 17.5 | 0.9 | 22.5 | 22.5 | 3 | N |  |  | OP | X | 10 | 1915 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1919 | hydro | TRUE | 20169 | Avista Corp | 3867 | Long Lake | WA | Lincoln | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 17.5 | 0.9 | 22.5 | 22.5 | 3 | N |  |  | OP | X | 12 | 1919 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1924 | hydro | TRUE | 20169 | Avista Corp | 3867 | Long Lake | WA | Lincoln | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 17.5 | 0.9 | 22.1 | 22.1 | 3 | N |  |  | OP | X | 2 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1915 | hydro | TRUE | 9143 | Hydro Technology Systems Inc | 3868 | Meyers Falls | WA | Stevens | UN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.9 | 1 | 0.9 | 0.9 | 0.2 | N |  |  | OP | X | 6 | 1915 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1915 | hydro | TRUE | 9143 | Hydro Technology Systems Inc | 3868 | Meyers Falls | WA | Stevens | UN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 6 | 1915 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage2006 | hydro | TRUE | 9143 | Hydro Technology Systems Inc | 3868 | Meyers Falls | WA | Stevens | UNA | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 1 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 2006 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage2006 | hydro | TRUE | 9143 | Hydro Technology Systems Inc | 3868 | Meyers Falls | WA | Stevens | UNB | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 1 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 2006 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1910 | hydro | TRUE | 20169 | Avista Corp | 3869 | Nine Mile | WA | Spokane | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8.8 | 0.8 | 8.8 | 8.8 | 2 | N |  |  | OP | X | 7 | 1910 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1908 | hydro | TRUE | 20169 | Avista Corp | 3869 | Nine Mile | WA | Spokane | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8.8 | 1 | 8.8 | 8.8 | 2 | N |  |  | OP | X | 7 | 1908 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1994 | hydro | TRUE | 20169 | Avista Corp | 3869 | Nine Mile | WA | Spokane | 3N | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 0.95 | 10 | 10 | 2 | N |  |  | OP | X | 6 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1994 | hydro | TRUE | 20169 | Avista Corp | 3869 | Nine Mile | WA | Spokane | 4N | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 0.95 | 10 | 10 | 2 | N |  |  | OP | X | 6 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1930 | hydro | TRUE | 3295 | City of Centralia - (WA) | 3878 | Yelm | WA | Thurston | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.8 | 2.7 | 2.7 | 0.5 | N |  |  | OP | X | 12 | 1930 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1930 | hydro | TRUE | 3295 | City of Centralia - (WA) | 3878 | Yelm | WA | Thurston | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.8 | 2.7 | 2.7 | 0.5 | N |  |  | OP | X | 12 | 1930 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1955 | hydro | TRUE | 3295 | City of Centralia - (WA) | 3878 | Yelm | WA | Thurston | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6 | 0.8 | 6 | 6 | 0.5 | N |  |  | OP | X | 12 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1961 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 3883 | Rocky Reach | WA | Chelan | C-1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 114 | 0.95 | 104.9 | 104.9 | 35 | N |  |  | OP | X | 6 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1974 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 3883 | Rocky Reach | WA | Chelan | C-10 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 125.4 | 0.95 | 129.9 | 129.9 | 35 | N |  |  | OP | X | 1 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | Y | 12 | 2024 | N
Vintage1974 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 3883 | Rocky Reach | WA | Chelan | C-11 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 125.4 | 0.95 | 129.9 | 129.9 | 35 | N |  |  | OP | X | 2 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | Y | 11 | 2023 | N
Vintage1961 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 3883 | Rocky Reach | WA | Chelan | C-2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 114 | 0.95 | 104.9 | 104.9 | 35 | N |  |  | OP | X | 6 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1961 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 3883 | Rocky Reach | WA | Chelan | C-3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 114 | 0.95 | 104.9 | 104.9 | 35 | N |  |  | OP | X | 6 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1961 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 3883 | Rocky Reach | WA | Chelan | C-4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 114 | 0.95 | 104.9 | 104.9 | 35 | N |  |  | OA | X | 8 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | Y | 8 | 2022 | N
Vintage1961 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 3883 | Rocky Reach | WA | Chelan | C-5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 114 | 0.95 | 104.9 | 104.9 | 35 | N |  |  | OA | X | 8 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | Y | 1 | 2023 | N
Vintage1961 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 3883 | Rocky Reach | WA | Chelan | C-6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 114 | 0.95 | 104.9 | 104.9 | 35 | N |  |  | OA | X | 8 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | Y | 5 | 2022 | N
Vintage1961 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 3883 | Rocky Reach | WA | Chelan | C-7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 114 | 0.95 | 104.9 | 104.9 | 35 | N |  |  | OP | X | 9 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1973 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 3883 | Rocky Reach | WA | Chelan | C-8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 125.4 | 0.95 | 129.9 | 129.9 | 40 | N |  |  | OP | X | 8 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1973 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 3883 | Rocky Reach | WA | Chelan | C-9 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 125.4 | 0.95 | 129.9 | 129.9 | 80 | N |  |  | OP | X | 11 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1967 | hydro | TRUE | 5326 | PUD No 1 of Douglas County | 3886 | Wells | WA | Douglas | U-1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 77.4 | 0.95 | 84 | 84 | 55 | N |  |  | OP | X | 9 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1969 | hydro | TRUE | 5326 | PUD No 1 of Douglas County | 3886 | Wells | WA | Douglas | U-10 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 77.4 | 0.95 | 84 | 84 | 55 | N |  |  | OA | X | 1 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1967 | hydro | TRUE | 5326 | PUD No 1 of Douglas County | 3886 | Wells | WA | Douglas | U-2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 77.4 | 0.95 | 84 | 84 | 55 | N |  |  | OP | X | 10 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1967 | hydro | TRUE | 5326 | PUD No 1 of Douglas County | 3886 | Wells | WA | Douglas | U-3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 77.4 | 0.95 | 84 | 84 | 55 | N |  |  | OP | X | 9 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1967 | hydro | TRUE | 5326 | PUD No 1 of Douglas County | 3886 | Wells | WA | Douglas | U-4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 77.4 | 0.95 | 84 | 84 | 55 | N |  |  | OP | X | 9 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1967 | hydro | TRUE | 5326 | PUD No 1 of Douglas County | 3886 | Wells | WA | Douglas | U-5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 77.4 | 0.95 | 84 | 84 | 55 | N |  |  | OP | X | 9 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1967 | hydro | TRUE | 5326 | PUD No 1 of Douglas County | 3886 | Wells | WA | Douglas | U-6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 77.4 | 0.95 | 84 | 84 | 55 | N |  |  | OP | X | 9 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1967 | hydro | TRUE | 5326 | PUD No 1 of Douglas County | 3886 | Wells | WA | Douglas | U-7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 77.4 | 0.95 | 84 | 84 | 55 | N |  |  | OP | X | 9 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1968 | hydro | TRUE | 5326 | PUD No 1 of Douglas County | 3886 | Wells | WA | Douglas | U-8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 77.4 | 0.95 | 84 | 84 | 55 | N |  |  | OP | X | 10 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1969 | hydro | TRUE | 5326 | PUD No 1 of Douglas County | 3886 | Wells | WA | Douglas | U-9 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 77.4 | 0.95 | 84 | 84 | 55 | N |  |  | OP | X | 1 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1961 | hydro | TRUE | 14624 | PUD No 2 of Grant County | 3887 | Priest Rapids | WA | Grant | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 95 | 0.95 | 95 | 95 | 50 | N |  |  | OP | X | 7 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1959 | hydro | TRUE | 14624 | PUD No 2 of Grant County | 3887 | Priest Rapids | WA | Grant | 10 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 95 | 0.95 | 95 | 95 | 50 | N |  |  | OP | X | 11 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1961 | hydro | TRUE | 14624 | PUD No 2 of Grant County | 3887 | Priest Rapids | WA | Grant | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 97.8 | 0.95 | 95 | 95 | 50 | N |  |  | OP | X | 5 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1960 | hydro | TRUE | 14624 | PUD No 2 of Grant County | 3887 | Priest Rapids | WA | Grant | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 95 | 0.95 | 95 | 95 | 50 | N |  |  | OP | X | 9 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1960 | hydro | TRUE | 14624 | PUD No 2 of Grant County | 3887 | Priest Rapids | WA | Grant | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 95 | 0.95 | 95 | 95 | 50 | N |  |  | OP | X | 9 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1960 | hydro | TRUE | 14624 | PUD No 2 of Grant County | 3887 | Priest Rapids | WA | Grant | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 95 | 0.95 | 95 | 95 | 50 | N |  |  | OP | X | 4 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1960 | hydro | TRUE | 14624 | PUD No 2 of Grant County | 3887 | Priest Rapids | WA | Grant | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 95 | 0.95 | 95 | 95 | 50 | N |  |  | OP | X | 2 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1960 | hydro | TRUE | 14624 | PUD No 2 of Grant County | 3887 | Priest Rapids | WA | Grant | 7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 95 | 0.95 | 95 | 95 | 50 | N |  |  | OP | X | 1 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1959 | hydro | TRUE | 14624 | PUD No 2 of Grant County | 3887 | Priest Rapids | WA | Grant | 8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 95 | 0.95 | 95 | 95 | 50 | N |  |  | OP | X | 12 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1959 | hydro | TRUE | 14624 | PUD No 2 of Grant County | 3887 | Priest Rapids | WA | Grant | 9 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 97.8 | 0.95 | 95 | 95 | 50 | N |  |  | OP | X | 10 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage2014 | hydro | TRUE | 14624 | PUD No 2 of Grant County | 3888 | Wanapum | WA | Grant | 10A | Conventional Hydroelectric | HY |  | S | X | X |  |  | 122 | 0.95 | 122 | 122 | 50 | N |  |  | OP | X | 6 | 2014 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage2013 | hydro | TRUE | 14624 | PUD No 2 of Grant County | 3888 | Wanapum | WA | Grant | 1A | Conventional Hydroelectric | HY |  | S | X | X |  |  | 122 | 0.95 | 122 | 122 | 50 | N |  |  | OP | X | 10 | 2013 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage2012 | hydro | TRUE | 14624 | PUD No 2 of Grant County | 3888 | Wanapum | WA | Grant | 2A | Conventional Hydroelectric | HY |  | S | X | X |  |  | 122 | 0.95 | 122 | 122 | 50 | N |  |  | OP | X | 12 | 2012 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage2017 | hydro | TRUE | 14624 | PUD No 2 of Grant County | 3888 | Wanapum | WA | Grant | 3A | Conventional Hydroelectric | HY |  | S | X | X |  |  | 122 | 0.95 | 122 | 122 | 50 | N |  |  | OP | X | 8 | 2017 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage2020 | hydro | TRUE | 14624 | PUD No 2 of Grant County | 3888 | Wanapum | WA | Grant | 4A | Conventional Hydroelectric | HY |  | S | X | X |  |  | 122 | 0.95 | 122 | 122 | 50 | N |  |  | OP | X | 9 | 2020 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage2012 | hydro | TRUE | 14624 | PUD No 2 of Grant County | 3888 | Wanapum | WA | Grant | 5A | Conventional Hydroelectric | HY |  | S | X | X |  |  | 122 | 0.95 | 122 | 122 | 50 | N |  |  | OP | X | 2 | 2012 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage2016 | hydro | TRUE | 14624 | PUD No 2 of Grant County | 3888 | Wanapum | WA | Grant | 6A | Conventional Hydroelectric | HY |  | S | X | X |  |  | 122 | 0.95 | 122 | 122 | 50 | N |  |  | OP | X | 7 | 2016 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage2011 | hydro | TRUE | 14624 | PUD No 2 of Grant County | 3888 | Wanapum | WA | Grant | 7A | Conventional Hydroelectric | HY |  | S | X | X |  |  | 122 | 0.95 | 122 | 122 | 50 | N |  |  | OP | X | 4 | 2011 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage2018 | hydro | TRUE | 14624 | PUD No 2 of Grant County | 3888 | Wanapum | WA | Grant | 8A | Conventional Hydroelectric | HY |  | S | X | X |  |  | 122 | 0.95 | 122 | 122 | 50 | N |  |  | OP | X | 11 | 2018 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage2015 | hydro | TRUE | 14624 | PUD No 2 of Grant County | 3888 | Wanapum | WA | Grant | 9A | Conventional Hydroelectric | HY |  | S | X | X |  |  | 122 | 0.95 | 122 | 122 | 50 | N |  |  | OP | X | 6 | 2015 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1955 | hydro | TRUE | 14653 | PUD No 1 of Pend Oreille County | 3891 | Box Canyon | WA | Pend Oreille | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 22.5 | 0.9 | 22.5 | 22.5 | 0 | N |  |  | OP | X | 6 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1955 | hydro | TRUE | 14653 | PUD No 1 of Pend Oreille County | 3891 | Box Canyon | WA | Pend Oreille | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 22.5 | 0.9 | 22.5 | 22.5 | 0 | N |  |  | OP | X | 7 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1955 | hydro | TRUE | 14653 | PUD No 1 of Pend Oreille County | 3891 | Box Canyon | WA | Pend Oreille | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 22.5 | 0.9 | 22.5 | 22.5 | 0 | N |  |  | OP | X | 8 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1955 | hydro | TRUE | 14653 | PUD No 1 of Pend Oreille County | 3891 | Box Canyon | WA | Pend Oreille | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 22.5 | 0.9 | 22.5 | 22.5 | 0 | N |  |  | OP | X | 8 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1957 | hydro | TRUE | 19400 | USACE Northwestern Division | 3895 | The Dalles | OR | Wasco | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 78 | 0.95 | 78 | 78 | 24.8 | N |  |  | OA | X | 10 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1959 | hydro | TRUE | 19400 | USACE Northwestern Division | 3895 | The Dalles | OR | Wasco | 10 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 78 | 0.95 | 78 | 78 | 24.8 | N |  |  | OP | X | 11 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1960 | hydro | TRUE | 19400 | USACE Northwestern Division | 3895 | The Dalles | OR | Wasco | 11 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 78 | 0.95 | 78 | 78 | 24.8 | N |  |  | OP | X | 2 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1960 | hydro | TRUE | 19400 | USACE Northwestern Division | 3895 | The Dalles | OR | Wasco | 12 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 78 | 0.95 | 78 | 78 | 24.8 | N |  |  | OA | X | 5 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1960 | hydro | TRUE | 19400 | USACE Northwestern Division | 3895 | The Dalles | OR | Wasco | 13 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 78 | 0.95 | 78 | 78 | 24.8 | N |  |  | OP | X | 8 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1960 | hydro | TRUE | 19400 | USACE Northwestern Division | 3895 | The Dalles | OR | Wasco | 14 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 78 | 0.95 | 78 | 78 | 24.8 | N |  |  | OP | X | 11 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1973 | hydro | TRUE | 19400 | USACE Northwestern Division | 3895 | The Dalles | OR | Wasco | 15 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 86 | 0.95 | 86 | 86 | 29 | N |  |  | OP | X | 2 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1973 | hydro | TRUE | 19400 | USACE Northwestern Division | 3895 | The Dalles | OR | Wasco | 16 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 86 | 0.95 | 86 | 86 | 29 | N |  |  | OP | X | 2 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1973 | hydro | TRUE | 19400 | USACE Northwestern Division | 3895 | The Dalles | OR | Wasco | 17 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 86 | 0.95 | 86 | 86 | 29 | N |  |  | OP | X | 3 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1973 | hydro | TRUE | 19400 | USACE Northwestern Division | 3895 | The Dalles | OR | Wasco | 18 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 86 | 0.95 | 86 | 86 | 29 | N |  |  | OP | X | 3 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1973 | hydro | TRUE | 19400 | USACE Northwestern Division | 3895 | The Dalles | OR | Wasco | 19 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 86 | 0.95 | 86 | 86 | 29 | N |  |  | OA | X | 5 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1957 | hydro | TRUE | 19400 | USACE Northwestern Division | 3895 | The Dalles | OR | Wasco | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 78 | 0.95 | 78 | 78 | 24.8 | N |  |  | OP | X | 11 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1973 | hydro | TRUE | 19400 | USACE Northwestern Division | 3895 | The Dalles | OR | Wasco | 20 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 86 | 0.95 | 86 | 86 | 29 | N |  |  | OA | X | 6 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1973 | hydro | TRUE | 19400 | USACE Northwestern Division | 3895 | The Dalles | OR | Wasco | 21 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 86 | 0.95 | 86 | 86 | 29 | N |  |  | OP | X | 11 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1973 | hydro | TRUE | 19400 | USACE Northwestern Division | 3895 | The Dalles | OR | Wasco | 22 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 86 | 0.95 | 86 | 86 | 29 | N |  |  | OP | X | 12 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1958 | hydro | TRUE | 19400 | USACE Northwestern Division | 3895 | The Dalles | OR | Wasco | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 78 | 0.95 | 78 | 78 | 24.8 | N |  |  | OP | X | 2 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1958 | hydro | TRUE | 19400 | USACE Northwestern Division | 3895 | The Dalles | OR | Wasco | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 78 | 0.95 | 78 | 78 | 24.8 | N |  |  | OP | X | 5 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1958 | hydro | TRUE | 19400 | USACE Northwestern Division | 3895 | The Dalles | OR | Wasco | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 89.7 | 0.95 | 92.7 | 92 | 24.8 | N |  |  | OP | X | 10 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1958 | hydro | TRUE | 19400 | USACE Northwestern Division | 3895 | The Dalles | OR | Wasco | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 78 | 0.95 | 78 | 78 | 24.8 | N |  |  | OP | X | 11 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1959 | hydro | TRUE | 19400 | USACE Northwestern Division | 3895 | The Dalles | OR | Wasco | 7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 78 | 0.95 | 78 | 78 | 24.8 | N |  |  | OP | X | 2 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1959 | hydro | TRUE | 19400 | USACE Northwestern Division | 3895 | The Dalles | OR | Wasco | 8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 78 | 0.95 | 78 | 78 | 24.8 | N |  |  | OP | X | 5 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1959 | hydro | TRUE | 19400 | USACE Northwestern Division | 3895 | The Dalles | OR | Wasco | 9 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 78 | 0.95 | 78 | 78 | 24.8 | N |  |  | OP | X | 11 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1957 | hydro | TRUE | 19400 | USACE Northwestern Division | 3895 | The Dalles | OR | Wasco | F1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 14 | 0.95 | 14 | 14 | 14 | N |  |  | OA | X | 6 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1957 | hydro | TRUE | 19400 | USACE Northwestern Division | 3895 | The Dalles | OR | Wasco | F2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 14 | 0.95 | 14 | 14 | 14 | N |  |  | OA | X | 7 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1947 | hydro | TRUE | 18429 | City of Tacoma - (WA) | 3913 | Alder | WA | Pierce | 11 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 25 | 1 | 25.2 | 21 | 4 | N |  |  | OP | X | 5 | 1947 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 1H
Vintage1945 | hydro | TRUE | 18429 | City of Tacoma - (WA) | 3913 | Alder | WA | Pierce | 12 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 25 | 1 | 25.2 | 21 | 4 | N |  |  | OP | X | 12 | 1945 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 1H
Vintage1926 | hydro | TRUE | 18429 | City of Tacoma - (WA) | 3914 | Cushman 1 | WA | Mason | 21 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 21.6 | 1 | 26.7 | 19 | 1 | N |  |  | OP | X | 6 | 1926 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 1H
Vintage1926 | hydro | TRUE | 18429 | City of Tacoma - (WA) | 3914 | Cushman 1 | WA | Mason | 22 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 21.6 | 1 | 26.7 | 19 | 1 | N |  |  | OP | X | 7 | 1926 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 1H
Vintage1930 | hydro | TRUE | 18429 | City of Tacoma - (WA) | 3915 | Cushman 2 | WA | Mason | 31 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 27 | 1 | 30 | 30 | 8 | N |  |  | OP | X | 12 | 1930 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 1H
Vintage1931 | hydro | TRUE | 18429 | City of Tacoma - (WA) | 3915 | Cushman 2 | WA | Mason | 32 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 27 | 1 | 30 | 30 | 8 | N |  |  | OP | X | 8 | 1931 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 1H
Vintage1952 | hydro | TRUE | 18429 | City of Tacoma - (WA) | 3915 | Cushman 2 | WA | Mason | 33 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 27 | 1 | 30 | 30 | 8 | N |  |  | OP | X | 12 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 1H
Vintage2013 | hydro | TRUE | 18429 | City of Tacoma - (WA) | 3915 | Cushman 2 | WA | Mason | 34 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 1 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 3 | 2013 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 1H
Vintage2013 | hydro | TRUE | 18429 | City of Tacoma - (WA) | 3915 | Cushman 2 | WA | Mason | 35 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 1 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 3 | 2013 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 1H
Vintage1912 | hydro | TRUE | 18429 | City of Tacoma - (WA) | 3916 | LaGrande | WA | Pierce | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6 | 1 | 6 | 6 | 1 | N |  |  | OP | X | 11 | 1912 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 1H
Vintage1912 | hydro | TRUE | 18429 | City of Tacoma - (WA) | 3916 | LaGrande | WA | Pierce | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6 | 1 | 6 | 6 | 1 | N |  |  | OP | X | 11 | 1912 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 1H
Vintage1912 | hydro | TRUE | 18429 | City of Tacoma - (WA) | 3916 | LaGrande | WA | Pierce | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6 | 1 | 6 | 6 | 1 | N |  |  | OP | X | 11 | 1912 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 1H
Vintage1912 | hydro | TRUE | 18429 | City of Tacoma - (WA) | 3916 | LaGrande | WA | Pierce | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6 | 1 | 6 | 6 | 1 | N |  |  | OP | X | 11 | 1912 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 1H
Vintage1945 | hydro | TRUE | 18429 | City of Tacoma - (WA) | 3916 | LaGrande | WA | Pierce | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40 | 1 | 40 | 40 | 8 | N |  |  | OP | X | 9 | 1945 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 1H
Vintage1983 | hydro | TRUE | 18429 | City of Tacoma - (WA) | 3917 | Mayfield | WA | Lewis | 41 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40.5 | 1 | 41 | 41 | 8 | N |  |  | OP | X | 5 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 1H
Vintage1963 | hydro | TRUE | 18429 | City of Tacoma - (WA) | 3917 | Mayfield | WA | Lewis | 42 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40.5 | 1 | 41 | 41 | 8 | N |  |  | OP | X | 3 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 1H
Vintage1963 | hydro | TRUE | 18429 | City of Tacoma - (WA) | 3917 | Mayfield | WA | Lewis | 43 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40.5 | 1 | 41 | 41 | 8 | N |  |  | OP | X | 4 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 1H
Vintage1963 | hydro | TRUE | 18429 | City of Tacoma - (WA) | 3917 | Mayfield | WA | Lewis | 44 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40.5 | 1 | 41 | 41 | 8 | N |  |  | OP | X | 6 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 1H
Vintage1968 | hydro | TRUE | 18429 | City of Tacoma - (WA) | 3918 | Mossyrock | WA | Lewis | 51 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 150 | 1 | 186 | 175.3 | 100 | N |  |  | OP | X | 11 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 1H
Vintage1968 | hydro | TRUE | 18429 | City of Tacoma - (WA) | 3918 | Mossyrock | WA | Lewis | 52 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 150 | 1 | 157 | 147 | 85 | N |  |  | OP | X | 10 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 1H
Vintage1958 | hydro | TRUE | 19400 | USACE Northwestern Division | 3921 | Chief Joseph | WA | Douglas | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 88.2 | 0.95 | 88.2 | 88.2 | 47.6 | N |  |  | OP | X | 10 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1955 | hydro | TRUE | 19400 | USACE Northwestern Division | 3921 | Chief Joseph | WA | Douglas | 10 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 88.2 | 0.95 | 88.2 | 88.2 | 47.6 | N |  |  | OP | X | 9 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1955 | hydro | TRUE | 19400 | USACE Northwestern Division | 3921 | Chief Joseph | WA | Douglas | 11 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 88.2 | 0.95 | 88.2 | 88.2 | 47.6 | N |  |  | OP | X | 9 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1955 | hydro | TRUE | 19400 | USACE Northwestern Division | 3921 | Chief Joseph | WA | Douglas | 12 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 88.2 | 0.95 | 88.2 | 88.2 | 47.6 | N |  |  | OP | X | 9 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1957 | hydro | TRUE | 19400 | USACE Northwestern Division | 3921 | Chief Joseph | WA | Douglas | 13 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 88.2 | 0.95 | 65 | 65 | 47.6 | N |  |  | OP | X | 2 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1957 | hydro | TRUE | 19400 | USACE Northwestern Division | 3921 | Chief Joseph | WA | Douglas | 14 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 88.2 | 0.95 | 88.2 | 88.2 | 47.6 | N |  |  | OP | X | 7 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1957 | hydro | TRUE | 19400 | USACE Northwestern Division | 3921 | Chief Joseph | WA | Douglas | 15 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 88.2 | 0.95 | 88.2 | 88.2 | 47.6 | N |  |  | OP | X | 9 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1957 | hydro | TRUE | 19400 | USACE Northwestern Division | 3921 | Chief Joseph | WA | Douglas | 16 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 88.2 | 0.95 | 88.2 | 88.2 | 47.6 | N |  |  | OP | X | 11 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1977 | hydro | TRUE | 19400 | USACE Northwestern Division | 3921 | Chief Joseph | WA | Douglas | 17 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 95 | 0.95 | 95 | 95 | 95 | N |  |  | OP | X | 7 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1977 | hydro | TRUE | 19400 | USACE Northwestern Division | 3921 | Chief Joseph | WA | Douglas | 18 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 95 | 0.95 | 95 | 95 | 95 | N |  |  | OP | X | 8 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1977 | hydro | TRUE | 19400 | USACE Northwestern Division | 3921 | Chief Joseph | WA | Douglas | 19 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 95 | 0.95 | 95 | 95 | 95 | N |  |  | OP | X | 11 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1958 | hydro | TRUE | 19400 | USACE Northwestern Division | 3921 | Chief Joseph | WA | Douglas | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 88.2 | 0.95 | 88.2 | 88.2 | 47.6 | N |  |  | OP | X | 7 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1978 | hydro | TRUE | 19400 | USACE Northwestern Division | 3921 | Chief Joseph | WA | Douglas | 20 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 95 | 0.95 | 95 | 95 | 95 | N |  |  | OA | X | 6 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1978 | hydro | TRUE | 19400 | USACE Northwestern Division | 3921 | Chief Joseph | WA | Douglas | 21 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 95 | 0.95 | 95 | 95 | 95 | N |  |  | OP | X | 6 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1978 | hydro | TRUE | 19400 | USACE Northwestern Division | 3921 | Chief Joseph | WA | Douglas | 22 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 95 | 0.95 | 95 | 95 | 95 | N |  |  | OP | X | 6 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1978 | hydro | TRUE | 19400 | USACE Northwestern Division | 3921 | Chief Joseph | WA | Douglas | 23 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 95 | 0.95 | 95 | 95 | 95 | N |  |  | OP | X | 9 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1979 | hydro | TRUE | 19400 | USACE Northwestern Division | 3921 | Chief Joseph | WA | Douglas | 24 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 95 | 0.95 | 95 | 95 | 95 | N |  |  | OP | X | 1 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1979 | hydro | TRUE | 19400 | USACE Northwestern Division | 3921 | Chief Joseph | WA | Douglas | 25 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 95 | 0.95 | 95 | 95 | 95 | N |  |  | OP | X | 1 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1979 | hydro | TRUE | 19400 | USACE Northwestern Division | 3921 | Chief Joseph | WA | Douglas | 26 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 95 | 0.95 | 95 | 95 | 95 | N |  |  | OP | X | 2 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1979 | hydro | TRUE | 19400 | USACE Northwestern Division | 3921 | Chief Joseph | WA | Douglas | 27 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 95 | 0.95 | 95 | 95 | 95 | N |  |  | OA | X | 5 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1958 | hydro | TRUE | 19400 | USACE Northwestern Division | 3921 | Chief Joseph | WA | Douglas | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 88.2 | 0.95 | 88.2 | 88.2 | 47.6 | N |  |  | OP | X | 5 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1958 | hydro | TRUE | 19400 | USACE Northwestern Division | 3921 | Chief Joseph | WA | Douglas | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 88.2 | 0.95 | 88.2 | 88.2 | 47.6 | N |  |  | OP | X | 2 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1957 | hydro | TRUE | 19400 | USACE Northwestern Division | 3921 | Chief Joseph | WA | Douglas | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 88.2 | 0.95 | 88.2 | 88.2 | 47.6 | N |  |  | OP | X | 2 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1956 | hydro | TRUE | 19400 | USACE Northwestern Division | 3921 | Chief Joseph | WA | Douglas | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 88.2 | 0.95 | 88.2 | 88.2 | 47.6 | N |  |  | OP | X | 12 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1956 | hydro | TRUE | 19400 | USACE Northwestern Division | 3921 | Chief Joseph | WA | Douglas | 7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 88.2 | 0.95 | 88.2 | 88.2 | 47.6 | N |  |  | OP | X | 11 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1956 | hydro | TRUE | 19400 | USACE Northwestern Division | 3921 | Chief Joseph | WA | Douglas | 8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 88.2 | 0.95 | 88.2 | 88.2 | 47.6 | N |  |  | OP | X | 9 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1955 | hydro | TRUE | 19400 | USACE Northwestern Division | 3921 | Chief Joseph | WA | Douglas | 9 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 88.2 | 0.95 | 65 | 65 | 47.6 | Y | 4 | 2021 | OP | X | 12 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1962 | hydro | TRUE | 19400 | USACE Northwestern Division | 3925 | Ice Harbor | WA | Walla Walla | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 90 | 0.95 | 72 | 72 | 70 | N |  |  | OA | X | 1 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1962 | hydro | TRUE | 19400 | USACE Northwestern Division | 3925 | Ice Harbor | WA | Walla Walla | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 90 | 0.95 | 90 | 90 | 35.7 | N |  |  | OP | X | 3 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1962 | hydro | TRUE | 19400 | USACE Northwestern Division | 3925 | Ice Harbor | WA | Walla Walla | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 90 | 0.95 | 76 | 76 | 35.7 | N |  |  | OA | X | 3 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1975 | hydro | TRUE | 19400 | USACE Northwestern Division | 3925 | Ice Harbor | WA | Walla Walla | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 111 | 0.95 | 87 | 87 | 42.2 | N |  |  | OP | X | 12 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1975 | hydro | TRUE | 19400 | USACE Northwestern Division | 3925 | Ice Harbor | WA | Walla Walla | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 111 | 0.95 | 87 | 87 | 42.2 | N |  |  | OP | X | 12 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1976 | hydro | TRUE | 19400 | USACE Northwestern Division | 3925 | Ice Harbor | WA | Walla Walla | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 111 | 0.95 | 87 | 87 | 42.2 | N |  |  | OP | X | 2 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1970 | hydro | TRUE | 19400 | USACE Northwestern Division | 3926 | Little Goose | WA | Columbia | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 135 | 135 | 51.3 | N |  |  | OA | X | 4 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1970 | hydro | TRUE | 19400 | USACE Northwestern Division | 3926 | Little Goose | WA | Columbia | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 135 | 135 | 51.3 | N |  |  | OA | X | 4 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1971 | hydro | TRUE | 19400 | USACE Northwestern Division | 3926 | Little Goose | WA | Columbia | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 135 | 135 | 51.3 | N |  |  | OA | X | 1 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1978 | hydro | TRUE | 19400 | USACE Northwestern Division | 3926 | Little Goose | WA | Columbia | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 135 | 135 | 59.7 | N |  |  | OP | X | 2 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1978 | hydro | TRUE | 19400 | USACE Northwestern Division | 3926 | Little Goose | WA | Columbia | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 135 | 135 | 59.7 | N |  |  | OS | X | 6 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1978 | hydro | TRUE | 19400 | USACE Northwestern Division | 3926 | Little Goose | WA | Columbia | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 135 | 135 | 59.7 | N |  |  | OP | X | 6 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1969 | hydro | TRUE | 19400 | USACE Northwestern Division | 3927 | Lower Monumental | WA | Walla Walla | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 135 | 135 | 53.8 | N |  |  | OP | X | 6 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1969 | hydro | TRUE | 19400 | USACE Northwestern Division | 3927 | Lower Monumental | WA | Walla Walla | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 135 | 135 | 53.8 | N |  |  | OA | X | 10 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1970 | hydro | TRUE | 19400 | USACE Northwestern Division | 3927 | Lower Monumental | WA | Walla Walla | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 135 | 135 | 53.8 | N |  |  | OP | X | 2 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1979 | hydro | TRUE | 19400 | USACE Northwestern Division | 3927 | Lower Monumental | WA | Walla Walla | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 135 | 135 | 63.3 | N |  |  | OP | X | 3 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1979 | hydro | TRUE | 19400 | USACE Northwestern Division | 3927 | Lower Monumental | WA | Walla Walla | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 115 | 115 | 63.3 | Y | 4 | 2021 | OP | X | 4 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1979 | hydro | TRUE | 19400 | USACE Northwestern Division | 3927 | Lower Monumental | WA | Walla Walla | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 135 | 135 | 63.3 | N |  |  | OP | X | 7 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1964 | hydro | TRUE | 20160 | Energy Northwest | 3929 | Packwood | WA | Lewis | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 27.5 | 0.95 | 26 | 26 | 3 | N |  |  | OP | X | 4 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 12H | [23 empty] | N
Vintage1971 | hard coal | TRUE | 733 | Appalachian Power Co | 3935 | John E Amos | WV | Putnam | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 816.3 | 0.9 | 800 | 800 | 300 | N |  |  | OP | X | 9 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: DFO |  |  | N | N |  | 12H |  | Y |  |  |  | Y | [17 empty] | N | N | N
Vintage1972 | hard coal | TRUE | 733 | Appalachian Power Co | 3935 | John E Amos | WV | Putnam | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 816.3 | 0.9 | 800 | 800 | 300 | N |  |  | OP | X | 6 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: DFO |  |  | N | N |  | 12H |  | Y |  |  |  | Y | [17 empty] | N | N | N
Vintage1973 | hard coal | TRUE | 733 | Appalachian Power Co | 3935 | John E Amos | WV | Putnam | 3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 1300 | 0.9 | 1300 | 1299 | 600 | N |  |  | OP | X | 10 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: DFO |  |  | N | N |  | 12H |  | Y |  |  |  | Y | [17 empty] | N | N | N
Vintage1967 | hard coal | TRUE | 12796 | Monongahela Power Co | 3943 | FirstEnergy Fort Martin Power Station | WV | Monongalia | 1 | Conventional Steam Coal | ST |  | S | X | X | FTMARTIN22KV GEN 1 | FTMARTIN22KV GEN 1 | 576 | 0.9 | 552 | 552 | 220 | N |  |  | OP | X | 10 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: DFO; DFO DFO DFO: DFO |  |  | N | N |  | 12H |  | Y |  |  |  | Y | [17 empty] | N | N | N
Vintage1968 | hard coal | TRUE | 12796 | Monongahela Power Co | 3943 | FirstEnergy Fort Martin Power Station | WV | Monongalia | 2 | Conventional Steam Coal | ST |  | S | X | X | FTMARTIN22KV GEN 2 | FTMARTIN22KV GEN 2 | 576 | 0.9 | 546 | 546 | 220 | N |  |  | OP | X | 12 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: DFO; DFO DFO DFO: DFO |  |  | N | N |  | 12H |  | Y |  |  |  | Y | [17 empty] | N | N | N
Vintage1972 | hard coal | TRUE | 12796 | Monongahela Power Co | 3944 | FirstEnergy Harrison Power Station | WV | Harrison | 1 | Conventional Steam Coal | ST |  | S | X | X | HARR APS20KV GEN1 | HARR APS20KV GEN1 | 684 | 0.92 | 652 | 662 | 375 | N |  |  | OP | X | 12 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N | N |  | 12H |  | Y |  |  |  | Y | [17 empty] | N | N | N
Vintage1973 | hard coal | TRUE | 12796 | Monongahela Power Co | 3944 | FirstEnergy Harrison Power Station | WV | Harrison | 2 | Conventional Steam Coal | ST |  | S | X | X | HARR APS20KV GEN2 | HARR APS20KV GEN2 | 684 | 0.92 | 651 | 661 | 375 | N |  |  | OP | X | 12 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N | N |  | 12H |  | Y |  |  |  | Y | [17 empty] | N | N | N
Vintage1974 | hard coal | TRUE | 12796 | Monongahela Power Co | 3944 | FirstEnergy Harrison Power Station | WV | Harrison | 3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 684 | 0.92 | 651 | 661 | 375 | N |  |  | OP | X | 12 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N | N |  | 12H |  | Y |  |  |  | Y | [17 empty] | N | N | N
Vintage1971 | hard coal | TRUE | 22053 | Kentucky Power Co | 3948 | Mitchell (WV) | WV | Marshall | 1 | Conventional Steam Coal | ST |  | J | X | X |  |  | 816.3 | 0.9 | 770 | 770 | 370 | N |  |  | OP | X | 5 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | N
Vintage1971 | hard coal | TRUE | 22053 | Kentucky Power Co | 3948 | Mitchell (WV) | WV | Marshall | 2 | Conventional Steam Coal | ST |  | J | X | X |  |  | 816.3 | 0.9 | 790 | 790 | 410 | N |  |  | OP | X | 5 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | N
Vintage1965 | hard coal | TRUE | 19876 | Virginia Electric & Power Co | 3954 | Mt Storm | WV | Grant | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 570.2 | 0.9 | 554 | 569 | 265 | N |  |  | OP | X | 9 | 1965 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: DFO; DFO DFO DFO: DFO | [5 empty] | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1966 | hard coal | TRUE | 19876 | Virginia Electric & Power Co | 3954 | Mt Storm | WV | Grant | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 570.2 | 0.9 | 555 | 570 | 265 | N |  |  | OP | X | 7 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: DFO; DFO DFO DFO: DFO | [5 empty] | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1973 | hard coal | TRUE | 19876 | Virginia Electric & Power Co | 3954 | Mt Storm | WV | Grant | 3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 522 | 0.9 | 520 | 537 | 300 | N |  |  | OP | X | 12 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: DFO; DFO DFO DFO: WO; DFO DFO DFO: DFO | [5 empty] | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1967 | petroleum | TRUE | 19876 | Virginia Electric & Power Co | 3954 | Mt Storm | WV | Grant | JF1 | Petroleum Liquids | GT |  | S | X | X |  |  | 18.5 | 0.85 | 11 | 15 | 5 | N |  |  | OP | X | 10 | 1967 |  |  | N | Electric Utility | 1 | [14 empty] | 1H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1921 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3971 | Biron | WI | Wood | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.4 | 1 | 1.3 | 1.3 | 1.3 | N |  |  | OP | X | 1 | 1921 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 12H | [23 empty] | N
Vintage1921 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3971 | Biron | WI | Wood | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.4 | 1 | 1.3 | 1.3 | 1.3 | N |  |  | OP | X | 1 | 1921 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 12H | [23 empty] | N
Vintage1916 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3971 | Biron | WI | Wood | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.4 | N |  |  | OS | X | 1 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 12H | [23 empty] | N
Vintage1896 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3971 | Biron | WI | Wood | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.4 | N |  |  | OS | X | 1 | 1896 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [23 empty] | N
Vintage1896 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3971 | Biron | WI | Wood | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.4 | N |  |  | OS | X | 1 | 1896 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [23 empty] | N
Vintage1896 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3971 | Biron | WI | Wood | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.4 | N |  |  | OP | X | 1 | 1896 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [23 empty] | N
Vintage1896 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3971 | Biron | WI | Wood | 7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.4 | N |  |  | OS | X | 1 | 1896 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [23 empty] | N
Vintage1896 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3971 | Biron | WI | Wood | 9 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | N |  |  | OP | X | 1 | 1896 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [23 empty] | N
Vintage1942 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3972 | Du Bay | WI | Portage | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.9 | 1.2 | 1.2 | 1.2 | N |  |  | OP | X | 1 | 1942 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 12H | [23 empty] | N
Vintage1942 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3972 | Du Bay | WI | Portage | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 1 | 2 | 2 | 2 | N |  |  | OP | X | 1 | 1942 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 12H | [23 empty] | N
Vintage1942 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3972 | Du Bay | WI | Portage | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 1 | 2 | 2 | 2 | N |  |  | OP | X | 1 | 1942 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 12H | [23 empty] | N
Vintage1942 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3972 | Du Bay | WI | Portage | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 1 | 2 | 2 | 2 | N |  |  | OP | X | 1 | 1942 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 12H | [23 empty] | N
Vintage1918 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3973 | Stevens Point | WI | Portage | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | N |  |  | OP | X | 1 | 1918 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [23 empty] | N
Vintage1918 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3973 | Stevens Point | WI | Portage | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | N |  |  | OP | X | 1 | 1918 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [23 empty] | N
Vintage1918 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3973 | Stevens Point | WI | Portage | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | N |  |  | OP | X | 1 | 1918 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [23 empty] | N
Vintage1918 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3973 | Stevens Point | WI | Portage | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | N |  |  | OP | X | 1 | 1918 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [23 empty] | N
Vintage1918 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3973 | Stevens Point | WI | Portage | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | N |  |  | OP | X | 1 | 1918 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [23 empty] | N
Vintage1918 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3973 | Stevens Point | WI | Portage | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | N |  |  | OS | X | 1 | 1918 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [23 empty] | N
Vintage1920 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3974 | Wisconsin Rapids | WI | Wood | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.3 | 1 | 2.3 | 2.3 | 1.5 | N |  |  | OP | X | 1 | 1920 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [23 empty] | N
Vintage1903 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3974 | Wisconsin Rapids | WI | Wood | 10 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.6 | N |  |  | OP | X | 1 | 1903 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [23 empty] | N
Vintage1920 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3974 | Wisconsin Rapids | WI | Wood | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.3 | 1 | 2.3 | 2.3 | 1.5 | N |  |  | OP | X | 1 | 1920 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [23 empty] | N
Vintage1903 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3974 | Wisconsin Rapids | WI | Wood | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.6 | N |  |  | OP | X | 1 | 1903 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [23 empty] | N
Vintage1903 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3974 | Wisconsin Rapids | WI | Wood | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.6 | N |  |  | OP | X | 1 | 1903 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [23 empty] | N
Vintage1903 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3974 | Wisconsin Rapids | WI | Wood | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.6 | N |  |  | OP | X | 1 | 1903 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [23 empty] | N
Vintage1903 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3974 | Wisconsin Rapids | WI | Wood | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.3 | N |  |  | OP | X | 1 | 1903 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [23 empty] | N
Vintage1903 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3974 | Wisconsin Rapids | WI | Wood | 7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.6 | N |  |  | OP | X | 1 | 1903 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [23 empty] | N
Vintage1903 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3974 | Wisconsin Rapids | WI | Wood | 8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.3 | N |  |  | OP | X | 1 | 1903 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [23 empty] | N
Vintage1903 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3974 | Wisconsin Rapids | WI | Wood | 9 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.6 | N |  |  | OP | X | 1 | 1903 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [23 empty] | N
Vintage1963 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3975 | Whiting | WI | Portage | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 1 | 1.2 | 1.2 | 1 | N |  |  | OS | X | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 12H | [23 empty] | N
Vintage1891 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3975 | Whiting | WI | Portage | 10 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.3 | N |  |  | OP | X | 1 | 1891 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 12H | [23 empty] | N
Vintage1891 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3975 | Whiting | WI | Portage | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.5 | N |  |  | OP | X | 1 | 1891 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 12H | [23 empty] | N
Vintage1891 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3975 | Whiting | WI | Portage | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.5 | N |  |  | OS | X | 1 | 1891 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [23 empty] | N
Vintage1891 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3975 | Whiting | WI | Portage | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.5 | N |  |  | OP | X | 1 | 1891 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [23 empty] | N
Vintage1891 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3975 | Whiting | WI | Portage | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.5 | N |  |  | OP | X | 1 | 1891 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [23 empty] | N
Vintage1891 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3975 | Whiting | WI | Portage | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.5 | N |  |  | OP | X | 1 | 1891 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [23 empty] | N
Vintage1891 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3975 | Whiting | WI | Portage | 7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.5 | N |  |  | OP | X | 1 | 1891 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [23 empty] | N
Vintage1891 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3975 | Whiting | WI | Portage | 8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.3 | N |  |  | OP | X | 1 | 1891 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [23 empty] | N
Vintage1891 | hydro | TRUE | 4247 | Consolidated Water Power Co | 3975 | Whiting | WI | Portage | 9 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.3 | N |  |  | OP | X | 1 | 1891 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 12H | [23 empty] | N
Vintage1955 | petroleum | TRUE | 4715 | Dahlberg Light & Power Co | 3976 | Gordon | WI | Douglas | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.7 | 0.8 | 0.7 | 0.7 | 0.7 | N |  |  | SB | Y | 8 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N
Vintage1949 | petroleum | TRUE | 4715 | Dahlberg Light & Power Co | 3976 | Gordon | WI | Douglas | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.7 | 0.8 | 0.7 | 0.7 | 0.7 | N |  |  | SB | Y | 8 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage2001 | petroleum | TRUE | 4715 | Dahlberg Light & Power Co | 3976 | Gordon | WI | Douglas | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.8 | 0.8 | 0.7 | 0.7 | 0.7 | N |  |  | SB | Y | 2 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage2001 | petroleum | TRUE | 4715 | Dahlberg Light & Power Co | 3976 | Gordon | WI | Douglas | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.8 | 0.8 | 0.7 | 0.7 | 0.7 | N |  |  | SB | Y | 2 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1952 | biomass | TRUE | 13781 | Northern States Power Co - Minnesota | 3982 | Bay Front | WI | Ashland | 5 | Wood/Wood Waste Biomass | ST |  | S | X | X | NSP BAYFRNT BAYFRN_5_UNIT | NSP BAYFRNT BAYFRN_5_UNIT | 20 | 0.87 | 18 | 18 | 11 | N |  |  | OP | X | 1 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WDS; DFO SUB SUB: TDF; DFO DFO DFO: NG; DFO DFO DFO: NG |  |  | N | N |  | 12H |  | N | N |  | N | [18 empty] | Y | Y | N
Vintage1957 | natural gas steam turbine | TRUE | 13781 | Northern States Power Co - Minnesota | 3982 | Bay Front | WI | Ashland | 6 | Natural Gas Steam Turbine | ST |  | S | X | X | NSP BAYFRNT BAYFRN_6_UNIT | NSP BAYFRNT BAYFRN_6_UNIT | 27.2 | 0.85 | 23 | 23 | 15 | N |  |  | OP | X | 1 | 1957 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H |  |  |  |  | N | [18 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1922 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 3983 | Big Falls | WI | Rusk | 1 | Conventional Hydroelectric | HY |  | S | X | X | NSP BIGFALL BIGFAL_A_UNIT | NSP BIGFALL BIGFAL_A_UNIT | 2.6 | 0.8 | 1.1 | 1 | 0.7 | N |  |  | OP | X | 1 | 1922 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 1H | [23 empty] | N
Vintage1922 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 3983 | Big Falls | WI | Rusk | 2 | Conventional Hydroelectric | HY |  | S | X | X | NSP BIGFALL BIGFAL_A_UNIT | NSP BIGFALL BIGFAL_A_UNIT | 2.6 | 0.8 | 1.1 | 1 | 0.7 | N |  |  | OP | X | 1 | 1922 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 1H | [23 empty] | N
Vintage1993 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 3983 | Big Falls | WI | Rusk | 3 | Conventional Hydroelectric | HY |  | S | X | X | NSP BIGFALL BIGFAL_A_UNIT | NSP BIGFALL BIGFAL_A_UNIT | 2.5 | 0.8 | 1.1 | 1 | 0.6 | N |  |  | OP | X | 9 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 1H | [23 empty] | N
Vintage1940 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 3986 | Ladysmith Dam | WI | Rusk | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.9 | 0.9 | 0.3 | 0.3 | 0.2 | N |  |  | OP | X | 1 | 1940 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1940 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 3986 | Ladysmith Dam | WI | Rusk | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.9 | 0.9 | 0.3 | 0.2 | 0.2 | N |  |  | OP | X | 1 | 1940 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1983 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 3986 | Ladysmith Dam | WI | Rusk | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.8 | 0.4 | 0.3 | 0.4 | N |  |  | OP | X | 11 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1927 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 3988 | Thornapple | WI | Rusk | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 1 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1929 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 3988 | Thornapple | WI | Rusk | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 1 | 1929 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1907 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 3989 | White River (WI) | WI | Ashland | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 1 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1907 | 7 | 2025 | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1907 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 3989 | White River (WI) | WI | Ashland | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 1 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1907 | 7 | 2025 | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1973 | natural gas peaker | TRUE | 11479 | Madison Gas & Electric Co | 3991 | Fitchburg | WI | Dane | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 28.8 | 0.85 | 16.1 | 16.1 | 3 | N |  |  | OP | X | 5 | 1973 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1973 | natural gas peaker | TRUE | 11479 | Madison Gas & Electric Co | 3991 | Fitchburg | WI | Dane | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 28.8 | 0.85 | 16.2 | 16.2 | 3 | N |  |  | OP | X | 5 | 1973 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1957 | natural gas steam turbine | TRUE | 11479 | Madison Gas & Electric Co | 3992 | Blount Street | WI | Dane | 6 | Natural Gas Steam Turbine | ST |  | S | X | X | MGE.BLTPLTG6 | MGE.BLTPLTG6 | 50 | 0.85 | 47.6 | 47.6 | 5 | N |  |  | OP | X | 6 | 1957 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER |  | N | [18 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1961 | natural gas steam turbine | TRUE | 11479 | Madison Gas & Electric Co | 3992 | Blount Street | WI | Dane | 7 | Natural Gas Steam Turbine | ST |  | S | X | X | MGE.BLTPLTG7 | MGE.BLTPLTG7 | 50 | 0.85 | 47.9 | 47.9 | 5 | N |  |  | OP | X | 7 | 1961 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER |  | N | [18 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1967 | natural gas peaker | TRUE | 11479 | Madison Gas & Electric Co | 3993 | Sycamore (WI) | WI | Dane | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 18 | 0.85 | 12.4 | 12.4 | 3 | N |  |  | OP | X | 12 | 1967 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1971 | natural gas peaker | TRUE | 11479 | Madison Gas & Electric Co | 3993 | Sycamore (WI) | WI | Dane | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 23.6 | 0.85 | 17.5 | 17.5 | 3 | N |  |  | OP | X | 6 | 1971 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1971 | hydro | TRUE | 58149 | Renewable World Energies LLC | 3995 | Arpin Dam | WI | Sawyer | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0 | N |  |  | OP | X | 9 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1971 | hydro | TRUE | 58149 | Renewable World Energies LLC | 3995 | Arpin Dam | WI | Sawyer | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0 | N |  |  | OP | X | 9 | 1971 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1973 | hydro | TRUE | 58149 | Renewable World Energies LLC | 3995 | Arpin Dam | WI | Sawyer | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0 | N |  |  | OP | X | 5 | 1973 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1915 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 3998 | Cedar Falls (WI) | WI | Dunn | 1 | Conventional Hydroelectric | HY |  | S | X | X | NSP CEDARFAL CEDARF_A_UNIT | NSP CEDARFAL CEDARF_A_UNIT | 2 | 0.8 | 1.3 | 1.2 | 1.2 | N |  |  | OP | X | 1 | 1915 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1911 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 3998 | Cedar Falls (WI) | WI | Dunn | 2 | Conventional Hydroelectric | HY |  | S | X | X | NSP CEDARFAL CEDARF_A_UNIT | NSP CEDARFAL CEDARF_A_UNIT | 2 | 0.8 | 1.1 | 1.1 | 1.1 | N |  |  | OP | X | 1 | 1911 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1910 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 3998 | Cedar Falls (WI) | WI | Dunn | 3 | Conventional Hydroelectric | HY |  | S | X | X | NSP CEDARFAL CEDARF_A_UNIT | NSP CEDARFAL CEDARF_A_UNIT | 2 | 0.8 | 1.2 | 1.1 | 1.1 | N |  |  | OP | X | 1 | 1910 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1928 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4000 | Chippewa Falls | WI | Chippewa | 1 | Conventional Hydroelectric | HY |  | S | X | X | NSP CHPFALLS CHP_TR1_UNIT | NSP CHPFALLS CHP_TR1_UNIT | 3.6 | 0.8 | 1.9 | 1.9 | 0.9 | N |  |  | OP | X | 1 | 1928 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1928 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4000 | Chippewa Falls | WI | Chippewa | 2 | Conventional Hydroelectric | HY |  | S | X | X | NSP CHPFALLS CHP_TR1_UNIT | NSP CHPFALLS CHP_TR1_UNIT | 3.6 | 0.8 | 2.1 | 2.1 | 0.9 | N |  |  | OP | X | 1 | 1928 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1928 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4000 | Chippewa Falls | WI | Chippewa | 3 | Conventional Hydroelectric | HY |  | S | X | X | NSP CHPFALLS CHP_TR1_UNIT | NSP CHPFALLS CHP_TR1_UNIT | 3.6 | 0.8 | 2 | 2 | 0.9 | N |  |  | OP | X | 1 | 1928 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1928 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4000 | Chippewa Falls | WI | Chippewa | 4 | Conventional Hydroelectric | HY |  | S | X | X | NSP CHPFALLS CHP_TR1_UNIT | NSP CHPFALLS CHP_TR1_UNIT | 3.6 | 0.8 | 2 | 2 | 0.9 | N |  |  | OP | X | 1 | 1928 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1928 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4000 | Chippewa Falls | WI | Chippewa | 5 | Conventional Hydroelectric | HY |  | S | X | X | NSP CHPFALLS CHP_TR1_UNIT | NSP CHPFALLS CHP_TR1_UNIT | 3.6 | 0.8 | 2 | 2 | 0.9 | N |  |  | OP | X | 1 | 1928 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1928 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4000 | Chippewa Falls | WI | Chippewa | 6 | Conventional Hydroelectric | HY |  | S | X | X | NSP CHPFALLS CHP_TR1_UNIT | NSP CHPFALLS CHP_TR1_UNIT | 3.6 | 0.8 | 2.1 | 2.1 | 0.9 | N |  |  | OP | X | 1 | 1928 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1923 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4002 | Dells | WI | Eau Claire | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.9 | 0.9 | 1.9 | 1.9 | 0.7 | N |  |  | OP | X | 1 | 1923 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1924 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4002 | Dells | WI | Eau Claire | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.6 | 0.85 | 1.5 | 1.5 | 0.7 | N |  |  | OP | X | 1 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1924 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4002 | Dells | WI | Eau Claire | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.6 | 0.85 | 1.5 | 1.5 | 0.7 | N |  |  | OP | X | 1 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1924 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4002 | Dells | WI | Eau Claire | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.6 | 0.85 | 1.5 | 1.5 | 0.7 | N |  |  | OP | X | 1 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1924 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4002 | Dells | WI | Eau Claire | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.8 | 0.9 | 0.9 | 0.4 | N |  |  | OP | X | 1 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1940 | biomass | TRUE | 13781 | Northern States Power Co - Minnesota | 4005 | French Island | WI | La Crosse | 1 | Wood/Wood Waste Biomass | ST |  | S | X | X | NSP FRENCH_G FRENCH_1_UNIT | NSP FRENCH_G FRENCH_1_UNIT | 15.2 | 0.87 | 9 | 9 | 6 | N |  |  | OP | X | 1 | 1940 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: WDS; DFO SUB SUB: MSW; DFO DFO DFO: NG; DFO DFO DFO: NG |  |  | N | N |  | 12H | N |  |  |  | N | [18 empty] | Y | Y | N
Vintage1948 | biomass | TRUE | 13781 | Northern States Power Co - Minnesota | 4005 | French Island | WI | La Crosse | 2 | Wood/Wood Waste Biomass | ST |  | S | X | X | NSP FRENCH_G FRENCH_2_UNIT | NSP FRENCH_G FRENCH_2_UNIT | 15.2 | 0.87 | 7 | 7 | 6 | N |  |  | OP | X | 1 | 1948 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: WDS; DFO SUB SUB: MSW; DFO DFO DFO: NG; DFO DFO DFO: NG |  |  | N | N |  | 12H | N |  |  |  | N | [18 empty] | Y | Y | N
Vintage1974 | petroleum | TRUE | 13781 | Northern States Power Co - Minnesota | 4005 | French Island | WI | La Crosse | 3 | Petroleum Liquids | GT |  | S | X | X | NSP FRENCH_G FRENCH_3_UNIT | NSP FRENCH_G FRENCH_3_UNIT | 78.8 | 0.9 | 61 | 81 | 22 | N |  |  | OP | X | 9 | 1974 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H |  |  |  |  | N | [18 empty] | N | N | N
Vintage1974 | petroleum | TRUE | 13781 | Northern States Power Co - Minnesota | 4005 | French Island | WI | La Crosse | 4 | Petroleum Liquids | GT |  | S | X | X | NSP FRENCH_G FRENCH_4_UNIT | NSP FRENCH_G FRENCH_4_UNIT | 78.8 | 0.9 | 61 | 81 | 22 | N |  |  | OP | X | 11 | 1974 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1950 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4007 | Holcombe | WI | Chippewa | 1 | Conventional Hydroelectric | HY |  | S | X | X | NSP HOLCOMB HOLC_HYD_UNIT | NSP HOLCOMB HOLC_HYD_UNIT | 11.3 | 0.9 | 7.3 | 7.3 | 2.8 | N |  |  | OP | X | 1 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1950 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4007 | Holcombe | WI | Chippewa | 2 | Conventional Hydroelectric | HY |  | S | X | X | NSP HOLCOMB HOLC_HYD_UNIT | NSP HOLCOMB HOLC_HYD_UNIT | 11.3 | 0.9 | 7.3 | 7.3 | 2.8 | N |  |  | OP | X | 1 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1950 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4007 | Holcombe | WI | Chippewa | 3 | Conventional Hydroelectric | HY |  | S | X | X | NSP HOLCOMB HOLC_HYD_UNIT | NSP HOLCOMB HOLC_HYD_UNIT | 11.3 | 0.9 | 7.3 | 7.3 | 2.8 | N |  |  | OP | X | 1 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1988 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4008 | Jim Falls | WI | Chippewa | 1 | Conventional Hydroelectric | HY |  | S | X | X | NSP JIM_FLS JIMF_HYD_UNIT | NSP JIM_FLS JIMF_HYD_UNIT | 29.6 | 0.93 | 12.3 | 12.3 | 7.4 | N |  |  | OP | X | 8 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1988 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4008 | Jim Falls | WI | Chippewa | 2 | Conventional Hydroelectric | HY |  | S | X | X | NSP JIM_FLS JIMF_HYD_UNIT | NSP JIM_FLS JIMF_HYD_UNIT | 29.6 | 0.93 | 12.5 | 12.5 | 7.4 | N |  |  | OP | X | 8 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1988 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4008 | Jim Falls | WI | Chippewa | 4 | Conventional Hydroelectric | HY |  | S | X | X | NSP JIM_FLS JIMF_HYD_UNIT | NSP JIM_FLS JIMF_HYD_UNIT | 0.6 | 1 | 0.2 | 0.2 | 0.2 | N |  |  | OP | X | 7 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1958 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4009 | Menomonie | WI | Dunn | 1 | Conventional Hydroelectric | HY |  | S | X | X | NSP MENOMONE MENOMO_A_UNIT | NSP MENOMONE MENOMO_A_UNIT | 2.7 | 0.9 | 1.1 | 1.2 | 0.7 | N |  |  | OP | X | 1 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1958 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4009 | Menomonie | WI | Dunn | 2 | Conventional Hydroelectric | HY |  | S | X | X | NSP MENOMONE MENOMO_A_UNIT | NSP MENOMONE MENOMO_A_UNIT | 2.7 | 0.9 | 1.1 | 1.2 | 0.6 | N |  |  | OP | X | 1 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1917 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4011 | St Croix Falls | WI | Polk | 1 | Conventional Hydroelectric | HY |  | S | X | X | NSP ST_CROIX STCR_HYD_UNIT | NSP ST_CROIX STCR_HYD_UNIT | 2.5 | 1 | 1.8 | 1.4 | 0.6 | N |  |  | OP | X | 1 | 1917 | 12 | 2027 | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1917 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4011 | St Croix Falls | WI | Polk | 2 | Conventional Hydroelectric | HY |  | S | X | X | NSP ST_CROIX STCR_HYD_UNIT | NSP ST_CROIX STCR_HYD_UNIT | 2.5 | 1 | 1.8 | 1.4 | 0.6 | N |  |  | OP | X | 1 | 1917 | 12 | 2027 | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1917 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4011 | St Croix Falls | WI | Polk | 3 | Conventional Hydroelectric | HY |  | S | X | X | NSP ST_CROIX STCR_HYD_UNIT | NSP ST_CROIX STCR_HYD_UNIT | 2.5 | 1 | 1.9 | 1.5 | 0.6 | N |  |  | OP | X | 1 | 1917 | 12 | 2027 | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1917 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4011 | St Croix Falls | WI | Polk | 4 | Conventional Hydroelectric | HY |  | S | X | X | NSP ST_CROIX STCR_HYD_UNIT | NSP ST_CROIX STCR_HYD_UNIT | 2.5 | 1 | 1.9 | 1.5 | 0.6 | N |  |  | OP | X | 1 | 1917 | 12 | 2027 | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1910 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4011 | St Croix Falls | WI | Polk | 5 | Conventional Hydroelectric | HY |  | S | X | X | NSP ST_CROIX STCR_HYD_UNIT | NSP ST_CROIX STCR_HYD_UNIT | 3.4 | 1 | 2 | 1.6 | 0.9 | N |  |  | OP | X | 1 | 1910 | 12 | 2027 | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1910 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4011 | St Croix Falls | WI | Polk | 6 | Conventional Hydroelectric | HY |  | S | X | X | NSP ST_CROIX STCR_HYD_UNIT | NSP ST_CROIX STCR_HYD_UNIT | 3.4 | 1 | 1.9 | 1.5 | 0.9 | N |  |  | OP | X | 1 | 1910 | 12 | 2027 | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1923 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4011 | St Croix Falls | WI | Polk | 7 | Conventional Hydroelectric | HY |  | S | X | X | NSP ST_CROIX STCR_HYD_UNIT | NSP ST_CROIX STCR_HYD_UNIT | 3.2 | 0.8 | 2 | 1.6 | 0.8 | N |  |  | OP | X | 1 | 1923 | 12 | 2027 | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1923 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4011 | St Croix Falls | WI | Polk | 8 | Conventional Hydroelectric | HY |  | S | X | X | NSP ST_CROIX STCR_HYD_UNIT | NSP ST_CROIX STCR_HYD_UNIT | 3.2 | 0.8 | 1.9 | 1.5 | 0.8 | N |  |  | OP | X | 1 | 1923 | 12 | 2027 | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 1H | [23 empty] | N
Vintage1927 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4012 | Trego | WI | Washburn | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 1 | 1927 | 11 | 2025 | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1927 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4012 | Trego | WI | Washburn | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 1 | 1927 | 11 | 2025 | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1973 | natural gas peaker | TRUE | 13781 | Northern States Power Co - Minnesota | 4014 | Wheaton | WI | Chippewa | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | NSP WHEATON2 WHEATO_1_UNIT | NSP WHEATON2 WHEATO_1_UNIT | 48.5 | 0.85 | 44 | 56 | 10 | N |  |  | OP | X | 1 | 1973 | 12 | 2025 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1973 | natural gas peaker | TRUE | 13781 | Northern States Power Co - Minnesota | 4014 | Wheaton | WI | Chippewa | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | NSP WHEATON2 WHEATO_2_UNIT | NSP WHEATON2 WHEATO_2_UNIT | 48.5 | 0.85 | 51 | 66 | 10 | N |  |  | OP | X | 4 | 1973 | 12 | 2025 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1973 | natural gas peaker | TRUE | 13781 | Northern States Power Co - Minnesota | 4014 | Wheaton | WI | Chippewa | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | NSP WHEATON2 WHEATO_3_UNIT | NSP WHEATON2 WHEATO_3_UNIT | 48.5 | 0.85 | 44 | 56 | 10 | N |  |  | OP | X | 4 | 1973 | 12 | 2025 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1973 | natural gas peaker | TRUE | 13781 | Northern States Power Co - Minnesota | 4014 | Wheaton | WI | Chippewa | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | NSP WHEATON2 WHEATO_4_UNIT | NSP WHEATON2 WHEATO_4_UNIT | 48.5 | 0.85 | 47 | 61 | 10 | N |  |  | OP | X | 4 | 1973 | 12 | 2025 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1973 | petroleum | TRUE | 13781 | Northern States Power Co - Minnesota | 4014 | Wheaton | WI | Chippewa | 6 | Petroleum Liquids | GT |  | S | X | X | NSP WHEATON2 WHEATO_6_UNIT | NSP WHEATON2 WHEATO_6_UNIT | 53.1 | 0.85 | 48 | 70 | 25 | N |  |  | OP | X | 6 | 1973 | 12 | 2025 | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1917 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4015 | Wissota | WI | Chippewa | 1 | Conventional Hydroelectric | HY |  | S | X | X | NSP WISSOTA WIS_TR3_UNIT | NSP WISSOTA WIS_TR3_UNIT | 6 | 0.8 | 3 | 3 | 1.5 | N |  |  | OP | X | 1 | 1917 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1917 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4015 | Wissota | WI | Chippewa | 2 | Conventional Hydroelectric | HY |  | S | X | X | NSP WISSOTA WIS_TR3_UNIT | NSP WISSOTA WIS_TR3_UNIT | 7.7 | 0.85 | 3.1 | 3.1 | 1.5 | N |  |  | OP | X | 1 | 1917 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1917 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4015 | Wissota | WI | Chippewa | 3 | Conventional Hydroelectric | HY |  | S | X | X | NSP WISSOTA WIS_TR3_UNIT | NSP WISSOTA WIS_TR3_UNIT | 6 | 0.8 | 3 | 3 | 1.5 | N |  |  | OP | X | 1 | 1917 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1917 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4015 | Wissota | WI | Chippewa | 4 | Conventional Hydroelectric | HY |  | S | X | X | NSP WISSOTA WIS_TR4_UNIT | NSP WISSOTA WIS_TR4_UNIT | 7.7 | 0.85 | 3 | 3 | 1.5 | N |  |  | OP | X | 1 | 1917 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1917 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4015 | Wissota | WI | Chippewa | 5 | Conventional Hydroelectric | HY |  | S | X | X | NSP WISSOTA WIS_TR4_UNIT | NSP WISSOTA WIS_TR4_UNIT | 6 | 0.8 | 2.9 | 2.9 | 1.5 | N |  |  | OP | X | 1 | 1917 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1917 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 4015 | Wissota | WI | Chippewa | 6 | Conventional Hydroelectric | HY |  | S | X | X | NSP WISSOTA WIS_TR4_UNIT | NSP WISSOTA WIS_TR4_UNIT | 6 | 0.8 | 3 | 3 | 1.5 | N |  |  | OP | X | 1 | 1917 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1942 | hydro | TRUE | 58149 | Renewable World Energies LLC | 4018 | Clam River Dam | WI | Burnett | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0 | N |  |  | OP | X | 12 | 1942 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1942 | hydro | TRUE | 58149 | Renewable World Energies LLC | 4018 | Clam River Dam | WI | Burnett | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0 | N |  |  | OP | X | 4 | 1942 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1967 | hydro | TRUE | 58149 | Renewable World Energies LLC | 4018 | Clam River Dam | WI | Burnett | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0 | N |  |  | OP | X | 4 | 1967 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1921 | hydro | TRUE | 58149 | Renewable World Energies LLC | 4019 | Danbury Dam | WI | Burnett | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0 | N |  |  | OP | X | 1 | 1921 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1927 | hydro | TRUE | 58149 | Renewable World Energies LLC | 4019 | Danbury Dam | WI | Burnett | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0 | N |  |  | OP | X | 3 | 1927 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1950 | hydro | TRUE | 58149 | Renewable World Energies LLC | 4019 | Danbury Dam | WI | Burnett | HY3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0 | N |  |  | OP | X | 6 | 1950 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 13815 | Northwestern Wisconsin Elec Co | 4020 | Frederic Diesel | WI | Polk | 10 | Petroleum Liquids | IC |  | S | X | X | dpc.nweload | dpc.nweload | 2.5 | 0.8 | 2.5 | 2.6 | 0.1 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1948 | petroleum | TRUE | 13815 | Northwestern Wisconsin Elec Co | 4020 | Frederic Diesel | WI | Polk | 2 | Petroleum Liquids | IC |  | S | X | X | dpc.nweload | dpc.nweload | 0.7 | 0.8 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 12 | 1948 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1949 | petroleum | TRUE | 13815 | Northwestern Wisconsin Elec Co | 4020 | Frederic Diesel | WI | Polk | 3 | Petroleum Liquids | IC |  | S | X | X | dpc.nweload | dpc.nweload | 0.7 | 0.8 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 12 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1955 | petroleum | TRUE | 13815 | Northwestern Wisconsin Elec Co | 4020 | Frederic Diesel | WI | Polk | 4 | Petroleum Liquids | IC |  | S | X | X | dpc.nweload | dpc.nweload | 0.7 | 0.8 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 12 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1955 | petroleum | TRUE | 13815 | Northwestern Wisconsin Elec Co | 4020 | Frederic Diesel | WI | Polk | 5 | Petroleum Liquids | IC |  | S | X | X | dpc.nweload | dpc.nweload | 0.6 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 12 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1970 | petroleum | TRUE | 13815 | Northwestern Wisconsin Elec Co | 4020 | Frederic Diesel | WI | Polk | 6 | Petroleum Liquids | IC |  | S | X | X | dpc.nweload | dpc.nweload | 1.8 | 0.8 | 1.7 | 1.7 | 0.1 | N |  |  | OP | X | 12 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1975 | petroleum | TRUE | 13815 | Northwestern Wisconsin Elec Co | 4020 | Frederic Diesel | WI | Polk | 7 | Petroleum Liquids | IC |  | S | X | X | dpc.nweload | dpc.nweload | 1.7 | 0.8 | 1.8 | 1.8 | 0.1 | N |  |  | OP | X | 9 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage2000 | petroleum | TRUE | 13815 | Northwestern Wisconsin Elec Co | 4020 | Frederic Diesel | WI | Polk | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.6 | 0.1 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage2000 | petroleum | TRUE | 13815 | Northwestern Wisconsin Elec Co | 4020 | Frederic Diesel | WI | Polk | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.6 | 0.1 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1995 | petroleum | TRUE | 13815 | Northwestern Wisconsin Elec Co | 4021 | Grantsburg Diesel | WI | Burnett | 1A | Petroleum Liquids | IC |  | S | X | X | nsp.nweload | nsp.nweload | 0.7 | 0.8 | 0.8 | 0.8 | 0.1 | N |  |  | OP | X | 3 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1963 | petroleum | TRUE | 13815 | Northwestern Wisconsin Elec Co | 4021 | Grantsburg Diesel | WI | Burnett | 2 | Petroleum Liquids | IC |  | S | X | X | nsp.nweload | sp.nweload | 0.7 | 0.8 | 0.8 | 0.8 | 0.1 | N |  |  | OP | X | 12 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1968 | petroleum | TRUE | 13815 | Northwestern Wisconsin Elec Co | 4021 | Grantsburg Diesel | WI | Burnett | 3 | Petroleum Liquids | IC |  | S | X | X | nsp.nweload | nsp.nweload | 1 | 0.8 | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 11 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1975 | petroleum | TRUE | 13815 | Northwestern Wisconsin Elec Co | 4021 | Grantsburg Diesel | WI | Burnett | 4 | Petroleum Liquids | IC |  | S | X | X | nsp.nweload | nsp.nweload | 2.2 | 0.8 | 2 | 2 | 0.1 | N |  |  | OP | X | 9 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage2007 | petroleum | TRUE | 13815 | Northwestern Wisconsin Elec Co | 4021 | Grantsburg Diesel | WI | Burnett | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.1 | N |  |  | OP | X | 6 | 2007 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage2008 | natural gas combined cycle | TRUE | 20847 | Wisconsin Electric Power Co | 4040 | Port Washington Generating Station | WI | Ozaukee | 1CT1 | Natural Gas Fired Combined Cycle | CT | PWG1 | W | X | N | WEC.PORTWA1CT1 | WEC.PORTWA1CT1 | 167.9 | 0.85 | 178.2 | 207 | 77.9 | N |  |  | OP | X | 5 | 2008 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2008 | natural gas combined cycle | TRUE | 20847 | Wisconsin Electric Power Co | 4040 | Port Washington Generating Station | WI | Ozaukee | 1CT2 | Natural Gas Fired Combined Cycle | CT | PWG1 | W | X | N | WEC.PORTWA1CT2 | WEC.PORTWA1CT2 | 167.9 | 0.85 | 178.8 | 207 | 77.9 | N |  |  | OP | X | 5 | 2008 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2005 | natural gas combined cycle | TRUE | 20847 | Wisconsin Electric Power Co | 4040 | Port Washington Generating Station | WI | Ozaukee | 2CT1 | Natural Gas Fired Combined Cycle | CT | PWG2 | W | X | N | WEC.PORTWCT1 | WEC.PORTWCT1 | 167.9 | 0.85 | 178.3 | 207 | 77.9 | N |  |  | OP | X | 7 | 2005 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2005 | natural gas combined cycle | TRUE | 20847 | Wisconsin Electric Power Co | 4040 | Port Washington Generating Station | WI | Ozaukee | 2CT2 | Natural Gas Fired Combined Cycle | CT | PWG2 | W | X | N | WEC.PORTWCT2 | WEC.PORTWCT2 | 167.9 | 0.85 | 179.2 | 207 | 77.9 | N |  |  | OP | X | 7 | 2005 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2008 | natural gas combined cycle | TRUE | 20847 | Wisconsin Electric Power Co | 4040 | Port Washington Generating Station | WI | Ozaukee | ST1 | Natural Gas Fired Combined Cycle | CA | PWG1 | W | Y | X | WEC.PORTWA1ST0 | WEC.PORTWA1ST0 | 268.6 | 0.85 | 265.1 | 265.2 | 124.2 | N |  |  | OP | X | 5 | 2008 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2005 | natural gas combined cycle | TRUE | 20847 | Wisconsin Electric Power Co | 4040 | Port Washington Generating Station | WI | Ozaukee | ST2 | Natural Gas Fired Combined Cycle | CA | PWG2 | W | Y | X | WEC.PORTWST1 | WEC.PORTWST1 | 268.6 | 0.85 | 266.2 | 265.6 | 124.2 | N |  |  | OP | X | 7 | 2005 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1959 | hard coal | TRUE | 20847 | Wisconsin Electric Power Co | 4041 | South Oak Creek | WI | Milwaukee | 5 | Conventional Steam Coal | ST |  | S | X | X | WEC.OAKCREKC5 | WEC.OAKCREKC5 | 299.2 | 0.85 | 242.2 | 242.2 | 80 | N |  |  | OP | X | 12 | 1959 | 5 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: NG; DFO DFO DFO: SUB; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1961 | hard coal | TRUE | 20847 | Wisconsin Electric Power Co | 4041 | South Oak Creek | WI | Milwaukee | 6 | Conventional Steam Coal | ST |  | S | X | X | WEC.OKCGC6 | WEC.OKCGC6 | 299.2 | 0.85 | 253.8 | 253.8 | 80 | N |  |  | OP | X | 12 | 1961 | 5 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: NG; DFO DFO DFO: SUB; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1965 | hard coal | TRUE | 20847 | Wisconsin Electric Power Co | 4041 | South Oak Creek | WI | Milwaukee | 7 | Conventional Steam Coal | ST |  | S | X | X | WEC.OKCGC7 | WEC.OKCGC7 | 317.6 | 0.9 | 306.5 | 309.3 | 80 | N |  |  | OP | X | 3 | 1965 | 5 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: NG; DFO DFO DFO: SUB; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | N | [17 empty] | N | N | N
Vintage1967 | hard coal | TRUE | 20847 | Wisconsin Electric Power Co | 4041 | South Oak Creek | WI | Milwaukee | 8 | Conventional Steam Coal | ST |  | S | X | X | WEC.OKCGC8 | WEC.OKCGC8 | 324 | 0.9 | 309.5 | 312.7 | 80 | N |  |  | OP | X | 10 | 1967 | 5 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: NG; DFO DFO DFO: SUB; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | N | [17 empty] | N | N | N
Vintage1968 | natural gas steam turbine | TRUE | 20847 | Wisconsin Electric Power Co | 4042 | Valley (WI) | WI | Milwaukee | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | WEC.VALLYGA1 | WEC.VALLYGA1 | 136 | 0.85 | 125.7 | 89.2 | 20 | N |  |  | OP | X | 6 | 1968 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | OVER | [5 empty] | N | [17 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1969 | natural gas steam turbine | TRUE | 20847 | Wisconsin Electric Power Co | 4042 | Valley (WI) | WI | Milwaukee | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | WEC.VALLYGA2 | WEC.VALLYGA2 | 136 | 0.85 | 140 | 140.9 | 20 | N |  |  | OP | X | 3 | 1969 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | OVER | [5 empty] | N | [17 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1969 | petroleum | TRUE | 20847 | Wisconsin Electric Power Co | 4042 | Valley (WI) | WI | Milwaukee | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2.7 | 2.7 | 1 | N |  |  | SB | Y | 3 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1980 | hydro | TRUE | 20847 | Wisconsin Electric Power Co | 4043 | Appleton | WI | Outagamie | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 0.1 | N |  |  | OP | X | 7 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1916 | hydro | TRUE | 20847 | Wisconsin Electric Power Co | 4043 | Appleton | WI | Outagamie | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 8 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1916 | hydro | TRUE | 20847 | Wisconsin Electric Power Co | 4043 | Appleton | WI | Outagamie | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 8 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1924 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 4044 | Oconto Falls Upper | WI | Oconto | 1 | Conventional Hydroelectric | HY |  | W | X | X | WEC.OCONTOFL |  | 0.4 | 1 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 1 | 1924 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1921 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 4044 | Oconto Falls Upper | WI | Oconto | 2 | Conventional Hydroelectric | HY |  | W | X | X | WEC.OCONTOFL |  | 0.4 | 1 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 1 | 1921 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1918 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 4044 | Oconto Falls Upper | WI | Oconto | 3 | Conventional Hydroelectric | HY |  | W | X | X | WEC.OCONTOFL |  | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 1 | 1918 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1922 | hydro | TRUE | 20847 | Wisconsin Electric Power Co | 4045 | Pine | WI | Florence | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0 | N |  |  | OP | X | 7 | 1922 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1922 | hydro | TRUE | 20847 | Wisconsin Electric Power Co | 4045 | Pine | WI | Florence | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0 | N |  |  | OP | X | 6 | 1922 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1970 | nuclear | TRUE | 55906 | NextEra Energy Point Beach LLC | 4046 | Point Beach Nuclear Plant | WI | Manitowoc | 1 | Nuclear | ST |  | S | X | X | WEC.PTBHGB1 | WEC.PTBHGB1 | 643 | 0.94 | 593.5 | 591.2 | 150 | N |  |  | OP | X | 12 | 1970 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  | N | N | 0 | OVER | [23 empty] | N
Vintage1972 | nuclear | TRUE | 55906 | NextEra Energy Point Beach LLC | 4046 | Point Beach Nuclear Plant | WI | Manitowoc | 2 | Nuclear | ST |  | S | X | X | WEC.PTBHGB2 | WEC.PTBHGB2 | 643 | 0.94 | 599.2 | 598.9 | 150 | N |  |  | OP | X | 10 | 1972 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N
Vintage1969 | petroleum | TRUE | 55906 | NextEra Energy Point Beach LLC | 4046 | Point Beach Nuclear Plant | WI | Manitowoc | 5 | Petroleum Liquids | GT |  | S | X | X | WEC.PTBEACB5 | WEC.PTBEACB5 | 25 | 0.85 | 15 | 18 | 4 | N |  |  | OP | X | 6 | 1969 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N
Vintage1985 | hard coal | TRUE | 20856 | Wisconsin Power & Light Co | 4050 | Edgewater | WI | Sheboygan | 5 | Conventional Steam Coal | ST |  | S | X | X | ALTE.EDG5G5 | ALTE.EDG5G5 | 413.7 | 0.9 | 405.3 | 406.7 | 85 | N |  |  | OP | X | 3 | 1985 | 6 | 2025 | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | N |  |  | N | N | N
Vintage1939 | hydro | TRUE | 20856 | Wisconsin Power & Light Co | 4053 | Kilbourn | WI | Columbia | 2 | Conventional Hydroelectric | HY | B059 | S | X | X | ALTE.KILBOUNIL | ALTE.KILBOUNIL | 2.5 | 0.83 | 9.5 | 9.5 | 0.5 | N |  |  | OP | X | 7 | 1939 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [20 empty] | N |  |  | N
Vintage1926 | hydro | TRUE | 20856 | Wisconsin Power & Light Co | 4053 | Kilbourn | WI | Columbia | HC1 | Conventional Hydroelectric | HY | B059 | S | X | X | ALTE.KILBOUNIL | ALTE.KILBOUNIL | 2.2 | 0.83 |  |  | 0.4 | N |  |  | OP | X | 7 | 1926 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [20 empty] | N |  |  | N
Vintage1935 | hydro | TRUE | 20856 | Wisconsin Power & Light Co | 4053 | Kilbourn | WI | Columbia | HC5 | Conventional Hydroelectric | HY | B059 | S | X | X | ALTE.KILBOUNIL | ALTE.KILBOUNIL | 2.5 | 0.83 |  |  | 0.5 | N |  |  | OP | X | 7 | 1935 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [20 empty] | N |  |  | N
Vintage1937 | hydro | TRUE | 20856 | Wisconsin Power & Light Co | 4053 | Kilbourn | WI | Columbia | HC6 | Conventional Hydroelectric | HY | B059 | S | X | X | ALTE.KILBOUNIL | ALTE.KILBOUNIL | 2.5 | 0.83 |  |  | 0.5 | N |  |  | OP | X | 7 | 1937 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  | N | 0 | 1H | [20 empty] | N |  |  | N
Vintage1915 | hydro | TRUE | 20856 | Wisconsin Power & Light Co | 4056 | Prairie Du Sac | WI | Sauk | 1 | Conventional Hydroelectric | HY | B061 | S | X | X | ALTE.PDSG1S1 | ALTE.PDSG1S1 | 3.5 | 0.8 | 29 | 29 | 0.7 | N |  |  | OP | X | 10 | 1915 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [20 empty] | N
Vintage1915 | hydro | TRUE | 20856 | Wisconsin Power & Light Co | 4056 | Prairie Du Sac | WI | Sauk | 2 | Conventional Hydroelectric | HY | B061 | S | X | X |  |  | 4.3 | 0.8 |  |  | 0.9 | N |  |  | OP | X | 12 | 1915 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [20 empty] | N
Vintage1920 | hydro | TRUE | 20856 | Wisconsin Power & Light Co | 4056 | Prairie Du Sac | WI | Sauk | 3 | Conventional Hydroelectric | HY | B061 | S | X | X |  |  | 4.8 | 0.8 |  |  | 1 | N |  |  | OP | X | 3 | 1920 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [20 empty] | N
Vintage1922 | hydro | TRUE | 20856 | Wisconsin Power & Light Co | 4056 | Prairie Du Sac | WI | Sauk | 4 | Conventional Hydroelectric | HY | B061 | S | X | X |  |  | 4.8 | 0.8 |  |  | 1 | N |  |  | OP | X | 2 | 1922 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [20 empty] | N
Vintage1938 | hydro | TRUE | 20856 | Wisconsin Power & Light Co | 4056 | Prairie Du Sac | WI | Sauk | 5 | Conventional Hydroelectric | HY | B061 | S | X | X |  |  | 4 | 0.8 |  |  | 0.7 | N |  |  | OP | X | 3 | 1938 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [20 empty] | N
Vintage1938 | hydro | TRUE | 20856 | Wisconsin Power & Light Co | 4056 | Prairie Du Sac | WI | Sauk | 6 | Conventional Hydroelectric | HY | B061 | S | X | X |  |  | 4 | 0.8 |  |  | 0.7 | N |  |  | OP | X | 3 | 1938 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [20 empty] | N
Vintage1940 | hydro | TRUE | 20856 | Wisconsin Power & Light Co | 4056 | Prairie Du Sac | WI | Sauk | 7 | Conventional Hydroelectric | HY | B061 | S | X | X |  |  | 4 | 0.8 |  |  | 0.7 | N |  |  | OP | X | 11 | 1940 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [20 empty] | N
Vintage1940 | hydro | TRUE | 20856 | Wisconsin Power & Light Co | 4056 | Prairie Du Sac | WI | Sauk | 8 | Conventional Hydroelectric | HY | B061 | S | X | X |  |  | 4 | 0.8 |  |  | 0.7 | N |  |  | OP | X | 10 | 1940 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [20 empty] | N
Vintage1925 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4060 | Alexander | WI | Lincoln | 1 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 1.4 | 0.8 | 1.4 | 1.4 | 0 | N |  |  | OP | X | 1 | 1925 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [20 empty] | N |  |  | N
Vintage1925 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4060 | Alexander | WI | Lincoln | 2 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 1.4 | 0.8 | 1.4 | 1.4 | 0 | N |  |  | OP | X | 1 | 1925 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [20 empty] | N |  |  | N
Vintage1925 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4060 | Alexander | WI | Lincoln | 3 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 1.4 | 0.8 | 1.4 | 1.4 | 0 | N |  |  | OP | X | 1 | 1925 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1924 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4061 | Caldron Falls | WI | Marinette | 1 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 3.2 | 0.85 | 3.2 | 3.2 | 0 | N |  |  | OP | X | 11 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [20 empty] | N |  |  | N
Vintage1924 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4061 | Caldron Falls | WI | Marinette | 2 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 3.2 | 0.85 | 3.2 | 3.2 | 0 | N |  |  | OP | X | 11 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1938 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4063 | Grandfather Falls | WI | Lincoln | 1 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 11 | 0.8 | 11 | 11 | 0 | N |  |  | OP | X | 12 | 1938 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [20 empty] | N |  |  | N
Vintage1938 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4063 | Grandfather Falls | WI | Lincoln | 2 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 6.2 | 0.8 | 6.2 | 6.2 | 0 | N |  |  | OP | X | 12 | 1938 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1923 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4064 | Hat Rapids | WI | Oneida | 1 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 0.8 | 1 | 0.8 | 0.8 | 0 | N |  |  | OP | X | 6 | 1923 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [20 empty] | N |  |  | N
Vintage1984 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4064 | Hat Rapids | WI | Oneida | 2A | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 0.5 | 1 | 0.5 | 0.5 | 0 | N |  |  | OP | X | 10 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1984 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4064 | Hat Rapids | WI | Oneida | 3A | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 0.4 | 1 | 0.4 | 0.4 | 0 | N |  |  | OP | X | 9 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1910 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4065 | High Falls (WI) | WI | Marinette | 1 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 1.4 | 0.85 | 1.4 | 1.4 | 0 | N |  |  | OP | X | 8 | 1910 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [20 empty] | N |  |  | N
Vintage1910 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4065 | High Falls (WI) | WI | Marinette | 2 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 1.4 | 0.85 | 1.4 | 1.4 | 0 | N |  |  | OP | X | 8 | 1910 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [20 empty] | N |  |  | N
Vintage1910 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4065 | High Falls (WI) | WI | Marinette | 3 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 1.4 | 0.85 | 1.4 | 1.4 | 0 | N |  |  | OP | X | 8 | 1910 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [20 empty] | N |  |  | N
Vintage1910 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4065 | High Falls (WI) | WI | Marinette | 4 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 1.4 | 0.85 | 1.4 | 1.4 | 0 | N |  |  | OP | X | 8 | 1910 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1910 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4065 | High Falls (WI) | WI | Marinette | 5 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 1.4 | 0.85 | 1.4 | 1.4 | 0 | N |  |  | OP | X | 8 | 1910 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [20 empty] | N |  |  | N
Vintage1923 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4067 | Johnson Falls | WI | Marinette | 1 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 1.7 | 0.85 | 1.7 | 1.7 | 0 | N |  |  | OP | X | 7 | 1923 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [20 empty] | N |  |  | N
Vintage1923 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4067 | Johnson Falls | WI | Marinette | 2 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 1.7 | 0.85 | 1.7 | 1.7 | 0 | N |  |  | OP | X | 7 | 1923 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1917 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4068 | Merrill | WI | Lincoln | 1 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 0.4 | 0.8 | 0.4 | 0.4 | 0 | N |  |  | OP | X | 3 | 1917 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [20 empty] | N |  |  | N
Vintage1917 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4068 | Merrill | WI | Lincoln | 2 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 0.4 | 0.8 | 0.4 | 0.4 | 0 | N |  |  | OP | X | 3 | 1917 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [20 empty] | N |  |  | N
Vintage1984 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4068 | Merrill | WI | Lincoln | 3 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 1.5 | 0.8 | 1.5 | 1.5 | 0 | N |  |  | OP | X | 6 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1926 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4071 | Potato Rapids | WI | Marinette | 1 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 0.5 | 0.8 | 0.5 | 0.5 | 0 | N |  |  | OP | X | 6 | 1926 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [20 empty] | N |  |  | N
Vintage1921 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4071 | Potato Rapids | WI | Marinette | 2 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 0.4 | 0.85 | 0.4 | 0.4 | 0 | N |  |  | OP | X | 5 | 1921 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [20 empty] | N |  |  | N
Vintage1921 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4071 | Potato Rapids | WI | Marinette | 3 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 0.4 | 0.85 | 0.4 | 0.4 | 0 | N |  |  | OP | X | 5 | 1921 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage2003 | natural gas peaker | TRUE | 20860 | Wisconsin Public Service Corp | 4072 | Pulliam | WI | Brown | 31 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | WPS.PULLIAM31 | WPS.PULLIAM31 | 91 | 0.85 | 79 | 105.9 | 55 | N |  |  | OP | X | 5 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H |  | N |  |  | N | [15 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1925 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4074 | Sandstone Rapids | WI | Marinette | 1 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 1.9 | 0.85 | 1.9 | 1.9 | 0 | N |  |  | OP | X | 1 | 1925 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [20 empty] | N |  |  | N
Vintage1925 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4074 | Sandstone Rapids | WI | Marinette | 2 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 1.9 | 0.85 | 1.9 | 1.9 | 0 | N |  |  | OP | X | 1 | 1925 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1938 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4075 | Tomahawk | WI | Lincoln | 1 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 1.3 | 0.8 | 1.3 | 1.3 | 0 | N |  |  | OP | X | 1 | 1938 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [20 empty] | N |  |  | N
Vintage1938 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4075 | Tomahawk | WI | Lincoln | 2 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 1.3 | 0.8 | 1.3 | 1.3 | 0 | N |  |  | OP | X | 1 | 1938 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1971 | natural gas peaker | TRUE | 20860 | Wisconsin Public Service Corp | 4076 | West Marinette | WI | Marinette | 31 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | WPS.WEM31 | WPS.WEM31 | 41.8 | 0.9 | 38.1 | 49.8 | 16 | N |  |  | OP | X | 6 | 1971 | 5 | 2024 | N | Electric Utility | 1 | [11 empty] | N |  |  | 10M | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1973 | natural gas peaker | TRUE | 20860 | Wisconsin Public Service Corp | 4076 | West Marinette | WI | Marinette | 32 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | WPS.WEM32 | WPS.WEM32 | 41.8 | 0.9 | 36.7 | 47.9 | 16 | N |  |  | OP | X | 4 | 1973 | 5 | 2024 | N | Electric Utility | 1 | [11 empty] | N |  |  | 10M | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1993 | natural gas peaker | TRUE | 20860 | Wisconsin Public Service Corp | 4076 | West Marinette | WI | Marinette | 33 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | WPS.WEM33 | WPS.WEM33 | 103.5 | 0.9 | 79.1 | 105.9 | 55 | N |  |  | OP | X | 5 | 1993 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1921 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4077 | Wausau | WI | Marathon | 1 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 1.8 | 0.8 | 1.8 | 1.8 | 0 | N |  |  | OP | X | 3 | 1921 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [20 empty] | N |  |  | N
Vintage1921 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4077 | Wausau | WI | Marathon | 2 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 1.8 | 0.8 | 1.8 | 1.8 | 0 | N |  |  | OP | X | 5 | 1921 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [20 empty] | N |  |  | N
Vintage1924 | hydro | TRUE | 20860 | Wisconsin Public Service Corp | 4077 | Wausau | WI | Marathon | 3 | Conventional Hydroelectric | HY |  | S | X | X | WPS.WPSM | WPS.WPSM | 1.8 | 0.8 | 1.8 | 1.8 | 0 | N |  |  | OP | X | 3 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1960 | natural gas steam turbine | TRUE | 20860 | Wisconsin Public Service Corp | 4078 | Weston | WI | Marathon | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | WPS.WESTON2 | WPS.WESTON2 | 81.6 | 0.85 | 75.4 | 80.3 | 24 | N |  |  | OA | X | 9 | 1960 | 1 | 2023 | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H |  | N |  |  | N | [15 empty] | N |  |  | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1981 | hard coal | TRUE | 20860 | Wisconsin Public Service Corp | 4078 | Weston | WI | Marathon | 3 | Conventional Steam Coal | ST |  | S | X | X | WPS.WESTON3 | WPS.WESTON3 | 350.5 | 0.9 | 338.7 | 342.5 | 70 | N |  |  | OP | X | 12 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: SUB; DFO DFO DFO: NG |  |  | N |  |  | OVER |  | Y |  |  | Y | [15 empty] | N |  |  | Y | Y | N
Vintage1969 | natural gas peaker | TRUE | 20860 | Wisconsin Public Service Corp | 4078 | Weston | WI | Marathon | 31 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | WPS.WESTON31 | WPS.WESTON31 | 19.6 | 0.85 | 16.1 | 24.2 | 4 | N |  |  | OP | X | 3 | 1969 | 5 | 2023 | N | Electric Utility | 1 | [11 empty] | N |  |  | 10M | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1973 | natural gas peaker | TRUE | 20860 | Wisconsin Public Service Corp | 4078 | Weston | WI | Marathon | 32 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | WPS.WESTON32 | WPS.WESTON32 | 56.7 | 0.9 | 46.5 | 63.7 | 19.4 | N |  |  | OP | X | 6 | 1973 | 5 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage2008 | hard coal | TRUE | 20860 | Wisconsin Public Service Corp | 4078 | Weston | WI | Marathon | 4 | Conventional Steam Coal | ST |  | J | X | X | WPS.WESTON4 | WPS.WESTON4 | 595 | 0.85 | 549.8 | 558.5 | 263 | N |  |  | OP | X | 7 | 2008 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: SUB; DFO DFO DFO: NG |  |  | N |  |  | OVER |  | Y |  |  |  | Y | [14 empty] | N |  |  | Y | Y | N
Vintage1951 | hydro | TRUE | 20863 | Wisconsin River Power Company | 4079 | Castle Rock | WI | Adams | 1 | Conventional Hydroelectric | HY |  | J | X | X | WPS.WPSM(50%)/ALTE.ALTE(50%) | WPS.WPSM(50%)/ALTE.ALTE(50%) | 3 | 0.8 | 2.8 | 2.8 | 0 | N |  |  | OP | X | 8 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [20 empty] | N |  |  | N
Vintage1950 | hydro | TRUE | 20863 | Wisconsin River Power Company | 4079 | Castle Rock | WI | Adams | 2 | Conventional Hydroelectric | HY |  | J | X | X | WPS.WPSM(50%)/ALTE.ALTE(50%) | WPS.WPSM(50%)/ALTE.ALTE(50%) | 3 | 0.8 | 2.8 | 2.8 | 0 | N |  |  | OP | X | 11 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [20 empty] | N |  |  | N
Vintage1950 | hydro | TRUE | 20863 | Wisconsin River Power Company | 4079 | Castle Rock | WI | Adams | 3 | Conventional Hydroelectric | HY |  | J | X | X | WPS.WPSM(50%)/ALTE.ALTE(50%) | WPS.WPSM(50%)/ALTE.ALTE(50%) | 3 | 0.8 | 2.8 | 2.8 | 0 | N |  |  | OP | X | 10 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [20 empty] | N |  |  | N
Vintage1950 | hydro | TRUE | 20863 | Wisconsin River Power Company | 4079 | Castle Rock | WI | Adams | 4 | Conventional Hydroelectric | HY |  | J | X | X | WPS.WPSM(50%)/ALTE.ALTE(50%) | WPS.WPSM(50%)/ALTE.ALTE(50%) | 3 | 0.8 | 2.8 | 2.8 | 0 | N |  |  | OP | X | 8 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [20 empty] | N |  |  | N
Vintage1950 | hydro | TRUE | 20863 | Wisconsin River Power Company | 4079 | Castle Rock | WI | Adams | 5 | Conventional Hydroelectric | HY |  | J | X | X | WPS.WPSM(50%)/ALTE.ALTE(50%) | WPS.WPSM(50%)/ALTE.ALTE(50%) | 3 | 0.8 | 2.8 | 2.8 | 0 | N |  |  | OP | X | 8 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [20 empty] | N |  |  | N
Vintage1949 | hydro | TRUE | 20863 | Wisconsin River Power Company | 4080 | Petenwell | WI | Juneau | 1 | Conventional Hydroelectric | HY |  | J | X | X | WPS.WPSM(50%)/ALTE.ALTE(50%) | WPS.WPSM(50%)/ALTE.ALTE(50%) | 5 | 0.8 | 5 | 5 | 0 | N |  |  | OP | X | 8 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1949 | hydro | TRUE | 20863 | Wisconsin River Power Company | 4080 | Petenwell | WI | Juneau | 2 | Conventional Hydroelectric | HY |  | J | X | X | WPS.WPSM(50%)/ALTE.ALTE(50%) | WPS.WPSM(50%)/ALTE.ALTE(50%) | 5 | 0.8 | 5 | 5 | 0 | N |  |  | OP | X | 10 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1949 | hydro | TRUE | 20863 | Wisconsin River Power Company | 4080 | Petenwell | WI | Juneau | 3 | Conventional Hydroelectric | HY |  | J | X | X | WPS.WPSM(50%)/ALTE.ALTE(50%) | WPS.WPSM(50%)/ALTE.ALTE(50%) | 5 | 0.8 | 5 | 5 | 0 | N |  |  | OP | X | 11 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1950 | hydro | TRUE | 20863 | Wisconsin River Power Company | 4080 | Petenwell | WI | Juneau | 4 | Conventional Hydroelectric | HY |  | J | X | X | WPS.WPSM(50%)/ALTE.ALTE(50%) | WPS.WPSM(50%)/ALTE.ALTE(50%) | 5 | 0.8 | 5 | 5 | 0 | N |  |  | OP | X | 1 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1956 | petroleum | TRUE | 765 | City of Arcadia - (WI) | 4100 | Arcadia Electric | WI | Trempealeau | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 1 | N |  |  | SB | Y | 1 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage2007 | petroleum | TRUE | 765 | City of Arcadia - (WI) | 4100 | Arcadia Electric | WI | Trempealeau | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1 | N |  |  | SB | Y | 5 | 2007 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1947 | petroleum | TRUE | 765 | City of Arcadia - (WI) | 4100 | Arcadia Electric | WI | Trempealeau | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.8 | N |  |  | SB | Y | 1 | 1947 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1940 | petroleum | TRUE | 765 | City of Arcadia - (WI) | 4100 | Arcadia Electric | WI | Trempealeau | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.4 | N |  |  | SB | Y | 1 | 1940 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1930 | petroleum | TRUE | 765 | City of Arcadia - (WI) | 4100 | Arcadia Electric | WI | Trempealeau | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0.2 | N |  |  | SB | Y | 1 | 1930 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1972 | natural gas peaker | TRUE | 765 | City of Arcadia - (WI) | 4100 | Arcadia Electric | WI | Trempealeau | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 2 | N |  |  | SB | Y | 9 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1987 | natural gas peaker | TRUE | 765 | City of Arcadia - (WI) | 4100 | Arcadia Electric | WI | Trempealeau | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 2 | N |  |  | SB | Y | 9 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage2002 | petroleum | TRUE | 765 | City of Arcadia - (WI) | 4100 | Arcadia Electric | WI | Trempealeau | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1 | N |  |  | SB | Y | 5 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage2002 | petroleum | TRUE | 765 | City of Arcadia - (WI) | 4100 | Arcadia Electric | WI | Trempealeau | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1 | N |  |  | SB | Y | 5 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage2002 | petroleum | TRUE | 765 | City of Arcadia - (WI) | 4100 | Arcadia Electric | WI | Trempealeau | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1 | N |  |  | SB | Y | 11 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1998 | petroleum | TRUE | 1278 | City of Barron - (WI) | 4102 | Barron | WI | Barron | 1A | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.5 | N |  |  | SB | Y | 6 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1998 | petroleum | TRUE | 1278 | City of Barron - (WI) | 4102 | Barron | WI | Barron | 2A | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.5 | N |  |  | SB | Y | 6 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1998 | petroleum | TRUE | 1278 | City of Barron - (WI) | 4102 | Barron | WI | Barron | 3A | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.5 | N |  |  | SB | Y | 6 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1998 | petroleum | TRUE | 1278 | City of Barron - (WI) | 4102 | Barron | WI | Barron | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.5 | N |  |  | SB | Y | 6 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1944 | petroleum | TRUE | 1278 | City of Barron - (WI) | 4102 | Barron | WI | Barron | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.6 | 0.6 | 0.4 | N |  |  | OS | X | 3 | 1944 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1954 | petroleum | TRUE | 1278 | City of Barron - (WI) | 4102 | Barron | WI | Barron | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 0.6 | N |  |  | SB | Y | 3 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1960 | petroleum | TRUE | 1278 | City of Barron - (WI) | 4102 | Barron | WI | Barron | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.8 | N |  |  | SB | Y | 3 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1923 | hydro | TRUE | 1278 | City of Barron - (WI) | 4102 | Barron | WI | Barron | H2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 8 | 1923 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1932 | petroleum | TRUE | 3156 | Village of Cashton - (WI) | 4107 | Cashton | WI | Monroe | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.4 | N |  |  | OP | X | 8 | 1932 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1970 | natural gas peaker | TRUE | 3156 | Village of Cashton - (WI) | 4107 | Cashton | WI | Monroe | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 1.1 | N |  |  | OP | X | 1 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | petroleum | TRUE | 3156 | Village of Cashton - (WI) | 4107 | Cashton | WI | Monroe | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1.5 | N |  |  | OP | X | 1 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1945 | petroleum | TRUE | 4627 | City of Cumberland - (WI) | 4112 | Cumberland (WI) | WI | Barron | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.7 | 0.8 | 0.7 | 0.7 | 0.6 | N |  |  | OP | X | 2 | 1945 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO DFO DFO: DFO |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1939 | petroleum | TRUE | 4627 | City of Cumberland - (WI) | 4112 | Cumberland (WI) | WI | Barron | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.2 | N |  |  | OP | X | 8 | 1939 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO DFO DFO: DFO |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1939 | petroleum | TRUE | 4627 | City of Cumberland - (WI) | 4112 | Cumberland (WI) | WI | Barron | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.2 | N |  |  | OP | X | 8 | 1939 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO DFO DFO: DFO |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1954 | petroleum | TRUE | 4627 | City of Cumberland - (WI) | 4112 | Cumberland (WI) | WI | Barron | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.2 | 1.2 | 1.2 | N |  |  | OP | X | 5 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO DFO DFO: DFO |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1966 | natural gas peaker | TRUE | 4627 | City of Cumberland - (WI) | 4112 | Cumberland (WI) | WI | Barron | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2 | 0.8 | 2.1 | 2.1 | 2 | N |  |  | OP | X | 7 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1979 | petroleum | TRUE | 4627 | City of Cumberland - (WI) | 4112 | Cumberland (WI) | WI | Barron | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 7.2 | 1 | 6.7 | 6.7 | 6.7 | N |  |  | OP | X | 4 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO DFO DFO: DFO |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage2001 | natural gas peaker | TRUE | 4627 | City of Cumberland - (WI) | 4112 | Cumberland (WI) | WI | Barron | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 6.6 | 0.9 | 6.2 | 6.2 | 6.2 | N |  |  | OP | X | 11 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2001 | natural gas peaker | TRUE | 4627 | City of Cumberland - (WI) | 4112 | Cumberland (WI) | WI | Barron | 8 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.5 | 0.8 | 3.5 | 3.5 | 3.5 | N |  |  | OP | X | 12 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2005 | petroleum | TRUE | 5834 | City of Elroy - (WI) | 4113 | Elroy | WI | Juneau | 1A | Petroleum Liquids | IC |  | S | X | X | BTM |  | 2.3 | 1 | 2.2 | 2.3 | 0.5 | N |  |  | OP | X | 2 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2005 | petroleum | TRUE | 5834 | City of Elroy - (WI) | 4113 | Elroy | WI | Juneau | 2A | Petroleum Liquids | IC |  | S | X | X | BTM |  | 2.3 | 1 | 2.2 | 2.3 | 0.5 | N |  |  | OP | X | 2 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1973 | petroleum | TRUE | 5834 | City of Elroy - (WI) | 4113 | Elroy | WI | Juneau | 5 | Petroleum Liquids | IC |  | S | X | X | BTM |  | 2 | 1 | 2.2 | 2.2 | 0.5 | N |  |  | OP | X | 5 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1964 | petroleum | TRUE | 6274 | City of Fennimore - (WI) | 4114 | Fennimore | WI | Grant | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.5 | N |  |  | SB | Y | 2 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1952 | petroleum | TRUE | 6274 | City of Fennimore - (WI) | 4114 | Fennimore | WI | Grant | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.9 | 0.9 | 0.5 | N |  |  | SB | Y | 2 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 6274 | City of Fennimore - (WI) | 4114 | Fennimore | WI | Grant | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | SB | Y | 12 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 6274 | City of Fennimore - (WI) | 4114 | Fennimore | WI | Grant | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | SB | Y | 12 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 6274 | City of Fennimore - (WI) | 4114 | Fennimore | WI | Grant | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | SB | Y | 12 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1969 | natural gas peaker | TRUE | 10056 | City of Kaukauna | 4118 | Kaukauna Gas Turbine | WI | Outagamie | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 18 | 0.9 | 15.8 | 18.3 | 2 | N |  |  | OP | X | 5 | 1969 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: X X X to DFO RC RC
Vintage1948 | hydro | TRUE | 10056 | City of Kaukauna | 4119 | Little Chute | WI | Outagamie | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.1 | 0.9 | 1.1 | 1.1 | 0.2 | N |  |  | OP | X | 6 | 1948 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1948 | hydro | TRUE | 10056 | City of Kaukauna | 4119 | Little Chute | WI | Outagamie | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.1 | 0.9 | 1.1 | 1.1 | 0.2 | N |  |  | OP | X | 6 | 1948 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1948 | hydro | TRUE | 10056 | City of Kaukauna | 4119 | Little Chute | WI | Outagamie | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.1 | 0.9 | 1.1 | 1.1 | 0.2 | N |  |  | OP | X | 6 | 1948 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage2014 | hydro | TRUE | 10056 | City of Kaukauna | 4120 | New Badger | WI | Outagamie | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.1 | 1 | 4 | 4 | 0.5 | N |  |  | OP | X | 1 | 2014 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M | [23 empty] | N
Vintage2014 | hydro | TRUE | 10056 | City of Kaukauna | 4120 | New Badger | WI | Outagamie | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.1 | 1 | 4 | 4 | 0.5 | N |  |  | OP | X | 1 | 2014 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M | [23 empty] | N
Vintage1926 | hydro | TRUE | 10056 | City of Kaukauna | 4122 | Rapide Croche | WI | Outagamie | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.9 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 1 | 1926 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H | [23 empty] | N
Vintage1926 | hydro | TRUE | 10056 | City of Kaukauna | 4122 | Rapide Croche | WI | Outagamie | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.9 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 1 | 1926 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H | [23 empty] | N
Vintage1926 | hydro | TRUE | 10056 | City of Kaukauna | 4122 | Rapide Croche | WI | Outagamie | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.9 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 1 | 1926 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H | [23 empty] | N
Vintage1926 | hydro | TRUE | 10056 | City of Kaukauna | 4122 | Rapide Croche | WI | Outagamie | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.9 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 1 | 1926 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H | [23 empty] | N
Vintage1990 | petroleum | TRUE | 10525 | La Farge Municipal Electric Co | 4124 | La Farge | WI | Vernon | 2A | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 1 | 1.5 | 1.5 | 1.4 | N |  |  | OP | X | 10 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1955 | biomass | TRUE | 11571 | Manitowoc Public Utilities | 4125 | Manitowoc | WI | Manitowoc | 5 | Wood/Wood Waste Biomass | ST |  | S | X | X | WPS.LAKEFRN95 |  | 22 | 0.8 | 22 | 22 | 6 | N |  |  | OP | X | 6 | 1955 |  |  | N | Electric Utility | 1 | X | WDS | PC | BIT | SUB |  |  | NG |  |  |  | N | N |  | 12H | Y |  |  |  | Y | [18 empty] | Y | Y
Vintage1962 | biomass | TRUE | 11571 | Manitowoc Public Utilities | 4125 | Manitowoc | WI | Manitowoc | 6 | Wood/Wood Waste Biomass | ST |  | S | X | X | WPS.LAKEFRN96 |  | 32 | 0.8 | 22 | 22 | 6 | N |  |  | OP | X | 6 | 1962 |  |  | N | Electric Utility | 1 | X | WDS | PC | BIT | SUB |  |  | NG |  |  |  | N | N |  | 12H | Y |  |  |  | Y | [18 empty] | Y | Y
Vintage2007 | petroleum | TRUE | 11571 | Manitowoc Public Utilities | 4125 | Manitowoc | WI | Manitowoc | 9 | Petroleum Coke | ST |  | S | X | X | WPS.LAKEFRN99 |  | 63.4 | 0.8 | 58.4 | 58.4 | 14 | N |  |  | OP | X | 4 | 2007 |  |  | Y | Electric Utility | 1 | T | PC | WDS | BIT | SUB |  |  | NG |  |  |  | N | N |  | OVER | Y |  |  |  | Y | [18 empty] | Y | Y | N
Vintage1966 | petroleum | TRUE | 13466 | City of New Lisbon | 4130 | New Lisbon | WI | Juneau | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.2 | 1.2 | 1.1 | N |  |  | OP | X | 1 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 12H | [23 empty] | N
Vintage1977 | petroleum | TRUE | 13466 | City of New Lisbon | 4130 | New Lisbon | WI | Juneau | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.4 | 0.8 | 2.4 | 2.4 | 2.3 | N |  |  | OP | X | 1 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 12H | [23 empty] | N
Vintage2005 | petroleum | TRUE | 13466 | City of New Lisbon | 4130 | New Lisbon | WI | Juneau | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.3 | 0.8 | 2 | 2.1 | 2 | N |  |  | OP | X | 7 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 12H | [23 empty] | N
Vintage2005 | petroleum | TRUE | 13466 | City of New Lisbon | 4130 | New Lisbon | WI | Juneau | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.3 | 0.8 | 2 | 2.1 | 2 | N |  |  | OP | X | 7 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 12H | [23 empty] | N
Vintage2002 | petroleum | TRUE | 19867 | Village of Viola - (WI) | 4139 | Viola | WI | Richland | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 1 | 1.8 | 1.8 | 1.7 | N |  |  | OP | X | 1 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1951 | hydro | TRUE | 4716 | Dairyland Power Coop | 4142 | Flambeau Hydroelectric Station | WI | Rusk | 1 | Conventional Hydroelectric | HY |  | S | X | X | DPC.FLAMBEAU | DPC.DPC | 7.9 | 0.8 | 8.1 | 8.1 | 0.5 | N |  |  | OP | X | 3 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1951 | hydro | TRUE | 4716 | Dairyland Power Coop | 4142 | Flambeau Hydroelectric Station | WI | Rusk | 2 | Conventional Hydroelectric | HY |  | S | X | X | DPC.FLAMBEAU | DPC.DPC | 6.2 | 0.8 | 8 | 8 | 0.5 | N |  |  | OP | X | 1 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1951 | hydro | TRUE | 4716 | Dairyland Power Coop | 4142 | Flambeau Hydroelectric Station | WI | Rusk | 3 | Conventional Hydroelectric | HY |  | S | X | X | DPC.FLAMBEAU | DPC.DPC | 7.9 | 0.8 | 8 | 8 | 0.5 | N |  |  | OP | X | 1 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1949 | hydro | TRUE | 13964 | Oconto Electric Cooperative | 4147 | Stiles | WI | Oconto | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 3 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1949 | hydro | TRUE | 13964 | Oconto Electric Cooperative | 4147 | Stiles | WI | Oconto | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 3 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M
Vintage1952 | petroleum | TRUE | 20153 | Washington Island El Coop, Inc | 4148 | Washington Island | WI | Door | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 8 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N | N | N
Vintage1945 | petroleum | TRUE | 20153 | Washington Island El Coop, Inc | 4148 | Washington Island | WI | Door | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 12 | 1945 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N | N | N
Vintage1951 | petroleum | TRUE | 20153 | Washington Island El Coop, Inc | 4148 | Washington Island | WI | Door | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0.2 | N |  |  | OP | X | 4 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N | N | N
Vintage1968 | petroleum | TRUE | 20153 | Washington Island El Coop, Inc | 4148 | Washington Island | WI | Door | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 6 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N | N | N
Vintage1972 | petroleum | TRUE | 20153 | Washington Island El Coop, Inc | 4148 | Washington Island | WI | Door | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 7 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N | N | N
Vintage1997 | petroleum | TRUE | 20153 | Washington Island El Coop, Inc | 4148 | Washington Island | WI | Door | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.1 | N |  |  | OP | X | 1 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N | N | N
Vintage1997 | petroleum | TRUE | 20153 | Washington Island El Coop, Inc | 4148 | Washington Island | WI | Door | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.1 | N |  |  | OP | X | 1 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO | [5 empty] | 1H | [23 empty] | N | N | N
Vintage1959 | hard coal | TRUE | 14354 | PacifiCorp | 4158 | Dave Johnston | WY | Converse | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 133.6 | 0.85 | 93 | 99 | 45 | N |  |  | OP | X | 2 | 1959 | 12 | 2027 | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: SUB; DFO DFO DFO: DFO; DFO DFO DFO: DFO |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1961 | hard coal | TRUE | 14354 | PacifiCorp | 4158 | Dave Johnston | WY | Converse | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 133.6 | 0.85 | 102 | 106 | 45 | N |  |  | OP | X | 1 | 1961 | 12 | 2027 | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: SUB; DFO DFO DFO: DFO; DFO DFO DFO: DFO |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1964 | hard coal | TRUE | 14354 | PacifiCorp | 4158 | Dave Johnston | WY | Converse | 3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 255 | 0.9 | 220 | 220 | 100 | N |  |  | OP | X | 12 | 1964 | 12 | 2027 | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: SUB; DFO DFO DFO: DFO; DFO DFO DFO: DFO |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1972 | hard coal | TRUE | 14354 | PacifiCorp | 4158 | Dave Johnston | WY | Converse | 4 | Conventional Steam Coal | ST |  | S | X | X |  |  | 400 | 0.9 | 330 | 330 | 125 | N |  |  | OP | X | 7 | 1972 | 12 | 2027 | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: SUB; DFO DFO DFO: DFO; DFO DFO DFO: DFO |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1963 | hard coal | TRUE | 14354 | PacifiCorp | 4162 | Naughton | WY | Lincoln | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 192 | 0.85 | 156 | 156 | 21 | N |  |  | OP | X | 5 | 1963 | 12 | 2025 | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1968 | hard coal | TRUE | 14354 | PacifiCorp | 4162 | Naughton | WY | Lincoln | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 256 | 0.85 | 201 | 201 | 28 | N |  |  | OP | X | 10 | 1968 | 12 | 2025 | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1971 | natural gas steam turbine | TRUE | 14354 | PacifiCorp | 4162 | Naughton | WY | Lincoln | 3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 384 | 0.85 | 247 | 247 | 27 | N |  |  | OP | X | 10 | 1971 | 12 | 2029 | N | Electric Utility | 1 | [11 empty] | N |  |  | OVER |  | N |  |  | N | [18 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1961 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 4176 | Fremont Canyon | WY | Natrona | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 33.4 | 0.95 | 33.4 | 33.4 | 0 | N |  |  | OP | X | 1 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1960 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 4176 | Fremont Canyon | WY | Natrona | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 33.4 | 0.95 | 33.4 | 33.4 | 0 | N |  |  | OP | X | 12 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1958 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 4177 | Glendo | WY | Platte | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 19 | 1 | 19 | 17.5 | 0 | N |  |  | OP | X | 12 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1959 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 4177 | Glendo | WY | Platte | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 19 | 1 | 19 | 19 | 0 | N |  |  | OP | X | 4 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1927 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 4178 | Guernsey | WY | Platte | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.2 | 1 | 3.2 | 2.9 | 0 | N |  |  | OP | X | 7 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1928 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 4178 | Guernsey | WY | Platte | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.2 | 1 | 3.2 | 3.2 | 0 | N |  |  | OP | X | 1 | 1928 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1951 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 4180 | Kortes | WY | Carbon | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 12 | 0.9 | 12.2 | 12.2 | 0 | N |  |  | OP | X | 1 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1950 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 4180 | Kortes | WY | Carbon | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 12 | 0.9 | 12.2 | 12.2 | 0 | N |  |  | OP | X | 8 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1950 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 4180 | Kortes | WY | Carbon | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 12 | 0.9 | 12.2 | 12.2 | 0 | N |  |  | OP | X | 6 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1939 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 4182 | Seminoe | WY | Carbon | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 17.2 | 1 | 17.2 | 17.2 | 0 | N |  |  | OP | X | 8 | 1939 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1939 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 4182 | Seminoe | WY | Carbon | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 17.2 | 1 | 17.2 | 17.2 | 0 | N |  |  | OP | X | 8 | 1939 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1939 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 4182 | Seminoe | WY | Carbon | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 17.2 | 1 | 17.2 | 17.2 | 0 | N |  |  | OP | X | 8 | 1939 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1922 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 4183 | Shoshone (WY) | WY | Park | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 1 | 3 | 3 | 0 | N |  |  | OP | X | 4 | 1922 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1968 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 4185 | Fontenelle | WY | Lincoln | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 0.91 | 11.2 | 11.2 | 0 | N |  |  | OP | X | 5 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage2010 | natural gas peaker | TRUE | 7634 | City of Greenville - (TX) | 4195 | Powerlane Plant | TX | Hunt | EP | Natural Gas Internal Combustion Engine | IC |  | S | X | X | STEAM_ENG123 | STEAM_ENG123 | 8.4 | 0.8 | 8.2 | 8.2 | 4.2 | N |  |  | OP | X | 6 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2010 | natural gas peaker | TRUE | 7634 | City of Greenville - (TX) | 4195 | Powerlane Plant | TX | Hunt | EP2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | STEAM_ENG123 | STEAM_ENG123 | 8.4 | 0.8 | 8.2 | 8.2 | 4.2 | N |  |  | OP | X | 6 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2010 | natural gas peaker | TRUE | 7634 | City of Greenville - (TX) | 4195 | Powerlane Plant | TX | Hunt | EP3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | STEAM_ENG123 | STEAM_ENG123 | 8.4 | 0.8 | 8.2 | 8.2 | 4.2 | N |  |  | OP | X | 6 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1966 | natural gas steam turbine | TRUE | 7634 | City of Greenville - (TX) | 4195 | Powerlane Plant | TX | Hunt | ST1 | Natural Gas Steam Turbine | ST |  | S | X | X | STEA_STEAM_1 | STEA_STEAM_1 | 18.8 | 0.85 | 18 | 18 | 10 | N |  |  | OP | X | 1 | 1966 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1967 | natural gas steam turbine | TRUE | 7634 | City of Greenville - (TX) | 4195 | Powerlane Plant | TX | Hunt | ST2 | Natural Gas Steam Turbine | ST |  | S | X | X | STEA_STEAM_2 | STEA_STEAM_2 | 25 | 0.85 | 23 | 23 | 10 | N |  |  | OP | X | 8 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | OVER | [23 empty] | Y | N | Y
Vintage1978 | natural gas steam turbine | TRUE | 7634 | City of Greenville - (TX) | 4195 | Powerlane Plant | TX | Hunt | ST3 | Natural Gas Steam Turbine | ST |  | S | X | X | STEA_STEAM_3 | STEA_STEAM_3 | 43.2 | 0.9 | 41 | 41 | 13 | N |  |  | OP | X | 8 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | OVER | [23 empty] | Y | N | Y
Vintage1988 | hydro | TRUE | 10056 | City of Kaukauna | 4201 | Combined Locks | WI | Outagamie | HC1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.1 | 0.9 | 3.1 | 3.1 | 0.2 | N |  |  | OA | X | 2 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M | [23 empty] | N
Vintage1988 | hydro | TRUE | 10056 | City of Kaukauna | 4201 | Combined Locks | WI | Outagamie | HC2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.1 | 0.9 | 3.1 | 3.1 | 0.2 | N |  |  | OP | X | 2 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 10M | [23 empty] | N
Vintage1994 | hydro | TRUE | 6169 | Fall River Rural Elec Coop Inc | 4204 | Island Park | ID | Fremont | HY1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.9 | 2.4 | 2.4 | 0.8 | N |  |  | OP | X | 4 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 12H | [23 empty] | N
Vintage1994 | hydro | TRUE | 6169 | Fall River Rural Elec Coop Inc | 4204 | Island Park | ID | Fremont | HY2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.9 | 2.4 | 2.4 | 0.8 | N |  |  | OP | X | 4 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 12H | [23 empty] | N
Vintage1982 | hydro | TRUE | 25835 | Portland City of | 4213 | PHP 1 | OR | Multnomah | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 23.7 | 0.95 | 24 | 24 | 12 | N |  |  | OP | X | 2 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1982 | hydro | TRUE | 25835 | Portland City of | 4214 | PHP 2 | OR | Clackamas | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 11.8 | 0.95 | 13.5 | 13.5 | 0.9 | N |  |  | OP | X | 2 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage2002 | natural gas peaker | TRUE | 11135 | City of Logan - (UT) | 4251 | Logan City | UT | Cache | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 5.3 | 0.8 | 4.5 | 5.2 | 3 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2002 | natural gas peaker | TRUE | 11135 | City of Logan - (UT) | 4251 | Logan City | UT | Cache | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 5.3 | 0.8 | 4.5 | 5.2 | 3 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2002 | natural gas peaker | TRUE | 11135 | City of Logan - (UT) | 4251 | Logan City | UT | Cache | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 5.3 | 0.8 | 4.5 | 5.2 | 3 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1986 | natural gas peaker | TRUE | 19281 | Turlock Irrigation District | 4256 | Walnut | CA | Stanislaus | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 24.9 | 0.9 | 23.5 | 24.9 | 11 | N |  |  | OP | X | 4 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 10M | [23 empty] | Y | Y | Y
Vintage1986 | natural gas peaker | TRUE | 19281 | Turlock Irrigation District | 4256 | Walnut | CA | Stanislaus | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 24.9 | 0.9 | 23.5 | 24.9 | 11 | N |  |  | OP | X | 4 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 10M | [23 empty] | Y | Y | Y
Vintage1995 | petroleum | TRUE | 5625 | Easton Utilities Comm | 4257 | Easton 2 | MD | Talbot | 201 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0 | N |  |  | OP | X | 5 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1995 | petroleum | TRUE | 5625 | Easton Utilities Comm | 4257 | Easton 2 | MD | Talbot | 202 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0 | N |  |  | OP | X | 5 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage2004 | petroleum | TRUE | 5625 | Easton Utilities Comm | 4257 | Easton 2 | MD | Talbot | 203 | Petroleum Liquids | GT |  | S | X | X |  |  | 5.4 | 0.8 | 4.5 | 5.1 | 0 | N |  |  | OP | X | 11 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage2004 | petroleum | TRUE | 5625 | Easton Utilities Comm | 4257 | Easton 2 | MD | Talbot | 204 | Petroleum Liquids | GT |  | S | X | X |  |  | 5.4 | 0.8 | 4.5 | 5.1 | 0 | N |  |  | OP | X | 11 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1978 | petroleum | TRUE | 5625 | Easton Utilities Comm | 4257 | Easton 2 | MD | Talbot | 21 | Petroleum Liquids | IC |  | S | X | X |  |  | 6.2 | 0.8 | 6.2 | 6.2 | 0 | N |  |  | OP | X | 3 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1978 | petroleum | TRUE | 5625 | Easton Utilities Comm | 4257 | Easton 2 | MD | Talbot | 22 | Petroleum Liquids | IC |  | S | X | X |  |  | 6.2 | 0.8 | 6.2 | 6.2 | 0 | N |  |  | OP | X | 3 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1989 | petroleum | TRUE | 5625 | Easton Utilities Comm | 4257 | Easton 2 | MD | Talbot | 23 | Petroleum Liquids | IC |  | S | X | X |  |  | 6.3 | 0.8 | 6.3 | 6.3 | 0 | N |  |  | OP | X | 6 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1989 | petroleum | TRUE | 5625 | Easton Utilities Comm | 4257 | Easton 2 | MD | Talbot | 24 | Petroleum Liquids | IC |  | S | X | X |  |  | 6.3 | 0.8 | 6.3 | 6.3 | 0 | N |  |  | OP | X | 6 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1982 | hydro | TRUE | 7977 | City of Hamilton - (OH) | 4258 | Greenup Hydro | OH | Scioto | 1 | Conventional Hydroelectric | HY |  | J | X | X | 112586233 |  | 23.4 | 0.98 | 23.4 | 23.4 | 1 | N |  |  | OP | X | 12 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1982 | hydro | TRUE | 7977 | City of Hamilton - (OH) | 4258 | Greenup Hydro | OH | Scioto | 2 | Conventional Hydroelectric | HY |  | J | X | X | 112586235 |  | 23.4 | 0.98 | 23.4 | 23.4 | 1 | N |  |  | OP | X | 12 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1982 | hydro | TRUE | 7977 | City of Hamilton - (OH) | 4258 | Greenup Hydro | OH | Scioto | 3 | Conventional Hydroelectric | HY |  | J | X | X | 112586237 |  | 23.4 | 0.98 | 23.4 | 23.4 | 1 | N |  |  | OP | X | 12 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1987 | hydro | TRUE | 2010 | City of Bountiful | 4263 | Echo Dam | UT | Summit | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.9 | 1 | 0.9 | 0.5 | N |  |  | OP | X | 3 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 1H | [23 empty] | N
Vintage1987 | hydro | TRUE | 2010 | City of Bountiful | 4263 | Echo Dam | UT | Summit | NA1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.7 | 0.9 | 1.7 | 1.7 | 0.5 | N |  |  | OP | X | 3 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 1H | [23 empty] | N
Vintage1987 | hydro | TRUE | 2010 | City of Bountiful | 4263 | Echo Dam | UT | Summit | NA2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.7 | 0.9 | 1.7 | 1.7 | 0.5 | N |  |  | OP | X | 3 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 1H | [23 empty] | N
Vintage1966 | natural gas steam turbine | TRUE | 6958 | City of Garland - (TX) | 4266 | Spencer | TX | Denton | 4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 61.1 | 0.9 | 61 | 61 | 10 | N |  |  | OP | X | 6 | 1966 |  |  | N | Electric Utility | 1 | [14 empty] | OVER | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1973 | natural gas steam turbine | TRUE | 6958 | City of Garland - (TX) | 4266 | Spencer | TX | Denton | 5 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 65.4 | 0.85 | 61 | 61 | 10 | N |  |  | OP | X | 5 | 1973 |  |  | N | Electric Utility | 1 | [14 empty] | OVER | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1985 | nuclear | TRUE | 11241 | Entergy Louisiana LLC | 4270 | Waterford 3 | LA | St Charles | 3 | Nuclear | ST |  | S | X | X | EES.WATRFD3 | EES.WATRFD3 | 1199.8 | 0.9 | 1165.4 | 1177 | 200 | N |  |  | OP | X | 9 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC |  |  | N |  |  | OVER | [23 empty] | N
Vintage1979 | hard coal | TRUE | 4716 | Dairyland Power Coop | 4271 | John P Madgett | WI | Buffalo | 1 | Conventional Steam Coal | ST |  | S | X | X | DPC.JPM | DPC.DPC | 387 | 0.9 | 389.8 | 392.5 | 125 | N |  |  | OP | X | 11 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage2014 | natural gas combined cycle | TRUE | 11269 | Lower Colorado River Authority | 4937 | Thomas C Ferguson | TX | Llano | CT-1 | Natural Gas Fired Combined Cycle | CT | CC1 | J | X | N | FERCCC_GT1_1 | FERCCC_GT1_1 | 185.3 | 0.85 | 168 | 181 | 95 | N |  |  | OP | X | 8 | 2014 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H |  |  |  |  | N | [15 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage2014 | natural gas combined cycle | TRUE | 11269 | Lower Colorado River Authority | 4937 | Thomas C Ferguson | TX | Llano | CT-2 | Natural Gas Fired Combined Cycle | CT | CC1 | J | X | N | FERCCC_GT1_1 | FERCCC_GT1_1 | 185.3 | 0.85 | 168 | 181 | 95 | N |  |  | OP | X | 8 | 2014 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H |  |  |  |  | N | [15 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage2014 | natural gas combined cycle | TRUE | 11269 | Lower Colorado River Authority | 4937 | Thomas C Ferguson | TX | Llano | STG | Natural Gas Fired Combined Cycle | CA | CC1 | J | N | X | FERCCC_GT1_1 | FERCCC_GT1_1 | 204 | 0.85 | 180 | 194 | 75 | N |  |  | OP | X | 8 | 2014 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1974 | natural gas steam turbine | TRUE | 49979 | Talen Texas, LLC | 4939 | Barney M Davis | TX | Nueces | 1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 352 | 0.9 | 292 | 292 | 60 | N |  |  | OP | X | 5 | 1974 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | OVER | [23 empty] | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1976 | natural gas combined cycle | TRUE | 49979 | Talen Texas, LLC | 4939 | Barney M Davis | TX | Nueces | 2 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 351 | 0.9 | 319 | 325 | 100 | N |  |  | OP | X | 7 | 1976 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2010 | natural gas combined cycle | TRUE | 49979 | Talen Texas, LLC | 4939 | Barney M Davis | TX | Nueces | 3 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 189.6 | 0.9 | 157 | 165 | 60 | N |  |  | OP | X | 3 | 2010 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2010 | natural gas combined cycle | TRUE | 49979 | Talen Texas, LLC | 4939 | Barney M Davis | TX | Nueces | 4 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 189.6 | 0.9 | 157 | 165 | 60 | N |  |  | OP | X | 3 | 2010 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1974 | natural gas steam turbine | TRUE | 15474 | Public Service Co of Oklahoma | 4940 | Riverside (OK) | OK | Tulsa | 1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 473 | 0.9 | 454 | 454 | 126 | N |  |  | OP | X | 4 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | OVER | [23 empty] | Y | Y | Y
Vintage1976 | natural gas steam turbine | TRUE | 15474 | Public Service Co of Oklahoma | 4940 | Riverside (OK) | OK | Tulsa | 2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 473 | 0.9 | 455 | 455 | 65 | N |  |  | OP | X | 5 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO; DFO DFO DFO: NG |  |  | N | N |  | OVER | [23 empty] | Y | Y | Y
Vintage2008 | natural gas peaker | TRUE | 15474 | Public Service Co of Oklahoma | 4940 | Riverside (OK) | OK | Tulsa | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 86.5 | 0.85 | 79 | 79 | 42 | N |  |  | OP | X | 3 | 2008 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2008 | natural gas peaker | TRUE | 15474 | Public Service Co of Oklahoma | 4940 | Riverside (OK) | OK | Tulsa | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 86.5 | 0.85 | 79 | 79 | 42 | N |  |  | OP | X | 3 | 2008 |  |  | N | Electric Utility | 1 | [14 empty] | 1H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1976 | petroleum | TRUE | 15474 | Public Service Co of Oklahoma | 4940 | Riverside (OK) | OK | Tulsa | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.85 | 2.8 | 2.8 | 2.8 | N |  |  | OP | X | 10 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N
Vintage1990 | natural gas peaker | TRUE | 56606 | Calpine New Jersey Generation LLC | 5083 | Cumberland (NJ) | NJ | Cumberland | CUMB | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 99.4 | 0.9 | 86.9 | 104.1 | 78.2 | N |  |  | OP | X | 5 | 1990 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage2009 | natural gas peaker | TRUE | 56606 | Calpine New Jersey Generation LLC | 5083 | Cumberland (NJ) | NJ | Cumberland | CUMB2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 131.8 | 0.9 | 96.5 | 102 | 90 | N |  |  | OP | X | 6 | 2009 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: KER |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1975 | nuclear | TRUE | 9324 | Indiana Michigan Power Co | 6000 | Donald C Cook | MI | Berrien | 1 | Nuclear | ST |  | S | X | X | 40243801 | 34497125 | 1152 | 0.9 | 1009 | 1084 | 1006 | N |  |  | OP | X | 8 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC |  |  | N |  |  | OVER | [23 empty] | N | N | N
Vintage1978 | nuclear | TRUE | 9324 | Indiana Michigan Power Co | 6000 | Donald C Cook | MI | Berrien | 2 | Nuclear | ST |  | S | X | X | 40243803 | 34497125 | 1133.3 | 0.85 | 1168 | 1194 | 1053 | N |  |  | OP | X | 7 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC |  |  | N |  |  | OVER | [23 empty] | N | N | N
Vintage1977 | nuclear | TRUE | 195 | Alabama Power Co | 6001 | Joseph M Farley | AL | Houston | 1 | Nuclear | ST |  | S | X | X |  |  | 888.2 | 0.85 | 895 | 895 | 250 | N |  |  | OP | X | 12 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC | [5 empty] | OVER | [23 empty] | N
Vintage1981 | nuclear | TRUE | 195 | Alabama Power Co | 6001 | Joseph M Farley | AL | Houston | 2 | Nuclear | ST |  | S | X | X |  |  | 888.2 | 0.85 | 896 | 896 | 250 | N |  |  | OP | X | 7 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC | [5 empty] | OVER | [23 empty] | N
Vintage1978 | hard coal | TRUE | 195 | Alabama Power Co | 6002 | James H Miller Jr | AL | Jefferson | 1 | Conventional Steam Coal | ST |  | J | X | X |  |  | 705.5 | 0.85 | 687.8 | 687.8 | 300 | N |  |  | OP | X | 10 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO DFO DFO: NG |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1985 | hard coal | TRUE | 195 | Alabama Power Co | 6002 | James H Miller Jr | AL | Jefferson | 2 | Conventional Steam Coal | ST |  | J | X | X |  |  | 705.5 | 0.85 | 692.7 | 692.7 | 300 | N |  |  | OP | X | 5 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO DFO DFO: NG |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1989 | hard coal | TRUE | 195 | Alabama Power Co | 6002 | James H Miller Jr | AL | Jefferson | 3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 705.5 | 0.85 | 693 | 693 | 300 | N |  |  | OP | X | 5 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO DFO DFO: NG |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1991 | hard coal | TRUE | 195 | Alabama Power Co | 6002 | James H Miller Jr | AL | Jefferson | 4 | Conventional Steam Coal | ST |  | S | X | X |  |  | 705.5 | 0.85 | 704 | 704 | 300 | N |  |  | OP | X | 3 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO DFO DFO: NG |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1979 | hard coal | TRUE | 64226 | Energy Harbor Generation LLC | 6004 | Pleasants Power Station | WV | Pleasants | 1 | Conventional Steam Coal | ST |  | S | X | X | PLEA APS26KV GEN1 | PLEA APS26KV GEN1 | 684 | 0.9 | 639 | 650 | 300 | N |  |  | OP | X | 4 | 1979 | 6 | 2023 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: RC; DFO SUB SUB: BIT; DFO DFO DFO: NG |  |  | N | N |  | 12H |  | Y |  |  |  | Y | [17 empty] | N | N | N
Vintage1980 | hard coal | TRUE | 64226 | Energy Harbor Generation LLC | 6004 | Pleasants Power Station | WV | Pleasants | 2 | Conventional Steam Coal | ST |  | S | X | X | PLEA APS26KV GEN2 | PLEA APS26KV GEN2 | 684 | 0.9 | 639 | 650 | 300 | N |  |  | OP | X | 12 | 1980 | 6 | 2023 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: RC; DFO SUB SUB: BIT; DFO DFO DFO: NG |  |  | N | N |  | 12H |  | Y |  |  |  | Y | [17 empty] | N | N | N
Vintage1983 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 6006 | Racine | OH | Meigs | 1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 23.7 | 0.95 | 10 | 13 | 1 | N |  |  | OP | X | 1 | 1983 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 12H
Vintage1982 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 6006 | Racine | OH | Meigs | 2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 23.7 | 0.95 | 10 | 13 | 1 | N |  |  | OP | X | 9 | 1982 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 12H
Vintage1986 | nuclear | TRUE | 803 | Arizona Public Service Co | 6008 | Palo Verde | AZ | Maricopa | 1 | Nuclear | ST |  | J | X | X |  |  | 1403.2 | 0.9 | 1311 | 1333 | 110 | N |  |  | OP | X | 1 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC; DFO DFO DFO: NUC |  |  | N |  |  | OVER | [23 empty] | N
Vintage1986 | nuclear | TRUE | 803 | Arizona Public Service Co | 6008 | Palo Verde | AZ | Maricopa | 2 | Nuclear | ST |  | J | X | X |  |  | 1403.2 | 0.9 | 1314 | 1336 | 110 | N |  |  | OP | X | 9 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC; DFO DFO DFO: NUC |  |  | N |  |  | OVER | [23 empty] | N
Vintage1988 | nuclear | TRUE | 803 | Arizona Public Service Co | 6008 | Palo Verde | AZ | Maricopa | 3 | Nuclear | ST |  | J | X | X |  |  | 1403.2 | 0.9 | 1312 | 1334 | 110 | N |  |  | OP | X | 1 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC; DFO DFO DFO: NUC |  |  | N |  |  | OVER | [23 empty] | N
Vintage1980 | hard coal | TRUE | 814 | Entergy Arkansas LLC | 6009 | White Bluff | AR | Jefferson | 1 | Conventional Steam Coal | ST |  | J | X | X | EAI.WH_BLUFF1 | EAI.WH_BLUFF1 | 900 | 0.9 | 817.7 | 817.7 | 200 | N |  |  | OP | X | 8 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO DFO DFO: DFO |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1981 | hard coal | TRUE | 814 | Entergy Arkansas LLC | 6009 | White Bluff | AR | Jefferson | 2 | Conventional Steam Coal | ST |  | J | X | X | EAI.WH_BLUFF2 | EAI.WH_BLUFF2 | 900 | 0.9 | 822.7 | 822.7 | 200 | N |  |  | OP | X | 8 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO DFO DFO: DFO |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1975 | nuclear | TRUE | 55951 | Exelon Nuclear | 6011 | Calvert Cliffs Nuclear Power Plant | MD | Calvert | 1 | Nuclear | ST |  | S | X | X |  |  | 918 | 0.9 | 866 | 920.6 | 50 | N |  |  | OP | X | 5 | 1975 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  | N |  |  | OVER | [23 empty] | N
Vintage1977 | nuclear | TRUE | 55951 | Exelon Nuclear | 6011 | Calvert Cliffs Nuclear Power Plant | MD | Calvert | 2 | Nuclear | ST |  | S | X | X |  |  | 932.4 | 0.9 | 841.8 | 895.1 | 50 | N |  |  | OP | X | 4 | 1977 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  | N |  |  | OVER | [23 empty] | N
Vintage1926 | hydro | TRUE | 61122 | Great River Hydro, LLC | 6012 | Sherman | MA | Franklin | GEN1 | Conventional Hydroelectric | HY |  | S | X | X | 567 |  | 7.2 | 0.8 | 6.1 | 6.2 | 3 | N |  |  | OP | X | 12 | 1926 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1959 | natural gas steam turbine | TRUE | 2507 | City of Burbank Water and Power | 6013 | Olive | CA | Los Angeles | O1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 50 | 0.8 | 44 | 44 | 5 | N |  |  | SB | Y | 10 | 1959 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1964 | natural gas steam turbine | TRUE | 2507 | City of Burbank Water and Power | 6013 | Olive | CA | Los Angeles | O2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 59.7 | 0.85 | 55 | 55 | 6 | N |  |  | SB | Y | 9 | 1964 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1977 | nuclear | TRUE | 3046 | Duke Energy Progress - (NC) | 6014 | Brunswick Nuclear | NC | Brunswick | 1 | Nuclear | ST |  | S | X | X |  |  | 1001.6 | 0.964 | 938 | 975 | 938 | N |  |  | OP | X | 3 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N | N
Vintage1975 | nuclear | TRUE | 3046 | Duke Energy Progress - (NC) | 6014 | Brunswick Nuclear | NC | Brunswick | 2 | Nuclear | ST |  | J | X | X |  |  | 1001.6 | 0.964 | 932 | 953 | 932 | N |  |  | OP | X | 11 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N | N
Vintage1987 | nuclear | TRUE | 3046 | Duke Energy Progress - (NC) | 6015 | Harris | NC | Wake | 1 | Nuclear | ST |  | S | X | X |  |  | 950.9 | 0.95 | 964 | 1009 | 964 | N |  |  | OP | X | 5 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N | N
Vintage1977 | hard coal | TRUE | 520 | Illinois Power Generating Co | 6017 | Newton | IL | Jasper | 1 | Conventional Steam Coal | ST |  | S | X | X | AMIL.NEWTON21 | AMIL.NEWTON21 | 617.4 | 0.9 | 595 | 615 | 200 | N |  |  | OP | X | 11 | 1977 | 12 | 2027 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: RC; DFO SUB SUB: SUB; DFO DFO DFO: DFO; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1981 | hard coal | TRUE | 55729 | Duke Energy Kentucky Inc | 6018 | East Bend | KY | Boone | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 772 | 0.9 | 600 | 600 | 440 | N |  |  | OP | X | 3 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: DFO; DFO DFO DFO: DFO |  |  |  | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1991 | hard coal | TRUE | 59920 | Dynegy W H Zimmer | 6019 | W H Zimmer | OH | Clermont | ST1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 1425.6 | 0.95 | 1305 | 1333 | 450 | N |  |  | OP | X | 3 | 1991 | 5 | 2022 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: RC; DFO SUB SUB: BIT; DFO DFO DFO: DFO; DFO NG NG: NG |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | N | N | N
Vintage1987 | nuclear | TRUE | 64225 | Energy Harbor Nuclear Generation LLC | 6020 | Perry | OH | Lake | 1 | Nuclear | ST |  | S | X | X |  |  | 1311.6 | 0.92 | 1240 | 1268 | 133 | N |  |  | OP | X | 11 | 1987 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [20 empty] | N |  |  | N
Vintage1980 | hard coal | TRUE | 30151 | Tri-State G & T Assn, Inc | 6021 | Craig (CO) | CO | Moffat | 1 | Conventional Steam Coal | ST |  | J | X | X |  |  | 446.4 | 0.9 | 427 | 427 | 130 | N |  |  | OP | X | 7 | 1980 | 12 | 2025 | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: BIT; DFO DFO DFO: DFO; DFO NG NG: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1979 | hard coal | TRUE | 30151 | Tri-State G & T Assn, Inc | 6021 | Craig (CO) | CO | Moffat | 2 | Conventional Steam Coal | ST |  | J | X | X |  |  | 446.4 | 0.9 | 410 | 410 | 130 | N |  |  | OP | X | 11 | 1979 | 9 | 2028 | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: BIT; DFO DFO DFO: DFO; DFO NG NG: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1984 | hard coal | TRUE | 30151 | Tri-State G & T Assn, Inc | 6021 | Craig (CO) | CO | Moffat | 3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 534.8 | 0.955 | 448 | 448 | 130 | N |  |  | OP | X | 10 | 1984 | 12 | 2029 | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO DFO DFO: DFO; DFO NG NG: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1988 | nuclear | TRUE | 55951 | Exelon Nuclear | 6022 | Braidwood Generation Station | IL | Will | 1 | Nuclear | ST |  | S | X | X | 86031201 | 86031201 | 1224.9 | 0.9 | 1183 | 1218.6 | 657.1 | N |  |  | OP | X | 7 | 1988 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N
Vintage1988 | nuclear | TRUE | 55951 | Exelon Nuclear | 6022 | Braidwood Generation Station | IL | Will | 2 | Nuclear | ST |  | S | X | X | 86031202 | 86031202 | 1224.9 | 0.9 | 1154 | 1182.5 | 657.6 | N |  |  | OP | X | 10 | 1988 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N
Vintage1985 | nuclear | TRUE | 55951 | Exelon Nuclear | 6023 | Byron Generating Station | IL | Ogle | 1 | Nuclear | ST |  | S | X | X | 86041201 | 86041201 | 1224.9 | 0.9 | 1164 | 1211.7 | 643.5 | N |  |  | OP | X | 9 | 1985 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N
Vintage1987 | nuclear | TRUE | 55951 | Exelon Nuclear | 6023 | Byron Generating Station | IL | Ogle | 2 | Nuclear | ST |  | S | X | X | 86041202 | 86041202 | 1224.9 | 0.9 | 1136 | 1174 | 646.7 | N |  |  | OP | X | 8 | 1987 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N
Vintage1984 | nuclear | TRUE | 55951 | Exelon Nuclear | 6026 | LaSalle Generating Station | IL | LaSalle | 1 | Nuclear | ST |  | S | X | X | 86191101 | 86191101 | 1170 | 0.9 | 1130.5 | 1171.9 | 135 | N |  |  | OP | X | 1 | 1984 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N
Vintage1984 | nuclear | TRUE | 55951 | Exelon Nuclear | 6026 | LaSalle Generating Station | IL | LaSalle | 2 | Nuclear | ST |  | S | X | X | 86191102 | 86191102 | 1170 | 0.9 | 1133.9 | 1174 | 133 | N |  |  | OP | X | 10 | 1984 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N
Vintage1979 | hard coal | TRUE | 7570 | Great River Energy | 6030 | Coal Creek | ND | McLean | 1 | Conventional Steam Coal | ST |  | S | X | X | GRE,COALC1_DC | GRE.COALC1_DC | 604.8 | 0.9 | 565.1 | 565.1 | 495 | N |  |  | OP | X | 6 | 1979 |  |  | Y | Electric Utility | 1 | X X X: T; DFO RC RC: RC; DFO SUB SUB: LIG; DFO DFO DFO: DFO |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1980 | hard coal | TRUE | 7570 | Great River Energy | 6030 | Coal Creek | ND | McLean | 2 | Conventional Steam Coal | ST |  | S | X | X | GRE.COALC2_DC | GRE.COALC2_DC | 604.8 | 0.9 | 579.9 | 579.9 | 285 | N |  |  | OP | X | 9 | 1980 |  |  | Y | Electric Utility | 1 | X X X: T; DFO RC RC: RC; DFO SUB SUB: LIG; DFO DFO DFO: DFO |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage2016 | petroleum | TRUE | 7570 | Great River Energy | 6030 | Coal Creek | ND | McLean | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 3 | N |  |  | SB | N | 2 | 2016 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2016 | petroleum | TRUE | 7570 | Great River Energy | 6030 | Coal Creek | ND | McLean | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 3 | N |  |  | SB | N | 1 | 2016 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | natural gas peaker | TRUE | 5109 | DTE Electric Company | 6034 | Belle River | MI | St Clair | 12-1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 85.3 | 0.85 | 75 | 93 | 12 | N |  |  | OP | X | 9 | 1999 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H |  | N |  |  | N | [18 empty] | N | N | bar: X X X to DFO RC RC
Vintage1999 | natural gas peaker | TRUE | 5109 | DTE Electric Company | 6034 | Belle River | MI | St Clair | 12-2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 85.3 | 0.85 | 75 | 93 | 12 | N |  |  | OP | X | 9 | 1999 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H |  | N |  |  | N | [18 empty] | N | N | bar: X X X to DFO RC RC
Vintage1999 | natural gas peaker | TRUE | 5109 | DTE Electric Company | 6034 | Belle River | MI | St Clair | 13-1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 85.3 | 0.85 | 74 | 92 | 12 | N |  |  | OP | X | 9 | 1999 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H |  | N |  |  | N | [18 empty] | N | N | bar: X X X to DFO RC RC
Vintage1981 | petroleum | TRUE | 5109 | DTE Electric Company | 6034 | Belle River | MI | St Clair | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 11 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M |  | N |  |  | N | [18 empty] | N | N
Vintage1981 | petroleum | TRUE | 5109 | DTE Electric Company | 6034 | Belle River | MI | St Clair | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 11 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M |  | N |  |  | N | [18 empty] | N | N
Vintage1981 | petroleum | TRUE | 5109 | DTE Electric Company | 6034 | Belle River | MI | St Clair | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 11 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M |  | N |  |  | N | [18 empty] | N | N
Vintage1981 | petroleum | TRUE | 5109 | DTE Electric Company | 6034 | Belle River | MI | St Clair | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2 | 2 | 0.6 | N |  |  | OP | X | 11 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M |  | N |  |  | N | [18 empty] | N | N
Vintage1981 | petroleum | TRUE | 5109 | DTE Electric Company | 6034 | Belle River | MI | St Clair | IC2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 3 | 3 | 0.6 | N |  |  | OP | X | 11 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M |  | N |  |  | N | [18 empty] | N | N
Vintage1984 | hard coal | TRUE | 5109 | DTE Electric Company | 6034 | Belle River | MI | St Clair | ST1 | Conventional Steam Coal | ST |  | J | X | X |  |  | 697.5 | 0.9 | 635 | 635 | 155 | N |  |  | OP | X | 8 | 1984 | 12 | 2028 | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: DFO; DFO DFO DFO: DFO; DFO NG NG: NG |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1985 | hard coal | TRUE | 5109 | DTE Electric Company | 6034 | Belle River | MI | St Clair | ST2 | Conventional Steam Coal | ST |  | J | X | X |  |  | 697.5 | 0.9 | 635 | 635 | 155 | N |  |  | OP | X | 7 | 1985 | 12 | 2028 | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: DFO; DFO DFO DFO: DFO; DFO NG NG: NG |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1979 | natural gas steam turbine | TRUE | 5109 | DTE Electric Company | 6035 | Greenwood (MI) | MI | St Clair | 1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 815.4 | 0.9 | 785 | 785 | 155 | N |  |  | OP | X | 7 | 1979 |  |  | N | Electric Utility | 1 | X | NG | DFO | WO | RFO |  |  | NG | RFO | DFO |  | N | N |  | 12H |  | N |  |  | N | [18 empty] | Y | Y | Y
Vintage1999 | natural gas peaker | TRUE | 5109 | DTE Electric Company | 6035 | Greenwood (MI) | MI | St Clair | 11-1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 85.3 | 0.85 | 75 | 93 | 12 | N |  |  | OP | X | 9 | 1999 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H |  | N |  |  | N | [18 empty] | N | N | bar: X X X to DFO RC RC
Vintage1999 | natural gas peaker | TRUE | 5109 | DTE Electric Company | 6035 | Greenwood (MI) | MI | St Clair | 11-2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 85.3 | 0.85 | 75 | 93 | 12 | N |  |  | OP | X | 9 | 1999 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H |  | N |  |  | N | [18 empty] | N | N | bar: X X X to DFO RC RC
Vintage1999 | natural gas peaker | TRUE | 5109 | DTE Electric Company | 6035 | Greenwood (MI) | MI | St Clair | 11-3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 85.3 | 0.85 | 74 | 92 | 12 | N |  |  | OP | X | 9 | 1999 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: X X X to DFO RC RC
Vintage1985 | nuclear | TRUE | 5416 | Duke Energy Carolinas, LLC | 6036 | Catawba | SC | York | 1 | Nuclear | ST |  | J | X | X |  |  | 1205.1 | 0.9 | 1160.1 | 1198.7 | 1160.1 | N |  |  | OP | X | 6 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N | N
Vintage1986 | nuclear | TRUE | 5416 | Duke Energy Carolinas, LLC | 6036 | Catawba | SC | York | 2 | Nuclear | ST |  | J | X | X |  |  | 1205.1 | 0.9 | 1150.1 | 1179.8 | 1150.1 | N |  |  | OP | X | 8 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N | N
Vintage1981 | nuclear | TRUE | 5416 | Duke Energy Carolinas, LLC | 6038 | McGuire | NC | Mecklenburg | 1 | Nuclear | ST |  | S | X | X |  |  | 1220.3 | 0.83 | 1158 | 1199 | 1158 | N |  |  | OP | X | 9 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N | N
Vintage1984 | nuclear | TRUE | 5416 | Duke Energy Carolinas, LLC | 6038 | McGuire | NC | Mecklenburg | 2 | Nuclear | ST |  | S | X | X |  |  | 1220.3 | 0.87 | 1157.6 | 1187.2 | 1157.6 | N |  |  | OP | X | 3 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N | N
Vintage1976 | nuclear | TRUE | 64225 | Energy Harbor Nuclear Generation LLC | 6040 | Beaver Valley | PA | Beaver | 1 | Nuclear | ST |  | S | X | X |  |  | 923.4 | 0.954 | 907 | 939 | 94 | N |  |  | OP | X | 9 | 1976 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1987 | nuclear | TRUE | 64225 | Energy Harbor Nuclear Generation LLC | 6040 | Beaver Valley | PA | Beaver | 2 | Nuclear | ST |  | S | X | X |  |  | 923.4 | 0.954 | 901 | 933 | 93 | N |  |  | OP | X | 11 | 1987 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1977 | hard coal | TRUE | 5580 | East Kentucky Power Coop, Inc | 6041 | H L Spurlock | KY | Mason | 1 | Conventional Steam Coal | ST |  | S | X | X | 1123180722 | 88140101 | 357.6 | 0.96 | 300 | 300 | 145 | N |  |  | OP | X | 9 | 1977 |  |  | Y | Electric Utility | 1 | X X X: T; DFO RC RC: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1981 | hard coal | TRUE | 5580 | East Kentucky Power Coop, Inc | 6041 | H L Spurlock | KY | Mason | 2 | Conventional Steam Coal | ST |  | S | X | X | 1123180723 | 88140102 | 592.1 | 0.96 | 510 | 510 | 280 | N |  |  | OP | X | 3 | 1981 |  |  | Y | Electric Utility | 1 | X X X: T; DFO RC RC: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage2005 | hard coal | TRUE | 5580 | East Kentucky Power Coop, Inc | 6041 | H L Spurlock | KY | Mason | 3 | Conventional Steam Coal | ST |  | S | X | X | 1123180720 | 88140103 | 329.4 | 0.85 | 268 | 268 | 180 | N |  |  | OP | X | 3 | 2005 |  |  | Y | Electric Utility | 1 | X X X: T; DFO RC RC: BIT; DFO SUB SUB: TDF; DFO DFO DFO: DFO |  |  | N | N |  | OVER | Y |  |  |  | Y | [18 empty] | Y | Y | N
Vintage2009 | hard coal | TRUE | 5580 | East Kentucky Power Coop, Inc | 6041 | H L Spurlock | KY | Mason | 4 | Conventional Steam Coal | ST |  | S | X | X | 1123180721 | 88140104 | 329.4 | 0.85 | 268 | 268 | 180 | N |  |  | OP | X | 4 | 2009 |  |  | Y | Electric Utility | 1 | X X X: T; DFO RC RC: BIT; DFO SUB SUB: TDF; DFO DFO DFO: DFO |  |  | N | N |  | OVER | Y |  |  |  | Y | [18 empty] | Y | Y | N
Vintage1976 | natural gas steam turbine | TRUE | 6452 | Florida Power & Light Co | 6042 | Manatee | FL | Manatee | 1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 863.3 | 0.89 | 809 | 819 | 190 | N |  |  | OP | X | 10 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: RFO; DFO DFO DFO: NG |  |  | N |  |  | 12H | [23 empty] | Y | Y | Y
Vintage1977 | natural gas steam turbine | TRUE | 6452 | Florida Power & Light Co | 6042 | Manatee | FL | Manatee | 2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 863.3 | 0.89 | 809 | 819 | 190 | N |  |  | OP | X | 12 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: RFO; DFO DFO DFO: NG |  |  | N |  |  | 12H | [23 empty] | Y | Y | Y
Vintage2005 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 6042 | Manatee | FL | Manatee | 3 | Natural Gas Fired Combined Cycle | CA | G341 | S | Y | X |  |  | 471.8 | 0.85 | 439 | 437 | 133 | N |  |  | OP | X | 6 | 2005 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2005 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 6042 | Manatee | FL | Manatee | A | Natural Gas Fired Combined Cycle | CT | G341 | S | X | N |  |  | 188.2 | 0.85 | 173.5 | 207 | 95 | N |  |  | OP | X | 6 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO | [5 empty] | 12H | [23 empty] | N |  | N
Vintage2005 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 6042 | Manatee | FL | Manatee | B | Natural Gas Fired Combined Cycle | CT | G341 | S | X | N |  |  | 188.2 | 0.85 | 173.5 | 207 | 95 | N |  |  | OP | X | 6 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO | [5 empty] | 12H | [23 empty] | N |  | N
Vintage2005 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 6042 | Manatee | FL | Manatee | C | Natural Gas Fired Combined Cycle | CT | G341 | S | X | N |  |  | 188.2 | 0.85 | 173.5 | 207 | 95 | N |  |  | OP | X | 6 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO | [5 empty] | 12H | [23 empty] | N |  | N
Vintage2005 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 6042 | Manatee | FL | Manatee | D | Natural Gas Fired Combined Cycle | CT | G341 | S | X | N |  |  | 188.2 | 0.85 | 173.5 | 207 | 95 | N |  |  | OP | X | 6 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO | [5 empty] | 12H | [23 empty] | N |  | N
Vintage1994 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 6043 | Martin | FL | Martin | 3GT1 | Natural Gas Fired Combined Cycle | CT | C796 | S | X | N |  |  | 204 | 0.8 | 165 | 185 | 143 | N |  |  | OP | X | 2 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 12H | [23 empty] | N | N | N
Vintage1994 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 6043 | Martin | FL | Martin | 3GT2 | Natural Gas Fired Combined Cycle | CT | C796 | S | X | N |  |  | 204 | 0.8 | 165 | 185 | 143 | N |  |  | OP | X | 2 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 12H | [23 empty] | N | N | N
Vintage1994 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 6043 | Martin | FL | Martin | 3ST | Natural Gas Fired Combined Cycle | CA | C796 | S | N | X |  |  | 204 | 0.8 | 157 | 163 | 143 | N |  |  | OP | X | 2 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: OTH |  |  | N |  |  | 12H | [23 empty] | N | N | N
Vintage1994 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 6043 | Martin | FL | Martin | 4GT1 | Natural Gas Fired Combined Cycle | CT | C797 | S | X | N |  |  | 204 | 0.8 | 165 | 185 | 143 | N |  |  | OP | X | 4 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 12H | [23 empty] | N | N | N
Vintage1994 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 6043 | Martin | FL | Martin | 4GT2 | Natural Gas Fired Combined Cycle | CT | C797 | S | X | N |  |  | 204 | 0.8 | 165 | 185 | 143 | N |  |  | OP | X | 4 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 12H | [23 empty] | N | N | N
Vintage1994 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 6043 | Martin | FL | Martin | 4ST | Natural Gas Fired Combined Cycle | CA | C797 | S | N | X |  |  | 204 | 0.8 | 157 | 163 | 143 | N |  |  | OP | X | 4 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO | [5 empty] | 12H | [23 empty] | N | N | N
Vintage2005 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 6043 | Martin | FL | Martin | 8 | Natural Gas Fired Combined Cycle | CA | G342 | S | Y | X |  |  | 471.7 | 0.85 | 447.8 | 443 | 133 | N |  |  | OP | X | 6 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: SUN; DFO DFO DFO: DFO |  |  | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage2001 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 6043 | Martin | FL | Martin | 8A | Natural Gas Fired Combined Cycle | CT | G342 | S | X | N |  |  | 188.2 | 0.85 | 196.8 | 207 | 95 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO | [5 empty] | 12H | [23 empty] | Y | N | Y
Vintage2001 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 6043 | Martin | FL | Martin | 8B | Natural Gas Fired Combined Cycle | CT | G342 | S | X | N |  |  | 188.2 | 0.85 | 196.8 | 207 | 95 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO | [5 empty] | 12H | [23 empty] | Y | N | Y
Vintage2005 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 6043 | Martin | FL | Martin | 8C | Natural Gas Fired Combined Cycle | CT | G342 | S | X | N |  |  | 188.2 | 0.85 | 196.8 | 207 | 95 | N |  |  | OP | X | 6 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage2005 | natural gas combined cycle | TRUE | 6452 | Florida Power & Light Co | 6043 | Martin | FL | Martin | 8D | Natural Gas Fired Combined Cycle | CT | G342 | S | X | N |  |  | 188.2 | 0.85 | 196.8 | 207 | 95 | N |  |  | OP | X | 6 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage1976 | nuclear | TRUE | 6452 | Florida Power & Light Co | 6045 | St Lucie | FL | St Lucie | 1 | Nuclear | ST |  | S | X | X |  |  | 1080 | 0.9 | 981 | 1003 | 981 | N |  |  | OP | X | 5 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC |  |  | N |  |  | OVER | [23 empty] | N
Vintage1983 | nuclear | TRUE | 6452 | Florida Power & Light Co | 6045 | St Lucie | FL | St Lucie | 2 | Nuclear | ST |  | J | X | X |  |  | 1080 | 0.9 | 987 | 987 | 987 | N |  |  | OP | X | 6 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC |  |  | N |  |  | OVER | [23 empty] | N
Vintage1992 | petroleum | TRUE | 6455 | Duke Energy Florida, LLC | 6046 | DeBary | FL | Volusia | 10 | Petroleum Liquids | GT |  | S | X | X |  |  | 103.5 | 0.84 | 72 | 88 | 40 | N |  |  | OP | X | 10 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N
Vintage1976 | petroleum | TRUE | 6455 | Duke Energy Florida, LLC | 6046 | DeBary | FL | Volusia | 2 | Petroleum Liquids | GT |  | S | X | X |  |  | 66.8 | 0.9 | 45 | 57 | 20 | N |  |  | OP | X | 3 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1975 | petroleum | TRUE | 6455 | Duke Energy Florida, LLC | 6046 | DeBary | FL | Volusia | 3 | Petroleum Liquids | GT |  | S | X | X |  |  | 66.8 | 0.9 | 45 | 59 | 20 | N |  |  | OP | X | 12 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1976 | petroleum | TRUE | 6455 | Duke Energy Florida, LLC | 6046 | DeBary | FL | Volusia | 4 | Petroleum Liquids | GT |  | S | X | X |  |  | 66.8 | 0.9 | 46 | 59 | 20 | N |  |  | OP | X | 4 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1975 | petroleum | TRUE | 6455 | Duke Energy Florida, LLC | 6046 | DeBary | FL | Volusia | 5 | Petroleum Liquids | GT |  | S | X | X |  |  | 66.8 | 0.9 | 45 | 58 | 20 | N |  |  | OP | X | 12 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1976 | petroleum | TRUE | 6455 | Duke Energy Florida, LLC | 6046 | DeBary | FL | Volusia | 6 | Petroleum Liquids | GT |  | S | X | X |  |  | 66.8 | 0.9 | 46 | 59 | 20 | N |  |  | OP | X | 4 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1992 | natural gas peaker | TRUE | 6455 | Duke Energy Florida, LLC | 6046 | DeBary | FL | Volusia | 7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 103.5 | 0.85 | 74 | 93 | 40 | N |  |  | OP | X | 10 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1992 | natural gas peaker | TRUE | 6455 | Duke Energy Florida, LLC | 6046 | DeBary | FL | Volusia | 8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 103.5 | 0.85 | 75 | 94 | 40 | N |  |  | OP | X | 10 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1992 | natural gas peaker | TRUE | 6455 | Duke Energy Florida, LLC | 6046 | DeBary | FL | Volusia | 9 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 103.5 | 0.85 | 76 | 94 | 40 | N |  |  | OP | X | 10 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1913 | hydro | TRUE | 61122 | Great River Hydro, LLC | 6047 | Deerfield 2 | MA | Franklin | GEN1 | Conventional Hydroelectric | HY |  | S | X | X | 465 |  | 1.6 | 0.8 | 2.2 | 2.2 | 1 | N |  |  | OP | X | 8 | 1913 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1913 | hydro | TRUE | 61122 | Great River Hydro, LLC | 6047 | Deerfield 2 | MA | Franklin | GEN2 | Conventional Hydroelectric | HY |  | S | X | X | 465 |  | 1.6 | 0.8 | 2.2 | 2.2 | 1 | N |  |  | OP | X | 8 | 1913 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1913 | hydro | TRUE | 61122 | Great River Hydro, LLC | 6047 | Deerfield 2 | MA | Franklin | GEN3 | Conventional Hydroelectric | HY |  | S | X | X | 465 |  | 1.6 | 0.8 | 2.2 | 2.2 | 1 | N |  |  | OP | X | 8 | 1913 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1975 | petroleum | TRUE | 64488 | Vineyard Reliability LLC | 6049 | West Tisbury Generating Facility | MA | Dukes | UN1 | Petroleum Liquids | IC |  | S | X | X | 1031 | 1031 | 2.7 | 0.8 | 2.8 | 2.8 | 2 | N |  |  | OP | X | 1 | 1975 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1975 | petroleum | TRUE | 64488 | Vineyard Reliability LLC | 6049 | West Tisbury Generating Facility | MA | Dukes | UN2 | Petroleum Liquids | IC |  | S | X | X | 1031 | 1031 | 2.7 | 0.8 | 2.8 | 2.8 | 2 | N |  |  | OP | X | 1 | 1975 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1975 | nuclear | TRUE | 7140 | Georgia Power Co | 6051 | Edwin I Hatch | GA | Appling | 1 | Nuclear | ST |  | J | X | X |  |  | 924 | 0.88 | 876 | 876 | 250 | N |  |  | OP | X | 12 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC |  |  | N |  |  | OVER | [23 empty] | N
Vintage1979 | nuclear | TRUE | 7140 | Georgia Power Co | 6051 | Edwin I Hatch | GA | Appling | 2 | Nuclear | ST |  | J | X | X |  |  | 924 | 0.88 | 883 | 883 | 250 | N |  |  | OP | X | 9 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC |  |  | N |  |  | OVER | [23 empty] | N
Vintage1976 | hard coal | TRUE | 7140 | Georgia Power Co | 6052 | Wansley | GA | Heard | 1 | Conventional Steam Coal | ST |  | J | X | X |  |  | 952 | 0.85 | 872 | 872 | 350 | N |  |  | OP | X | 12 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: DFO; DFO DFO DFO: DFO |  |  | N |  |  | OVER |  | Y |  |  |  | Y | [17 empty] | N
Vintage1978 | hard coal | TRUE | 7140 | Georgia Power Co | 6052 | Wansley | GA | Heard | 2 | Conventional Steam Coal | ST |  | J | X | X |  |  | 952 | 0.85 | 872 | 872 | 350 | N |  |  | OP | X | 4 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: DFO; DFO DFO DFO: DFO |  |  | N |  |  | OVER |  | Y |  |  |  | Y | [17 empty] | N
Vintage1980 | petroleum | TRUE | 7140 | Georgia Power Co | 6052 | Wansley | GA | Heard | 5A | Petroleum Liquids | GT |  | J | X | X |  |  | 52.8 | 0.9 | 49 | 60 | 5 | N |  |  | OP | X | 11 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1981 | hard coal | TRUE | 11252 | Louisiana Generating LLC | 6055 | Big Cajun 2 | LA | Pointe Coupee | 1 | Conventional Steam Coal | ST |  | S | X | X | LAGN.BC2_1 | LAGN.BC2_1 | 657.9 | 0.9 | 537 | 537 | 225 | N |  |  | OP | X | 7 | 1981 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1982 | natural gas steam turbine | TRUE | 11252 | Louisiana Generating LLC | 6055 | Big Cajun 2 | LA | Pointe Coupee | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | LAGN.BC2_2 | LAGN.BC2_2 | 626 | 0.9 | 575 | 575 | 100 | N |  |  | OP | X | 7 | 1982 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | OVER |  | N |  |  | N | [18 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1983 | hard coal | TRUE | 11252 | Louisiana Generating LLC | 6055 | Big Cajun 2 | LA | Pointe Coupee | 3 | Conventional Steam Coal | ST |  | J | X | X | LAGN.BC2_3 | LAGN.BC2_3 | 619 | 0.9 | 557.4 | 557.4 | 180 | N |  |  | OP | X | 4 | 1983 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1948 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 6056 | Kahului | HI | Maui | 1 | Petroleum Liquids | ST |  | S | X | X |  |  | 5 | 0.8 | 4.7 | 4.7 | 2 | N |  |  | OP | X | 5 | 1948 | 1 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: RFO; DFO DFO DFO: RFO |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1949 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 6056 | Kahului | HI | Maui | 2 | Petroleum Liquids | ST |  | S | X | X |  |  | 5 | 0.8 | 4.8 | 4.8 | 2 | N |  |  | OP | X | 12 | 1949 | 1 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: RFO; DFO DFO DFO: RFO |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1954 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 6056 | Kahului | HI | Maui | 3 | Petroleum Liquids | ST |  | S | X | X |  |  | 11.5 | 0.85 | 11 | 11 | 3 | N |  |  | OP | X | 4 | 1954 | 1 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: RFO; DFO DFO DFO: RFO |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1966 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 6056 | Kahului | HI | Maui | 4 | Petroleum Liquids | ST |  | S | X | X |  |  | 12.5 | 0.8 | 11.9 | 11.9 | 3 | N |  |  | OP | X | 10 | 1966 | 1 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: RFO; DFO DFO DFO: RFO |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1975 | natural gas peaker | TRUE | 16181 | Rochester Public Utilities | 6058 | Cascade Creek | MN | Olmsted | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SMP.MMPA.CCRK1 | SMP.MMPA.CCRK1 | 35 | 0.95 | 27.9 | 30.2 | 5 | N |  |  | OP | X | 6 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 16181 | Rochester Public Utilities | 6058 | Cascade Creek | MN | Olmsted | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SMP.MMPA.CCRK2 | SMP.MMPA.CCRK2 | 49.9 | 0.95 | 49.5 | 49.9 | 5 | N |  |  | OP | X | 4 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 10M | [20 empty] | N |  |  | Y | N | Y
Vintage1973 | natural gas peaker | TRUE | 9216 | Imperial Irrigation District | 6060 | Coachella | CA | Riverside | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 23.1 | 0.9 | 18.6 | 18.5 | 3 | N |  |  | OP | X | 6 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1973 | natural gas peaker | TRUE | 9216 | Imperial Irrigation District | 6060 | Coachella | CA | Riverside | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 23.1 | 0.9 | 19 | 16.1 | 3 | N |  |  | OP | X | 6 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1974 | natural gas peaker | TRUE | 9216 | Imperial Irrigation District | 6060 | Coachella | CA | Riverside | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 23.1 | 0.9 | 18.3 | 20.3 | 3 | N |  |  | OP | X | 4 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1976 | natural gas peaker | TRUE | 9216 | Imperial Irrigation District | 6060 | Coachella | CA | Riverside | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 23.1 | 0.9 | 18 | 19.2 | 3 | N |  |  | OP | X | 5 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1975 | natural gas peaker | TRUE | 12341 | MidAmerican Energy Co | 6063 | Electrifarm | IA | Black Hawk | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MEC.EL Farm1 | MEC.EL FARM1 | 71.2 | 0.9 | 53.5 | 71 | 6 | N |  |  | OP | X | 5 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1978 | natural gas peaker | TRUE | 12341 | MidAmerican Energy Co | 6063 | Electrifarm | IA | Black Hawk | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MEC.EL FARM 2 | MEC.EL Farm2 | 89 | 0.9 | 62.8 | 78 | 6 | N |  |  | OP | X | 1 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1978 | natural gas peaker | TRUE | 12341 | MidAmerican Energy Co | 6063 | Electrifarm | IA | Black Hawk | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MEC.EL Farm3 | MEC.EL FARM3 | 103.9 | 0.9 | 65.3 | 85 | 6 | N |  |  | OP | X | 1 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1981 | hard coal | TRUE | 9996 | City of Kansas City - (KS) | 6064 | Nearman Creek | KS | Wyandotte | 1 | Conventional Steam Coal | ST |  | S | X | X | kacy | kacy | 261 | 0.97 | 243 | 243 | 150 | N |  |  | OP | X | 6 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | N |  |  | N | N | N
Vintage2006 | natural gas peaker | TRUE | 9996 | City of Kansas City - (KS) | 6064 | Nearman Creek | KS | Wyandotte | CT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | kacy | kacy | 94 | 0.97 | 76 | 76 | 45 | N |  |  | OP | X | 2 | 2006 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1980 | hard coal | TRUE | 10000 | Evergy Metro | 6065 | Iatan | MO | Platte | 1 | Conventional Steam Coal | ST |  | J | X | X | KCPLIATANUNIAT1 | IATANUNIAT1 | 726 | 0.9 | 703 | 703 | 366 | N |  |  | OP | X | 5 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage2010 | hard coal | TRUE | 10000 | Evergy Metro | 6065 | Iatan | MO | Platte | 2 | Conventional Steam Coal | ST |  | J | X | X | KCPLIATANUNIAT2 | IATANUNIAT2 | 999 | 0.9 | 877 | 877 | 657 | N |  |  | OP | X | 8 | 2010 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO DFO DFO: DFO |  |  | N | N |  | 12H |  | Y |  |  |  | Y | [17 empty] | N
Vintage1978 | hard coal | TRUE | 22500 | Evergy Kansas Central, Inc | 6068 | Jeffrey Energy Center | KS | Pottawatomie | 1 | Conventional Steam Coal | ST |  | J | X | X | WR.JEC.1 | WR.JEC.1 | 720 | 0.9 | 669.6 | 669.6 | 230 | N |  |  | OP | X | 7 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1980 | hard coal | TRUE | 22500 | Evergy Kansas Central, Inc | 6068 | Jeffrey Energy Center | KS | Pottawatomie | 2 | Conventional Steam Coal | ST |  | J | X | X | WR.JEC.2 | WR.JEC.2 | 720 | 0.9 | 671.7 | 671.7 | 220 | N |  |  | OP | X | 5 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1983 | hard coal | TRUE | 22500 | Evergy Kansas Central, Inc | 6068 | Jeffrey Energy Center | KS | Pottawatomie | 3 | Conventional Steam Coal | ST |  | J | X | X | WR.JEC.3 | WR.JEC.3 | 720 | 0.9 | 669.3 | 669.3 | 220 | N |  |  | OP | X | 5 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1990 | hard coal | TRUE | 11249 | Louisville Gas & Electric Co | 6071 | Trimble County | KY | Trimble | 1 | Conventional Steam Coal | ST |  | J | X | X |  |  | 566.1 | 0.9 | 511 | 511 | 141 | N |  |  | OP | X | 12 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: BIT; DFO DFO DFO: SUB; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage2004 | natural gas peaker | TRUE | 11249 | Louisville Gas & Electric Co | 6071 | Trimble County | KY | Trimble | 10 | Natural Gas Fired Combustion Turbine | GT |  | J | X | X |  |  | 199 | 0.85 | 159 | 179 | 80 | N |  |  | OP | X | 7 | 2004 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage2011 | hard coal | TRUE | 11249 | Louisville Gas & Electric Co | 6071 | Trimble County | KY | Trimble | 2 | Conventional Steam Coal | ST |  | J | X | X |  |  | 834 | 0.85 | 732 | 760 | 315 | N |  |  | OP | X | 2 | 2011 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: BIT; DFO DFO DFO: SUB; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | N | N | N
Vintage2002 | natural gas peaker | TRUE | 11249 | Louisville Gas & Electric Co | 6071 | Trimble County | KY | Trimble | 5 | Natural Gas Fired Combustion Turbine | GT |  | J | X | X |  |  | 199 | 0.85 | 159 | 179 | 80 | N |  |  | OP | X | 5 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage2002 | natural gas peaker | TRUE | 11249 | Louisville Gas & Electric Co | 6071 | Trimble County | KY | Trimble | 6 | Natural Gas Fired Combustion Turbine | GT |  | J | X | X |  |  | 199 | 0.85 | 159 | 179 | 80 | N |  |  | OP | X | 5 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage2004 | natural gas peaker | TRUE | 11249 | Louisville Gas & Electric Co | 6071 | Trimble County | KY | Trimble | 7 | Natural Gas Fired Combustion Turbine | GT |  | J | X | X |  |  | 199 | 0.85 | 159 | 179 | 80 | N |  |  | OP | X | 6 | 2004 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage2004 | natural gas peaker | TRUE | 11249 | Louisville Gas & Electric Co | 6071 | Trimble County | KY | Trimble | 8 | Natural Gas Fired Combustion Turbine | GT |  | J | X | X |  |  | 199 | 0.85 | 159 | 179 | 80 | N |  |  | OP | X | 6 | 2004 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage2004 | natural gas peaker | TRUE | 11249 | Louisville Gas & Electric Co | 6071 | Trimble County | KY | Trimble | 9 | Natural Gas Fired Combustion Turbine | GT |  | J | X | X |  |  | 199 | 0.85 | 159 | 179 | 80 | N |  |  | OP | X | 7 | 2004 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H |  | N | [21 empty] | N | N | N | bar: X X X to DFO RC RC; DFO DFO DFO
Vintage1985 | nuclear | TRUE | 12465 | System Energy Resources, Inc | 6072 | Grand Gulf | MS | Claiborne | 1 | Nuclear | ST |  | J | X | X | EES.G_GULF_A | EES.G_GULF_A | 1440 | 0.9 | 1401 | 1428 | 300 | N |  |  | OP | X | 7 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC |  |  | N |  |  | OVER | [23 empty] | N
Vintage1977 | hard coal | TRUE | 12686 | Mississippi Power Co | 6073 | Victor J Daniel Jr | MS | Jackson | 1 | Conventional Steam Coal | ST |  | J | X | X |  |  | 548.3 | 0.85 | 502 | 502 | 165 | N |  |  | OP | X | 9 | 1977 | 12 | 2027 | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: BIT; DFO DFO DFO: DFO; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | N |  |  | Y | Y | N
Vintage1981 | hard coal | TRUE | 12686 | Mississippi Power Co | 6073 | Victor J Daniel Jr | MS | Jackson | 2 | Conventional Steam Coal | ST |  | J | X | X |  |  | 548.3 | 0.85 | 502 | 502 | 165 | N |  |  | OP | X | 6 | 1981 | 12 | 2027 | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: BIT; DFO DFO DFO: DFO; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | N |  |  | Y | Y | N
Vintage2001 | natural gas combined cycle | TRUE | 12686 | Mississippi Power Co | 6073 | Victor J Daniel Jr | MS | Jackson | 3 | Natural Gas Fired Combined Cycle | CT | 3 | S | X | N |  |  | 185.5 | 0.85 | 539 | 560 | 110 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [7 empty] | 27 | 30 | 10 | 2022 | [9 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage2001 | natural gas combined cycle | TRUE | 12686 | Mississippi Power Co | 6073 | Victor J Daniel Jr | MS | Jackson | 3CT | Natural Gas Fired Combined Cycle | CT | 3 | S | X | N |  |  | 185.5 | 0.85 |  |  | 110 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage2001 | natural gas combined cycle | TRUE | 12686 | Mississippi Power Co | 6073 | Victor J Daniel Jr | MS | Jackson | 3ST | Natural Gas Fired Combined Cycle | CA | 3 | S | Y | X |  |  | 195.2 | 0.85 |  |  | 145 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage2001 | natural gas combined cycle | TRUE | 12686 | Mississippi Power Co | 6073 | Victor J Daniel Jr | MS | Jackson | 4 | Natural Gas Fired Combined Cycle | CT | 4 | S | X | N |  |  | 185.5 | 0.85 | 559 | 577 | 110 | N |  |  | OP | X | 4 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [7 empty] | 19 | 22 | 5 | 2024 | [9 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage2001 | natural gas combined cycle | TRUE | 12686 | Mississippi Power Co | 6073 | Victor J Daniel Jr | MS | Jackson | 4CT | Natural Gas Fired Combined Cycle | CT | 4 | S | X | N |  |  | 185.5 | 0.85 |  |  | 110 | N |  |  | OP | X | 4 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage2001 | natural gas combined cycle | TRUE | 12686 | Mississippi Power Co | 6073 | Victor J Daniel Jr | MS | Jackson | 4ST | Natural Gas Fired Combined Cycle | CA | 4 | S | Y | X |  |  | 195.2 | 0.85 |  |  | 145 | N |  |  | OP | X | 4 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X X X to DFO RC RC
Vintage1975 | natural gas peaker | TRUE | 56211 | Evergy Missouri West | 6074 | Greenwood (MO) | MO | Jackson | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MPSGRNWD1UN1 | MPSGRNWD1UN1 | 64.7 | 0.9 | 62.7 | 62.7 | 5 | N |  |  | OP | X | 5 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO | [5 empty] | 1H | [23 empty] | Y |  | N
Vintage1975 | natural gas peaker | TRUE | 56211 | Evergy Missouri West | 6074 | Greenwood (MO) | MO | Jackson | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MPSGRNWD1UN2 | MPSGRNWD1UN2 | 64.7 | 0.9 | 63 | 63 | 5 | N |  |  | OP | X | 5 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO | [5 empty] | 1H | [23 empty] | Y |  | N
Vintage1977 | natural gas peaker | TRUE | 56211 | Evergy Missouri West | 6074 | Greenwood (MO) | MO | Jackson | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MPSGRNWD1UN3 | MPSGRNWD1UN3 | 64.7 | 0.9 | 62.1 | 62.1 | 5 | N |  |  | OP | X | 6 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO | [5 empty] | 1H | [23 empty] | Y |  | N
Vintage1979 | natural gas peaker | TRUE | 56211 | Evergy Missouri West | 6074 | Greenwood (MO) | MO | Jackson | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MPSGRNWD1UN4 | MPSGRNWD1UN4 | 64.7 | 0.9 | 61.4 | 61.4 | 5 | N |  |  | OP | X | 6 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO | [5 empty] | 1H | [23 empty] | Y |  | N
Vintage2016 | solar pv | TRUE | 56211 | Evergy Missouri West | 6074 | Greenwood (MO) | MO | Jackson | 5 | Solar Photovoltaic | PV |  | S | X | X |  |  | 3 |  | 3 | 3 |  | N |  |  | OP | X | 6 | 2016 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUN
Vintage1984 | hard coal | TRUE | 15298 | Talen Montana LLC | 6076 | Colstrip | MT | Rosebud | 3 | Conventional Steam Coal | ST |  | J | X | X | NA | NA | 823.7 | 0.95 | 740 | 740 | 200 | N |  |  | OP | X | 1 | 1984 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: SUB; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1986 | hard coal | TRUE | 15298 | Talen Montana LLC | 6076 | Colstrip | MT | Rosebud | 4 | Conventional Steam Coal | ST |  | J | X | X | NA | NA | 823.7 | 0.95 | 740 | 740 | 200 | N |  |  | OP | X | 4 | 1986 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: SUB; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1979 | hard coal | TRUE | 13337 | Nebraska Public Power District | 6077 | Gerald Gentleman | NE | Lincoln | 1 | Conventional Steam Coal | ST |  | S | X | X | NPPD_GGS1 | NPPD_GGS1 | 681.3 | 0.9 | 665 | 665 | 0 | N |  |  | OP | X | 4 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1982 | hard coal | TRUE | 13337 | Nebraska Public Power District | 6077 | Gerald Gentleman | NE | Lincoln | 2 | Conventional Steam Coal | ST |  | S | X | X | NPPD_GGS2 | NPPD_GGS2 | 681.3 | 0.9 | 700 | 700 | 0 | N |  |  | OP | X | 1 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1982 | petroleum | TRUE | 11806 | Massachusetts Mun Wholes Electric Co | 6081 | Stony Brook | MA | Hampden | 1 | Petroleum Liquids | GT |  | J | X | X | UN.STONTBRK13.2ST2A | .Z.WCMASS | 85 | 0.9 | 65 | 85 | 40 | N |  |  | OP | X | 11 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1982 | petroleum | TRUE | 11806 | Massachusetts Mun Wholes Electric Co | 6081 | Stony Brook | MA | Hampden | 2 | Petroleum Liquids | GT |  | J | X | X | UN.STONYBRK13.2ST2B | .Z.WCMASS | 85 | 0.9 | 65 | 85 | 40 | N |  |  | OP | X | 11 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage2018 | solar pv | TRUE | 11806 | Massachusetts Mun Wholes Electric Co | 6081 | Stony Brook | MA | Hampden | 5051S | Solar Photovoltaic | PV |  | S | X | X | 4007 | Z.WCMASS | 6.9 | 1 | 6.9 | 6.9 | 0 | N |  |  | OP | X | 6 | 2018 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUN
Vintage2007 | petroleum | TRUE | 11806 | Massachusetts Mun Wholes Electric Co | 6081 | Stony Brook | MA | Hampden | BS#1 | Petroleum Liquids | IC |  | J | X | X |  |  | 2 | 0.9 | 2 | 2 | 0.2 | N |  |  | SB | N | 9 | 2007 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO; DFO SUB SUB: NG |  |  | N |  |  | 10M | [23 empty] | N |  | N
Vintage2007 | petroleum | TRUE | 11806 | Massachusetts Mun Wholes Electric Co | 6081 | Stony Brook | MA | Hampden | BS#2 | Petroleum Liquids | IC |  | J | X | X |  |  | 2 | 0.9 | 2 | 2 | 0.2 | N |  |  | SB | N | 9 | 2007 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage1981 | petroleum | TRUE | 11806 | Massachusetts Mun Wholes Electric Co | 6081 | Stony Brook | MA | Hampden | CA1 | Petroleum Liquids | CA | CC1 | J | N | X |  |  | 105 | 0.9 | 96 | 105 | 20 | N |  |  | OP | X | 11 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 12H | [23 empty] | N
Vintage1981 | natural gas combined cycle | TRUE | 11806 | Massachusetts Mun Wholes Electric Co | 6081 | Stony Brook | MA | Hampden | CT1 | Natural Gas Fired Combined Cycle | CT | CC1 | J | X | N | UN.STONYBRK13.2ST1A | .Z.WCMASS | 85 | 0.9 | 69.7 | 87 | 40 | N |  |  | OP | X | 11 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1981 | natural gas combined cycle | TRUE | 11806 | Massachusetts Mun Wholes Electric Co | 6081 | Stony Brook | MA | Hampden | CT2 | Natural Gas Fired Combined Cycle | CT | CC1 | J | X | Y | UN.STONYBRK13.2ST1B | .Z.WCMASS | 85 | 0.9 | 69.7 | 87 | 55 | N |  |  | OP | X | 11 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1981 | natural gas combined cycle | TRUE | 11806 | Massachusetts Mun Wholes Electric Co | 6081 | Stony Brook | MA | Hampden | CT3 | Natural Gas Fired Combined Cycle | CT | CC1 | J | X | N | UN.STONYBRK13.2ST1C | .Z.WCMASS | 85 | 0.9 | 69.7 | 87 | 40 | N |  |  | OP | X | 11 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1981 | petroleum | TRUE | 11806 | Massachusetts Mun Wholes Electric Co | 6081 | Stony Brook | MA | Hampden | EDSI | Petroleum Liquids | IC |  | J | X | X |  |  | 0.6 | 0.9 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 11 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1912 | hydro | TRUE | 61122 | Great River Hydro, LLC | 6083 | Deerfield 3 | MA | Franklin | GEN1 | Conventional Hydroelectric | HY |  | S | X | X | 465 |  | 1.6 | 0.8 | 2 | 2 | 1 | N |  |  | OP | X | 8 | 1912 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1912 | hydro | TRUE | 61122 | Great River Hydro, LLC | 6083 | Deerfield 3 | MA | Franklin | GEN2 | Conventional Hydroelectric | HY |  | S | X | X | 465 |  | 1.6 | 0.8 | 2 | 2 | 1 | N |  |  | OP | X | 8 | 1912 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1912 | hydro | TRUE | 61122 | Great River Hydro, LLC | 6083 | Deerfield 3 | MA | Franklin | GEN3 | Conventional Hydroelectric | HY |  | S | X | X | 465 |  | 1.6 | 0.8 | 2 | 2 | 1 | N |  |  | OP | X | 8 | 1912 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1979 | natural gas peaker | TRUE | 13756 | Northern Indiana Pub Serv Co | 6085 | R M Schahfer | IN | Jasper | 16A | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | NIPS.SCHAHP16A | NIPS.SCHAHP16A | 129 | 0.9 | 78 | 78 | 70 | N |  |  | OP | X | 12 | 1979 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1979 | natural gas peaker | TRUE | 13756 | Northern Indiana Pub Serv Co | 6085 | R M Schahfer | IN | Jasper | 16B | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | NIPS.SCHAHP16B | NIPS.SCHAHP16B | 129 | 0.9 | 77 | 77 | 70 | N |  |  | OP | X | 12 | 1979 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1983 | hard coal | TRUE | 13756 | Northern Indiana Pub Serv Co | 6085 | R M Schahfer | IN | Jasper | 17 | Conventional Steam Coal | ST |  | S | X | X | NIPS.SCHAHP17 | NIPS.SCHAHP17 | 423.5 | 0.9 | 361 | 361 | 110 | N |  |  | OP | X | 4 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1986 | hard coal | TRUE | 13756 | Northern Indiana Pub Serv Co | 6085 | R M Schahfer | IN | Jasper | 18 | Conventional Steam Coal | ST |  | S | X | X | NIPS.SCHAHP18 | NIPS.SCHAHP18 | 423.5 | 0.9 | 361 | 361 | 110 | N |  |  | OP | X | 2 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1976 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 6086 | Cornell | WI | Chippewa | 1 | Conventional Hydroelectric | HY |  | S | X | X | NSP CORNELL2 CORN_HYD_UNIT | NSP CORNELL2 CORN_HYD_UNIT | 11.5 | 0.9 | 6.2 | 6.2 | 2.9 | N |  |  | OP | X | 7 | 1976 | 11 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1976 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 6086 | Cornell | WI | Chippewa | 2 | Conventional Hydroelectric | HY |  | S | X | X | NSP CORNELL2 CORN_HYD_UNIT | NSP CORNELL2 CORN_HYD_UNIT | 11.5 | 0.9 | 6.4 | 6.4 | 2.9 | N |  |  | OP | X | 8 | 1976 | 11 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1976 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 6086 | Cornell | WI | Chippewa | 3 | Conventional Hydroelectric | HY |  | S | X | X | NSP CORNELL2 CORN_HYD_UNIT | NSP CORNELL2 CORN_HYD_UNIT | 11.5 | 0.9 | 6.9 | 6.9 | 2.9 | N |  |  | OP | X | 7 | 1976 | 11 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1977 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 6086 | Cornell | WI | Chippewa | 4 | Conventional Hydroelectric | HY |  | S | X | X | NSP CORNELL2 CORN_HYD_UNIT | NSP CORNELL2 CORN_HYD_UNIT | 0.8 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 4 | 1977 | 11 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1980 | other | TRUE | 7140 | Georgia Power Co | 6087 | Wallace Dam | GA | Hancock | 1 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 52.2 | 0.9 | 53.6 | 53.3 | 50.7 | N |  |  | OP | X | 7 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 1H | [23 empty] | N
Vintage1980 | other | TRUE | 7140 | Georgia Power Co | 6087 | Wallace Dam | GA | Hancock | 2 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 52.2 | 0.9 | 53.6 | 53.3 | 50.7 | N |  |  | OP | X | 12 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 1H | [23 empty] | N
Vintage1980 | hydro | TRUE | 7140 | Georgia Power Co | 6087 | Wallace Dam | GA | Hancock | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 56.2 | 0.9 | 56.8 | 57.1 | 54.6 | N |  |  | OP | X | 2 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 1H | [23 empty] | N
Vintage1980 | hydro | TRUE | 7140 | Georgia Power Co | 6087 | Wallace Dam | GA | Hancock | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 56.2 | 0.9 | 56.8 | 57.1 | 54.6 | N |  |  | OP | X | 4 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 1H | [23 empty] | N
Vintage1980 | other | TRUE | 7140 | Georgia Power Co | 6087 | Wallace Dam | GA | Hancock | 5 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 52.2 | 0.9 | 53.6 | 53.3 | 50.7 | N |  |  | OP | X | 1 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 1H | [23 empty] | N
Vintage1979 | other | TRUE | 7140 | Georgia Power Co | 6087 | Wallace Dam | GA | Hancock | 6 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 52.2 | 0.9 | 53.6 | 53.3 | 50.7 | N |  |  | OP | X | 12 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 1H | [23 empty] | N
Vintage1972 | natural gas peaker | TRUE | 24211 | Tucson Electric Power Co | 6088 | North Loop | AZ | Pima | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 27 | 0.85 | 25 | 26.8 | 5 | N |  |  | OP | X | 12 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1972 | natural gas peaker | TRUE | 24211 | Tucson Electric Power Co | 6088 | North Loop | AZ | Pima | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 27 | 0.85 | 25 | 26.8 | 5 | N |  |  | OP | X | 12 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1972 | natural gas peaker | TRUE | 24211 | Tucson Electric Power Co | 6088 | North Loop | AZ | Pima | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 27 | 0.85 | 25 | 26.8 | 5 | N |  |  | OP | X | 12 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2001 | natural gas peaker | TRUE | 24211 | Tucson Electric Power Co | 6088 | North Loop | AZ | Pima | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 26.8 | 0.8 | 20 | 21.4 | 10 | N |  |  | OP | X | 7 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage2016 | natural gas peaker | TRUE | 12199 | Montana-Dakota Utilities Co | 6089 | Lewis & Clark | MT | Richland | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | MDU.LEWIS2 | MDU.LEWIS2 | 9.3 | 0.8 | 9.1 | 9.1 | 3.5 | N |  |  | OP | X | 4 | 2016 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage2016 | natural gas peaker | TRUE | 12199 | Montana-Dakota Utilities Co | 6089 | Lewis & Clark | MT | Richland | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | MDU.LEWIS2 | MDU.LEWIS2 | 9.3 | 0.8 | 9.1 | 9.1 | 3.5 | N |  |  | OP | X | 4 | 2016 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to DFO RC RC
Vintage1976 | hard coal | TRUE | 13781 | Northern States Power Co - Minnesota | 6090 | Sherburne County | MN | Sherburne | 1 | Conventional Steam Coal | ST |  | S | X | X | NSP SHERCO SHERCO_1_UNIT | NSP SHERCO SHERCO_1_UNIT | 765.3 | 0.91 | 680 | 680 | 260 | N |  |  | OP | X | 4 | 1976 | 12 | 2025 | Y | Electric Utility | 1 | X X X: T; DFO RC RC: SUB; DFO SUB SUB: DFO; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1977 | hard coal | TRUE | 13781 | Northern States Power Co - Minnesota | 6090 | Sherburne County | MN | Sherburne | 2 | Conventional Steam Coal | ST |  | S | X | X | NSP SHERCO SHERCO_2_UNIT | NSP SHERCO SHERCO_2_UNIT | 765.3 | 0.91 | 682 | 682 | 260 | N |  |  | OP | X | 3 | 1977 | 12 | 2023 | Y | Electric Utility | 1 | X X X: T; DFO RC RC: SUB; DFO SUB SUB: DFO; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1987 | hard coal | TRUE | 13781 | Northern States Power Co - Minnesota | 6090 | Sherburne County | MN | Sherburne | 3 | Conventional Steam Coal | ST |  | J | X | X | NSP SHERCO SHERCN_3_UNIT | NSP SHERCO SHERCN_3_UNIT | 938.7 | 0.9 | 876 | 876 | 400 | N |  |  | OP | X | 10 | 1987 | 12 | 2034 | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: DFO; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1978 | petroleum | TRUE | 1307 | Basin Electric Power Coop | 6092 | Spirit Mound | SD | Clay | 1 | Petroleum Liquids | GT |  | S | X | X | WAUESPIRITMUNSPIRIT_1_UNIT_RA | WAUE.BEPM.SMS1 | 67.5 | 0.9 | 50 | 60 | 10 | N |  |  | OP | X | 6 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1978 | petroleum | TRUE | 1307 | Basin Electric Power Coop | 6092 | Spirit Mound | SD | Clay | 2 | Petroleum Liquids | GT |  | S | X | X | WAUESPIRITMUNSPIRIT_2_UNIT_RA | WAUE.BEPM.SMS2 | 67.5 | 0.9 | 45 | 60 | 10 | N |  |  | OP | X | 6 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1979 | hard coal | TRUE | 14063 | Oklahoma Gas & Electric Co | 6095 | Sooner | OK | Noble | 1 | Conventional Steam Coal | ST |  | S | X | X | OKGESO1 | OKGESO1 | 569 | 0.9 | 516 | 516 | 200 | N |  |  | OP | X | 11 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: DFO; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1980 | hard coal | TRUE | 14063 | Oklahoma Gas & Electric Co | 6095 | Sooner | OK | Noble | 2 | Conventional Steam Coal | ST |  | S | X | X | OKGESO2 | OKGESO2 | 569 | 0.9 | 515 | 515 | 200 | N |  |  | OP | X | 12 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: DFO; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1979 | hard coal | TRUE | 14127 | Omaha Public Power District | 6096 | Nebraska City | NE | Otoe | 1 | Conventional Steam Coal | ST |  | S | X | X | NEBRASKA_CITY_1 |  | 651.6 | 0.9 | 654.3 | 654.3 | 180 | N |  |  | OP | X | 4 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO DFO DFO: NG; DFO NG NG: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage2009 | hard coal | TRUE | 14127 | Omaha Public Power District | 6096 | Nebraska City | NE | Otoe | 2 | Conventional Steam Coal | ST |  | S | X | X | NEBRASKA_CITY_2 |  | 738 | 0.9 | 691 | 691 | 235 | N |  |  | OP | X | 5 | 2009 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO DFO DFO: NG; DFO NG NG: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1975 | hard coal | TRUE | 14232 | Otter Tail Power Co | 6098 | Big Stone | SD | Grant | 1 | Conventional Steam Coal | ST |  | J | X | X | OTP.BIGSTON1 | OTP.BIGSTON1 | 450 | 0.9 | 474 | 474 | 150 | N |  |  | OP | X | 5 | 1975 |  |  | Y | Electric Utility | 1 | X X X: T; DFO RC RC: SUB; DFO SUB SUB: DFO; DFO DFO DFO: AB; DFO DFO DFO: DFO |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1975 | petroleum | TRUE | 14232 | Otter Tail Power Co | 6098 | Big Stone | SD | Grant | D1 | Petroleum Liquids | IC |  | J | X | X |  |  | 1 | 0.8 | 0.6 | 0.6 | 0.1 | N |  |  | SB | Y | 5 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1985 | nuclear | TRUE | 14328 | Pacific Gas & Electric Co. | 6099 | Diablo Canyon | CA | San Luis Obispo | 1 | Nuclear | ST |  | S | X | X | DIABLO1_7_B1 | DIABLO1_7_B1 | 1159 | 0.9 | 1122 | 1122 | 0 | N |  |  | OP | X | 5 | 1985 | 11 | 2024 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC |  |  | N |  |  | OVER | [23 empty] | N
Vintage1986 | nuclear | TRUE | 14328 | Pacific Gas & Electric Co. | 6099 | Diablo Canyon | CA | San Luis Obispo | 2 | Nuclear | ST |  | S | X | X | DIABLO2_7_B1 | DIABLO2_7_B1 | 1164 | 0.9 | 1118 | 1118 | 0 | N |  |  | OP | X | 3 | 1986 | 8 | 2025 | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC |  |  | N |  |  | OVER | [23 empty] | N
Vintage1984 | other | TRUE | 14328 | Pacific Gas & Electric Co. | 6100 | Helms Pumped Storage | CA | Fresno | 1 | Hydroelectric Pumped Storage | PS |  | S | X | X | HELMS1_7_B1 | HELMS1_7_B1 | 351 | 0.9 | 404 | 404 | 83 | N |  |  | OS | X | 6 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1984 | other | TRUE | 14328 | Pacific Gas & Electric Co. | 6100 | Helms Pumped Storage | CA | Fresno | 2 | Hydroelectric Pumped Storage | PS |  | S | X | X | HELMS2_7_B1 | HELMS2_7_B1 | 351 | 0.9 | 404 | 404 | 83 | N |  |  | OP | X | 6 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1984 | other | TRUE | 14328 | Pacific Gas & Electric Co. | 6100 | Helms Pumped Storage | CA | Fresno | 3 | Hydroelectric Pumped Storage | PS |  | S | X | X | HELMS3_7_B1 | HELMS3_7_B1 | 351 | 0.9 | 404 | 404 | 83 | N |  |  | OP | X | 6 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1978 | hard coal | TRUE | 14354 | PacifiCorp | 6101 | Wyodak | WY | Campbell | 1 | Conventional Steam Coal | ST |  | J | X | X |  |  | 402.3 | 0.9 | 332 | 335 | 130 | N |  |  | OP | X | 9 | 1978 | 12 | 2039 | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: DFO; DFO DFO DFO: DFO |  |  | N |  |  | OVER |  | Y |  |  | Y |  | N | [16 empty] | N
Vintage1983 | nuclear | TRUE | 14266 | TalenEnergy Susquehanna LLC | 6103 | TalenEnergy Susquehanna | PA | Luzerne | 1 | Nuclear | ST |  | J | X | X | 50654 | 50654 | 1266 | 0.935 | 1247 | 1247 | 170 | N |  |  | OP | X | 6 | 1983 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  |  | N |  | OVER | [23 empty] | N | N | N
Vintage1985 | nuclear | TRUE | 14266 | TalenEnergy Susquehanna LLC | 6103 | TalenEnergy Susquehanna | PA | Luzerne | 2 | Nuclear | ST |  | J | X | X | 50655 | 50655 | 1266 | 0.935 | 1247 | 1247 | 170 | N |  |  | OP | X | 2 | 1985 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  |  | N |  | OVER | [23 empty] | N | N | N
Vintage1986 | nuclear | TRUE | 55951 | Exelon Nuclear | 6105 | Limerick | PA | Montgomery | 1 | Nuclear | ST |  | S | X | X | 20021101 | 20021101 | 1138.5 | 0.9 | 1119.7 | 1180.1 | 55 | N |  |  | OP | X | 2 | 1986 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N
Vintage1990 | nuclear | TRUE | 55951 | Exelon Nuclear | 6105 | Limerick | PA | Montgomery | 2 | Nuclear | ST |  | S | X | X | 20021102 | 20021102 | 1138.5 | 0.9 | 1122.1 | 1188.1 | 55 | N |  |  | OP | X | 1 | 1990 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N
Vintage1976 | nuclear | TRUE | 55951 | Exelon Nuclear | 6110 | James A Fitzpatrick | NY | Oswego | 1 | Nuclear | ST |  | S | X | X | 23598 | 23598 | 883.3 | 0.9 | 854 | 855.5 | 125 | N |  |  | OP | X | 8 | 1976 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1998 | natural gas combined cycle | TRUE | 15466 | Public Service Co of Colorado | 6112 | Fort St Vrain | CO | Weld | 1 | Natural Gas Fired Combined Cycle | CA | FSV0 | S | Y | X |  |  | 342.6 | 0.85 | 301 | 304 | 39 | N |  |  | OP | X | 7 | 1998 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | bar: X X X to DFO RC RC
Vintage1996 | natural gas combined cycle | TRUE | 15466 | Public Service Co of Colorado | 6112 | Fort St Vrain | CO | Weld | 2 | Natural Gas Fired Combined Cycle | CT | FSV0 | S | X | Y |  |  | 175.1 | 0.85 | 123 | 134 | 65 | N |  |  | OP | X | 5 | 1996 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: X X X to DFO RC RC
Vintage1999 | natural gas combined cycle | TRUE | 15466 | Public Service Co of Colorado | 6112 | Fort St Vrain | CO | Weld | 3 | Natural Gas Fired Combined Cycle | CT | FSV0 | S | X | Y |  |  | 175.1 | 0.85 | 128 | 139 | 65 | N |  |  | OP | X | 1 | 1999 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: X X X to DFO RC RC
Vintage2001 | natural gas combined cycle | TRUE | 15466 | Public Service Co of Colorado | 6112 | Fort St Vrain | CO | Weld | 4 | Natural Gas Fired Combined Cycle | CT | FSV0 | S | X | Y |  |  | 175.1 | 0.85 | 133 | 163 | 65 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [7 empty] | 5 | 24 | 1 | 2022 | [12 empty] | N | N | bar: X X X to DFO RC RC
Vintage2009 | natural gas peaker | TRUE | 15466 | Public Service Co of Colorado | 6112 | Fort St Vrain | CO | Weld | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 140.3 | 0.85 | 144 | 159 | 55 | N |  |  | OP | X | 5 | 2009 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: X X X to DFO RC RC
Vintage2009 | natural gas peaker | TRUE | 15466 | Public Service Co of Colorado | 6112 | Fort St Vrain | CO | Weld | 6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 140.3 | 0.85 | 144 | 159 | 52 | N |  |  | OP | X | 5 | 2009 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: X X X to DFO RC RC
Vintage1976 | hard coal | TRUE | 15470 | Duke Energy Indiana, LLC | 6113 | Gibson | IN | Gibson | 1 | Conventional Steam Coal | ST |  | S | X | X | CP/Comm Pricing | CP/Comm Pricing | 667.9 | 0.9 | 630 | 635 | 200 | N |  |  | OP | X | 5 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: DFO; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | N
Vintage1975 | hard coal | TRUE | 15470 | Duke Energy Indiana, LLC | 6113 | Gibson | IN | Gibson | 2 | Conventional Steam Coal | ST |  | S | X | X | CP/Comm Pricing | CP/Comm Pricing | 667.9 | 0.9 | 630 | 635 | 200 | N |  |  | OP | X | 4 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: DFO; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | N
Vintage1978 | hard coal | TRUE | 15470 | Duke Energy Indiana, LLC | 6113 | Gibson | IN | Gibson | 3 | Conventional Steam Coal | ST |  | S | X | X | CP/Comm Pricing | CP/Comm Pricing | 667.9 | 0.9 | 630 | 635 | 200 | N |  |  | OP | X | 3 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: DFO; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | N
Vintage1979 | hard coal | TRUE | 15470 | Duke Energy Indiana, LLC | 6113 | Gibson | IN | Gibson | 4 | Conventional Steam Coal | ST |  | S | X | X | CP/Comm Pricing | CP/Comm Pricing | 667.9 | 0.9 | 622 | 627 | 200 | N |  |  | OP | X | 3 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: DFO; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | N
Vintage1982 | hard coal | TRUE | 15470 | Duke Energy Indiana, LLC | 6113 | Gibson | IN | Gibson | 5 | Conventional Steam Coal | ST |  | J | X | X | CP/Comm Pricing | CP/Comm Pricing | 667.9 | 0.9 | 620 | 625 | 200 | N |  |  | OP | X | 10 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: DFO; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | N
Vintage1990 | nuclear | TRUE | 6854 | NextEra Energy Seabrook LLC | 6115 | Seabrook | NH | Rockingham | 1 | Nuclear | ST |  | J | X | X |  |  | 1242 | 0.95 | 1248.1 | 1251.4 | 360 | N |  |  | OP | X | 8 | 1990 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1986 | nuclear | TRUE | 15478 | PSEG Nuclear LLC | 6118 | PSEG Hope Creek Generating Station | NJ | Salem | 1 | Nuclear | ST |  | S | X | X | 50483 | HOPECREE25 KV | 1290.7 | 0.94 | 1172 | 1172 | 1172 | N |  |  | OP | X | 12 | 1986 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1912 | hydro | TRUE | 61122 | Great River Hydro, LLC | 6119 | Deerfield 4 | MA | Franklin | GEN1 | Conventional Hydroelectric | HY |  | S | X | X | 465 |  | 1.6 | 0.8 | 2 | 2 | 1 | N |  |  | OP | X | 8 | 1912 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1912 | hydro | TRUE | 61122 | Great River Hydro, LLC | 6119 | Deerfield 4 | MA | Franklin | GEN2 | Conventional Hydroelectric | HY |  | S | X | X | 465 |  | 1.6 | 0.8 | 2 | 2 | 1 | N |  |  | OP | X | 8 | 1912 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1912 | hydro | TRUE | 61122 | Great River Hydro, LLC | 6119 | Deerfield 4 | MA | Franklin | GEN3 | Conventional Hydroelectric | HY |  | S | X | X | 465 |  | 1.6 | 0.8 | 2 | 2 | 1 | N |  |  | OP | X | 8 | 1912 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1981 | natural gas peaker | TRUE | 15500 | Puget Sound Energy Inc | 6120 | Whitehorn | WA | Whatcom | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 84.6 | 0.9 | 67 | 81.1 | 5 | N |  |  | OP | X | 10 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1981 | natural gas peaker | TRUE | 15500 | Puget Sound Energy Inc | 6120 | Whitehorn | WA | Whatcom | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 84.6 | 0.9 | 67 | 81.1 | 5 | N |  |  | OP | X | 10 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1970 | nuclear | TRUE | 55951 | Exelon Nuclear | 6122 | R E Ginna Nuclear Power Plant | NY | Wayne | 1 | Nuclear | ST |  | S | X | X |  |  | 614 | 0.92 | 580.2 | 581.3 | 133 | N |  |  | OP | X | 7 | 1970 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N
Vintage1995 | natural gas peaker | TRUE | 7140 | Georgia Power Co | 6124 | McIntosh | GA | Effingham | CT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 101.3 | 0.85 | 82.2 | 94.5 | 57 | N |  |  | OP | X | 5 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1995 | natural gas peaker | TRUE | 7140 | Georgia Power Co | 6124 | McIntosh | GA | Effingham | CT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 101.3 | 0.85 | 82.2 | 94.5 | 57 | N |  |  | OP | X | 4 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1994 | natural gas peaker | TRUE | 7140 | Georgia Power Co | 6124 | McIntosh | GA | Effingham | CT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 101.3 | 0.85 | 82.2 | 94.5 | 57 | N |  |  | OP | X | 6 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1994 | natural gas peaker | TRUE | 7140 | Georgia Power Co | 6124 | McIntosh | GA | Effingham | CT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 101.3 | 0.85 | 82.2 | 94.5 | 57 | N |  |  | OP | X | 5 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1994 | natural gas peaker | TRUE | 7140 | Georgia Power Co | 6124 | McIntosh | GA | Effingham | CT5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 101.3 | 0.85 | 82.2 | 94.5 | 57 | N |  |  | OP | X | 4 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1994 | natural gas peaker | TRUE | 7140 | Georgia Power Co | 6124 | McIntosh | GA | Effingham | CT6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 101.3 | 0.85 | 82.2 | 94.5 | 57 | N |  |  | OP | X | 5 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1994 | natural gas peaker | TRUE | 7140 | Georgia Power Co | 6124 | McIntosh | GA | Effingham | CT7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 101.3 | 0.85 | 82.2 | 94.5 | 57 | N |  |  | OP | X | 4 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1994 | natural gas peaker | TRUE | 7140 | Georgia Power Co | 6124 | McIntosh | GA | Effingham | CT8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 101.3 | 0.85 | 82.2 | 94.5 | 57 | N |  |  | OP | X | 2 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1969 | petroleum | TRUE | 17127 | Town of Shrewsbury - (MA) | 6125 | Shrewsbury | MA | Worcester | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.8 | 0.8 | 2.8 | 2.8 | 0.6 | N |  |  | OP | X | 11 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1969 | petroleum | TRUE | 17127 | Town of Shrewsbury - (MA) | 6125 | Shrewsbury | MA | Worcester | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.8 | 0.8 | 2.8 | 2.8 | 0.6 | N |  |  | OP | X | 11 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1975 | petroleum | TRUE | 17127 | Town of Shrewsbury - (MA) | 6125 | Shrewsbury | MA | Worcester | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.8 | 0.8 | 2.8 | 2.8 | 0.6 | N |  |  | OP | X | 12 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1975 | petroleum | TRUE | 17127 | Town of Shrewsbury - (MA) | 6125 | Shrewsbury | MA | Worcester | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.8 | 0.8 | 2.8 | 2.8 | 0.6 | N |  |  | OP | X | 12 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1978 | petroleum | TRUE | 17127 | Town of Shrewsbury - (MA) | 6125 | Shrewsbury | MA | Worcester | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.8 | 0.8 | 2.8 | 2.8 | 0.6 | N |  |  | OP | X | 5 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1978 | other | TRUE | 17539 | Dominion Energy South Carolina, Inc | 6126 | Fairfield Pumped Storage | SC | Fairfield | 1 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 73.4 | 0.9 | 72 | 72 | 50 | N |  |  | OP | X | 6 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1978 | other | TRUE | 17539 | Dominion Energy South Carolina, Inc | 6126 | Fairfield Pumped Storage | SC | Fairfield | 2 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 73.4 | 0.9 | 72 | 72 | 50 | N |  |  | OP | X | 6 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1978 | other | TRUE | 17539 | Dominion Energy South Carolina, Inc | 6126 | Fairfield Pumped Storage | SC | Fairfield | 3 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 73.4 | 0.9 | 72 | 72 | 50 | N |  |  | OP | X | 6 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1978 | other | TRUE | 17539 | Dominion Energy South Carolina, Inc | 6126 | Fairfield Pumped Storage | SC | Fairfield | 4 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 73.4 | 0.9 | 72 | 72 | 50 | N |  |  | OP | X | 6 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1978 | other | TRUE | 17539 | Dominion Energy South Carolina, Inc | 6126 | Fairfield Pumped Storage | SC | Fairfield | 5 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 73.4 | 0.9 | 72 | 72 | 50 | N |  |  | OP | X | 12 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1978 | other | TRUE | 17539 | Dominion Energy South Carolina, Inc | 6126 | Fairfield Pumped Storage | SC | Fairfield | 6 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 73.4 | 0.9 | 72 | 72 | 50 | N |  |  | OP | X | 12 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1978 | other | TRUE | 17539 | Dominion Energy South Carolina, Inc | 6126 | Fairfield Pumped Storage | SC | Fairfield | 7 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 73.4 | 0.9 | 72 | 72 | 50 | N |  |  | OP | X | 12 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1978 | other | TRUE | 17539 | Dominion Energy South Carolina, Inc | 6126 | Fairfield Pumped Storage | SC | Fairfield | 8 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 73.4 | 0.9 | 72 | 72 | 50 | N |  |  | OP | X | 12 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1984 | nuclear | TRUE | 17539 | Dominion Energy South Carolina, Inc | 6127 | V C Summer | SC | Fairfield | 1 | Nuclear | ST |  | J | X | X |  |  | 1029.6 | 0.905 | 977.2 | 994.1 | 150 | N |  |  | OP | X | 1 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [20 empty] | N |  |  | N | N | N
Vintage1983 | hydro | TRUE | 9339 | International Bound & Wtr Comm | 6128 | Amistad Dam & Power | TX | Val Verde | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 33 | 0.9 | 29 | 29 | 29 | N |  |  | OP | X | 6 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1983 | hydro | TRUE | 9339 | International Bound & Wtr Comm | 6128 | Amistad Dam & Power | TX | Val Verde | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 33 | 0.9 | 29 | 29 | 27 | N |  |  | OP | X | 10 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1975 | hydro | TRUE | 27813 | USCE-Mobile District | 6130 | Carters | GA | Murray | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 125 | 0.95 | 120 | 140 | 120 | N |  |  | OP | X | 11 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1975 | hydro | TRUE | 27813 | USCE-Mobile District | 6130 | Carters | GA | Murray | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 125 | 0.95 | 120 | 140 | 120 | N |  |  | OP | X | 7 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1977 | other | TRUE | 27813 | USCE-Mobile District | 6130 | Carters | GA | Murray | 3 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 125 | 0.95 | 160 | 160 | 140 | N |  |  | OP | X | 9 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1977 | other | TRUE | 27813 | USCE-Mobile District | 6130 | Carters | GA | Murray | 4 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 125 | 0.95 | 160 | 160 | 140 | N |  |  | OP | X | 6 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M
Vintage1975 | hydro | TRUE | 27813 | USCE-Mobile District | 6131 | Jones Bluff | AL | Autauga | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 20.5 | 0.95 | 20.5 | 20.5 | 15 | N |  |  | OP | X | 6 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1975 | hydro | TRUE | 27813 | USCE-Mobile District | 6131 | Jones Bluff | AL | Autauga | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 20.5 | 0.95 | 20.5 | 20.5 | 15 | N |  |  | OP | X | 7 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1975 | hydro | TRUE | 27813 | USCE-Mobile District | 6131 | Jones Bluff | AL | Autauga | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 20.5 | 0.95 | 20.5 | 20.5 | 15 | N |  |  | OP | X | 9 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1975 | hydro | TRUE | 27813 | USCE-Mobile District | 6131 | Jones Bluff | AL | Autauga | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 20.5 | 0.95 | 20.5 | 20.5 | 15 | N |  |  | OP | X | 10 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1985 | hydro | TRUE | 19375 | USCE-Savannah District | 6132 | Richard B Russell | GA | Elbert | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 75 | 0.95 | 84 | 84 | 70 | N |  |  | OP | X | 1 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 19375 | USCE-Savannah District | 6132 | Richard B Russell | GA | Elbert | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 75 | 0.95 | 84 | 84 | 70 | N |  |  | OP | X | 2 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 19375 | USCE-Savannah District | 6132 | Richard B Russell | GA | Elbert | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 75 | 0.95 | 84 | 84 | 70 | N |  |  | OP | X | 7 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage1986 | hydro | TRUE | 19375 | USCE-Savannah District | 6132 | Richard B Russell | GA | Elbert | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 75 | 0.95 | 84 | 84 | 70 | N |  |  | OP | X | 1 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage2002 | other | TRUE | 19375 | USCE-Savannah District | 6132 | Richard B Russell | GA | Elbert | 5 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 82 | 0.95 | 82 | 82 | 70 | N |  |  | OS | X | 9 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage2002 | other | TRUE | 19375 | USCE-Savannah District | 6132 | Richard B Russell | GA | Elbert | 6 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 82 | 0.95 | 82 | 82 | 70 | N |  |  | OP | X | 9 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage2002 | other | TRUE | 19375 | USCE-Savannah District | 6132 | Richard B Russell | GA | Elbert | 7 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 82 | 0.95 | 82 | 82 | 70 | N |  |  | OP | X | 9 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage2002 | other | TRUE | 19375 | USCE-Savannah District | 6132 | Richard B Russell | GA | Elbert | 8 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 82 | 0.95 | 82 | 82 | 70 | N |  |  | OP | X | 9 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1975 | hydro | TRUE | 27813 | USCE-Mobile District | 6133 | West Point (GA) | GA | Troup | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.3 | 0.9 | 3 | 3 | 3 | N |  |  | OP | X | 4 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1975 | hydro | TRUE | 27813 | USCE-Mobile District | 6133 | West Point (GA) | GA | Troup | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 35 | 0.9 | 42 | 42 | 35 | N |  |  | OP | X | 4 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1975 | hydro | TRUE | 27813 | USCE-Mobile District | 6133 | West Point (GA) | GA | Troup | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 35 | 0.9 | 42 | 42 | 35 | N |  |  | OP | X | 4 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  | 0 | 10M
Vintage1979 | hard coal | TRUE | 17633 | Southern Indiana Gas & Elec Co | 6137 | A B Brown | IN | Posey | 1 | Conventional Steam Coal | ST |  | S | X | X | SIGE.10ABBGN1 | SIGE.10ABBGN1 | 265.2 | 0.9 | 245 | 245 | 120 | N |  |  | OP | X | 3 | 1979 | 10 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N
Vintage1986 | hard coal | TRUE | 17633 | Southern Indiana Gas & Elec Co | 6137 | A B Brown | IN | Posey | 2 | Conventional Steam Coal | ST |  | S | X | X | SIGE.10ABBGN2 | SIGE.10ABBGN2 | 265.2 | 0.9 | 245 | 245 | 120 | N |  |  | OP | X | 2 | 1986 | 10 | 2023 | N | Electric Utility | 1 | X X X: X; DFO RC RC: BIT; DFO SUB SUB: NG; DFO DFO DFO: NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N
Vintage1991 | natural gas peaker | TRUE | 17633 | Southern Indiana Gas & Elec Co | 6137 | A B Brown | IN | Posey | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SIGE.10ABGTGT | SIGE.10ABGTGT | 88.2 | 0.85 | 80 | 87 | 10 | N |  |  | OP | X | 6 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NG; DFO SUB SUB: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 17633 | Southern Indiana Gas & Elec Co | 6137 | A B Brown | IN | Posey | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SIGE.10ABBROWUN4 | SIGE.10ABBROWUN4 | 88.2 | 0.85 | 80 | 87 | 10 | N |  |  | OP | X | 5 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to DFO RC RC
Vintage1978 | hard coal | TRUE | 17698 | Southwestern Electric Power Co | 6138 | Flint Creek | AR | Benton | 1 | Conventional Steam Coal | ST |  | J | X | X |  |  | 558 | 0.9 | 494 | 494 | 190 | N |  |  | OP | X | 5 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: DFO; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1977 | hard coal | TRUE | 17698 | Southwestern Electric Power Co | 6139 | Welsh | TX | Titus | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 558 | 0.9 | 500 | 500 | 150 | N |  |  | OP | X | 3 | 1977 | 1 | 2028 | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1982 | hard coal | TRUE | 17698 | Southwestern Electric Power Co | 6139 | Welsh | TX | Titus | 3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 558 | 0.9 | 500 | 500 | 150 | N |  |  | OP | X | 3 | 1982 | 1 | 2028 | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1984 | hydro | TRUE | 26618 | USCE-St Louis District | 6140 | Clarence Cannon | MO | Ralls | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 27 | 0.95 | 27 | 27 | 27 | N |  |  | OP | X | 11 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H
Vintage1984 | other | TRUE | 26618 | USCE-St Louis District | 6140 | Clarence Cannon | MO | Ralls | 2 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 31 | 0.95 | 31 | 31 | 31 | N |  |  | OP | X | 11 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H
Vintage1982 | other | TRUE | 25477 | USCE-Kansas City District | 6141 | Harry Truman | MO | Benton | 1 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 26.9 | 0.95 | 31 | 31 | 3 | N |  |  | OP | X | 5 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1982 | other | TRUE | 25477 | USCE-Kansas City District | 6141 | Harry Truman | MO | Benton | 2 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 26.9 | 0.95 | 31 | 31 | 3 | N |  |  | OP | X | 8 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1982 | other | TRUE | 25477 | USCE-Kansas City District | 6141 | Harry Truman | MO | Benton | 3 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 26.9 | 0.95 | 31 | 31 | 3 | N |  |  | OP | X | 7 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1982 | other | TRUE | 25477 | USCE-Kansas City District | 6141 | Harry Truman | MO | Benton | 4 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 26.9 | 0.95 | 31 | 31 | 3 | N |  |  | OP | X | 2 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1981 | other | TRUE | 25477 | USCE-Kansas City District | 6141 | Harry Truman | MO | Benton | 5 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 26.9 | 0.95 | 31 | 31 | 3 | N |  |  | OP | X | 12 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1979 | other | TRUE | 25477 | USCE-Kansas City District | 6141 | Harry Truman | MO | Benton | 6 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 26.9 | 0.95 | 31 | 31 | 3 | N |  |  | OP | X | 12 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1972 | hydro | TRUE | 19647 | USCE-Little Rock District | 6142 | Ozark | AR | Franklin | 1 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 20 | 0.95 | 23 | 23 | 7 | N |  |  | OA | X | 11 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1973 | hydro | TRUE | 19647 | USCE-Little Rock District | 6142 | Ozark | AR | Franklin | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 20 | 0.95 | 23 | 23 | 7 | N |  |  | OP | X | 8 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1973 | hydro | TRUE | 19647 | USCE-Little Rock District | 6142 | Ozark | AR | Franklin | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 20 | 0.95 | 23 | 23 | 7 | N |  |  | OP | X | 10 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1973 | hydro | TRUE | 19647 | USCE-Little Rock District | 6142 | Ozark | AR | Franklin | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 20 | 0.95 | 23 | 23 | 7 | N |  |  | OS | X | 12 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1974 | hydro | TRUE | 19647 | USCE-Little Rock District | 6142 | Ozark | AR | Franklin | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 20 | 0.95 | 23 | 23 | 7 | N |  |  | OA | X | 5 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N |  |  | 10M | [23 empty] | N
Vintage1990 | nuclear | TRUE | 55983 | Luminant Generation Company LLC | 6145 | Comanche Peak | TX | Somervell | 1 | Nuclear | ST |  | W | X | X |  |  | 1215 | 0.9 | 1205 | 1235 | 1112 | N |  |  | OP | X | 8 | 1990 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N
Vintage1993 | nuclear | TRUE | 55983 | Luminant Generation Company LLC | 6145 | Comanche Peak | TX | Somervell | 2 | Nuclear | ST |  | W | X | X |  |  | 1215 | 0.9 | 1195 | 1225 | 1103 | N |  |  | OP | X | 4 | 1993 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N
Vintage1977 | hard coal | TRUE | 55983 | Luminant Generation Company LLC | 6146 | Martin Lake | TX | Rusk | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 793.2 | 0.95 | 800 | 815 | 220 | N |  |  | OP | X | 5 | 1977 |  |  | N | IPP Non-CHP | 2 | X | SUB | LIG | DFO | RC |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | Y | Y | N
Vintage1978 | hard coal | TRUE | 55983 | Luminant Generation Company LLC | 6146 | Martin Lake | TX | Rusk | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 793.2 | 0.95 | 805 | 820 | 220 | N |  |  | OP | X | 5 | 1978 |  |  | N | IPP Non-CHP | 2 | X | SUB | LIG | DFO | RC |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | Y | Y | N
Vintage1979 | hard coal | TRUE | 55983 | Luminant Generation Company LLC | 6146 | Martin Lake | TX | Rusk | 3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 793.2 | 0.95 | 805 | 820 | 230 | N |  |  | OP | X | 4 | 1979 |  |  | N | IPP Non-CHP | 2 | X | SUB | LIG | DFO | RC |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | Y | Y | N
Vintage1977 | nuclear | TRUE | 64225 | Energy Harbor Nuclear Generation LLC | 6149 | Davis Besse | OH | Ottawa | 1 | Nuclear | ST |  | S | X | X |  |  | 925.2 | 0.9 | 894 | 908 | 110 | N |  |  | OP | X | 11 | 1977 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NUC |  |  | N | N |  | OVER | [23 empty] | N | N
Vintage1998 | petroleum | TRUE | 18642 | Tennessee Valley Authority | 6150 | Bellefonte | AL | Jackson | DG-1 | Petroleum Liquids | IC |  | S | X | X |  |  | 7 | 0.8 | 7 | 7 | 7 | N |  |  | OS | X | 12 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage1998 | petroleum | TRUE | 18642 | Tennessee Valley Authority | 6150 | Bellefonte | AL | Jackson | DG-2 | Petroleum Liquids | IC |  | S | X | X |  |  | 7 | 0.8 | 7 | 7 | 7 | N |  |  | OS | X | 12 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: DFO |  |  | N |  |  | 10M | [23 empty] | N
Vintage1979 | other | TRUE | 18642 | Tennessee Valley Authority | 6151 | Raccoon Mountain | TN | Hamilton | 1 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 428.4 | 0.9 | 404.7 | 404.7 | 40 | N |  |  | OP | X | 1 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1978 | other | TRUE | 18642 | Tennessee Valley Authority | 6151 | Raccoon Mountain | TN | Hamilton | 2 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 428.4 | 0.9 | 404.1 | 404.1 | 300 | N |  |  | OP | X | 12 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1979 | other | TRUE | 18642 | Tennessee Valley Authority | 6151 | Raccoon Mountain | TN | Hamilton | 3 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 428.4 | 0.9 | 403.5 | 403.5 | 300 | N |  |  | OP | X | 2 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1979 | other | TRUE | 18642 | Tennessee Valley Authority | 6151 | Raccoon Mountain | TN | Hamilton | 4 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 428.4 | 0.9 | 404 | 404 | 300 | N |  |  | OP | X | 8 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1981 | nuclear | TRUE | 18642 | Tennessee Valley Authority | 6152 | Sequoyah | TN | Hamilton | 1 | Nuclear | ST |  | S | X | X |  |  | 1220.5 | 0.9 | 1152 | 1177.4 | 1152 | N |  |  | OP | X | 7 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC | [5 empty] | OVER | [23 empty] | N
Vintage1982 | nuclear | TRUE | 18642 | Tennessee Valley Authority | 6152 | Sequoyah | TN | Hamilton | 2 | Nuclear | ST |  | S | X | X |  |  | 1220.5 | 0.9 | 1125.7 | 1155.1 | 1125.7 | N |  |  | OP | X | 6 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC | [5 empty] | OVER | [23 empty] | N
Vintage1984 | nuclear | TRUE | 19436 | Union Electric Co - (MO) | 6153 | Callaway | MO | Callaway | 1 | Nuclear | ST |  | S | X | X | AMMO.CALLAWAY1 |  | 1235.8 | 0.9 | 1247 | 1295 | 800 | N |  |  | OP | X | 12 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC |  |  | N |  |  | OVER | [23 empty] | N
Vintage1976 | hard coal | TRUE | 19436 | Union Electric Co - (MO) | 6155 | Rush Island | MO | Jefferson | 1 | Conventional Steam Coal | ST |  | S | X | X | AMMO.RUSHIS1 | AMMO.RUSHIS1 | 621 | 0.9 | 622 | 643 | 275 | N |  |  | OP | X | 3 | 1976 | 12 | 2039 | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: SUB; DFO DFO DFO: DFO |  |  | N |  |  | OVER |  | Y |  |  | Y | N | [17 empty] | Y | N | N
Vintage1977 | hard coal | TRUE | 19436 | Union Electric Co - (MO) | 6155 | Rush Island | MO | Jefferson | 2 | Conventional Steam Coal | ST |  | S | X | X | AMMO.RUSHIS2 | AMMO.RUSHIS2 | 621 | 0.9 | 622 | 643 | 280 | N |  |  | OP | X | 3 | 1977 | 12 | 2039 | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: SUB; DFO DFO DFO: DFO |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1975 | natural gas steam turbine | TRUE | 15452 | PSEG Power Connecticut LLC | 6156 | New Haven Harbor | CT | New Haven | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | 513 | 513 | 460 | 0.9 | 432.6 | 453.3 | 100 | N |  |  | OP | X | 7 | 1975 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: NG; DFO SUB SUB: RFO; DFO DFO DFO: DFO |  |  | N | N |  | OVER | [23 empty] | Y | Y | Y
Vintage2012 | other | TRUE | 15452 | PSEG Power Connecticut LLC | 6156 | New Haven Harbor | CT | New Haven | 2 | Petroleum Liquids | GT |  | W | X | X | 15477 | 15477 | 60.5 | 0.85 | 43.2 | 47.7 | 43 | N |  |  | OP | X | 6 | 2012 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: KER; DFO SUB SUB: NG |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2012 | other | TRUE | 15452 | PSEG Power Connecticut LLC | 6156 | New Haven Harbor | CT | New Haven | 3 | Petroleum Liquids | GT |  | W | X | X | 40052 | 40052 | 60.5 | 0.85 | 43.2 | 47.7 | 43 | N |  |  | OP | X | 6 | 2012 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: KER; DFO SUB SUB: NG |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2012 | other | TRUE | 15452 | PSEG Power Connecticut LLC | 6156 | New Haven Harbor | CT | New Haven | 4 | Petroleum Liquids | GT |  | W | X | X | 40053 | 40053 | 60.5 | 0.85 | 43.2 | 47.7 | 43 | N |  |  | OP | X | 6 | 2012 |  |  | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: KER; DFO SUB SUB: NG |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1979 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6158 | New Melones | CA | Tuolumne | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 150 | 1 | 191 | 191 | 0 | N |  |  | OP | X | 6 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1979 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6158 | New Melones | CA | Tuolumne | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 150 | 1 | 191 | 191 | 0 | N |  |  | OP | X | 6 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1978 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6159 | Crystal | CO | Montrose | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 28 | 0.9 | 35 | 35 | 0 | N |  |  | OP | X | 6 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1942 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 125 | 1 | 125 | 125 | 0 | N |  |  | OP | X | 4 | 1942 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1951 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | 10 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 125 | 1 | 125 | 125 | 0 | N |  |  | OP | X | 9 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1951 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | 11 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 125 | 1 | 125 | 125 | 0 | N |  |  | OP | X | 6 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1951 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | 12 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 125 | 1 | 125 | 125 | 0 | N |  |  | OP | X | 4 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1950 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | 13 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 125 | 1 | 125 | 125 | 0 | N |  |  | OP | X | 10 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1950 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | 14 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 125 | 1 | 125 | 125 | 0 | N |  |  | OP | X | 7 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1950 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | 15 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 125 | 1 | 125 | 125 | 0 | N |  |  | OP | X | 4 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1949 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | 16 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 125 | 1 | 125 | 125 | 0 | N |  |  | OP | X | 9 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1949 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | 17 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 125 | 1 | 125 | 125 | 0 | N |  |  | OP | X | 7 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1949 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | 18 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 125 | 1 | 125 | 125 | 0 | N |  |  | OP | X | 5 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1975 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | 19 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 600 | 0.98 | 690 | 690 | 0 | N |  |  | OP | X | 9 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1942 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 125 | 1 | 125 | 125 | 0 | N |  |  | OP | X | 1 | 1942 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1976 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | 20 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 600 | 0.98 | 690 | 690 | 0 | N |  |  | OP | X | 4 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1976 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | 21 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 600 | 0.98 | 690 | 690 | 0 | N |  |  | OP | X | 12 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1978 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | 22 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 805 | 0.98 | 805 | 805 | 0 | N |  |  | OP | X | 5 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1979 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | 23 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 805 | 0.98 | 805 | 805 | 0 | N |  |  | OP | X | 11 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1980 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | 24 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 805 | 0.98 | 805 | 805 | 0 | N |  |  | OP | X | 5 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1941 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 125 | 1 | 125 | 125 | 0 | N |  |  | OP | X | 9 | 1941 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1944 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 125 | 1 | 125 | 125 | 0 | N |  |  | OP | X | 2 | 1944 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1943 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 125 | 1 | 125 | 125 | 0 | N |  |  | OP | X | 11 | 1943 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1943 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 125 | 1 | 125 | 125 | 0 | N |  |  | OP | X | 8 | 1943 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1947 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | 7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 125 | 1 | 125 | 125 | 0 | N |  |  | OP | X | 10 | 1947 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1943 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | 8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 125 | 1 | 125 | 125 | 0 | N |  |  | OP | X | 2 | 1943 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1948 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | 9 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 125 | 1 | 125 | 125 | 0 | N |  |  | OP | X | 4 | 1948 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1941 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | LS1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 1 | 10 | 10 | 0 | N |  |  | OP | X | 3 | 1941 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1941 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | LS2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 1 | 10 | 10 | 0 | N |  |  | OP | X | 3 | 1941 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1951 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | LS3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 1 | 10 | 10 | 0 | N |  |  | OP | X | 1 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1983 | other | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | PG10 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 53.5 | 1 | 53.5 | 53.5 | 0 | N |  |  | OP | X | 6 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1983 | other | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | PG11 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 53.5 | 1 | 53.5 | 53.5 | 0 | N |  |  | OP | X | 11 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1984 | other | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | PG12 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 53.5 | 1 | 53.5 | 53.5 | 0 | N |  |  | OP | X | 4 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1973 | other | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | PG7 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 50 | 1 | 50 | 50 | 0 | N |  |  | OP | X | 10 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1973 | other | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | PG8 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 50 | 1 | 50 | 50 | 0 | N |  |  | OP | X | 11 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1983 | other | TRUE | 2518 | U S Bureau of Reclamation | 6163 | Grand Coulee | WA | Grant | PG9 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 53.5 | 1 | 53.5 | 53.5 | 0 | N |  |  | OP | X | 4 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1978 | hard coal | TRUE | 14354 | PacifiCorp | 6165 | Hunter | UT | Emery | 1 | Conventional Steam Coal | ST |  | J | X | X |  |  | 525 | 0.93 | 446 | 446 | 80 | N |  |  | OP | X | 6 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: BIT; DFO DFO DFO: DFO; DFO DFO DFO: DFO |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1980 | hard coal | TRUE | 14354 | PacifiCorp | 6165 | Hunter | UT | Emery | 2 | Conventional Steam Coal | ST |  | J | X | X |  |  | 525 | 0.93 | 446 | 446 | 80 | N |  |  | OP | X | 6 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: BIT; DFO DFO DFO: DFO; DFO DFO DFO: DFO |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1983 | hard coal | TRUE | 14354 | PacifiCorp | 6165 | Hunter | UT | Emery | 3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 527.2 | 0.94 | 471 | 471 | 60 | N |  |  | OP | X | 6 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO SUB SUB: BIT; DFO DFO DFO: DFO; DFO DFO DFO: DFO |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1984 | hard coal | TRUE | 9324 | Indiana Michigan Power Co | 6166 | Rockport | IN | Spencer | 1 | Conventional Steam Coal | ST |  | J | X | X | 40243837 | 34497125 | 1300 | 0.9 | 1300 | 1299 | 500 | N |  |  | OP | X | 12 | 1984 | 12 | 2028 | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | N | N | N
Vintage1989 | hard coal | TRUE | 9324 | Indiana Michigan Power Co | 6166 | Rockport | IN | Spencer | 2 | Conventional Steam Coal | ST |  | J | X | X | 40243839 | 34497125 | 1300 | 0.9 | 1300 | 1299 | 500 | N |  |  | OP | X | 12 | 1989 | 12 | 2028 | N | Electric Utility | 1 | X X X: X; DFO RC RC: SUB; DFO SUB SUB: BIT; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | N | N | N
Vintage1985 | other | TRUE | 19876 | Virginia Electric & Power Co | 6167 | Bath County | VA | Bath | 1 | Hydroelectric Pumped Storage | PS |  | J | X | X |  |  | 477 | 0.9 | 500 | 500 | 207 | N |  |  | OP | X | 12 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 1H
Vintage1985 | other | TRUE | 19876 | Virginia Electric & Power Co | 6167 | Bath County | VA | Bath | 2 | Hydroelectric Pumped Storage | PS |  | J | X | X |  |  | 477 | 0.9 | 500 | 500 | 207 | N |  |  | OP | X | 12 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 1H
Vintage1985 | other | TRUE | 19876 | Virginia Electric & Power Co | 6167 | Bath County | VA | Bath | 3 | Hydroelectric Pumped Storage | PS |  | J | X | X |  |  | 477 | 0.9 | 502 | 502 | 207 | N |  |  | OP | X | 12 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 1H
Vintage1985 | other | TRUE | 19876 | Virginia Electric & Power Co | 6167 | Bath County | VA | Bath | 4 | Hydroelectric Pumped Storage | PS |  | J | X | X |  |  | 477 | 0.9 | 500 | 500 | 207 | N |  |  | OP | X | 12 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 1H
Vintage1985 | other | TRUE | 19876 | Virginia Electric & Power Co | 6167 | Bath County | VA | Bath | 5 | Hydroelectric Pumped Storage | PS |  | J | X | X |  |  | 477 | 0.9 | 501 | 501 | 207 | N |  |  | OP | X | 12 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 1H
Vintage1985 | other | TRUE | 19876 | Virginia Electric & Power Co | 6167 | Bath County | VA | Bath | 6 | Hydroelectric Pumped Storage | PS |  | J | X | X |  |  | 477 | 0.9 | 500 | 500 | 207 | N |  |  | OP | X | 12 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 1H
Vintage1978 | nuclear | TRUE | 19876 | Virginia Electric & Power Co | 6168 | North Anna | VA | Louisa | 1 | Nuclear | ST |  | J | X | X |  |  | 979.7 | 0.9 | 948 | 982 | 185 | N |  |  | OP | X | 6 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC | [5 empty] | OVER | [23 empty] | N
Vintage1980 | nuclear | TRUE | 19876 | Virginia Electric & Power Co | 6168 | North Anna | VA | Louisa | 2 | Nuclear | ST |  | J | X | X |  |  | 979.7 | 0.9 | 944 | 976 | 185 | N |  |  | OP | X | 12 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: NUC | [5 empty] | OVER | [23 empty] | N
Vintage1987 | hydro | TRUE | 19876 | Virginia Electric & Power Co | 6168 | North Anna | VA | Louisa | HC1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.9 | 1 | 1 | 0 | N |  |  | OP | X | 12 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  |  |  | 0 | 1H | [23 empty] | N
Vintage1977 | hydro | TRUE | 19462 | USCE-Nashville District | 6171 | Laurel Dam | KY | Laurel | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 70 | 0.9 | 61 | 61 | 61 | N |  |  | OP | X | 11 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1975 | hydro | TRUE | 19400 | USACE Northwestern Division | 6172 | Libby | MT | Lincoln | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 105 | 0.95 | 105 | 105 | 105 | N |  |  | OP | X | 8 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1975 | hydro | TRUE | 19400 | USACE Northwestern Division | 6172 | Libby | MT | Lincoln | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 105 | 0.95 | 105 | 105 | 105 | N |  |  | OP | X | 10 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1976 | hydro | TRUE | 19400 | USACE Northwestern Division | 6172 | Libby | MT | Lincoln | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 105 | 0.95 | 105 | 105 | 105 | N |  |  | OP | X | 1 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1976 | hydro | TRUE | 19400 | USACE Northwestern Division | 6172 | Libby | MT | Lincoln | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 105 | 0.95 | 105 | 105 | 105 | N |  |  | OP | X | 4 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1984 | hydro | TRUE | 19400 | USACE Northwestern Division | 6172 | Libby | MT | Lincoln | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 105 | 0.95 | 105 | 105 | 105 | N |  |  | OP | X | 9 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1977 | hydro | TRUE | 19400 | USACE Northwestern Division | 6174 | Lost Creek | OR | Jackson | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 24.5 | 0.95 | 24.5 | 24.5 | 24.4 | N |  |  | OP | X | 9 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1977 | hydro | TRUE | 19400 | USACE Northwestern Division | 6174 | Lost Creek | OR | Jackson | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 24.5 | 0.95 | 24.5 | 24.5 | 24.4 | N |  |  | OP | X | 12 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1975 | hydro | TRUE | 19400 | USACE Northwestern Division | 6175 | Lower Granite | WA | Whitman | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 135 | 135 | 110 | N |  |  | OA | X | 4 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1975 | hydro | TRUE | 19400 | USACE Northwestern Division | 6175 | Lower Granite | WA | Whitman | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 127 | 127 | 46.4 | N |  |  | OP | X | 5 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1975 | hydro | TRUE | 19400 | USACE Northwestern Division | 6175 | Lower Granite | WA | Whitman | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 135 | 135 | 46.4 | N |  |  | OP | X | 6 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1978 | hydro | TRUE | 19400 | USACE Northwestern Division | 6175 | Lower Granite | WA | Whitman | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 135 | 135 | 57.5 | N |  |  | OP | X | 2 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1978 | hydro | TRUE | 19400 | USACE Northwestern Division | 6175 | Lower Granite | WA | Whitman | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 135 | 135 | 57.5 | N |  |  | OP | X | 4 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1978 | hydro | TRUE | 19400 | USACE Northwestern Division | 6175 | Lower Granite | WA | Whitman | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 135 | 0.95 | 135 | 135 | 57.5 | N |  |  | OP | X | 4 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; DFO RC RC: WAT | [5 empty] | 10M
Vintage1979 | hard coal | TRUE | 16572 | Salt River Project | 6177 | Coronado | AZ | Apache | CO1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 410.9 | 0.9 | 380 | 380 | 50 | N |  |  | OP | X | 12 | 1979 | 12 | 2032 | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | N |  |  | N | N | N
Vintage1980 | hard coal | TRUE | 16572 | Salt River Project | 6177 | Coronado | AZ | Apache | CO2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 410.9 | 0.9 | 382 | 382 | 170 | N |  |  | OP | X | 10 | 1980 | 12 | 2032 | N | Electric Utility | 1 | X X X: X; DFO RC RC: RC; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | N |  |  | N | N | N
Vintage1980 | hard coal | TRUE | 56570 | Coleto Creek Power LP | 6178 | Coleto Creek | TX | Goliad | 1 | Conventional Steam Coal | ST |  | W | X | X |  |  | 622.4 | 0.9 | 655 | 655 | 175 | N |  |  | OP | X | 6 | 1980 | 12 | 2027 | N | IPP Non-CHP | 2 | X X X: X; DFO RC RC: RC; DFO SUB SUB: SUB; DFO DFO DFO: DFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1979 | hard coal | TRUE | 11269 | Lower Colorado River Authority | 6179 | Fayette Power Project | TX | Fayette | 1 | Conventional Steam Coal | ST |  | J | X | X |  |  | 615 | 0.9 | 590 | 598 | 156 | N |  |  | OP | X | 6 | 1979 |  |  | N | Electric Utility | 1 | X | RC | SUB | WC | WO | MSW | LIG | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | N | [14 empty] | N |  |  | N | N | N
Vintage1980 | hard coal | TRUE | 11269 | Lower Colorado River Authority | 6179 | Fayette Power Project | TX | Fayette | 2 | Conventional Steam Coal | ST |  | J | X | X |  |  | 615 | 0.9 | 590 | 598 | 156 | N |  |  | OP | X | 5 | 1980 |  |  | N | Electric Utility | 1 | X | RC | SUB | WC | WO | MSW | LIG | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | N | [14 empty] | N |  |  | N | N | N
Vintage1988 | hard coal | TRUE | 11269 | Lower Colorado River Authority | 6179 | Fayette Power Project | TX | Fayette | 3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 460 | 0.9 | 435 | 440 | 180 | N |  |  | OP | X | 4 | 1988 |  |  | N | Electric Utility | 1 | X | RC | SUB | WC | WO | MSW | LIG | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | N | [14 empty] | N |  |  | N | N | N
Vintage2010 | hard coal | TRUE | 55983 | Luminant Generation Company LLC | 6180 | Oak Grove (TX) | TX | Robertson | OG1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 916.8 | 0.96 | 855 | 855 | 348 | N |  |  | OP | X | 4 | 2010 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: RC; SUB SUB SUB: LIG; DFO DFO DFO: NG |  |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | Y | Y | N
Vintage2011 | hard coal | TRUE | 55983 | Luminant Generation Company LLC | 6180 | Oak Grove (TX) | TX | Robertson | OG2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 878.6 | 0.92 | 855 | 855 | 455 | N |  |  | OP | X | 4 | 2011 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: RC; SUB SUB SUB: LIG; DFO DFO DFO: NG |  |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | Y | Y | N
Vintage1977 | hard coal | TRUE | 16604 | City of San Antonio - (TX) | 6181 | J T Deely | TX | Bexar | 1 | Conventional Steam Coal | ST |  | S | X | X | CALAVER_JTD1 | CALAVER_JTD1 | 486 | 0.9 | 420 | 420 | 125 | N |  |  | OS | X | 8 | 1977 | 12 | 2024 | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; DFO DFO DFO: NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1978 | hard coal | TRUE | 16604 | City of San Antonio - (TX) | 6181 | J T Deely | TX | Bexar | 2 | Conventional Steam Coal | ST |  | S | X | X | CALAVER_JTD2 | CALAVER_JTD2 | 446 | 0.9 | 420 | 420 | 125 | N |  |  | OS | X | 8 | 1978 | 12 | 2024 | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; DFO DFO DFO: NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1982 | lignite | TRUE | 16624 | San Miguel Electric Coop, Inc | 6183 | San Miguel | TX | Atascosa | 1 | Conventional Steam Coal | ST |  | S | X | X | SAN_SANMIGG1 | SAN_SANMIGG1 | 410 | 0.9 | 391 | 391 | 250 | N |  |  | OP | X | 1 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: LIG; DFO DFO DFO: DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1983 | hydro | TRUE | 195 | Alabama Power Co | 6188 | Harris Dam | AL | Randolph | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 67.5 | 0.9 | 66.5 | 61.5 | 61.5 | N |  |  | OP | X | 4 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [5 empty] | 0 | 1H | [23 empty] | N
Vintage1983 | hydro | TRUE | 195 | Alabama Power Co | 6188 | Harris Dam | AL | Randolph | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 67.5 | 0.9 | 66.5 | 61.5 | 61.5 | N |  |  | OP | X | 4 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [5 empty] | 0 | 1H | [23 empty] | N
Vintage1995 | other | TRUE | 13994 | Oglethorpe Power Corporation | 6189 | Rocky Mountain Hydroelectric Plant | GA | Floyd | 1 | Hydroelectric Pumped Storage | PS |  | J | X | X |  |  | 282.6 | 0.9 | 345 | 345 | 100 | N |  |  | OP | X | 7 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1995 | other | TRUE | 13994 | Oglethorpe Power Corporation | 6189 | Rocky Mountain Hydroelectric Plant | GA | Floyd | 2 | Hydroelectric Pumped Storage | PS |  | J | X | X |  |  | 282.6 | 0.9 | 345 | 345 | 100 | N |  |  | OP | X | 6 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1995 | other | TRUE | 13994 | Oglethorpe Power Corporation | 6189 | Rocky Mountain Hydroelectric Plant | GA | Floyd | 3 | Hydroelectric Pumped Storage | PS |  | J | X | X |  |  | 282.6 | 0.9 | 345 | 345 | 100 | N |  |  | OP | X | 6 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1975 | natural gas steam turbine | TRUE | 3265 | Cleco Power LLC | 6190 | Brame Energy Center | LA | Rapides | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | CLEC.NPS1 |  | 445.5 | 0.9 | 426.2 | 422 | 55 | N |  |  | OP | X | 6 | 1975 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage1982 | hard coal | TRUE | 3265 | Cleco Power LLC | 6190 | Brame Energy Center | LA | Rapides | 2 | Conventional Steam Coal | ST |  | J | X | X | CLEC.RPS2 |  | 558 | 0.9 | 495.9 | 493 | 180 | N |  |  | OP | X | 8 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; DFO DFO DFO: NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage2010 | petroleum | TRUE | 3265 | Cleco Power LLC | 6190 | Brame Energy Center | LA | Rapides | 3 | Petroleum Coke | ST |  | S | X | X | CLECO.MPS3 |  | 703.8 | 0.85 | 624.8 | 628 | 400 | N |  |  | OP | X | 2 | 2010 |  |  | N | Electric Utility | 1 | X | PC | BIT | NG | SUB | LIG |  | NG |  |  |  | N | N |  | OVER | Y |  |  |  | Y | [18 empty] | Y | Y | N
Vintage1976 | hard coal | TRUE | 17718 | Southwestern Public Service Co | 6193 | Harrington | TX | Potter | 1 | Conventional Steam Coal | ST |  | S | X | X | SPS.HARRNGTN1 | SPS.HARRNGTN1 | 360 | 0.9 | 339 | 339 | 120 | N |  |  | OP | X | 1 | 1976 | 12 | 2036 | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; SUB SUB SUB: NG; DFO DFO DFO: NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1978 | hard coal | TRUE | 17718 | Southwestern Public Service Co | 6193 | Harrington | TX | Potter | 2 | Conventional Steam Coal | ST |  | S | X | X | SPS.HARRNGTN2 | SPS.HARRNGTN2 | 360 | 0.9 | 339 | 339 | 120 | N |  |  | OP | X | 1 | 1978 | 12 | 2038 | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; SUB SUB SUB: NG; DFO DFO DFO: NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1980 | hard coal | TRUE | 17718 | Southwestern Public Service Co | 6193 | Harrington | TX | Potter | 3 | Conventional Steam Coal | ST |  | S | X | X | SPS.HARRNGTN3 | SPS.HARRNGTN3 | 360 | 0.9 | 340 | 340 | 125 | N |  |  | OP | X | 1 | 1980 | 12 | 2040 | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; SUB SUB SUB: NG; DFO DFO DFO: NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1982 | hard coal | TRUE | 17718 | Southwestern Public Service Co | 6194 | Tolk | TX | Lamb | 1 | Conventional Steam Coal | ST |  | S | X | X | SPS.TOLK1 | SPS.TOLK1 | 567.9 | 0.9 | 532 | 532 | 125 | N |  |  | OP | X | 1 | 1982 | 12 | 2037 | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; SUB SUB SUB: NG; DFO DFO DFO: NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1985 | hard coal | TRUE | 17718 | Southwestern Public Service Co | 6194 | Tolk | TX | Lamb | 2 | Conventional Steam Coal | ST |  | S | X | X | SPS.TOLK2 | SPS.TOLK2 | 567.9 | 0.9 | 535 | 535 | 125 | N |  |  | OP | X | 1 | 1985 | 12 | 2037 | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; SUB SUB SUB: NG; DFO DFO DFO: NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1983 | natural gas peaker | TRUE | 17833 | City Utilities of Springfield - (MO) | 6195 | John Twitty Energy Center | MO | Greene | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SPRM_SWCT1 |  | 57 | 0.9 | 52 | 52 | 30 | N |  |  | OP | X | 6 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | N
Vintage1983 | natural gas peaker | TRUE | 17833 | City Utilities of Springfield - (MO) | 6195 | John Twitty Energy Center | MO | Greene | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SPRM_SWCT2 |  | 52 | 0.9 | 52 | 52 | 30 | N |  |  | OP | X | 6 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | N
Vintage1976 | hard coal | TRUE | 17833 | City Utilities of Springfield - (MO) | 6195 | John Twitty Energy Center | MO | Greene | ST1 | Conventional Steam Coal | ST |  | S | X | X | SPRM_SWPS1 |  | 194 | 0.9 | 184 | 184 | 84 | N |  |  | OP | X | 6 | 1976 |  |  | N | Electric Utility | 1 | X | SUB | NG | BIT |  |  |  | NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage2011 | hard coal | TRUE | 17833 | City Utilities of Springfield - (MO) | 6195 | John Twitty Energy Center | MO | Greene | ST2 | Conventional Steam Coal | ST |  | S | X | X | SPRM_SWPS2 |  | 300 | 0.85 | 275 | 275 | 116 | N |  |  | OP | X | 1 | 2011 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; SUB SUB SUB: NG; DFO DFO DFO: NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1982 | hydro | TRUE | 3255 | California Dept. of Water Resources | 6196 | W E Warne | CA | Los Angeles | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 37.1 | 0.95 | 38 | 38 | 5 | N |  |  | OP | X | 11 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage1983 | hydro | TRUE | 3255 | California Dept. of Water Resources | 6196 | W E Warne | CA | Los Angeles | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 37.1 | 0.95 | 38 | 38 | 5 | N |  |  | OP | X | 2 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage1931 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 6200 | Rock Island | WA | Chelan | A | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 0.2 | N |  |  | OP | X | 10 | 1931 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1931 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 6200 | Rock Island | WA | Chelan | B-1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 20.7 | 0.9 | 15 | 15 | 10 | N |  |  | OS | X | 11 | 1931 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | Y | 9 | 2024 | N
Vintage1953 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 6200 | Rock Island | WA | Chelan | B-10 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 22.5 | 0.9 | 19 | 19 | 10 | N |  |  | OP | X | 4 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1931 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 6200 | Rock Island | WA | Chelan | B-2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 20.7 | 0.9 | 15 | 15 | 10 | N |  |  | OS | X | 10 | 1931 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | Y | 1 | 2024 | N
Vintage1932 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 6200 | Rock Island | WA | Chelan | B-3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 20.7 | 0.9 | 15 | 15 | 10 | N |  |  | OS | X | 12 | 1932 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | Y | 4 | 2023 | N
Vintage1932 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 6200 | Rock Island | WA | Chelan | B-4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 20.7 | 0.9 | 15 | 15 | 10 | N |  |  | OP | X | 10 | 1932 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1952 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 6200 | Rock Island | WA | Chelan | B-5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 22.5 | 0.9 | 17 | 17 | 10 | N |  |  | OA | X | 9 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | Y | 8 | 2022 | N
Vintage1952 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 6200 | Rock Island | WA | Chelan | B-6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 22.5 | 0.9 | 17 | 17 | 10 | N |  |  | OA | X | 10 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | Y | 12 | 2022 | N
Vintage1952 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 6200 | Rock Island | WA | Chelan | B-7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 22.5 | 0.9 | 17 | 17 | 10 | N |  |  | OA | X | 11 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | Y | 6 | 2022 | N
Vintage1953 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 6200 | Rock Island | WA | Chelan | B-8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 22.5 | 0.9 | 17 | 17 | 10 | N |  |  | OP | X | 1 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | Y | 6 | 2023 | N
Vintage1953 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 6200 | Rock Island | WA | Chelan | B-9 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 22.5 | 0.9 | 19 | 19 | 10 | N |  |  | OP | X | 3 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | Y | 7 | 2023 | N
Vintage1979 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 6200 | Rock Island | WA | Chelan | U-1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 51.3 | 0.95 | 42 | 42 | 10 | N |  |  | OP | X | 8 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | Y | 10 | 2030 | N
Vintage1979 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 6200 | Rock Island | WA | Chelan | U-2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 51.3 | 0.95 | 42 | 42 | 10 | N |  |  | OP | X | 6 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | Y | 11 | 2029 | N
Vintage1979 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 6200 | Rock Island | WA | Chelan | U-3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 51.3 | 0.95 | 42 | 42 | 10 | N |  |  | OP | X | 4 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | Y | 3 | 2026 | N
Vintage1979 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 6200 | Rock Island | WA | Chelan | U-4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 51.3 | 0.95 | 42 | 42 | 10 | N |  |  | OP | X | 2 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | Y | 2 | 2027 | N
Vintage1978 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 6200 | Rock Island | WA | Chelan | U-5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 51.3 | 0.95 | 42 | 42 | 10 | N |  |  | OP | X | 12 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | Y | 2 | 2024 | N
Vintage1978 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 6200 | Rock Island | WA | Chelan | U-6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 51.3 | 0.95 | 42 | 42 | 10 | N |  |  | OP | X | 10 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | Y | 12 | 2028 | N
Vintage1978 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 6200 | Rock Island | WA | Chelan | U-7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 51.3 | 0.95 | 42 | 42 | 10 | N |  |  | OP | X | 8 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | Y | 4 | 2025 | N
Vintage1978 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 6200 | Rock Island | WA | Chelan | U-8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 51.3 | 0.95 | 42 | 42 | 10 | N |  |  | OP | X | 7 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | Y | 1 | 2028 | N
Vintage1956 | hydro | TRUE | 16868 | City of Seattle - (WA) | 6202 | Ross | WA | Whatcom | 41 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 112.5 | 0.9 | 112.5 | 112.5 | 0 | N |  |  | OP | X | 11 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | Y | 12 | 2023 | N
Vintage1954 | hydro | TRUE | 16868 | City of Seattle - (WA) | 6202 | Ross | WA | Whatcom | 42 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 112.5 | 0.9 | 112.5 | 112.5 | 0 | N |  |  | OP | X | 1 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | Y | 12 | 2023 | N
Vintage1953 | hydro | TRUE | 16868 | City of Seattle - (WA) | 6202 | Ross | WA | Whatcom | 43 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 112.5 | 0.9 | 112.5 | 112.5 | 0 | N |  |  | OP | X | 4 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | Y | 12 | 2024 | N
Vintage1952 | hydro | TRUE | 16868 | City of Seattle - (WA) | 6202 | Ross | WA | Whatcom | 44 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 112.5 | 0.9 | 112.5 | 112.5 | 0 | N |  |  | OP | X | 12 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | Y | 12 | 2024 | N
Vintage1981 | hard coal | TRUE | 1307 | Basin Electric Power Coop | 6204 | Laramie River Station | WY | Platte | 1 | Conventional Steam Coal | ST |  | J | X | X | WAUELARAMIEUNBEPM_LARAMIE_RA | WAUE.BEPM.LRS1 | 621 | 0.9 | 560 | 560 | 200 | N |  |  | OP | X | 9 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: RC; SUB SUB SUB: SUB; DFO DFO DFO: DFO |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1981 | hard coal | TRUE | 1307 | Basin Electric Power Coop | 6204 | Laramie River Station | WY | Platte | 2 | Conventional Steam Coal | ST |  | J | X | X |  |  | 621 | 0.9 | 570 | 570 | 200 | N |  |  | OP | X | 7 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: RC; SUB SUB SUB: SUB; DFO DFO DFO: DFO |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1982 | hard coal | TRUE | 1307 | Basin Electric Power Coop | 6204 | Laramie River Station | WY | Platte | 3 | Conventional Steam Coal | ST |  | J | X | X |  |  | 621 | 0.9 | 570 | 570 | 230 | N |  |  | OP | X | 11 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: RC; SUB SUB SUB: SUB; DFO DFO DFO: DFO |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1906 | hydro | TRUE | 15466 | Public Service Co of Colorado | 6206 | Tacoma | CO | La Plata | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.3 | 1 | 2.3 | 2.3 | 1 | N |  |  | OP | X | 6 | 1906 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  |  | N |  | 10M | [23 empty] | N
Vintage1905 | hydro | TRUE | 15466 | Public Service Co of Colorado | 6206 | Tacoma | CO | La Plata | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.3 | 1 | 2.3 | 2.3 | 1 | N |  |  | OP | X | 6 | 1905 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1906 | hydro | TRUE | 15466 | Public Service Co of Colorado | 6207 | Ames Hydro | CO | San Miguel | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.6 | 0.8 | 2.8 | 2.8 | 1 | N |  |  | OP | X | 6 | 1906 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1981 | other | TRUE | 2518 | U S Bureau of Reclamation | 6208 | Mount Elbert | CO | Lake | 1 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 100 | 0.95 | 115 | 115 | 0 | N |  |  | OP | X | 6 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1984 | other | TRUE | 2518 | U S Bureau of Reclamation | 6208 | Mount Elbert | CO | Lake | 2 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 100 | 0.95 | 115 | 115 | 0 | N |  |  | OP | X | 2 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1978 | natural gas peaker | TRUE | 20169 | Avista Corp | 6210 | Northeast (WA) | WA | Spokane | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 61.8 | 0.9 | 45 | 66 | 1 | N |  |  | OP | X | 12 | 1978 | 12 | 2035 | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC
Vintage1978 | petroleum | TRUE | 54803 | Dynegy Oakland, LLC | 6211 | Dynegy Oakland Power Plant | CA | Alameda | GEN1 | Petroleum Liquids | GT |  | S | X | X |  |  | 74.5 | 0.9 | 55 | 55 | 15 | N |  |  | OP | X | 11 | 1978 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: JF; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1978 | petroleum | TRUE | 54803 | Dynegy Oakland, LLC | 6211 | Dynegy Oakland Power Plant | CA | Alameda | GEN3 | Petroleum Liquids | GT |  | S | X | X |  |  | 74.5 | 0.9 | 55 | 55 | 15 | N |  |  | OP | X | 11 | 1978 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: JF; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1983 | hard coal | TRUE | 9267 | Hoosier Energy R E C, Inc | 6213 | Merom | IN | Sullivan | 1 | Conventional Steam Coal | ST |  | S | X | X | HE.MEROM1 | HE.MEROM1 | 540 | 0.9 | 495 | 502 | 250 | N |  |  | OP | X | 9 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: BIT; SUB SUB SUB: DFO; DFO DFO DFO: DFO |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1982 | hard coal | TRUE | 9267 | Hoosier Energy R E C, Inc | 6213 | Merom | IN | Sullivan | 2 | Conventional Steam Coal | ST |  | S | X | X | HE.MEROM2 | HE.MEROM2 | 540 | 0.9 | 494 | 498 | 240 | N |  |  | OP | X | 2 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: BIT; SUB SUB SUB: DFO; DFO DFO DFO: DFO |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1998 | petroleum | TRUE | 5529 | City of Durant - (IA) | 6220 | Durant | IA | Cedar | 7 | Petroleum Liquids | IC |  | S | X | X | ALTW.ALTW | ALTW.ALTW | 1.8 | 0.9 | 1.8 | 1.8 | 1.2 | N |  |  | SB | Y | 1 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2011 | petroleum | TRUE | 5529 | City of Durant - (IA) | 6220 | Durant | IA | Cedar | 8 | Petroleum Liquids | IC |  | S | X | X | ALTW.ALTW | ALTW.ALTW | 2.6 | 0.9 | 2.6 | 2.6 | 1.5 | N |  |  | SB | Y | 5 | 2011 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1978 | natural gas peaker | TRUE | 5860 | Empire District Electric Co | 6223 | Empire Energy Center | MO | Jasper | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | EDELAR3821UN1_RA | EDELAR3821UN1_RA | 129 | 0.9 | 79.4 | 95 | 30 | N |  |  | OP | X | 3 | 1978 | 12 | 2026 | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: JF |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1981 | natural gas peaker | TRUE | 5860 | Empire District Electric Co | 6223 | Empire Energy Center | MO | Jasper | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | EDELAR3821UN2_RA | EDELAR3821UN2_RA | 129 | 0.9 | 79.7 | 95 | 30 | N |  |  | OP | X | 6 | 1981 | 12 | 2026 | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: JF |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2003 | natural gas peaker | TRUE | 5860 | Empire District Electric Co | 6223 | Empire Energy Center | MO | Jasper | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | EDELAR3821UN3_RA | EDELAR3821UN3_RA | 60.5 | 0.9 | 40 | 55 | 25 | N |  |  | OP | X | 4 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: JF |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2003 | natural gas peaker | TRUE | 5860 | Empire District Electric Co | 6223 | Empire Energy Center | MO | Jasper | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | EDELAR3821UN4_RA | EDELAR3821UN4_RA | 60.5 | 0.9 | 40 | 58 | 25 | N |  |  | OP | X | 4 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: JF |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1980 | petroleum | TRUE | 13337 | Nebraska Public Power District | 6229 | Mobile | NE | York | 1 | Petroleum Liquids | IC |  | S | X | X | N/A | N/A | 1 | 0.8 | 1 | 1 | 0 | N |  |  | OP | X | 1 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1996 | petroleum | TRUE | 13337 | Nebraska Public Power District | 6229 | Mobile | NE | York | 2 | Petroleum Liquids | IC |  | S | X | X | N/A | N/A | 1.6 | 0.8 | 1.6 | 1.6 | 0 | N |  |  | OP | X | 3 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1994 | petroleum | TRUE | 13337 | Nebraska Public Power District | 6229 | Mobile | NE | York | 500 | Petroleum Liquids | IC |  | S | X | X | N/A | N/A | 0.5 | 0.8 | 0.5 | 0.5 | 0 | N |  |  | OP | X | 10 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1901 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 6231 | Apple River | WI | St Croix | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 1 | 0.4 | 0.5 | 0.2 | N |  |  | OP | X | 1 | 1901 | 12 | 2024 | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1901 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 6231 | Apple River | WI | St Croix | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 1 | 0.5 | 0.6 | 0.2 | N |  |  | OP | X | 1 | 1901 | 12 | 2024 | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1901 | hydro | TRUE | 13781 | Northern States Power Co - Minnesota | 6231 | Apple River | WI | St Croix | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 1 | 0.5 | 0.6 | 0.2 | N |  |  | OP | X | 1 | 1901 | 12 | 2024 | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1973 | petroleum | TRUE | 40307 | Prairie Power, Inc | 6238 | Pearl Station | IL | Pike | GT1 | Petroleum Liquids | GT |  | S | X | X | AMIL.PEARLG2 |  | 24 | 0.9 | 20.1 | 22 | 2 | N |  |  | OP | X | 6 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; DFO DFO DFO: DFO |  |  |  | N | N |  | 12H | N | N | [21 empty] | N | N | N
Vintage1978 | natural gas steam turbine | TRUE | 2442 | City of Bryan - (TX) | 6243 | Dansby | TX | Brazos | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | DANSBY | DANSBY | 105 | 0.9 | 110 | 110 | 12 | N |  |  | OP | X | 9 | 1978 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | OVER | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2004 | natural gas peaker | TRUE | 2442 | City of Bryan - (TX) | 6243 | Dansby | TX | Brazos | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | DANSBY | DANSBY | 49.1 | 0.85 | 47.1 | 48.1 | 12 | N |  |  | OP | X | 2 | 2004 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2010 | natural gas peaker | TRUE | 2442 | City of Bryan - (TX) | 6243 | Dansby | TX | Brazos | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | DANSBY | DANSBY | 49.1 | 0.85 | 47.1 | 48.1 | 12 | N |  |  | OP | X | 3 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1981 | hard coal | TRUE | 15466 | Public Service Co of Colorado | 6248 | Pawnee | CO | Morgan | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 552.3 | 0.9 | 505 | 505 | 200 | N |  |  | OP | X | 11 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; SUB SUB SUB: NG; DFO DFO DFO: NG |  |  |  | N | N |  | OVER | N | Y |  |  | Y | [18 empty] | Y | N
Vintage1975 | hard coal | TRUE | 17543 | South Carolina Public Service Authority | 6249 | Winyah | SC | Georgetown | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 315 | 0.9 | 275 | 280 | 100 | N |  |  | OP | X | 3 | 1975 | 12 | 2028 | N | Electric Utility | 1 | X | RC | BIT | WO |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1977 | hard coal | TRUE | 17543 | South Carolina Public Service Authority | 6249 | Winyah | SC | Georgetown | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 315 | 0.9 | 285 | 290 | 100 | N |  |  | OP | X | 7 | 1977 | 12 | 2028 | N | Electric Utility | 1 | X | RC | BIT | WO |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1980 | hard coal | TRUE | 17543 | South Carolina Public Service Authority | 6249 | Winyah | SC | Georgetown | 3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 315 | 0.9 | 285 | 290 | 100 | N |  |  | OP | X | 5 | 1980 | 12 | 2028 | N | Electric Utility | 1 | X X X: X; RC RC RC: RC; SUB SUB SUB: BIT; DFO DFO DFO: DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1981 | hard coal | TRUE | 17543 | South Carolina Public Service Authority | 6249 | Winyah | SC | Georgetown | 4 | Conventional Steam Coal | ST |  | S | X | X |  |  | 315 | 0.9 | 285 | 290 | 110 | N |  |  | OP | X | 11 | 1981 | 12 | 2028 | N | Electric Utility | 1 | X X X: X; RC RC RC: RC; SUB SUB SUB: BIT; DFO DFO DFO: DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1983 | hard coal | TRUE | 3046 | Duke Energy Progress - (NC) | 6250 | Mayo | NC | Person | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 763.2 | 0.9 | 704 | 713 | 75 | N |  |  | OP | X | 3 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: BIT; DFO DFO DFO: DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N
Vintage1988 | nuclear | TRUE | 21535 | STP Nuclear Operating Co | 6251 | South Texas Project | TX | Matagorda | 1 | Nuclear | ST |  | J | X | X |  |  | 1354.3 | 0.9 | 1300 | 1340 | 1280 | N |  |  | OP | X | 8 | 1988 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NUC |  |  |  | N | N | 0 | OVER |  | N | [21 empty] | N
Vintage1989 | nuclear | TRUE | 21535 | STP Nuclear Operating Co | 6251 | South Texas Project | TX | Matagorda | 2 | Nuclear | ST |  | J | X | X |  |  | 1354.3 | 0.9 | 1280 | 1320 | 1280 | N |  |  | OP | X | 6 | 1989 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NUC |  |  |  | N | N |  | OVER | [23 empty] | N
Vintage1978 | petroleum | TRUE | 20847 | Wisconsin Electric Power Co | 6253 | Germantown | WI | Washington | 1 | Petroleum Liquids | GT |  | S | X | X | WEC.GERMANOT1 | WEC.GERMANOT1 | 61.2 | 0.9 | 48.6 | 69.2 | 30 | N |  |  | OP | X | 7 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1978 | petroleum | TRUE | 20847 | Wisconsin Electric Power Co | 6253 | Germantown | WI | Washington | 2 | Petroleum Liquids | GT |  | S | X | X | WEC.GERMANOT2 | WEC.GERMANOT2 | 61.2 | 0.9 | 47.5 | 67.6 | 30 | N |  |  | OP | X | 7 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1978 | petroleum | TRUE | 20847 | Wisconsin Electric Power Co | 6253 | Germantown | WI | Washington | 3 | Petroleum Liquids | GT |  | S | X | X | WEC.GERMANOT3 | WEC.GERMANOT3 | 61.2 | 0.9 | 45.4 | 64.7 | 30 | N |  |  | OP | X | 7 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1978 | petroleum | TRUE | 20847 | Wisconsin Electric Power Co | 6253 | Germantown | WI | Washington | 4 | Petroleum Liquids | GT |  | S | X | X | WEC.GERMANOT4 | WEC.GERMANOT4 | 61.2 | 0.9 | 45.8 | 65.2 | 30 | N |  |  | OP | X | 7 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2000 | natural gas peaker | TRUE | 20847 | Wisconsin Electric Power Co | 6253 | Germantown | WI | Washington | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | WEC.GERMANOT5 | WEC.GERMANOT5 | 90.9 | 0.85 | 76.3 | 104.3 | 50 | N |  |  | OP | X | 5 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1981 | hard coal | TRUE | 9417 | Interstate Power and Light Co | 6254 | Ottumwa | IA | Wapello | 1 | Conventional Steam Coal | ST |  | J | X | X | ALTW.OTTUMW1 | ALTW.OTTUMW1 | 725.9 | 0.9 | 712.4 | 724.7 | 190 | N |  |  | OP | X | 5 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; DFO DFO DFO: DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | N |  |  | N | N
Vintage1982 | hard coal | TRUE | 7140 | Georgia Power Co | 6257 | Scherer | GA | Monroe | 1 | Conventional Steam Coal | ST |  | J | X | X |  |  | 891 | 0.9 | 860 | 860 | 350 | N |  |  | OP | X | 3 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; SUB SUB SUB: DFO; DFO DFO DFO: DFO |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1984 | hard coal | TRUE | 7140 | Georgia Power Co | 6257 | Scherer | GA | Monroe | 2 | Conventional Steam Coal | ST |  | J | X | X |  |  | 891 | 0.9 | 860 | 860 | 350 | N |  |  | OP | X | 2 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; SUB SUB SUB: DFO; DFO DFO DFO: DFO |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1987 | hard coal | TRUE | 7140 | Georgia Power Co | 6257 | Scherer | GA | Monroe | 3 | Conventional Steam Coal | ST |  | J | X | X |  |  | 891 | 0.9 | 860 | 860 | 350 | N |  |  | OP | X | 1 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; SUB SUB SUB: DFO; DFO DFO DFO: DFO |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1989 | hard coal | TRUE | 7140 | Georgia Power Co | 6257 | Scherer | GA | Monroe | 4 | Conventional Steam Coal | ST |  | J | X | X |  |  | 891 | 0.9 | 860 | 860 | 350 | N |  |  | OP | X | 2 | 1989 | 1 | 2022 | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; SUB SUB SUB: DFO; DFO DFO DFO: DFO |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1972 | petroleum | TRUE | 7140 | Georgia Power Co | 6258 | Wilson | GA | Burke | 5A | Petroleum Liquids | GT |  | S | X | X |  |  | 52.5 | 0.85 | 41 | 54 | 4 | N |  |  | OP | X | 12 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1972 | petroleum | TRUE | 7140 | Georgia Power Co | 6258 | Wilson | GA | Burke | 5B | Petroleum Liquids | GT |  | S | X | X |  |  | 52.5 | 0.85 | 56 | 67 | 4 | N |  |  | OP | X | 12 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1972 | petroleum | TRUE | 7140 | Georgia Power Co | 6258 | Wilson | GA | Burke | 5C | Petroleum Liquids | GT |  | S | X | X |  |  | 52.5 | 0.85 | 49 | 61 | 4 | N |  |  | OP | X | 12 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1973 | petroleum | TRUE | 7140 | Georgia Power Co | 6258 | Wilson | GA | Burke | 5D | Petroleum Liquids | GT |  | S | X | X |  |  | 52.5 | 0.85 | 41 | 56 | 4 | N |  |  | OP | X | 2 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1973 | petroleum | TRUE | 7140 | Georgia Power Co | 6258 | Wilson | GA | Burke | 5E | Petroleum Liquids | GT |  | S | X | X |  |  | 52.5 | 0.85 | 54 | 61 | 4 | N |  |  | OP | X | 4 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1973 | petroleum | TRUE | 7140 | Georgia Power Co | 6258 | Wilson | GA | Burke | 5F | Petroleum Liquids | GT |  | S | X | X |  |  | 52.5 | 0.85 | 54 | 65 | 4 | N |  |  | OP | X | 4 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1972 | petroleum | TRUE | 7140 | Georgia Power Co | 6258 | Wilson | GA | Burke | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.6 | 0.8 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 12 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1980 | hard coal | TRUE | 733 | Appalachian Power Co | 6264 | Mountaineer | WV | Mason | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 1300 | 0.9 | 1299 | 1299 | 500 | N |  |  | OP | X | 9 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: BIT; DFO DFO DFO: DFO |  |  |  | N |  |  | 12H |  | Y |  |  |  | Y | [17 empty] | N
Vintage1959 | hydro | TRUE | 14354 | PacifiCorp | 6265 | Swift 2 | WA | Cowlitz | 21 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 36 | 0.9 | 34 | 34 | 0 | N |  |  | OS | X | 1 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1958 | hydro | TRUE | 14354 | PacifiCorp | 6265 | Swift 2 | WA | Cowlitz | 22 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 36 | 0.9 | 31 | 31 | 0 | N |  |  | OS | X | 12 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1931 | hydro | TRUE | 5860 | Empire District Electric Co | 6280 | Ozark Beach | MO | Taney | 5 | Conventional Hydroelectric | HY |  | S | X | X | EDEOZRK_BUN5_RA | EDEOZRK_BUN5_RA | 4 | 0.8 | 4 | 4 | 1 | N |  |  | OP | X | 6 | 1931 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1931 | hydro | TRUE | 5860 | Empire District Electric Co | 6280 | Ozark Beach | MO | Taney | 6 | Conventional Hydroelectric | HY |  | S | X | X | EDEOZRK_BUN6_RA | EDEOZRK_BUN6_RA | 4 | 0.8 | 4 | 4 | 1 | N |  |  | OP | X | 6 | 1931 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1931 | hydro | TRUE | 5860 | Empire District Electric Co | 6280 | Ozark Beach | MO | Taney | 7 | Conventional Hydroelectric | HY |  | S | X | X | EDEOZRK_BUN7_RA | EDEOZRK_BUN7_RA | 4 | 0.8 | 4 | 4 | 1 | N |  |  | OP | X | 6 | 1931 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1931 | hydro | TRUE | 5860 | Empire District Electric Co | 6280 | Ozark Beach | MO | Taney | 8 | Conventional Hydroelectric | HY |  | S | X | X | EDEOZRK_BUN8_RA | EDEOZRK_BUN8_RA | 4 | 0.8 | 4 | 4 | 1 | N |  |  | OP | X | 6 | 1931 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1976 | petroleum | TRUE | 10433 | Kodiak Electric Assn Inc | 6281 | Kodiak Microgrid | AK | Kodiak Island | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 0.6 | N |  |  | OP | X | 12 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2005 | petroleum | TRUE | 10433 | Kodiak Electric Assn Inc | 6281 | Kodiak Microgrid | AK | Kodiak Island | 2c | Petroleum Liquids | IC |  | S | X | X |  |  | 4.4 | 0.9 | 4.4 | 4.4 | 1.1 | N |  |  | OP | X | 6 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage2005 | petroleum | TRUE | 10433 | Kodiak Electric Assn Inc | 6281 | Kodiak Microgrid | AK | Kodiak Island | 3c | Petroleum Liquids | IC |  | S | X | X |  |  | 4.4 | 0.9 | 4.4 | 4.4 | 1.1 | N |  |  | OP | X | 6 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1981 | petroleum | TRUE | 10433 | Kodiak Electric Assn Inc | 6281 | Kodiak Microgrid | AK | Kodiak Island | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 7 | 0.9 | 7 | 7 | 2.5 | N |  |  | OP | X | 7 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2017 | petroleum | TRUE | 10433 | Kodiak Electric Assn Inc | 6282 | Port Lions Microgrid | AK | Kodiak Island | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 9 | 2017 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  |  | N |  | 1H | [23 empty] | N | N | N
Vintage2004 | petroleum | TRUE | 19558 | Homer Electric Assn Inc | 6283 | Seldovia | AK | Kenai Peninsula | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.9 | 1.2 | 1.2 | 0.1 | N |  |  | OP | X | 12 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage2017 | petroleum | TRUE | 19558 | Homer Electric Assn Inc | 6283 | Seldovia | AK | Kenai Peninsula | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.1 | N |  |  | OP | X | 10 | 2017 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1976 | petroleum | TRUE | 7353 | Golden Valley Elec Assn Inc | 6285 | North Pole | AK | Fairbanks North Star | 1 | Petroleum Liquids | GT |  | S | X | X |  |  | 60.5 | 0.9 | 44 | 60 | 8 | N |  |  | OP | X | 12 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; DFO DFO DFO: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1977 | petroleum | TRUE | 7353 | Golden Valley Elec Assn Inc | 6285 | North Pole | AK | Fairbanks North Star | 2 | Petroleum Liquids | GT |  | S | X | X |  |  | 60.5 | 0.9 | 50 | 64 | 8 | N |  |  | OP | X | 2 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; DFO DFO DFO: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2007 | petroleum | TRUE | 7353 | Golden Valley Elec Assn Inc | 6285 | North Pole | AK | Fairbanks North Star | GT3 | Petroleum Liquids | CT | CST1 | S | X | N |  |  | 47 | 0.9 | 41 | 53 | 15 | N |  |  | OP | X | 3 | 2007 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WO; SUB SUB SUB: DFO; DFO DFO DFO: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2007 | petroleum | TRUE | 7353 | Golden Valley Elec Assn Inc | 6285 | North Pole | AK | Fairbanks North Star | STG1 | Petroleum Liquids | CA | CST1 | S | N | X |  |  | 13 | 0.85 | 10 | 12 | 8 | N |  |  | OP | X | 3 | 2007 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WO; SUB SUB SUB: DFO; DFO DFO DFO: DFO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1970 | petroleum | TRUE | 7353 | Golden Valley Elec Assn Inc | 6286 | Fairbanks | AK | Fairbanks North Star | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2.8 | 2.8 | 2.8 | N |  |  | SB | Y | 5 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; DFO DFO DFO: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1970 | petroleum | TRUE | 7353 | Golden Valley Elec Assn Inc | 6286 | Fairbanks | AK | Fairbanks North Star | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2.8 | 2.8 | 2.8 | N |  |  | SB | Y | 9 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; DFO DFO DFO: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1971 | petroleum | TRUE | 7353 | Golden Valley Elec Assn Inc | 6286 | Fairbanks | AK | Fairbanks North Star | GT1 | Petroleum Liquids | GT |  | S | X | X |  |  | 18.4 | 0.85 | 15.5 | 17.7 | 3 | N |  |  | OP | X | 5 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; DFO DFO DFO: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1972 | petroleum | TRUE | 7353 | Golden Valley Elec Assn Inc | 6286 | Fairbanks | AK | Fairbanks North Star | GT2 | Petroleum Liquids | GT |  | S | X | X |  |  | 18.4 | 0.85 | 15 | 17.7 | 3 | N |  |  | OP | X | 11 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; DFO DFO DFO: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1967 | lignite | TRUE | 7353 | Golden Valley Elec Assn Inc | 6288 | Healy | AK | Denali | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 28 | 0.85 | 25 | 25 | 1.5 | N |  |  | OP | X | 11 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: LIG; SUB SUB SUB: WC; DFO DFO DFO: DFO |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1998 | lignite | TRUE | 7353 | Golden Valley Elec Assn Inc | 6288 | Healy | AK | Denali | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 62 | 0.85 | 50 | 50 | 8 | N |  |  | OP | X | 1 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: LIG; SUB SUB SUB: WC; DFO DFO DFO: DFO |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1967 | petroleum | TRUE | 7353 | Golden Valley Elec Assn Inc | 6288 | Healy | AK | Denali | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.8 | 0.8 | 2.8 | 2.8 | 2.5 | N |  |  | OP | X | 9 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage1961 | hydro | TRUE | 3522 | Chugach Electric Assn Inc | 6291 | Cooper Lake | AK | Kenai Peninsula | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9.7 | 0.85 | 9.7 | 9.7 | 6.5 | N |  |  | OP | X | 5 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H
Vintage1961 | hydro | TRUE | 3522 | Chugach Electric Assn Inc | 6291 | Cooper Lake | AK | Kenai Peninsula | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9.7 | 0.85 | 9.7 | 9.7 | 6.5 | N |  |  | OP | X | 5 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H
Vintage1971 | natural gas peaker | TRUE | 19558 | Homer Electric Assn Inc | 6292 | Bernice Lake | AK | Kenai Peninsula | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 20.7 | 0.95 | 17 | 19 | 2 | N |  |  | OP | X | 11 | 1971 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage1978 | natural gas peaker | TRUE | 19558 | Homer Electric Assn Inc | 6292 | Bernice Lake | AK | Kenai Peninsula | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 28.8 | 0.95 | 22.9 | 26 | 5 | N |  |  | OP | X | 12 | 1978 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage1981 | natural gas peaker | TRUE | 19558 | Homer Electric Assn Inc | 6292 | Bernice Lake | AK | Kenai Peninsula | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 27.2 | 0.95 | 22.5 | 26 | 5 | N |  |  | OP | X | 11 | 1981 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage1964 | natural gas peaker | TRUE | 3522 | Chugach Electric Assn Inc | 6293 | International | AK | Anchorage | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 15 | 0.85 | 12.6 | 14.1 | 1 | N |  |  | OS | X | 12 | 1964 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2010 | petroleum | TRUE | 40548 | Unalakleet Valley Elec Coop | 6299 | Unalakleet | AK | Nome | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.95 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 5 | 2010 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2010 | petroleum | TRUE | 40548 | Unalakleet Valley Elec Coop | 6299 | Unalakleet | AK | Nome | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.95 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 5 | 2010 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2010 | petroleum | TRUE | 40548 | Unalakleet Valley Elec Coop | 6299 | Unalakleet | AK | Nome | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.95 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 12 | 2010 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2010 | petroleum | TRUE | 40548 | Unalakleet Valley Elec Coop | 6299 | Unalakleet | AK | Nome | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.95 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 12 | 2010 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 13201 | Naknek Electric Assn, Inc | 6301 | Naknek | AK | Bristol Bay | 4A | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.97 | 1.3 | 1.3 | 1 | N |  |  | OP | X | 7 | 1999 |  |  | Y | Electric Utility | 1 | X X X: T; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2005 | petroleum | TRUE | 13201 | Naknek Electric Assn, Inc | 6301 | Naknek | AK | Bristol Bay | 5A | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.97 | 1 | 1 | 1 | N |  |  | OP | X | 5 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  |  | N |  | 10M | [23 empty] | N
Vintage2006 | petroleum | TRUE | 13201 | Naknek Electric Assn, Inc | 6301 | Naknek | AK | Bristol Bay | 6A | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.97 | 1 | 1 | 1 | N |  |  | OP | X | 4 | 2006 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2006 | petroleum | TRUE | 13201 | Naknek Electric Assn, Inc | 6301 | Naknek | AK | Bristol Bay | 7A | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.97 | 1 | 1 | 1 | N |  |  | OP | X | 4 | 2006 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1977 | petroleum | TRUE | 13201 | Naknek Electric Assn, Inc | 6301 | Naknek | AK | Bristol Bay | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.97 | 1 | 1 | 1 | N |  |  | OP | X | 12 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1988 | petroleum | TRUE | 13201 | Naknek Electric Assn, Inc | 6301 | Naknek | AK | Bristol Bay | NA1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.97 | 1.1 | 1.1 | 1 | N |  |  | OP | X | 5 | 1988 |  |  | Y | Electric Utility | 1 | X X X: T; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1988 | petroleum | TRUE | 13201 | Naknek Electric Assn, Inc | 6301 | Naknek | AK | Bristol Bay | NA2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.97 | 1.1 | 1.1 | 1 | N |  |  | OP | X | 5 | 1988 |  |  | Y | Electric Utility | 1 | X X X: T; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1991 | petroleum | TRUE | 13201 | Naknek Electric Assn, Inc | 6301 | Naknek | AK | Bristol Bay | NA3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.97 | 0.8 | 0.8 | 0.8 | N |  |  | OP | X | 5 | 1991 |  |  | Y | Electric Utility | 1 | X X X: T; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1992 | petroleum | TRUE | 13201 | Naknek Electric Assn, Inc | 6301 | Naknek | AK | Bristol Bay | NA4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.97 | 0.8 | 0.8 | 0.8 | N |  |  | OP | X | 6 | 1992 |  |  | Y | Electric Utility | 1 | X X X: T; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1993 | petroleum | TRUE | 13201 | Naknek Electric Assn, Inc | 6301 | Naknek | AK | Bristol Bay | NA5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.97 | 0.8 | 0.8 | 0.8 | N |  |  | OP | X | 9 | 1993 |  |  | Y | Electric Utility | 1 | X X X: T; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2019 | petroleum | TRUE | 13201 | Naknek Electric Assn, Inc | 6301 | Naknek | AK | Bristol Bay | NA6 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.3 | 0.8 | 3 | 0.1 | 1.7 | N |  |  | OP | X | 4 | 2019 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2019 | petroleum | TRUE | 13201 | Naknek Electric Assn, Inc | 6301 | Naknek | AK | Bristol Bay | NA7 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.3 | 0.8 | 3 | 0.1 | 1.7 | N |  |  | OP | X | 4 | 2019 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1956 | hydro | TRUE | 12385 | Metlakatla Power & Light | 6302 | Purple Lake | AK | Prince of Wales Ketchikan | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 0.2 | N |  |  | OP | X | 1 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1956 | hydro | TRUE | 12385 | Metlakatla Power & Light | 6302 | Purple Lake | AK | Prince of Wales Ketchikan | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 0.2 | N |  |  | OP | X | 1 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1962 | hydro | TRUE | 12385 | Metlakatla Power & Light | 6302 | Purple Lake | AK | Prince of Wales Ketchikan | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 0.2 | N |  |  | OP | X | 12 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1992 | petroleum | TRUE | 10451 | Kotzebue Electric Assn Inc | 6304 | Kotzebue Hybrid | AK | NORTHWEST ARCTIC | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 1.5 | N |  |  | OP | X | 12 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 12H | [23 empty] | N | N | N
Vintage2005 | onshore wind | TRUE | 10451 | Kotzebue Electric Assn Inc | 6304 | Kotzebue Hybrid | AK | NORTHWEST ARCTIC | 11wt | Onshore Wind Turbine | WT |  | S | X | X |  |  | 0.1 |  | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 5 | 2005 | 5 | 2025 | N | Electric Utility | 1 | X X X: X; RC RC RC: WND |  |  |  | N |  | 1
Vintage2006 | onshore wind | TRUE | 10451 | Kotzebue Electric Assn Inc | 6304 | Kotzebue Hybrid | AK | NORTHWEST ARCTIC | 13WT | Onshore Wind Turbine | WT |  | S | X | X |  |  | 0.1 |  | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 5 | 2006 | 5 | 2025 | N | Electric Utility | 1 | X X X: X; RC RC RC: WND |  |  |  | N |  | 1
Vintage1994 | petroleum | TRUE | 10451 | Kotzebue Electric Assn Inc | 6304 | Kotzebue Hybrid | AK | NORTHWEST ARCTIC | 14 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.8 | 0.8 | 2.8 | 2.8 | 1 | N |  |  | OP | X | 7 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 12H | [23 empty] | N | N | N
Vintage2002 | onshore wind | TRUE | 10451 | Kotzebue Electric Assn Inc | 6304 | Kotzebue Hybrid | AK | NORTHWEST ARCTIC | 14wt | Onshore Wind Turbine | WT |  | S | X | X |  |  | 0.1 |  | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 5 | 2002 | 5 | 2025 | N | Electric Utility | 1 | X X X: X; RC RC RC: WND |  |  |  | N |  | 1
Vintage2006 | petroleum | TRUE | 10451 | Kotzebue Electric Assn Inc | 6304 | Kotzebue Hybrid | AK | NORTHWEST ARCTIC | 15 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.8 | 0.8 | 2.8 | 2.8 | 1 | N |  |  | OP | X | 2 | 2006 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 12H | [23 empty] | N | N | N
Vintage2006 | onshore wind | TRUE | 10451 | Kotzebue Electric Assn Inc | 6304 | Kotzebue Hybrid | AK | NORTHWEST ARCTIC | 15WT | Onshore Wind Turbine | WT |  | S | X | X |  |  | 0.1 |  | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 5 | 2006 | 5 | 2025 | N | Electric Utility | 1 | X X X: X; RC RC RC: WND |  |  |  | N |  | 1
Vintage2013 | petroleum | TRUE | 10451 | Kotzebue Electric Assn Inc | 6304 | Kotzebue Hybrid | AK | NORTHWEST ARCTIC | 16 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.4 | 0.8 | 1.4 | 1.4 | 0.6 | N |  |  | OP | X | 8 | 2013 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 12H | [23 empty] | N |  | N
Vintage2006 | onshore wind | TRUE | 10451 | Kotzebue Electric Assn Inc | 6304 | Kotzebue Hybrid | AK | NORTHWEST ARCTIC | 16WT | Onshore Wind Turbine | WT |  | S | X | X |  |  | 0.1 |  | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 5 | 2006 | 5 | 2025 | N | Electric Utility | 1 | X X X: X; RC RC RC: WND |  |  |  | N |  | 1
Vintage2016 | petroleum | TRUE | 10451 | Kotzebue Electric Assn Inc | 6304 | Kotzebue Hybrid | AK | NORTHWEST ARCTIC | 17 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.7 | 0.8 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 5 | 2016 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 12H | [23 empty] | N | N | N
Vintage2006 | onshore wind | TRUE | 10451 | Kotzebue Electric Assn Inc | 6304 | Kotzebue Hybrid | AK | NORTHWEST ARCTIC | 17WT | Onshore Wind Turbine | WT |  | S | X | X |  |  | 0.1 |  | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 5 | 2006 | 5 | 2025 | N | Electric Utility | 1 | X X X: X; RC RC RC: WND | [5 empty] | 1
Vintage2012 | onshore wind | TRUE | 10451 | Kotzebue Electric Assn Inc | 6304 | Kotzebue Hybrid | AK | NORTHWEST ARCTIC | 18WT | Onshore Wind Turbine | WT |  | S | X | X |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | N |  |  | OP | X | 5 | 2012 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WND | [5 empty] | 1
Vintage2012 | onshore wind | TRUE | 10451 | Kotzebue Electric Assn Inc | 6304 | Kotzebue Hybrid | AK | NORTHWEST ARCTIC | 19WT | Onshore Wind Turbine | WT |  | S | X | X |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | N |  |  | OP | X | 5 | 2012 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WND | [5 empty] | 1
Vintage1999 | onshore wind | TRUE | 10451 | Kotzebue Electric Assn Inc | 6304 | Kotzebue Hybrid | AK | NORTHWEST ARCTIC | 1WT | Onshore Wind Turbine | WT |  | S | X | X |  |  | 0.6 |  | 0.6 | 0.6 | 0.6 | N |  |  | OP | X | 5 | 1999 | 5 | 2025 | N | Electric Utility | 1 | X X X: X; RC RC RC: WND |  |  |  | N |  | 10
Vintage1999 | onshore wind | TRUE | 10451 | Kotzebue Electric Assn Inc | 6304 | Kotzebue Hybrid | AK | NORTHWEST ARCTIC | 2WT | Onshore Wind Turbine | WT |  | S | X | X |  |  | 0.1 |  | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 5 | 1999 | 5 | 2025 | N | Electric Utility | 1 | X X X: X; RC RC RC: WND |  |  |  | N |  | 1
Vintage1997 | onshore wind | TRUE | 10451 | Kotzebue Electric Assn Inc | 6304 | Kotzebue Hybrid | AK | NORTHWEST ARCTIC | 3WT | Onshore Wind Turbine | WT |  | S | X | X |  |  | 0.2 |  | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1997 | 5 | 2025 | N | Electric Utility | 1 | X X X: X; RC RC RC: WND |  |  |  | N |  | 3
Vintage1987 | petroleum | TRUE | 10451 | Kotzebue Electric Assn Inc | 6304 | Kotzebue Hybrid | AK | NORTHWEST ARCTIC | 7A | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.4 | N |  |  | OP | X | 8 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 12H | [23 empty] | N | N | N
Vintage2015 | other | TRUE | 10451 | Kotzebue Electric Assn Inc | 6304 | Kotzebue Hybrid | AK | NORTHWEST ARCTIC | ES1 | Batteries | BA |  | S | X | X |  |  | 1.2 |  | 1.2 | 1.2 | 0 | N |  |  | OP | X | 12 | 2015 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: MWH |  |  |  | N | N |  | 10M
Vintage2020 | solar pv | TRUE | 10451 | Kotzebue Electric Assn Inc | 6304 | Kotzebue Hybrid | AK | NORTHWEST ARCTIC | PV1 | Solar Photovoltaic | PV |  | S | X | X |  |  | 0.1 |  | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 7 | 2020 | 7 | 2040 | N | Electric Utility | 1 | X X X: X; RC RC RC: SUN
Vintage2020 | solar pv | TRUE | 10451 | Kotzebue Electric Assn Inc | 6304 | Kotzebue Hybrid | AK | NORTHWEST ARCTIC | PV2 | Solar Photovoltaic | PV |  | S | X | X |  |  | 0.1 |  | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 7 | 2020 | 7 | 2040 | N | Electric Utility | 1 | X X X: X; RC RC RC: SUN
Vintage2020 | solar pv | TRUE | 10451 | Kotzebue Electric Assn Inc | 6304 | Kotzebue Hybrid | AK | NORTHWEST ARCTIC | PV3 | Solar Photovoltaic | PV |  | S | X | X |  |  | 0.1 |  | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 7 | 2020 | 7 | 2040 | N | Electric Utility | 1 | X X X: X; RC RC RC: SUN
Vintage2020 | solar pv | TRUE | 10451 | Kotzebue Electric Assn Inc | 6304 | Kotzebue Hybrid | AK | NORTHWEST ARCTIC | PV4 | Solar Photovoltaic | PV |  | S | X | X |  |  | 0.1 |  | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 7 | 2020 | 7 | 2040 | N | Electric Utility | 1 | X X X: X; RC RC RC: SUN
Vintage2020 | solar pv | TRUE | 10451 | Kotzebue Electric Assn Inc | 6304 | Kotzebue Hybrid | AK | NORTHWEST ARCTIC | PV5 | Solar Photovoltaic | PV |  | S | X | X |  |  | 0.1 |  | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 7 | 2020 | 7 | 2040 | N | Electric Utility | 1 | X X X: X; RC RC RC: SUN
Vintage2020 | solar pv | TRUE | 10451 | Kotzebue Electric Assn Inc | 6304 | Kotzebue Hybrid | AK | NORTHWEST ARCTIC | PV6 | Solar Photovoltaic | PV |  | S | X | X |  |  | 0.1 |  | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 7 | 2020 | 7 | 2040 | N | Electric Utility | 1 | X X X: X; RC RC RC: SUN
Vintage2020 | solar pv | TRUE | 10451 | Kotzebue Electric Assn Inc | 6304 | Kotzebue Hybrid | AK | NORTHWEST ARCTIC | PV7 | Solar Photovoltaic | PV |  | S | X | X |  |  | 0.1 |  | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 7 | 2020 | 7 | 2040 | N | Electric Utility | 1 | X X X: X; RC RC RC: SUN
Vintage2020 | solar pv | TRUE | 10451 | Kotzebue Electric Assn Inc | 6304 | Kotzebue Hybrid | AK | NORTHWEST ARCTIC | PV8 | Solar Photovoltaic | PV |  | S | X | X |  |  | 0.1 |  | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 7 | 2020 | 7 | 2040 | N | Electric Utility | 1 | X X X: X; RC RC RC: SUN
Vintage1976 | petroleum | TRUE | 4329 | Copper Valley Elec Assn, Inc | 6305 | Glennallen | AK | Valdez Cordova | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.6 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 5 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1976 | petroleum | TRUE | 4329 | Copper Valley Elec Assn, Inc | 6305 | Glennallen | AK | Valdez Cordova | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.6 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 5 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 4329 | Copper Valley Elec Assn, Inc | 6305 | Glennallen | AK | Valdez Cordova | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 0.2 | N |  |  | OP | X | 2 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2010 | petroleum | TRUE | 4329 | Copper Valley Elec Assn, Inc | 6305 | Glennallen | AK | Valdez Cordova | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.8 | 0.8 | 2.8 | 2.8 | 0.5 | N |  |  | OP | X | 5 | 2010 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage2017 | petroleum | TRUE | 4329 | Copper Valley Elec Assn, Inc | 6306 | Valdez | AK | Valdez Cordova | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.1 | N |  |  | OP | X | 6 | 2017 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 10M | [23 empty] | N | N | N
Vintage2017 | petroleum | TRUE | 4329 | Copper Valley Elec Assn, Inc | 6306 | Valdez | AK | Valdez Cordova | 12 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.1 | N |  |  | OP | X | 6 | 2017 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 10M | [23 empty] | N | N | N
Vintage1972 | petroleum | TRUE | 4329 | Copper Valley Elec Assn, Inc | 6306 | Valdez | AK | Valdez Cordova | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.9 | 0.8 | 1.5 | 1.5 | 0.2 | N |  |  | OP | X | 10 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1975 | petroleum | TRUE | 4329 | Copper Valley Elec Assn, Inc | 6306 | Valdez | AK | Valdez Cordova | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.6 | 0.8 | 2 | 2 | 0.5 | N |  |  | OP | X | 6 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1974 | petroleum | TRUE | 4329 | Copper Valley Elec Assn, Inc | 6306 | Valdez | AK | Valdez Cordova | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.8 | 0.8 | 0.1 | N |  |  | OP | X | 8 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2009 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6311 | Chevak | AK | Bethel | 1A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.9 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 10 | 2009 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2009 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6311 | Chevak | AK | Bethel | 2A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.9 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 10 | 2009 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2009 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6311 | Chevak | AK | Bethel | 3A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.9 | 0.8 | 0.8 | 0.1 | N |  |  | OP | X | 10 | 2009 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2012 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6314 | Emmonak | AK | Wade Hampton | 2A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.9 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 10 | 2012 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2005 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6314 | Emmonak | AK | Wade Hampton | 4a | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.9 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 4 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N |  | N
Vintage2016 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6314 | Emmonak | AK | Wade Hampton | 5B | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.9 | 1.3 | 1.3 | 0.3 | N |  |  | OP | X | 6 | 2016 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N |  | N
Vintage1995 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6314 | Emmonak | AK | Wade Hampton | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.2 | N |  |  | OP | X | 4 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N |  | N
Vintage2018 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6319 | Hooper Bay | AK | Bethel | 3B | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.9 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 4 | 2018 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  |  | N |  | 10M | [23 empty] | N | N | N
Vintage2013 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6319 | Hooper Bay | AK | Bethel | 4B | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.9 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 7 | 2013 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2016 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6319 | Hooper Bay | AK | Bethel | 5A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.9 | 0.8 | 0.8 | 0.2 | N |  |  | OP | X | 6 | 2016 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  |  | N |  | 10M | [23 empty] | N | N | N
Vintage1997 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6319 | Hooper Bay | AK | Bethel | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.9 | 0.5 | 0.5 | 0.2 | N |  |  | OP | X | 10 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2001 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6323 | Kiana | AK | Northwest Arctic | 1B | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.9 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 9 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2019 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6323 | Kiana | AK | Northwest Arctic | 3B | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.9 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 8 | 2019 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1984 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6323 | Kiana | AK | Northwest Arctic | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.9 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 7 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1984 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6329 | Mountain Village | AK | Bethel | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.9 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 4 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2005 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6329 | Mountain Village | AK | Bethel | 3B | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.9 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 3 | 2005 | 11 | 2022 | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  |  | N |  | 10M | [23 empty] | N
Vintage2015 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6329 | Mountain Village | AK | Bethel | 4A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.9 | 0.8 | 0.8 | 0.2 | N |  |  | OP | X | 12 | 2015 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  |  | N |  | 10M | [23 empty] | N | N | N
Vintage2010 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6329 | Mountain Village | AK | Bethel | 5A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.7 | 0.9 | 0.7 | 0.7 | 0.2 | N |  |  | OP | X | 12 | 2010 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  |  | N |  | 10M | [23 empty] | N
Vintage1997 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6330 | Noorvik | AK | Northwest Arctic | 1A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.9 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 9 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2017 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6330 | Noorvik | AK | Northwest Arctic | 2B | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.9 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 7 | 2017 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  |  | N |  | 10M | [23 empty] | N | N | N
Vintage2003 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6330 | Noorvik | AK | Northwest Arctic | 3A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.7 | 0.9 | 0.7 | 0.7 | 0.2 | N |  |  | OP | X | 12 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2006 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6333 | Nunapitchuk | AK | Bethel | 1A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.9 | 0.5 | 0.5 | 0.1 | N |  |  | SB | Y | 7 | 2006 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  |  | N |  | 10M | [23 empty] | N
Vintage2006 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6338 | St Marys IC | AK | Bethel | 1B | Petroleum Liquids | IC |  | S | X | X |  |  | 5 | 0.9 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 12 | 2006 | 11 | 2022 | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1980 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6338 | St Marys IC | AK | Bethel | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.9 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 11 | 1980 | 11 | 2022 | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1974 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6338 | St Marys IC | AK | Bethel | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.2 | N |  |  | OP | X | 11 | 1974 | 11 | 2022 | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2020 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6341 | Selawik | AK | Northwest Arctic | 1B | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.9 | 0.8 | 0.8 | 0.2 | N |  |  | OP | X | 12 | 2020 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 10M | [23 empty] | N
Vintage2013 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6341 | Selawik | AK | Northwest Arctic | 2B | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.9 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 8 | 2013 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  |  | N |  | 10M | [23 empty] | N
Vintage2014 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6341 | Selawik | AK | Northwest Arctic | 3B | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | N |  |  | OP | X | 4 | 2014 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  |  | N |  | 10M | [23 empty] | N
Vintage2004 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6345 | Shishmaref | AK | Nome | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.9 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 6 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1976 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6345 | Shishmaref | AK | Nome | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.9 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 12 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2002 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6345 | Shishmaref | AK | Nome | 3A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.9 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 4 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  |  | N |  | 10M | [23 empty] | N
Vintage2006 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6345 | Shishmaref | AK | Nome | 4A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.9 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 7 | 2006 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2019 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6348 | Togiak | AK | Dillingham | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.9 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 4 | 2019 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2019 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6348 | Togiak | AK | Dillingham | 2B | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.9 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 4 | 2019 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  |  | N |  | 10M | [23 empty] | N
Vintage2019 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6348 | Togiak | AK | Dillingham | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.9 | 1.1 | 1.1 | 0.2 | N |  |  | OP | X | 4 | 2019 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  |  | N |  | 10M | [23 empty] | N
Vintage2019 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6348 | Togiak | AK | Dillingham | 4C | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.9 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 4 | 2019 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 10M | [23 empty] | N
Vintage1974 | petroleum | TRUE | 8723 | City of Holland | 6356 | Sixth Street Gas Turbine | MI | Ottawa | 1 | Petroleum Liquids | GT |  | S | X | X |  |  | 24 | 0.9 | 16 | 20 | 10 | N |  |  | OP | X | 5 | 1974 | 6 | 2023 | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1994 | natural gas combined cycle | TRUE | 9130 | Hutchinson Utilities Comm | 6358 | Hutchinson Plant #2 | MN | McLeod | 2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | GRE.HUC | GRE.HUC | 54 | 0.8 | 41 | 41 | 10 | N |  |  | OP | X | 11 | 1994 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1994 | natural gas combined cycle | TRUE | 9130 | Hutchinson Utilities Comm | 6358 | Hutchinson Plant #2 | MN | McLeod | 3 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X | GRE.HUC | GRE.HUC | 11.5 | 0.8 | 10 | 10 | 2.5 | N |  |  | OP | X | 11 | 1994 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 9130 | Hutchinson Utilities Comm | 6358 | Hutchinson Plant #2 | MN | McLeod | 9 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | GRE.HUC | GRE.HUC | 25 | 0.8 | 22 | 24.3 | 5 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1986 | hydro | TRUE | 6169 | Fall River Rural Elec Coop Inc | 6359 | Felt | ID | Teton | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.7 | 1 | 2.3 | 2.3 | 1 | N |  |  | OP | X | 1 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1986 | hydro | TRUE | 6169 | Fall River Rural Elec Coop Inc | 6359 | Felt | ID | Teton | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.7 | 1 | 2.3 | 2.3 | 1 | N |  |  | OP | X | 1 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1946 | hydro | TRUE | 6169 | Fall River Rural Elec Coop Inc | 6359 | Felt | ID | Teton | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.9 | 0.9 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 9 | 1946 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1947 | hydro | TRUE | 6169 | Fall River Rural Elec Coop Inc | 6359 | Felt | ID | Teton | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.1 | 0.9 | 0.8 | 0.8 | 0.7 | N |  |  | OP | X | 9 | 1947 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 12H | [23 empty] | N
Vintage1973 | petroleum | TRUE | 3828 | Cloverland Electric Co-op | 6369 | Detour | MI | Chippewa | 6 | Petroleum Liquids | IC |  | S | X | X | MIUP.DETRDBN1 |  | 3 | 0.9 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 10 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  |  | N |  | 1H | [23 empty] | N
Vintage1976 | petroleum | TRUE | 3828 | Cloverland Electric Co-op | 6369 | Detour | MI | Chippewa | 7 | Petroleum Liquids | IC |  | S | X | X | MIUP.DETRDBN1 |  | 3 | 0.9 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 8 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  |  | N |  | 1H | [23 empty] | N
Vintage1975 | natural gas peaker | TRUE | 11018 | Lincoln Electric System | 6373 | Rokeby | NE | Lancaster | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | LESROKEBYUN1_RA | LES_ROKEBY_1 | 72.4 | 0.9 | 70.5 | 72 | 10 | N |  |  | OP | X | 7 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1997 | natural gas peaker | TRUE | 11018 | Lincoln Electric System | 6373 | Rokeby | NE | Lancaster | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | LESROKEBYUN2_RA | LES_ROKEBY_2 | 95.4 | 0.8 | 90.4 | 91 | 20 | N |  |  | OP | X | 5 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 11018 | Lincoln Electric System | 6373 | Rokeby | NE | Lancaster | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | LESROKEBYUN3_RA | LES_ROKEBY_3 | 95.4 | 0.8 | 94.2 | 96 | 50 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1997 | petroleum | TRUE | 11018 | Lincoln Electric System | 6373 | Rokeby | NE | Lancaster | BSU | Petroleum Liquids | IC |  | S | X | X |  |  | 2.9 | 0.8 | 3.2 | 3.2 | 0 | N |  |  | OP | X | 4 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1991 | petroleum | TRUE | 13683 | North Carolina El Member Corp | 6377 | Ocracoke Hybrid | NC | Hyde | 1 | Petroleum Liquids | IC |  | S | X | X | Buxton 34.5 KV OCRACOK1 | Buxton 34.5 KV OCRACOK1 | 3 | 0.8 | 3 | 3 | 3 | N |  |  | OP | X | 4 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2017 | other | TRUE | 13683 | North Carolina El Member Corp | 6377 | Ocracoke Hybrid | NC | Hyde | BAT | Batteries | BA |  | S | X | X |  |  | 1 |  | 1 | 1 |  | N |  |  | OP | X | 1 | 2017 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: MWH | [6 empty] | 10M | [23 empty] | N | N | N
Vintage1920 | hydro | TRUE | 61350 | Central Rivers Power MA, LLC | 6378 | Dwight | MA | Hampden | DW2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.4 | N |  |  | OP | X | 1 | 1920 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N |  | 0 | 1H
Vintage1920 | hydro | TRUE | 61350 | Central Rivers Power MA, LLC | 6378 | Dwight | MA | Hampden | DW3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.4 | N |  |  | OP | X | 1 | 1920 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N |  | 0 | 1H
Vintage1920 | hydro | TRUE | 61350 | Central Rivers Power MA, LLC | 6378 | Dwight | MA | Hampden | DW4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.4 | N |  |  | OP | X | 1 | 1920 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N |  | 0 | 1H
Vintage1928 | hydro | TRUE | 61350 | Central Rivers Power MA, LLC | 6379 | Indian Orchard | MA | Hampden | IO3 | Conventional Hydroelectric | HY |  | S | X | X | 867 |  | 1.5 | 0.8 | 1.5 | 1.5 | 1.5 | N |  |  | OP | X | 1 | 1928 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N |  | 0 | 1H
Vintage1928 | hydro | TRUE | 61350 | Central Rivers Power MA, LLC | 6379 | Indian Orchard | MA | Hampden | IO4 | Conventional Hydroelectric | HY |  | S | X | X | 867 |  | 2.2 | 0.8 | 2.2 | 2.2 | 2.2 | N |  |  | OP | X | 1 | 1928 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N |  | 0 | 1H
Vintage1913 | hydro | TRUE | 58185 | FirstLight Power Resources, Inc. - MA | 6388 | Turners Falls | MA | Franklin | 1 | Conventional Hydroelectric | HY |  | S | X | X | N.MONTAGUE13.8TURN | N.MONTAGUE13.8TURN | 1.4 | 1 | 1.9 | 1.9 | 0.9 | N |  |  | OP | X | 1 | 1913 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1913 | hydro | TRUE | 58185 | FirstLight Power Resources, Inc. - MA | 6388 | Turners Falls | MA | Franklin | 2 | Conventional Hydroelectric | HY |  | S | X | X | N.MONTAGUE13.8TURN | N.MONTAGUE13.8TURN | 0.4 | 1 | 0.4 | 0.4 | 0.4 | N |  |  | OP | X | 1 | 1913 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1910 | hydro | TRUE | 58185 | FirstLight Power Resources, Inc. - MA | 6388 | Turners Falls | MA | Franklin | 3 | Conventional Hydroelectric | HY |  | S | X | X | N.MONTAGUE13.8TURN | N.MONTAGUE13.8TURN | 1.3 | 1 | 1.3 | 1.3 | 1.3 | N |  |  | OP | X | 1 | 1910 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N |  | 0 | 1H | [23 empty] | N
Vintage1905 | hydro | TRUE | 58185 | FirstLight Power Resources, Inc. - MA | 6388 | Turners Falls | MA | Franklin | 5 | Conventional Hydroelectric | HY |  | S | X | X | N.MONTAGUE13.8TURN | N.MONTAGUE13.8TURN | 1.3 | 1 | 1.4 | 1.4 | 1.3 | N |  |  | OP | X | 1 | 1905 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1910 | hydro | TRUE | 58185 | FirstLight Power Resources, Inc. - MA | 6388 | Turners Falls | MA | Franklin | 7 | Conventional Hydroelectric | HY |  | S | X | X | N.MONTAGUE13.8TURN | N.MONTAGUE13.8TURN | 1.3 | 1 | 1.4 | 1.4 | 1.3 | N |  |  | OP | X | 1 | 1910 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1993 | petroleum | TRUE | 84 | A & N Electric Coop | 6390 | Tangier | VA | Accomack | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 0.1 | N |  |  | OP | X | 12 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1993 | petroleum | TRUE | 84 | A & N Electric Coop | 6390 | Tangier | VA | Accomack | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 0.1 | N |  |  | OP | X | 12 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1994 | petroleum | TRUE | 84 | A & N Electric Coop | 6391 | Smith Island | MD | Somerset | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 3 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2021 | petroleum | TRUE | 84 | A & N Electric Coop | 6391 | Smith Island | MD | Somerset | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.1 | N |  |  | OP | X | 6 | 2021 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 1H | [23 empty] | N
Vintage1940 | hydro | TRUE | 11273 | Lower Valley Energy Inc | 6393 | Strawberry Creek | WY | Lincoln | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.86 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 8 | 1940 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1940 | hydro | TRUE | 11273 | Lower Valley Energy Inc | 6393 | Strawberry Creek | WY | Lincoln | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.86 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 8 | 1940 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1951 | hydro | TRUE | 11273 | Lower Valley Energy Inc | 6393 | Strawberry Creek | WY | Lincoln | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.86 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 1 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage2009 | hydro | TRUE | 11273 | Lower Valley Energy Inc | 6394 | Swift Creek | WY | Lincoln | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.817 | 0.8 | 0.8 | 0.1 | N |  |  | OP | X | 4 | 2009 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage2010 | hydro | TRUE | 11273 | Lower Valley Energy Inc | 6394 | Swift Creek | WY | Lincoln | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.817 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 2 | 2010 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage2010 | hydro | TRUE | 11273 | Lower Valley Energy Inc | 6394 | Swift Creek | WY | Lincoln | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 12 | 2010 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1950 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6395 | Anderson Ranch | ID | Elmore | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 20 | 1 | 20 | 20 | 0 | N |  |  | OP | X | 12 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1951 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6395 | Anderson Ranch | ID | Elmore | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 20 | 1 | 20 | 20 | 0 | N |  |  | OP | X | 7 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1925 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6396 | Black Canyon | ID | Gem | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.1 | 1 | 5.1 | 5.1 | 0 | N |  |  | OP | X | 12 | 1925 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1925 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6396 | Black Canyon | ID | Gem | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.1 | 1 | 5.1 | 5.1 | 0 | N |  |  | OP | X | 12 | 1925 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage2004 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6397 | Boise R Diversion | ID | Ada | 1A | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.1 | 1 | 1.1 | 1.1 | 0 | N |  |  | OP | X | 6 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage2004 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6397 | Boise R Diversion | ID | Ada | 2A | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.1 | 1 | 1.1 | 1.1 | 0 | N |  |  | OP | X | 6 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage2004 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6397 | Boise R Diversion | ID | Ada | 3A | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.1 | 1 | 1.1 | 1.1 | 0 | N |  |  | OP | X | 6 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage1927 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6398 | Minidoka | ID | Minidoka | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.7 | 0.9 | 2.7 | 2.7 | 0 | N |  |  | OP | X | 6 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1942 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6398 | Minidoka | ID | Minidoka | 7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5 | 0.83 | 5 | 5 | 0 | N |  |  | OP | X | 5 | 1942 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1997 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6398 | Minidoka | ID | Minidoka | 8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 0.9 | 10 | 10 | 0 | N |  |  | OP | X | 6 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1997 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6398 | Minidoka | ID | Minidoka | 9 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 0.9 | 10 | 10 | 0 | N |  |  | OP | X | 6 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1953 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6400 | Canyon Ferry | MT | Lewis and Clark | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 16.6 | 1 | 19.2 | 19.2 | 0 | N |  |  | OP | X | 12 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1954 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6400 | Canyon Ferry | MT | Lewis and Clark | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 16.6 | 1 | 19.2 | 19.2 | 0 | N |  |  | OP | X | 4 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1954 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6400 | Canyon Ferry | MT | Lewis and Clark | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 16.6 | 1 | 19.2 | 19.2 | 0 | N |  |  | OP | X | 3 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1940 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6402 | Elephant Butte | NM | Sierra | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9.3 | 0.93 | 9.3 | 9.3 | 0 | N |  |  | OP | X | 11 | 1940 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1940 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6402 | Elephant Butte | NM | Sierra | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9.3 | 0.93 | 9.3 | 9.3 | 0 | N |  |  | OP | X | 11 | 1940 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1940 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6402 | Elephant Butte | NM | Sierra | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9.3 | 0.93 | 9.3 | 9.3 | 0 | N |  |  | OP | X | 11 | 1940 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1960 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6403 | Green Springs | OR | Jackson | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 17.2 | 0.95 | 17.2 | 17.2 | 0 | N |  |  | OP | X | 5 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1958 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6404 | Deer Creek (UT) | UT | Wasatch | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.9 | 2.7 | 2.7 | 0 | N |  |  | OP | X | 2 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1958 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6404 | Deer Creek (UT) | UT | Wasatch | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.9 | 2.7 | 2.7 | 0 | N |  |  | OP | X | 2 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1963 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6405 | Flaming Gorge | UT | Daggett | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 50.6 | 0.9 | 50.6 | 50.6 | 0 | N |  |  | OP | X | 11 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1963 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6405 | Flaming Gorge | UT | Daggett | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 50.6 | 0.9 | 50.6 | 50.6 | 0 | N |  |  | OP | X | 12 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1964 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6405 | Flaming Gorge | UT | Daggett | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 50.6 | 0.9 | 50.6 | 50.6 | 0 | N |  |  | OP | X | 2 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1956 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6406 | Chandler | WA | Benton | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6 | 1 | 6 | 6 | 0 | N |  |  | OP | X | 2 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1956 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6406 | Chandler | WA | Benton | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6 | 1 | 6 | 6 | 0 | N |  |  | OP | X | 2 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1958 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6407 | Roza | WA | Yakima | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 12.9 | 0.95 | 12.9 | 12.9 | 0 | N |  |  | OP | X | 8 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1948 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6408 | Heart Mountain | WY | Park | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5 | 0.83 | 5 | 4.6 | 0 | N |  |  | OP | X | 12 | 1948 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1955 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6409 | Alcova | WY | Natrona | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 20.7 | 1 | 20.7 | 20.7 | 0 | N |  |  | OP | X | 7 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1955 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 6409 | Alcova | WY | Natrona | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 20.7 | 1 | 20.7 | 20.7 | 0 | N |  |  | OP | X | 7 | 1955 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1954 | hydro | TRUE | 9339 | International Bound & Wtr Comm | 6410 | Falcon Dam & Power | TX | Starr | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10.5 | 0.9 | 10.5 | 10.5 | 3 | N |  |  | OP | X | 10 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1954 | hydro | TRUE | 9339 | International Bound & Wtr Comm | 6410 | Falcon Dam & Power | TX | Starr | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10.5 | 0.9 | 10 | 10 | 3 | N |  |  | OP | X | 10 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1954 | hydro | TRUE | 9339 | International Bound & Wtr Comm | 6410 | Falcon Dam & Power | TX | Starr | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10.5 | 0.9 | 10 | 10 | 3 | N |  |  | OP | X | 10 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1965 | hydro | TRUE | 19449 | USACE-Fort Worth District | 6413 | Sam Rayburn Dam | TX | Jasper | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 26 | 0.95 | 26 | 26 | 10 | N |  |  | OP | X | 9 | 1965 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1965 | hydro | TRUE | 19449 | USACE-Fort Worth District | 6413 | Sam Rayburn Dam | TX | Jasper | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 26 | 0.95 | 26 | 26 | 10 | N |  |  | OP | X | 9 | 1965 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1953 | hydro | TRUE | 19449 | USACE-Fort Worth District | 6414 | Whitney | TX | Bosque | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 20.9 | 0.9 | 21 | 21 | 1 | N |  |  | OP | X | 6 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1953 | hydro | TRUE | 19449 | USACE-Fort Worth District | 6414 | Whitney | TX | Bosque | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 20.9 | 0.9 | 21 | 21 | 1 | N |  |  | OP | X | 6 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1970 | hydro | TRUE | 27470 | USCE-Tulsa District | 6415 | Broken Bow Dam | OK | McCurtain | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 50 | 0.95 | 57.5 | 57.5 | 18 | N |  |  | OP | X | 1 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H
Vintage1970 | hydro | TRUE | 27470 | USCE-Tulsa District | 6415 | Broken Bow Dam | OK | McCurtain | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 50 | 0.95 | 57.5 | 57.5 | 18 | N |  |  | OP | X | 6 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H
Vintage1945 | hydro | TRUE | 27470 | USCE-Tulsa District | 6416 | Denison | TX | Grayson | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 53.5 | 0.95 | 50 | 50 | 25 | N |  |  | OP | X | 3 | 1945 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 1H
Vintage1949 | hydro | TRUE | 27470 | USCE-Tulsa District | 6416 | Denison | TX | Grayson | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 50.8 | 0.95 | 40 | 40 | 25 | N |  |  | OA | X | 9 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 1H | [7 empty] | 10 | 10 | 4 | 2022
Vintage1950 | hydro | TRUE | 19462 | USCE-Nashville District | 6417 | Center Hill | TN | DeKalb | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 45 | 0.9 | 52 | 52 | 45 | N |  |  | OP | X | 11 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1951 | hydro | TRUE | 19462 | USCE-Nashville District | 6417 | Center Hill | TN | DeKalb | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 50 | 0.9 | 50 | 50 | 45 | N |  |  | OP | X | 1 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1951 | hydro | TRUE | 19462 | USCE-Nashville District | 6417 | Center Hill | TN | DeKalb | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 45 | 0.9 | 52 | 52 | 45 | N |  |  | OP | X | 4 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1958 | hydro | TRUE | 19462 | USCE-Nashville District | 6418 | Cheatham | TN | Dickson | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 12 | 0.9 | 13.8 | 13.8 | 12 | N |  |  | OP | X | 5 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1958 | hydro | TRUE | 19462 | USCE-Nashville District | 6418 | Cheatham | TN | Dickson | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 12 | 0.9 | 13.8 | 13.8 | 12 | N |  |  | OP | X | 9 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1958 | hydro | TRUE | 19462 | USCE-Nashville District | 6418 | Cheatham | TN | Dickson | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 12 | 0.9 | 13.8 | 13.8 | 12 | N |  |  | OP | X | 11 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1964 | hydro | TRUE | 27470 | USCE-Tulsa District | 6419 | Eufaula Dam | OK | Haskell | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 30 | 0.95 | 34.5 | 34.5 | 10 | N |  |  | OP | X | 7 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H
Vintage1964 | hydro | TRUE | 27470 | USCE-Tulsa District | 6419 | Eufaula Dam | OK | Haskell | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 30 | 0.95 | 34.5 | 34.5 | 10 | N |  |  | OP | X | 9 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H
Vintage1964 | hydro | TRUE | 27470 | USCE-Tulsa District | 6419 | Eufaula Dam | OK | Haskell | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 30 | 0.95 | 34.5 | 34.5 | 10 | N |  |  | OP | X | 8 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H
Vintage1956 | hydro | TRUE | 14354 | PacifiCorp | 6421 | Lemolo 2 | OR | Douglas | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 43.7 | 0.97 | 38.5 | 38.5 | 0 | N |  |  | OP | X | 11 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1906 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 6422 | Madison Dam | MT | Madison | MAD1 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 4.1 | 0.9 | 3.7 | 3.7 | 1 | Y | 12 | 2021 | OP | X | 9 | 1906 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1906 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 6422 | Madison Dam | MT | Madison | MAD2 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 4.1 | 0.9 | 3.7 | 3.7 | 1 | Y | 12 | 2021 | OP | X | 9 | 1906 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1906 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 6422 | Madison Dam | MT | Madison | MAD3 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 2.2 | 1 | 2 | 2 | 1 | N |  |  | OA | X | 9 | 1906 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [7 empty] | 1.7 | 1.7 | 1 | 2022 | [12 empty] | N
Vintage1908 | hydro | TRUE | 13902 | NorthWestern Energy (MT hdro) | 6422 | Madison Dam | MT | Madison | MAD4 | Conventional Hydroelectric | HY |  | S | X | X | NA | NA | 2.2 | 1 | 2 | 2 | 1 | N |  |  | OA | X | 7 | 1908 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [7 empty] | 1.7 | 1.7 | 1 | 2022 | [12 empty] | N
Vintage1927 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 6424 | Chelan | WA | Chelan | A-1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 29.6 | 0.8 | 31.4 | 31.4 | 23 | N |  |  | OP | X | 9 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1928 | hydro | TRUE | 3413 | PUD No 1 of Chelan County | 6424 | Chelan | WA | Chelan | A-2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 29.6 | 0.8 | 30.7 | 30.7 | 23 | N |  |  | OP | X | 8 | 1928 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1921 | hydro | TRUE | 16868 | City of Seattle - (WA) | 6430 | Cedar Falls (WA) | WA | King | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.95 | 15 | 15 | 0.2 | N |  |  | OP | X | 11 | 1921 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 12H | [20 empty] | Y | 12 | 2022 | N
Vintage1929 | hydro | TRUE | 16868 | City of Seattle - (WA) | 6430 | Cedar Falls (WA) | WA | King | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 15 | 0.95 | 15 | 15 | 0.2 | N |  |  | OP | X | 11 | 1929 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 12H | [20 empty] | Y | 12 | 2022 | N
Vintage1924 | hydro | TRUE | 16868 | City of Seattle - (WA) | 6431 | Gorge | WA | Whatcom | 21 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 36.8 | 0.97 | 32 | 32 | 0 | N |  |  | OP | X | 9 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | Y | 3 | 2026 | N
Vintage1924 | hydro | TRUE | 16868 | City of Seattle - (WA) | 6431 | Gorge | WA | Whatcom | 22 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 36.8 | 0.97 | 32 | 32 | 0 | N |  |  | OP | X | 9 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | Y | 6 | 2027 | N
Vintage1929 | hydro | TRUE | 16868 | City of Seattle - (WA) | 6431 | Gorge | WA | Whatcom | 23 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 36.8 | 0.97 | 32 | 32 | 0 | N |  |  | OP | X | 5 | 1929 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | Y | 9 | 2028 | N
Vintage1951 | hydro | TRUE | 16868 | City of Seattle - (WA) | 6431 | Gorge | WA | Whatcom | 24 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 96.9 | 0.97 | 97 | 97 | 0 | N |  |  | OP | X | 6 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | Y | 4 | 2029 | N
Vintage1937 | hydro | TRUE | 16868 | City of Seattle - (WA) | 6432 | Diablo | WA | Whatcom | 31 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 90 | 0.9 | 90 | 90 | 0 | N |  |  | OP | X | 4 | 1937 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [20 empty] | Y | 11 | 2024 | N
Vintage1936 | hydro | TRUE | 16868 | City of Seattle - (WA) | 6432 | Diablo | WA | Whatcom | 32 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 90 | 0.9 | 90 | 90 | 0 | N |  |  | OP | X | 10 | 1936 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [20 empty] | Y | 11 | 2024 | N
Vintage1936 | hydro | TRUE | 16868 | City of Seattle - (WA) | 6432 | Diablo | WA | Whatcom | 35 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 0 | N |  |  | OP | X | 10 | 1936 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [20 empty] | Y | 9 | 2024 | N
Vintage1936 | hydro | TRUE | 16868 | City of Seattle - (WA) | 6432 | Diablo | WA | Whatcom | 36 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 0 | N |  |  | OP | X | 10 | 1936 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [20 empty] | Y | 12 | 2025 | N
Vintage1967 | hydro | TRUE | 16868 | City of Seattle - (WA) | 6433 | Boundary | WA | Pend Oreille | 51 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 158.4 | 0.95 | 158.4 | 158.4 | 0 | N |  |  | OP | X | 10 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [7 empty] | 22.1 | 22.1 | 8 | 2025 | [9 empty] | N |  |  | N
Vintage1967 | hydro | TRUE | 16868 | City of Seattle - (WA) | 6433 | Boundary | WA | Pend Oreille | 52 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 161.5 | 0.95 | 161.5 | 161.5 | 0 | N |  |  | OP | X | 8 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [7 empty] | 19 | 19 | 8 | 2023 | [9 empty] | Y | 8 | 2023 | N
Vintage1967 | hydro | TRUE | 16868 | City of Seattle - (WA) | 6433 | Boundary | WA | Pend Oreille | 53 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 158.4 | 0.95 | 158.4 | 158.4 | 0 | N |  |  | OP | X | 9 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | Y | 8 | 2024 | N
Vintage1967 | hydro | TRUE | 16868 | City of Seattle - (WA) | 6433 | Boundary | WA | Pend Oreille | 54 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 161.5 | 0.95 | 161.5 | 161.5 | 0 | N |  |  | OP | X | 8 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [7 empty] | 19 | 19 | 8 | 2022 | [9 empty] | Y | 8 | 2022 | N
Vintage1985 | hydro | TRUE | 16868 | City of Seattle - (WA) | 6433 | Boundary | WA | Pend Oreille | 55 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 239.4 | 0.95 | 232 | 232 | 0 | N |  |  | OP | X | 11 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1986 | hydro | TRUE | 16868 | City of Seattle - (WA) | 6433 | Boundary | WA | Pend Oreille | 56 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 239.4 | 0.95 | 232 | 232 | 0 | N |  |  | OP | X | 5 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1949 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 6438 | Queens Creek | NC | Macon | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.4 | 0.8 | 1.4 | 1.4 | 1.4 | N |  |  | OP | X | 1 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1925 | hydro | TRUE | 18642 | Tennessee Valley Authority | 6440 | Wilson Dam | AL | Lauderdale | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 23 | 0.8 | 22 | 21.8 | 21 | N |  |  | OP | X | 9 | 1925 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1942 | hydro | TRUE | 18642 | Tennessee Valley Authority | 6440 | Wilson Dam | AL | Lauderdale | 10 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 29.2 | 0.9 | 29.5 | 29.2 | 18 | N |  |  | OP | X | 5 | 1942 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1942 | hydro | TRUE | 18642 | Tennessee Valley Authority | 6440 | Wilson Dam | AL | Lauderdale | 11 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 29.2 | 0.9 | 29.2 | 29 | 18 | N |  |  | OP | X | 7 | 1942 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1942 | hydro | TRUE | 18642 | Tennessee Valley Authority | 6440 | Wilson Dam | AL | Lauderdale | 12 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 29.2 | 0.9 | 29.2 | 29 | 22 | N |  |  | OP | X | 8 | 1942 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1943 | hydro | TRUE | 18642 | Tennessee Valley Authority | 6440 | Wilson Dam | AL | Lauderdale | 13 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 29.2 | 0.9 | 29.4 | 29.1 | 18 | N |  |  | OP | X | 4 | 1943 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1943 | hydro | TRUE | 18642 | Tennessee Valley Authority | 6440 | Wilson Dam | AL | Lauderdale | 14 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 25.2 | 0.9 | 29.4 | 29.1 | 22 | N |  |  | OP | X | 11 | 1943 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1949 | hydro | TRUE | 18642 | Tennessee Valley Authority | 6440 | Wilson Dam | AL | Lauderdale | 15 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 29.2 | 0.9 | 29.2 | 29 | 18 | N |  |  | OP | X | 12 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1950 | hydro | TRUE | 18642 | Tennessee Valley Authority | 6440 | Wilson Dam | AL | Lauderdale | 16 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 29.2 | 0.9 | 29.2 | 29 | 18 | N |  |  | OP | X | 1 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1950 | hydro | TRUE | 18642 | Tennessee Valley Authority | 6440 | Wilson Dam | AL | Lauderdale | 17 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 29.2 | 0.9 | 29 | 28.8 | 18 | N |  |  | OP | X | 2 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1950 | hydro | TRUE | 18642 | Tennessee Valley Authority | 6440 | Wilson Dam | AL | Lauderdale | 18 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 25.2 | 0.9 | 29 | 28.7 | 18 | N |  |  | OP | X | 3 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1961 | hydro | TRUE | 18642 | Tennessee Valley Authority | 6440 | Wilson Dam | AL | Lauderdale | 19 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 54 | 0.9 | 55 | 54.9 | 50 | N |  |  | OP | X | 12 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1925 | hydro | TRUE | 18642 | Tennessee Valley Authority | 6440 | Wilson Dam | AL | Lauderdale | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 23 | 0.8 | 22.3 | 22.1 | 21 | N |  |  | OP | X | 9 | 1925 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1962 | hydro | TRUE | 18642 | Tennessee Valley Authority | 6440 | Wilson Dam | AL | Lauderdale | 20 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 54 | 0.9 | 55 | 55 | 50 | N |  |  | OP | X | 1 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1962 | hydro | TRUE | 18642 | Tennessee Valley Authority | 6440 | Wilson Dam | AL | Lauderdale | 21 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 54 | 0.9 | 55 | 55 | 51.2 | N |  |  | OP | X | 4 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1925 | hydro | TRUE | 18642 | Tennessee Valley Authority | 6440 | Wilson Dam | AL | Lauderdale | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 23 | 0.8 | 23 | 22.7 | 21 | N |  |  | OP | X | 9 | 1925 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1925 | hydro | TRUE | 18642 | Tennessee Valley Authority | 6440 | Wilson Dam | AL | Lauderdale | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 23 | 0.8 | 22 | 21.8 | 21 | N |  |  | OP | X | 9 | 1925 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1925 | hydro | TRUE | 18642 | Tennessee Valley Authority | 6440 | Wilson Dam | AL | Lauderdale | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 36 | 0.9 | 30.3 | 30 | 20 | N |  |  | OP | X | 9 | 1925 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1925 | hydro | TRUE | 18642 | Tennessee Valley Authority | 6440 | Wilson Dam | AL | Lauderdale | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 30.9 | 0.9 | 30.4 | 30.1 | 20 | N |  |  | OP | X | 9 | 1925 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1925 | hydro | TRUE | 18642 | Tennessee Valley Authority | 6440 | Wilson Dam | AL | Lauderdale | 7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 30.9 | 0.9 | 29.1 | 28.8 | 20 | N |  |  | OP | X | 9 | 1925 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1925 | hydro | TRUE | 18642 | Tennessee Valley Authority | 6440 | Wilson Dam | AL | Lauderdale | 8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 30.9 | 0.9 | 30.7 | 30.4 | 20 | N |  |  | OP | X | 9 | 1925 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1942 | hydro | TRUE | 18642 | Tennessee Valley Authority | 6440 | Wilson Dam | AL | Lauderdale | 9 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 29.2 | 0.9 | 29.6 | 29.3 | 18 | N |  |  | OP | X | 3 | 1942 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1949 | hydro | TRUE | 14534 | City of Pasadena - (CA) | 6449 | Azusa | CA | Los Angeles | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.85 | 2 | 2 | 2 | N |  |  | OP | X | 2 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H |  |  |  | N | [19 empty] | N
Vintage1927 | hydro | TRUE | 7601 | Green Mountain Power Corp | 6450 | Proctor | VT | Rutland | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.2 | N |  |  | OP | X | 8 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [5 empty] | 0 | 10M
Vintage1905 | hydro | TRUE | 7601 | Green Mountain Power Corp | 6450 | Proctor | VT | Rutland | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.7 | 0.7 | 0.2 | N |  |  | OP | X | 8 | 1905 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [5 empty] | 0 | 10M
Vintage1905 | hydro | TRUE | 7601 | Green Mountain Power Corp | 6450 | Proctor | VT | Rutland | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.7 | 0.7 | 0.2 | N |  |  | OP | X | 8 | 1905 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [5 empty] | 0 | 10M
Vintage1905 | hydro | TRUE | 7601 | Green Mountain Power Corp | 6450 | Proctor | VT | Rutland | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.7 | 0.7 | 0.2 | N |  |  | OP | X | 8 | 1905 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [5 empty] | 0 | 10M
Vintage1984 | hydro | TRUE | 7601 | Green Mountain Power Corp | 6450 | Proctor | VT | Rutland | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.9 | 0.8 | 2.8 | 2.9 | 0.2 | N |  |  | OP | X | 10 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [5 empty] | 0 | 10M
Vintage1913 | hydro | TRUE | 7601 | Green Mountain Power Corp | 6451 | Beldens | VT | Addison | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.6 | 0.8 | 0.2 | N |  |  | OP | X | 8 | 1913 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [5 empty] | 0 | 10M
Vintage1913 | hydro | TRUE | 7601 | Green Mountain Power Corp | 6451 | Beldens | VT | Addison | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.6 | 0.8 | 0.2 | N |  |  | OP | X | 8 | 1913 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [5 empty] | 0 | 10M
Vintage1988 | hydro | TRUE | 7601 | Green Mountain Power Corp | 6451 | Beldens | VT | Addison | HC3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.1 | 0.8 | 3.2 | 4.1 | 0.2 | N |  |  | OP | X | 12 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1922 | hydro | TRUE | 7601 | Green Mountain Power Corp | 6456 | Carver Falls | NY | Washington | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 0.2 | N |  |  | OP | X | 2 | 1922 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1922 | hydro | TRUE | 7601 | Green Mountain Power Corp | 6456 | Carver Falls | NY | Washington | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 2 | 1922 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1927 | hydro | TRUE | 14354 | PacifiCorp | 6459 | Big Fork | MT | Flathead | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.7 | 0.8 | 1.9 | 1.9 | 0 | N |  |  | OP | X | 7 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1928 | hydro | TRUE | 14354 | PacifiCorp | 6459 | Big Fork | MT | Flathead | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.7 | 0.8 | 1.9 | 1.9 | 0 | N |  |  | OP | X | 7 | 1928 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1910 | hydro | TRUE | 14354 | PacifiCorp | 6459 | Big Fork | MT | Flathead | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.8 | 0.8 | 0.8 | 0 | N |  |  | OP | X | 7 | 1910 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1986 | nuclear | TRUE | 11241 | Entergy Louisiana LLC | 6462 | River Bend | LA | West Feliciana | 1 | Nuclear | ST |  | S | X | X | EES.RVRBEND1 | EES.RVRBEND1 | 1035.9 | 0.9 | 967.5 | 967 | 103.6 | N |  |  | OP | X | 6 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NUC |  |  |  | N |  |  | OVER | [23 empty] | N
Vintage1972 | petroleum | TRUE | 554 | City of Ames - (IA) | 6463 | Ames GT | IA | Story | GT1 | Petroleum Liquids | GT |  | S | X | X |  |  | 21.3 | 0.85 | 15.2 | 19.5 | 1 | N |  |  | OP | X | 5 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2005 | petroleum | TRUE | 554 | City of Ames - (IA) | 6463 | Ames GT | IA | Story | GT2 | Petroleum Liquids | GT |  | S | X | X |  |  | 57.4 | 0.85 | 25.7 |  | 15 | N |  |  | OP | X | 9 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1984 | hard coal | TRUE | 1307 | Basin Electric Power Coop | 6469 | Antelope Valley | ND | Mercer | 1 | Conventional Steam Coal | ST |  | S | X | X | WAUEANTELOPUNANTELO_1_UNIT_RA | WAUE.BEPM.AVS1 | 477 | 0.9 | 450 | 450 | 200 | N |  |  | OP | X | 7 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: RC; SUB SUB SUB: LIG; DFO DFO DFO: NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1986 | hard coal | TRUE | 1307 | Basin Electric Power Coop | 6469 | Antelope Valley | ND | Mercer | 2 | Conventional Steam Coal | ST |  | S | X | X | WAUEANTELOPUNANTELO_2_UNIT_RA | WAUE.BEPM.AVS2 | 477 | 0.9 | 450 | 450 | 200 | N |  |  | OP | X | 7 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: RC; SUB SUB SUB: LIG; DFO DFO DFO: NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1968 | petroleum | TRUE | 10071 | Kauai Island Utility Cooperative | 6474 | Port Allen (HI) | HI | Kauai | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 6 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: OBL |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1968 | petroleum | TRUE | 10071 | Kauai Island Utility Cooperative | 6474 | Port Allen (HI) | HI | Kauai | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 1.2 | 1.2 | 0.5 | N |  |  | OP | X | 6 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: OBL |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1968 | petroleum | TRUE | 10071 | Kauai Island Utility Cooperative | 6474 | Port Allen (HI) | HI | Kauai | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 6 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: OBL |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1991 | petroleum | TRUE | 10071 | Kauai Island Utility Cooperative | 6474 | Port Allen (HI) | HI | Kauai | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 8.6 | 0.8 | 7.6 | 7.6 | 1 | N |  |  | OP | X | 12 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: WO; WC WC WC: OBL |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1991 | petroleum | TRUE | 10071 | Kauai Island Utility Cooperative | 6474 | Port Allen (HI) | HI | Kauai | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 8.6 | 0.8 | 7.6 | 7.6 | 1 | N |  |  | OP | X | 12 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: WO; WC WC WC: OBL |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1990 | petroleum | TRUE | 10071 | Kauai Island Utility Cooperative | 6474 | Port Allen (HI) | HI | Kauai | D6 | Petroleum Liquids | IC |  | S | X | X |  |  | 8.6 | 0.8 | 7.6 | 7.6 | 1 | N |  |  | OP | X | 11 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: WO; WC WC WC: OBL |  |  |  |  | N |  | 1H | [23 empty] | N | N | N
Vintage1990 | petroleum | TRUE | 10071 | Kauai Island Utility Cooperative | 6474 | Port Allen (HI) | HI | Kauai | D7 | Petroleum Liquids | IC |  | S | X | X |  |  | 8.6 | 0.8 | 7.6 | 7.6 | 1 | N |  |  | OP | X | 11 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: WO; WC WC WC: OBL |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1973 | petroleum | TRUE | 10071 | Kauai Island Utility Cooperative | 6474 | Port Allen (HI) | HI | Kauai | GT1 | Petroleum Liquids | GT | CC1 | S | X | X |  |  | 19.2 | 0.8 | 19 | 19 | 1 | N |  |  | OP | X | 8 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: OBL |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1977 | petroleum | TRUE | 10071 | Kauai Island Utility Cooperative | 6474 | Port Allen (HI) | HI | Kauai | GT2 | Petroleum Liquids | GT | CC1 | S | X | X |  |  | 23.8 | 0.85 | 21.5 | 21.5 | 1 | N |  |  | OP | X | 12 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: OBL |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1964 | petroleum | TRUE | 10071 | Kauai Island Utility Cooperative | 6474 | Port Allen (HI) | HI | Kauai | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.5 | 1.5 | 0.5 | N |  |  | OP | X | 1 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: OBL |  |  |  | N | N |  | 10M |  |  |  | N | [19 empty] | N | N | N
Vintage1964 | petroleum | TRUE | 10071 | Kauai Island Utility Cooperative | 6474 | Port Allen (HI) | HI | Kauai | IC2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.5 | 1.5 | 0.5 | N |  |  | OP | X | 1 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: OBL |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1928 | hydro | TRUE | 7601 | Green Mountain Power Corp | 6475 | Gorge 18 | VT | Chittenden | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 0.3 | N |  |  | OP | X | 1 | 1928 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  | 0 | 10M
Vintage1983 | hydro | TRUE | 11208 | Los Angeles Department of Water & Power | 6479 | San Francisquito 1 | CA | Los Angeles | 1A | Conventional Hydroelectric | HY |  | S | X | X | none | none | 22.5 | 0.9 | 27 | 27 | 0.1 | N |  |  | OP | X | 12 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1917 | hydro | TRUE | 11208 | Los Angeles Department of Water & Power | 6479 | San Francisquito 1 | CA | Los Angeles | 3 | Conventional Hydroelectric | HY |  | S | X | X | none | none | 9.9 | 0.8 | 11 | 11 | 0.1 | N |  |  | OP | X | 4 | 1917 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1923 | hydro | TRUE | 11208 | Los Angeles Department of Water & Power | 6479 | San Francisquito 1 | CA | Los Angeles | 4 | Conventional Hydroelectric | HY |  | S | X | X | none | none | 10.6 | 0.85 | 12 | 12 | 0.1 | N |  |  | OP | X | 5 | 1923 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1987 | hydro | TRUE | 11208 | Los Angeles Department of Water & Power | 6479 | San Francisquito 1 | CA | Los Angeles | 6 | Conventional Hydroelectric | HY |  | S | X | X | none | none | 22.5 | 0.9 | 27 | 27 | 0.1 | N |  |  | OP | X | 4 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1920 | hydro | TRUE | 11208 | Los Angeles Department of Water & Power | 6480 | San Francisquito 2 | CA | Los Angeles | 1 | Conventional Hydroelectric | HY |  | S | X | X | none | none | 14 | 0.8 | 14.5 | 14.5 | 0.1 | N |  |  | OS | X | 7 | 1920 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1920 | hydro | TRUE | 11208 | Los Angeles Department of Water & Power | 6480 | San Francisquito 2 | CA | Los Angeles | 2 | Conventional Hydroelectric | HY |  | S | X | X | none | none | 14 | 0.8 | 14.4 | 14.4 | 0.1 | N |  |  | OP | X | 8 | 1920 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1932 | hydro | TRUE | 11208 | Los Angeles Department of Water & Power | 6480 | San Francisquito 2 | CA | Los Angeles | 3 | Conventional Hydroelectric | HY |  | S | X | X | none | none | 18 | 0.9 | 16 | 16 | 0.1 | N |  |  | OP | X | 9 | 1932 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1986 | hard coal | TRUE | 11208 | Los Angeles Department of Water & Power | 6481 | Intermountain Power Project | UT | Millard | 1 | Conventional Steam Coal | ST |  | W | X | X |  |  | 820 | 0.9 | 900 | 900 | 270 | N |  |  | OP | X | 6 | 1986 | 7 | 2025 | N | Electric Utility | 1 | X X X: X; RC RC RC: BIT; SUB SUB SUB: SUB; DFO DFO DFO: DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1987 | hard coal | TRUE | 11208 | Los Angeles Department of Water & Power | 6481 | Intermountain Power Project | UT | Millard | 2 | Conventional Steam Coal | ST |  | W | X | X |  |  | 820 | 0.9 | 900 | 900 | 270 | N |  |  | OP | X | 5 | 1987 | 7 | 2025 | N | Electric Utility | 1 | X X X: X; RC RC RC: BIT; SUB SUB SUB: SUB; DFO DFO DFO: DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1931 | hydro | TRUE | 61122 | Great River Hydro, LLC | 6483 | Mcindoes | VT | Caledonia | GEN1 | Conventional Hydroelectric | HY |  | S | X | X | 473 |  | 2.6 | 0.8 | 2.3 | 2.4 | 2.3 | N |  |  | OP | X | 1 | 1931 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1931 | hydro | TRUE | 61122 | Great River Hydro, LLC | 6483 | Mcindoes | VT | Caledonia | GEN2 | Conventional Hydroelectric | HY |  | S | X | X | 473 |  | 2.6 | 0.8 | 2.3 | 2.4 | 2.3 | N |  |  | OP | X | 1 | 1931 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1931 | hydro | TRUE | 61122 | Great River Hydro, LLC | 6483 | Mcindoes | VT | Caledonia | GEN3 | Conventional Hydroelectric | HY |  | S | X | X | 473 |  | 2.6 | 0.8 | 2.8 | 3 | 2.5 | N |  |  | OP | X | 1 | 1931 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1931 | hydro | TRUE | 61122 | Great River Hydro, LLC | 6483 | Mcindoes | VT | Caledonia | GEN4 | Conventional Hydroelectric | HY |  | S | X | X | 473 |  | 2.6 | 0.8 | 2.8 | 3 | 2.5 | N |  |  | OP | X | 1 | 1931 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M
Vintage1913 | hydro | TRUE | 14354 | PacifiCorp | 6484 | Bend | OR | Deschutes | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0 | N |  |  | OP | X | 7 | 1913 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1916 | hydro | TRUE | 14354 | PacifiCorp | 6484 | Bend | OR | Deschutes | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 1 | 0.3 | 0.3 | 0 | N |  |  | OP | X | 7 | 1916 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1917 | hydro | TRUE | 14354 | PacifiCorp | 6484 | Bend | OR | Deschutes | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 1 | 0.5 | 0.5 | 0 | N |  |  | OP | X | 7 | 1917 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1944 | hydro | TRUE | 13511 | New York State Elec & Gas Corp | 6486 | Mill C | NY | Clinton | 1 | Conventional Hydroelectric | HY |  | S | X | X | 23628 | 23628 | 1 | 0.8 | 1 | 1 | 0 | N |  |  | OP | X | 8 | 1944 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1943 | hydro | TRUE | 13511 | New York State Elec & Gas Corp | 6486 | Mill C | NY | Clinton | 2 | Conventional Hydroelectric | HY |  | S | X | X | 23628 | 23628 | 1.2 | 0.8 | 1.2 | 1.2 | 0 | N |  |  | OP | X | 8 | 1943 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1984 | hydro | TRUE | 13511 | New York State Elec & Gas Corp | 6486 | Mill C | NY | Clinton | 3 | Conventional Hydroelectric | HY |  | S | X | X | 23628 | 23628 | 3.8 | 0.95 | 3.8 | 3.8 | 0 | N |  |  | OA | X | 11 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1971 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 6504 | Maalaea | HI | Maui | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.6 | 0.8 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 12 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1979 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 6504 | Maalaea | HI | Maui | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 12.5 | 0.8 | 12.3 | 12.3 | 8 | N |  |  | OP | X | 12 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1980 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 6504 | Maalaea | HI | Maui | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 12.5 | 0.8 | 12.3 | 12.3 | 8 | N |  |  | OP | X | 7 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1988 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 6504 | Maalaea | HI | Maui | 12 | Petroleum Liquids | IC |  | S | X | X |  |  | 12.5 | 0.8 | 12.3 | 12.3 | 8 | N |  |  | OP | X | 4 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1989 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 6504 | Maalaea | HI | Maui | 13 | Petroleum Liquids | IC |  | S | X | X |  |  | 12.5 | 0.8 | 12.3 | 12.3 | 8 | N |  |  | OP | X | 5 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1992 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 6504 | Maalaea | HI | Maui | 14 | Petroleum Liquids | CT | CC1 | S | X | Y |  |  | 23.6 | 0.9 | 21.1 | 21.1 | 8 | N |  |  | OP | X | 5 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1993 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 6504 | Maalaea | HI | Maui | 15 | Petroleum Liquids | CA | CC1 | S | N | X |  |  | 18 | 0.9 | 12 | 12 | 4 | N |  |  | OP | X | 10 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1993 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 6504 | Maalaea | HI | Maui | 16 | Petroleum Liquids | CT | CC1 | S | X | Y |  |  | 23.6 | 0.9 | 21.1 | 21.1 | 8 | N |  |  | OP | X | 5 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1998 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 6504 | Maalaea | HI | Maui | 17 | Petroleum Liquids | CT | CC2 | S | X | Y |  |  | 25 | 0.8 | 17.6 | 17.6 | 14 | N |  |  | OP | X | 12 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2006 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 6504 | Maalaea | HI | Maui | 18 | Petroleum Liquids | CA | CC2 | S | N | X |  |  | 18 | 0.8 | 13.8 | 13.8 | 8.5 | N |  |  | OP | X | 10 | 2006 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2000 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 6504 | Maalaea | HI | Maui | 19 | Petroleum Liquids | CT | CC2 | S | X | Y |  |  | 25 | 0.8 | 17.6 | 17.6 | 14 | N |  |  | OP | X | 9 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1972 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 6504 | Maalaea | HI | Maui | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.6 | 0.8 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 7 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1972 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 6504 | Maalaea | HI | Maui | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.6 | 0.8 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 9 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1973 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 6504 | Maalaea | HI | Maui | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 5.6 | 0.8 | 5.5 | 5.5 | 3 | N |  |  | OP | X | 11 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1973 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 6504 | Maalaea | HI | Maui | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 5.6 | 0.8 | 5.5 | 5.5 | 3 | N |  |  | OP | X | 12 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1975 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 6504 | Maalaea | HI | Maui | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 5.6 | 0.8 | 5.5 | 5.5 | 3 | N |  |  | OP | X | 3 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1975 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 6504 | Maalaea | HI | Maui | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 5.6 | 0.8 | 5.5 | 5.5 | 3 | N |  |  | OP | X | 8 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1977 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 6504 | Maalaea | HI | Maui | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 5.6 | 0.8 | 5.5 | 5.5 | 3 | N |  |  | OP | X | 11 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1978 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 6504 | Maalaea | HI | Maui | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 5.6 | 0.8 | 5.5 | 5.5 | 3 | N |  |  | OP | X | 7 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1987 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 6504 | Maalaea | HI | Maui | X1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.6 | 0.8 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 3 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N | N | N
Vintage1987 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 6504 | Maalaea | HI | Maui | X2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.6 | 0.8 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 3 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N | N | N
Vintage1924 | hydro | TRUE | 15248 | Portland General Electric Co | 6505 | Oak Grove | OR | Clackamas | 1 | Conventional Hydroelectric | HY |  | S | X | X | OGP1_1_GNODE1 |  | 25.5 | 0.85 | 22 | 22 | 4 | N |  |  | OS | X | 8 | 1924 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1931 | hydro | TRUE | 15248 | Portland General Electric Co | 6505 | Oak Grove | OR | Clackamas | 2 | Conventional Hydroelectric | HY |  | S | X | X | OGP1_1_GNODE1 |  | 25.5 | 0.85 | 22 | 22 | 4 | N |  |  | OS | X | 3 | 1931 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1941 | hydro | TRUE | 1956 | City of Bonners Ferry | 6506 | Moyie Springs | ID | Boundary | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.8 | 1.1 | 1.1 | 0.7 | N |  |  | OP | X | 12 | 1941 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1921 | hydro | TRUE | 1956 | City of Bonners Ferry | 6506 | Moyie Springs | ID | Boundary | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.3 | N |  |  | OP | X | 12 | 1921 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1950 | hydro | TRUE | 1956 | City of Bonners Ferry | 6506 | Moyie Springs | ID | Boundary | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.8 | 1.1 | 1.1 | 0.7 | N |  |  | OP | X | 12 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1982 | hydro | TRUE | 1956 | City of Bonners Ferry | 6506 | Moyie Springs | ID | Boundary | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 0.8 | 1.7 | 1.7 | 1.2 | N |  |  | OP | X | 2 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 1H
Vintage1942 | hydro | TRUE | 56621 | Yakama Power | 6507 | Drop 2 (WA) | WA | Yakima | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 0.9 | 2.1 | 2.1 | 0.8 | N |  |  | OS | X | 8 | 1942 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H
Vintage1932 | hydro | TRUE | 56621 | Yakama Power | 6508 | Drop 3 (WA) | WA | Yakima | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.5 | 0.5 | 0.2 | N |  |  | OS | X | 5 | 1932 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 1H
Vintage1932 | hydro | TRUE | 56621 | Yakama Power | 6508 | Drop 3 (WA) | WA | Yakima | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.5 | 0.5 | 0.2 | N |  |  | OS | X | 5 | 1932 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 1H
Vintage1960 | petroleum | TRUE | 17166 | Sierra Pacific Power Co | 6510 | Brunswick | NV | Carson City | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1.7 | N |  |  | OS | X | 9 | 1960 | 9 | 2023 | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 10M | [23 empty] | N
Vintage1960 | petroleum | TRUE | 17166 | Sierra Pacific Power Co | 6510 | Brunswick | NV | Carson City | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1.7 | N |  |  | OS | X | 9 | 1960 | 9 | 2023 | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 10M | [23 empty] | N
Vintage1960 | petroleum | TRUE | 17166 | Sierra Pacific Power Co | 6510 | Brunswick | NV | Carson City | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1.7 | N |  |  | OS | X | 9 | 1960 | 9 | 2023 | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 10M | [23 empty] | N
Vintage1914 | hydro | TRUE | 56369 | Truckee Meadows Water Authority | 6513 | Fleish | NV | Washoe | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.8 | 2.5 | 2.2 | 0.2 | N |  |  | OP | X | 1 | 1914 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1989 | natural gas peaker | TRUE | 19728 | UNS Electric, Inc | 6515 | Valencia | AZ | Santa Cruz | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 18 | 0.85 | 13.5 | 14.8 | 8 | N |  |  | SB | Y | 8 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | N | N |  |  |  | N | N | [16 empty] | Y | Y | Y
Vintage1989 | natural gas peaker | TRUE | 19728 | UNS Electric, Inc | 6515 | Valencia | AZ | Santa Cruz | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 18 | 0.85 | 13.5 | 14.8 | 8 | N |  |  | SB | Y | 8 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | N | N |  |  |  | N | N | [16 empty] | Y | Y | Y
Vintage1989 | natural gas peaker | TRUE | 19728 | UNS Electric, Inc | 6515 | Valencia | AZ | Santa Cruz | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 18 | 0.85 | 13.5 | 14.8 | 8 | N |  |  | SB | Y | 8 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | N | N |  |  |  | N | N | [16 empty] | Y | Y | Y
Vintage2006 | natural gas peaker | TRUE | 19728 | UNS Electric, Inc | 6515 | Valencia | AZ | Santa Cruz | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 54 | 0.8 | 19.8 | 21.2 | 5 | N |  |  | OP | X | 6 | 2006 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | N | N |  |  |  | N | N | [16 empty] | Y | Y | Y
Vintage1964 | petroleum | TRUE | 56146 | Black Hills Colorado Electric, LLC | 6516 | Rocky Ford | CO | Otero | IC1A | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 2 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1964 | petroleum | TRUE | 56146 | Black Hills Colorado Electric, LLC | 6516 | Rocky Ford | CO | Otero | IC2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 6 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1964 | petroleum | TRUE | 56146 | Black Hills Colorado Electric, LLC | 6516 | Rocky Ford | CO | Otero | IC3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 6 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1964 | petroleum | TRUE | 56146 | Black Hills Colorado Electric, LLC | 6516 | Rocky Ford | CO | Otero | IC4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 6 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1964 | petroleum | TRUE | 56146 | Black Hills Colorado Electric, LLC | 6516 | Rocky Ford | CO | Otero | IC5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 6 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1971 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 6517 | Keowee | SC | Pickens | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 78.8 | 0.9 | 76 | 76 | 76 | N |  |  | OP | X | 4 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M
Vintage1971 | hydro | TRUE | 5416 | Duke Energy Carolinas, LLC | 6517 | Keowee | SC | Pickens | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 78.8 | 0.9 | 76 | 76 | 76 | N |  |  | OP | X | 4 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M
Vintage2008 | petroleum | TRUE | 57222 | Liberty Utilities (CalPeco Electric) LLC | 6518 | Kings Beach | CA | Placer | KB1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.94 | 2 | 2 | 0.6 | N |  |  | OP | X | 10 | 2008 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2008 | petroleum | TRUE | 57222 | Liberty Utilities (CalPeco Electric) LLC | 6518 | Kings Beach | CA | Placer | KB2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.94 | 2 | 2 | 0.6 | N |  |  | OP | X | 10 | 2008 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2008 | petroleum | TRUE | 57222 | Liberty Utilities (CalPeco Electric) LLC | 6518 | Kings Beach | CA | Placer | KB3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.94 | 2 | 2 | 0.6 | N |  |  | OP | X | 10 | 2008 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2008 | petroleum | TRUE | 57222 | Liberty Utilities (CalPeco Electric) LLC | 6518 | Kings Beach | CA | Placer | KB4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.94 | 2 | 2 | 0.6 | N |  |  | OP | X | 10 | 2008 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage2008 | petroleum | TRUE | 57222 | Liberty Utilities (CalPeco Electric) LLC | 6518 | Kings Beach | CA | Placer | KB5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.94 | 2 | 2 | 0.6 | N |  |  | OP | X | 10 | 2008 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage2008 | petroleum | TRUE | 57222 | Liberty Utilities (CalPeco Electric) LLC | 6518 | Kings Beach | CA | Placer | KB6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.94 | 2 | 2 | 0.6 | N |  |  | OP | X | 10 | 2008 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1912 | hydro | TRUE | 7601 | Green Mountain Power Corp | 6519 | Vergennes 9 | VT | Addison | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.8 | 0.7 | 0.7 | 0.2 | N |  |  | OP | X | 1 | 1912 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  | 0 | 10M
Vintage1912 | hydro | TRUE | 7601 | Green Mountain Power Corp | 6519 | Vergennes 9 | VT | Addison | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.8 | 0.7 | 0.7 | 0.2 | N |  |  | OP | X | 1 | 1912 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  | 0 | 10M
Vintage1943 | hydro | TRUE | 7601 | Green Mountain Power Corp | 6519 | Vergennes 9 | VT | Addison | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.2 | N |  |  | OP | X | 1 | 1943 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  | 0 | 10M
Vintage1953 | hydro | TRUE | 7601 | Green Mountain Power Corp | 6520 | Waterbury 22 | VT | Washington | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.5 | 0.8 | 5 | 5 | 2.5 | N |  |  | OP | X | 6 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  | 0 | 1H
Vintage1911 | hydro | TRUE | 40444 | Truckee-Carson Irrigation District | 6521 | Lahontan | NV | Churchill | 1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 1 | 1911 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1911 | hydro | TRUE | 40444 | Truckee-Carson Irrigation District | 6521 | Lahontan | NV | Churchill | 2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 1 | 1911 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1911 | hydro | TRUE | 40444 | Truckee-Carson Irrigation District | 6521 | Lahontan | NV | Churchill | 3 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 1 | 1911 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1965 | other | TRUE | 64574 | Yards Creek Energy | 6522 | Yards Creek Energy | NJ | Warren | 1 | Hydroelectric Pumped Storage | PS |  | S | X | X | YARDSCRE14 KV UNIT01 | YARDSCRE14 KV UNIT01 | 151 | 0.98 | 140 | 140 | 70 | N |  |  | OP | X | 11 | 1965 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1965 | other | TRUE | 64574 | Yards Creek Energy | 6522 | Yards Creek Energy | NJ | Warren | 2 | Hydroelectric Pumped Storage | PS |  | S | X | X | YARDSCRE14 KV UNIT02 | YARDSCRE14 KV UNIT02 | 151 | 0.98 | 140 | 140 | 70 | N |  |  | OP | X | 12 | 1965 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1965 | other | TRUE | 64574 | Yards Creek Energy | 6522 | Yards Creek Energy | NJ | Warren | 3 | Hydroelectric Pumped Storage | PS |  | S | X | X | YARDSCRE14 KV UNIT03 | YARDSCRE14 KV UNIT03 | 151 | 0.98 | 140 | 140 | 70 | N |  |  | OP | X | 9 | 1965 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1926 | hydro | TRUE | 13511 | New York State Elec & Gas Corp | 6526 | Rainbow Falls Auscble | NY | Clinton | 1 | Conventional Hydroelectric | HY |  | S | X | X | 23628 | 23628 | 1.3 | 0.8 | 1.3 | 1.3 | 0 | N |  |  | OA | X | 8 | 1926 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1927 | hydro | TRUE | 13511 | New York State Elec & Gas Corp | 6526 | Rainbow Falls Auscble | NY | Clinton | 2 | Conventional Hydroelectric | HY |  | S | X | X | 23628 | 23628 | 1.3 | 0.8 | 1.3 | 1.3 | 0 | N |  |  | OP | X | 8 | 1927 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1930 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 6527 | E J West | NY | Saratoga | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24058 | 24058 | 11 | 0.8 | 10.2 | 11 | 1 | N |  |  | OP | X | 1 | 1930 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1930 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 6527 | E J West | NY | Saratoga | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24058 | 24058 | 11 | 0.8 | 10.4 | 11.1 | 1 | N |  |  | OP | X | 1 | 1930 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1922 | hydro | TRUE | 61122 | Great River Hydro, LLC | 6529 | Searsburg | VT | Bennington | GEN1 | Conventional Hydroelectric | HY |  | S | X | X | 561 |  | 4 | 0.8 | 4.5 | 4.6 | 1 | N |  |  | OP | X | 3 | 1922 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1911 | hydro | TRUE | 56369 | Truckee Meadows Water Authority | 6531 | Verdi | NV | Washoe | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 2.4 | 2.4 | 0.2 | N |  |  | OP | X | 1 | 1911 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1904 | hydro | TRUE | 56369 | Truckee Meadows Water Authority | 6532 | Washoe | NV | Washoe | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 0.8 | 0.9 | 0.7 | 0.2 | N |  |  | OP | X | 1 | 1904 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1904 | hydro | TRUE | 56369 | Truckee Meadows Water Authority | 6532 | Washoe | NV | Washoe | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 0.8 | 0.9 | 0.7 | 0.2 | N |  |  | OP | X | 1 | 1904 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1983 | hydro | TRUE | 13137 | City of Murray - (UT) | 6537 | Little Cottonwood | UT | Salt Lake | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.99 | 2.4 | 2.4 | 0.1 | N |  |  | OP | X | 4 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1983 | hydro | TRUE | 13137 | City of Murray - (UT) | 6537 | Little Cottonwood | UT | Salt Lake | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.99 | 2.4 | 2.4 | 0.1 | N |  |  | OP | X | 4 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1909 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 6543 | Dam No. 4 Hydro Station | WV | Jefferson | 1 | Conventional Hydroelectric | HY |  | W | X | X | RIVERTON138KV DUM HYD | RIVERTON138KV DUM HYD | 0.5 | 1 | 0.5 | 0.5 | 0.2 | N |  |  | OP | X | 1 | 1909 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M
Vintage1909 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 6543 | Dam No. 4 Hydro Station | WV | Jefferson | 2 | Conventional Hydroelectric | HY |  | W | X | X | RIVERTO138KV DUMHYD | RIVERTON138KV DUM HYD | 0.5 | 1 | 0.5 | 0.5 | 0.2 | N |  |  | OP | X | 1 | 1909 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M
Vintage1991 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 6543 | Dam No. 4 Hydro Station | WV | Jefferson | 3 | Conventional Hydroelectric | HY |  | W | X | X | RIVRTON138KV DUM HYD | RIVERTON138KV DUM HYD | 0.9 | 1 | 0.9 | 0.9 | 0.2 | N |  |  | OP | X | 9 | 1991 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M
Vintage1919 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 6544 | Dam No. 5 Hydro Station | WV | Berkeley | 1 | Conventional Hydroelectric | HY |  | W | X | X | RIVERTON138KV DUM HYD | RIVERTON138KV DUM HYD | 0.5 | 1 | 0.5 | 0.5 | 0.2 | N |  |  | OP | X | 1 | 1919 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M
Vintage1919 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 6544 | Dam No. 5 Hydro Station | WV | Berkeley | 2 | Conventional Hydroelectric | HY |  | W | X | X | RIVERTON138 DUM HYD | RIVERTON138 KV DUM HYD | 0.5 | 1 | 0.5 | 0.5 | 0.2 | N |  |  | OP | X | 1 | 1919 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M
Vintage1913 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 6546 | Millville Hydro Station | WV | Jefferson | 1 | Conventional Hydroelectric | HY |  | W | X | X | RIVERTON138KV DUM HYD | RIVERTON138KV DUM HYD | 0.8 | 1 | 0.6 | 0.8 | 0.2 | N |  |  | OP | X | 1 | 1913 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M
Vintage1939 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 6546 | Millville Hydro Station | WV | Jefferson | 2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1 | 1 | 0.8 | 1 | 0.3 | N |  |  | OP | X | 12 | 1939 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M
Vintage1938 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 6546 | Millville Hydro Station | WV | Jefferson | 3 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1 | 1 | 1 | 1.2 | 0.3 | N |  |  | OP | X | 12 | 1938 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  |  | N | 0 | 10M
Vintage1968 | hydro | TRUE | 19400 | USACE Northwestern Division | 6552 | Foster | OR | Linn | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 0.95 | 10 | 10 | 10 | N |  |  | OP | X | 9 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1968 | hydro | TRUE | 19400 | USACE Northwestern Division | 6552 | Foster | OR | Linn | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 0.95 | 10 | 10 | 10 | N |  |  | OP | X | 10 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1993 | petroleum | TRUE | 20214 | Waverly Municipal Elec Utility | 6554 | Waverly Municipal Electric North Plant | IA | Bremer | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 7 | 0.8 | 7 | 7 | 1.5 | N |  |  | OP | X | 4 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage2015 | petroleum | TRUE | 20214 | Waverly Municipal Elec Utility | 6554 | Waverly Municipal Electric North Plant | IA | Bremer | 17 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 6 | 2015 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage2015 | petroleum | TRUE | 20214 | Waverly Municipal Elec Utility | 6554 | Waverly Municipal Electric North Plant | IA | Bremer | 18 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 6 | 2015 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 1H | [23 empty] | N | N
Vintage2015 | petroleum | TRUE | 20214 | Waverly Municipal Elec Utility | 6554 | Waverly Municipal Electric North Plant | IA | Bremer | 19 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 6 | 2015 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 1H | [23 empty] | N | N
Vintage2015 | petroleum | TRUE | 20214 | Waverly Municipal Elec Utility | 6554 | Waverly Municipal Electric North Plant | IA | Bremer | 20 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 6 | 2015 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 1H | [23 empty] | N | N
Vintage1958 | natural gas peaker | TRUE | 20214 | Waverly Municipal Elec Utility | 6554 | Waverly Municipal Electric North Plant | IA | Bremer | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.5 | 0.8 | 3.5 | 3.5 | 1.5 | N |  |  | OP | X | 8 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1967 | natural gas peaker | TRUE | 20214 | Waverly Municipal Elec Utility | 6554 | Waverly Municipal Electric North Plant | IA | Bremer | 8 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.7 | 0.8 | 3.7 | 3.7 | 1.5 | N |  |  | OP | X | 8 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1967 | natural gas peaker | TRUE | 20214 | Waverly Municipal Elec Utility | 6554 | Waverly Municipal Electric North Plant | IA | Bremer | 9 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.7 | 0.8 | 3.7 | 3.7 | 1.5 | N |  |  | OP | X | 8 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage2021 | petroleum | TRUE | 12119 | McGrath Light & Power Co | 6555 | McGrath | AK | Yukon Koyukuk | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 4 | 2021 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage2021 | petroleum | TRUE | 12119 | McGrath Light & Power Co | 6555 | McGrath | AK | Yukon Koyukuk | 12 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 4 | 2021 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2021 | petroleum | TRUE | 12119 | McGrath Light & Power Co | 6555 | McGrath | AK | Yukon Koyukuk | 13 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 4 | 2021 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage2021 | petroleum | TRUE | 12119 | McGrath Light & Power Co | 6555 | McGrath | AK | Yukon Koyukuk | 14 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 4 | 2021 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage2016 | natural gas peaker | TRUE | 298 | City of Alexandria - (LA) | 6558 | D G Hunter | LA | Rapides | 10 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 9.3 | 0.8 | 8.6 | 8.6 | 3 | N |  |  | OP | X | 3 | 2016 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2016 | natural gas peaker | TRUE | 298 | City of Alexandria - (LA) | 6558 | D G Hunter | LA | Rapides | 11 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 9.3 | 0.8 | 8.6 | 8.6 | 3 | N |  |  | OP | X | 3 | 2016 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2016 | natural gas peaker | TRUE | 298 | City of Alexandria - (LA) | 6558 | D G Hunter | LA | Rapides | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 9.3 | 0.8 | 8.6 | 8.6 | 3 | N |  |  | OP | X | 3 | 2016 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2016 | natural gas peaker | TRUE | 298 | City of Alexandria - (LA) | 6558 | D G Hunter | LA | Rapides | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 9.3 | 0.8 | 8.6 | 8.6 | 3 | N |  |  | OP | X | 3 | 2016 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2016 | natural gas peaker | TRUE | 298 | City of Alexandria - (LA) | 6558 | D G Hunter | LA | Rapides | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 9.3 | 0.8 | 8.6 | 8.6 | 3 | N |  |  | OP | X | 3 | 2016 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2016 | natural gas peaker | TRUE | 298 | City of Alexandria - (LA) | 6558 | D G Hunter | LA | Rapides | 8 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 9.3 | 0.8 | 8.6 | 8.6 | 3 | N |  |  | OP | X | 3 | 2016 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2016 | natural gas peaker | TRUE | 298 | City of Alexandria - (LA) | 6558 | D G Hunter | LA | Rapides | 9 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 9.3 | 0.8 | 8.6 | 8.6 | 3 | N |  |  | OP | X | 3 | 2016 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2017 | natural gas combined cycle | TRUE | 3522 | Chugach Electric Assn Inc | 6559 | George M Sullivan Generation Plant 2 | AK | Anchorage | 10 | Natural Gas Fired Combined Cycle | CT | CC2 | S | X | N |  |  | 60.4 | 0.85 | 50 | 50 | 5 | N |  |  | OP | X | 2 | 2017 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage2017 | natural gas combined cycle | TRUE | 3522 | Chugach Electric Assn Inc | 6559 | George M Sullivan Generation Plant 2 | AK | Anchorage | 11 | Natural Gas Fired Combined Cycle | CA | CC2 | S | N | X |  |  | 30.9 | 0.85 | 29 | 29 | 3 | N |  |  | OP | X | 2 | 2017 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage1979 | natural gas peaker | TRUE | 3522 | Chugach Electric Assn Inc | 6559 | George M Sullivan Generation Plant 2 | AK | Anchorage | 7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 102.6 | 0.9 | 102.6 | 81.8 | 8 | N |  |  | OP | X | 6 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2017 | natural gas combined cycle | TRUE | 3522 | Chugach Electric Assn Inc | 6559 | George M Sullivan Generation Plant 2 | AK | Anchorage | 9 | Natural Gas Fired Combined Cycle | CT | CC2 | S | X | N |  |  | 60.4 | 0.85 | 50 | 50 | 5 | N |  |  | OP | X | 2 | 2017 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage1984 | natural gas peaker | TRUE | 3522 | Chugach Electric Assn Inc | 6559 | George M Sullivan Generation Plant 2 | AK | Anchorage | GT8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 92.6 | 0.85 | 77.7 | 86.5 | 5 | N |  |  | SB | Y | 12 | 1984 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage1935 | hydro | TRUE | 733 | Appalachian Power Co | 6560 | London | WV | Kanawha | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.8 | 0.8 | 4.8 | 4.8 | 1 | N |  |  | OP | X | 12 | 1935 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [5 empty] | 0 | 12H
Vintage1935 | hydro | TRUE | 733 | Appalachian Power Co | 6560 | London | WV | Kanawha | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.8 | 0.8 | 4.8 | 4.8 | 1 | N |  |  | OP | X | 12 | 1935 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [5 empty] | 0 | 12H
Vintage1935 | hydro | TRUE | 733 | Appalachian Power Co | 6560 | London | WV | Kanawha | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.8 | 0.8 | 4.8 | 4.8 | 1 | N |  |  | OP | X | 12 | 1935 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [5 empty] | 0 | 12H
Vintage1935 | hydro | TRUE | 733 | Appalachian Power Co | 6561 | Marmet | WV | Kanawha | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.8 | 0.8 | 4.8 | 4.8 | 1 | N |  |  | OP | X | 12 | 1935 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [5 empty] | 0 | 12H
Vintage1935 | hydro | TRUE | 733 | Appalachian Power Co | 6561 | Marmet | WV | Kanawha | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.8 | 0.8 | 4.8 | 4.8 | 1 | N |  |  | OP | X | 12 | 1935 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [5 empty] | 0 | 12H
Vintage1935 | hydro | TRUE | 733 | Appalachian Power Co | 6561 | Marmet | WV | Kanawha | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.8 | 0.8 | 4.8 | 4.8 | 1 | N |  |  | OP | X | 12 | 1935 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [5 empty] | 0 | 12H
Vintage1938 | hydro | TRUE | 733 | Appalachian Power Co | 6562 | Winfield | WV | Putnam | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 14.7 | 0.8 | 8.9 | 14.5 | 1 | N |  |  | OP | X | 1 | 1938 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [5 empty] | 0 | 12H
Vintage1938 | hydro | TRUE | 733 | Appalachian Power Co | 6562 | Winfield | WV | Putnam | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.9 | 0.8 | 4.9 | 4.9 | 1 | N |  |  | OP | X | 1 | 1938 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [5 empty] | 0 | 12H
Vintage1938 | hydro | TRUE | 733 | Appalachian Power Co | 6562 | Winfield | WV | Putnam | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.9 | 0.8 | 4.9 | 4.9 | 1 | N |  |  | OP | X | 1 | 1938 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [5 empty] | 0 | 12H
Vintage1976 | petroleum | TRUE | 924 | Associated Electric Coop, Inc | 6563 | Unionville | MO | Putnam | 1 | Petroleum Liquids | GT |  | S | X | X |  |  | 26.6 | 0.9 | 22 | 22 | 22 | N |  |  | OS | X | 6 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1976 | petroleum | TRUE | 924 | Associated Electric Coop, Inc | 6563 | Unionville | MO | Putnam | 2 | Petroleum Liquids | GT |  | S | X | X |  |  | 26.6 | 0.9 | 22 | 22 | 22 | N |  |  | OS | X | 6 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1961 | petroleum | TRUE | 1615 | Town of Berlin - (MD) | 6565 | Berlin | MD | Worcester | 1A | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.8 | N |  |  | OP | X | 6 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1989 | petroleum | TRUE | 1615 | Town of Berlin - (MD) | 6565 | Berlin | MD | Worcester | 5A | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 1.2 | N |  |  | OP | X | 12 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2020 | natural gas peaker | TRUE | 1615 | Town of Berlin - (MD) | 6565 | Berlin | MD | Worcester | 8A | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2 | 1 | 2 | 2 | 1 | N |  |  | OP | X | 9 | 2020 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage1976 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6566 | Bethel | AK | Bethel | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.1 | 0.85 | 2.1 | 2.1 | 1.4 | N |  |  | OP | X | 11 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1976 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6566 | Bethel | AK | Bethel | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.1 | 0.85 | 2.1 | 2.1 | 1.4 | N |  |  | OP | X | 11 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1976 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6566 | Bethel | AK | Bethel | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.1 | 0.85 | 2.1 | 2.1 | 1.4 | N |  |  | OP | X | 11 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1976 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6566 | Bethel | AK | Bethel | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.1 | 0.85 | 2.1 | 2.1 | 1.4 | N |  |  | OP | X | 11 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1989 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6566 | Bethel | AK | Bethel | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.1 | 0.85 | 2.1 | 2.1 | 1.4 | N |  |  | OP | X | 4 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1992 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6566 | Bethel | AK | Bethel | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.1 | 0.85 | 2.1 | 2.1 | 1.4 | N |  |  | OP | X | 12 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2001 | petroleum | TRUE | 1857 | Block Island Utility District | 6567 | Block Island | RI | Washington | 23 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 1.2 | N |  |  | SB | Y | 7 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage2002 | petroleum | TRUE | 1857 | Block Island Utility District | 6567 | Block Island | RI | Washington | 24 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 1.6 | N |  |  | SB | Y | 4 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage2006 | petroleum | TRUE | 1857 | Block Island Utility District | 6567 | Block Island | RI | Washington | 25 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | SB | Y | 3 | 2006 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2018 | petroleum | TRUE | 1857 | Block Island Utility District | 6567 | Block Island | RI | Washington | 27 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 0.3 | N |  |  | SB | Y | 6 | 2018 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage2017 | petroleum | TRUE | 9776 | City of Johnson - (KS) | 6579 | Johnson | KS | Stanton | CAT8 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 0.5 | N |  |  | OP | X | 8 | 2017 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N | N | N
Vintage2017 | petroleum | TRUE | 9776 | City of Johnson - (KS) | 6579 | Johnson | KS | Stanton | CAT9 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 0.5 | N |  |  | OP | X | 8 | 2017 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N | N | N
Vintage1947 | hydro | TRUE | 10210 | Ketchikan Public Utilities | 6580 | Beaver Falls | AK | Ketchikan Gateway | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.3 | N |  |  | OP | X | 1 | 1947 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 1H
Vintage1954 | hydro | TRUE | 10210 | Ketchikan Public Utilities | 6580 | Beaver Falls | AK | Ketchikan Gateway | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 0.88 | 2.2 | 1.8 | 0.3 | N |  |  | OP | X | 1 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 1H
Vintage1954 | hydro | TRUE | 10210 | Ketchikan Public Utilities | 6580 | Beaver Falls | AK | Ketchikan Gateway | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 0.88 | 2.2 | 1.8 | 0.3 | N |  |  | OP | X | 1 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 1H
Vintage1968 | hydro | TRUE | 10210 | Ketchikan Public Utilities | 6581 | Silvis | AK | Ketchikan Gateway | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.1 | 0.84 | 2.1 | 2.1 | 0.1 | N |  |  | OP | X | 1 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 1H
Vintage2012 | petroleum | TRUE | 50079 | Utility Board of Key West City | 6584 | Stock Island | FL | Monroe | EP2 | Petroleum Liquids | IC |  | W | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 1 | N |  |  | OP | X | 6 | 2012 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1978 | petroleum | TRUE | 50079 | Utility Board of Key West City | 6584 | Stock Island | FL | Monroe | GT1 | Petroleum Liquids | GT |  | W | X | X |  |  | 23.4 | 0.9 | 19 | 19 | 5 | N |  |  | OP | X | 11 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 50079 | Utility Board of Key West City | 6584 | Stock Island | FL | Monroe | GT2 | Petroleum Liquids | GT |  | W | X | X |  |  | 19.7 | 0.9 | 17 | 17 | 5 | N |  |  | OP | X | 9 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 50079 | Utility Board of Key West City | 6584 | Stock Island | FL | Monroe | GT3 | Petroleum Liquids | GT |  | W | X | X |  |  | 19.7 | 0.85 | 17 | 17 | 5 | N |  |  | OP | X | 9 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2006 | petroleum | TRUE | 50079 | Utility Board of Key West City | 6584 | Stock Island | FL | Monroe | GT4 | Petroleum Liquids | GT |  | W | X | X |  |  | 42 | 0.85 | 44 | 44 | 10 | N |  |  | OP | X | 6 | 2006 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1991 | petroleum | TRUE | 50079 | Utility Board of Key West City | 6584 | Stock Island | FL | Monroe | MSD1 | Petroleum Liquids | IC |  | W | X | X |  |  | 9.6 | 0.8 | 7.5 | 7.5 | 4 | N |  |  | OP | X | 6 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1991 | petroleum | TRUE | 50079 | Utility Board of Key West City | 6584 | Stock Island | FL | Monroe | MSD2 | Petroleum Liquids | IC |  | W | X | X |  |  | 9.6 | 0.8 | 7.5 | 7.5 | 4 | N |  |  | OP | X | 6 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1975 | petroleum | TRUE | 11624 | Town of Marblehead - (MA) | 6586 | Wilkins Station | MA | Essex | 1 | Petroleum Liquids | IC |  | S | X | X | UN.RAILYARD23 MARB | UN.RAILYARD23 MARB | 2.7 | 0.8 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 11 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1975 | petroleum | TRUE | 11624 | Town of Marblehead - (MA) | 6586 | Wilkins Station | MA | Essex | 2 | Petroleum Liquids | IC |  | S | X | X | UN.RAILYARD23 MARB | UN.RAILYARD23 MARB | 2.7 | 0.8 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 11 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1969 | hydro | TRUE | 55937 | Entergy Texas Inc. | 6595 | Toledo Bend | TX | Newton | 1 | Conventional Hydroelectric | HY |  | J | X | X | EES.TOL_BEND1 |  | 40.5 | 0.95 | 40 | 40 | 32 | N |  |  | OP | X | 2 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1969 | hydro | TRUE | 55937 | Entergy Texas Inc. | 6595 | Toledo Bend | TX | Newton | 2 | Conventional Hydroelectric | HY |  | J | X | X | EES.TOL_BEND2 |  | 40.5 | 0.95 | 40 | 40 | 32 | N |  |  | OP | X | 2 | 1969 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1963 | hydro | TRUE | 16534 | Sacramento Municipal Util Dist | 6612 | Union Valley | CA | El Dorado | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 38.6 | 0.95 | 38.6 | 38.6 | 1 | N |  |  | OP | X | 10 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1930 | hydro | TRUE | 18371 | Village of Swanton - (VT) | 6618 | Highgate Falls | VT | Franklin | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.1 | 0.8 | 1 | 1 | 0.1 | N |  |  | OP | X | 8 | 1930 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1923 | hydro | TRUE | 18371 | Village of Swanton - (VT) | 6618 | Highgate Falls | VT | Franklin | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.1 | N |  |  | OP | X | 8 | 1923 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1954 | hydro | TRUE | 18371 | Village of Swanton - (VT) | 6618 | Highgate Falls | VT | Franklin | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.2 | 0.8 | 2.9 | 2.9 | 0.1 | N |  |  | OP | X | 8 | 1954 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1990 | hydro | TRUE | 18371 | Village of Swanton - (VT) | 6618 | Highgate Falls | VT | Franklin | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.8 | 1 | 4.8 | 4.8 | 0.1 | N |  |  | OP | X | 5 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage2012 | hydro | TRUE | 18371 | Village of Swanton - (VT) | 6618 | Highgate Falls | VT | Franklin | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 1 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 5 | 2012 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1977 | petroleum | TRUE | 30151 | Tri-State G & T Assn, Inc | 6619 | Burlington (CO) | CO | Kit Carson | 1 | Petroleum Liquids | GT |  | S | X | X |  |  | 64.7 | 0.9 | 50 | 60 | 25 | N |  |  | SB | Y | 6 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1977 | petroleum | TRUE | 30151 | Tri-State G & T Assn, Inc | 6619 | Burlington (CO) | CO | Kit Carson | 2 | Petroleum Liquids | GT |  | S | X | X |  |  | 64.7 | 0.9 | 50 | 60 | 25 | N |  |  | SB | Y | 7 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1943 | hydro | TRUE | 19635 | USACE-Omaha | 6623 | Fort Peck | MT | McCone | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 41.2 | 0.9 | 50 | 50 | 0 | N |  |  | OP | X | 7 | 1943 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1948 | hydro | TRUE | 19635 | USACE-Omaha | 6623 | Fort Peck | MT | McCone | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 17.3 | 0.9 | 20 | 20 | 0 | N |  |  | OS | X | 2 | 1948 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1951 | hydro | TRUE | 19635 | USACE-Omaha | 6623 | Fort Peck | MT | McCone | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 41.2 | 0.9 | 50 | 50 | 0 | N |  |  | OP | X | 12 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1961 | hydro | TRUE | 19635 | USACE-Omaha | 6623 | Fort Peck | MT | McCone | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40 | 0.95 | 49 | 49 | 0 | N |  |  | OP | X | 6 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1961 | hydro | TRUE | 19635 | USACE-Omaha | 6623 | Fort Peck | MT | McCone | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 40 | 0.95 | 49 | 49 | 0 | N |  |  | OP | X | 6 | 1961 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1956 | hydro | TRUE | 19635 | USACE-Omaha | 6624 | Gavins Point | NE | Cedar | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 44.1 | 0.95 | 34 | 34 | 0 | N |  |  | OP | X | 9 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  |  | N |  | 10M | [23 empty] | N
Vintage1956 | hydro | TRUE | 19635 | USACE-Omaha | 6624 | Gavins Point | NE | Cedar | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 44.1 | 0.95 | 34 | 34 | 0 | N |  |  | OP | X | 10 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  |  | N |  | 10M | [23 empty] | N
Vintage1957 | hydro | TRUE | 19635 | USACE-Omaha | 6624 | Gavins Point | NE | Cedar | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 44.1 | 0.95 | 34 | 34 | 0 | N |  |  | OP | X | 1 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  |  | N |  | 10M | [23 empty] | N
Vintage2007 | natural gas peaker | TRUE | 4180 | Connecticut Mun Elec Engy Coop | 6635 | A L Pierce | CT | New Haven | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 84 | 0.95 | 74.1 | 94.6 | 40 | N |  |  | OP | X | 10 | 2007 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO; WC WC WC: LFG |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1926 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 6636 | Lake Lynn Hydro Station | PA | Fayette | 1 | Conventional Hydroelectric | HY |  | W | X | X | LAKELYNN11KV GEN1-4 | LAKELYNN11KV GEN1-4 | 12.8 | 0.9 | 13 | 13 | 3 | N |  |  | OP | X | 9 | 1926 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M
Vintage1929 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 6636 | Lake Lynn Hydro Station | PA | Fayette | 2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 12.8 | 0.9 | 13 | 13 | 3 | N |  |  | OP | X | 7 | 1929 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M
Vintage1926 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 6636 | Lake Lynn Hydro Station | PA | Fayette | 3 | Conventional Hydroelectric | HY |  | W | X | X | LAKELYNN11KV GEN1-4 | LAKELYNN11KV GEN1-4 | 12.8 | 0.9 | 13 | 13 | 3 | N |  |  | OP | X | 6 | 1926 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M
Vintage1926 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 6636 | Lake Lynn Hydro Station | PA | Fayette | 4 | Conventional Hydroelectric | HY |  | W | X | X | LAKELYNN11KV GEN1-4 | LAKELYNN11KV GEN1-4 | 12.8 | 0.9 | 13 | 13 | 3 | N |  |  | OP | X | 5 | 1926 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M
Vintage1999 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6637 | Yakutat | AK | Yakutat | 2B | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0 | N |  |  | OP | X | 6 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1999 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6637 | Yakutat | AK | Yakutat | 3A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0 | N |  |  | OP | X | 6 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2007 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6637 | Yakutat | AK | Yakutat | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 0 | N |  |  | OP | X | 9 | 2007 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2012 | petroleum | TRUE | 221 | Alaska Village Elec Coop, Inc | 6637 | Yakutat | AK | Yakutat | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 0 | N |  |  | OP | X | 7 | 2012 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1979 | hard coal | TRUE | 1692 | Big Rivers Electric Corp | 6639 | R D Green | KY | Webster | 1 | Conventional Steam Coal | ST |  | S | X | X | BREC.GREEN1 | BREC.GREEN1 | 293 | 0.9 | 231 | 231 | 105 | N |  |  | OP | X | 12 | 1979 |  |  | N | Electric Utility | 1 | X | BIT | DFO | PC |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | Y | 5 | 2022 | Y | Y | N
Vintage1981 | hard coal | TRUE | 1692 | Big Rivers Electric Corp | 6639 | R D Green | KY | Webster | 2 | Conventional Steam Coal | ST |  | S | X | X | BREC.GREEN2 | BREC.GREEN2 | 293 | 0.9 | 223 | 223 | 110 | N |  |  | OP | X | 1 | 1981 |  |  | N | Electric Utility | 1 | X | BIT | DFO | PC |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | Y | 5 | 2022 | Y | Y | N
Vintage1983 | hard coal | TRUE | 814 | Entergy Arkansas LLC | 6641 | Independence Steam Electric Station | AR | Independence | 1 | Conventional Steam Coal | ST |  | J | X | X | EAI.INDEPEND1 | EAI.INDEPEND1 | 900 | 0.9 | 821.7 | 821.7 | 220 | N |  |  | OP | X | 1 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; DFO DFO DFO: DFO |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1984 | hard coal | TRUE | 814 | Entergy Arkansas LLC | 6641 | Independence Steam Electric Station | AR | Independence | 2 | Conventional Steam Coal | ST |  | J | X | X | EAI.INDEPEND2 | EAI.INDEPEND2 | 900 | 0.9 | 842 | 842 | 220 | N |  |  | OP | X | 12 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; DFO DFO DFO: DFO |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1980 | hydro | TRUE | 12397 | Metropolitan Water District of S CA | 6644 | Lake Mathews | CA | Riverside | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.9 | 0.85 | 4.9 | 4.9 | 2 | N |  |  | OP | X | 8 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 12H
Vintage1981 | hydro | TRUE | 12397 | Metropolitan Water District of S CA | 6645 | Foothill Feeder | CA | Los Angeles | 1 | Conventional Hydroelectric | HY | A184 | S | X | X |  |  | 4.5 | 0.84 | 7.1 | 6.7 | 2 | N |  |  | OP | X | 4 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 12H
Vintage1981 | hydro | TRUE | 12397 | Metropolitan Water District of S CA | 6645 | Foothill Feeder | CA | Los Angeles | 2 | Conventional Hydroelectric | HY | A184 | S | X | X |  |  | 4.5 | 0.84 |  |  | 2 | N |  |  | OP | X | 4 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 12H
Vintage1981 | hydro | TRUE | 12397 | Metropolitan Water District of S CA | 6646 | San Dimas | CA | Los Angeles | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9.9 | 1 | 9.9 | 9.9 | 1 | N |  |  | OP | X | 6 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 12H
Vintage1981 | hydro | TRUE | 12397 | Metropolitan Water District of S CA | 6647 | Yorba Linda | CA | Orange | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.1 | 1 | 5.1 | 5.1 | 1 | N |  |  | OP | X | 11 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 12H
Vintage1978 | petroleum | TRUE | 19436 | Union Electric Co - (MO) | 6650 | Mexico | MO | Audrain | 1 | Petroleum Liquids | GT |  | S | X | X | AMMO.MEXCTG1 | AMMO.MEXCTG1 | 60.7 | 0.9 | 54 | 69 | 6 | N |  |  | OP | X | 9 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1978 | petroleum | TRUE | 19436 | Union Electric Co - (MO) | 6651 | Moberly | MO | Randolph | 1 | Petroleum Liquids | GT |  | S | X | X | AMMO.MOBCTG1 | AMMO.MOBCTG1 | 60.6 | 0.9 | 54 | 69 | 6 | N |  |  | OP | X | 8 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1978 | petroleum | TRUE | 19436 | Union Electric Co - (MO) | 6652 | Moreau | MO | Cole | 1 | Petroleum Liquids | GT |  | S | X | X | AMMO.MORUCTG1 | AMMO.MORUCTG1 | 60.8 | 0.9 | 54 | 69 | 6 | N |  |  | OP | X | 8 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1983 | hard coal | TRUE | 12341 | MidAmerican Energy Co | 6664 | Louisa | IA | Louisa | 1 | Conventional Steam Coal | ST |  | J | X | X | MEC.LOUISA_1 | MEC.LOUISA_1 | 811.9 | 0.9 | 746.1 | 746.1 | 175 | N |  |  | OP | X | 10 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: RC; SUB SUB SUB: SUB; DFO DFO DFO: DFO | NG |  |  | N | N | 0 | OVER |  | Y |  |  | Y | [18 empty] | N |  | N
Vintage1984 | hydro | TRUE | 29297 | Pelican Utility | 6702 | Pelican | AK | Skagway Hoonah Angoon | HC1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.6 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 7 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1984 | hydro | TRUE | 29297 | Pelican Utility | 6702 | Pelican | AK | Skagway Hoonah Angoon | HC2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.8 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OS | X | 5 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage2008 | petroleum | TRUE | 29297 | Pelican Utility | 6702 | Pelican | AK | Skagway Hoonah Angoon | IC6 | Petroleum Liquids | IC |  | W | X | X |  |  | 0.4 | 0.9 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 9 | 2008 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2008 | petroleum | TRUE | 29297 | Pelican Utility | 6702 | Pelican | AK | Skagway Hoonah Angoon | IC7 | Petroleum Liquids | IC |  | W | X | X |  |  | 0.4 | 0.9 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 9 | 2008 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2008 | petroleum | TRUE | 29297 | Pelican Utility | 6702 | Pelican | AK | Skagway Hoonah Angoon | IC8 | Petroleum Liquids | IC |  | W | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 9 | 2008 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1966 | petroleum | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.9 | N |  |  | OP | X | 7 | 1966 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1976 | petroleum | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | 12 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 1.3 | N |  |  | OP | X | 6 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1986 | petroleum | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | 14 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.4 | 0.8 | 1.4 | 1.4 | 1.1 | N |  |  | OP | X | 10 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1995 | petroleum | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | 15 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.8 | 0.8 | 2.8 | 2.8 | 2.2 | N |  |  | OP | X | 12 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1958 | petroleum | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.8 | N |  |  | OP | X | 7 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1963 | petroleum | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 1.2 | N |  |  | OP | X | 6 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2011 | other | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | MT01 | Petroleum Liquids | GT |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 12 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2011 | other | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | MT02 | Petroleum Liquids | GT |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 12 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2011 | other | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | MT03 | Petroleum Liquids | GT |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 12 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2011 | other | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | MT04 | Petroleum Liquids | GT |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 12 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2011 | other | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | MT05 | Petroleum Liquids | GT |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 12 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2011 | other | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | MT06 | Petroleum Liquids | GT |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OS | X | 12 | 2011 |  |  | N | Electric Utility | 1 | [14 empty] | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2011 | other | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | MT07 | Petroleum Liquids | GT |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 12 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2011 | other | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | MT08 | Petroleum Liquids | GT |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 12 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2011 | other | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | MT09 | Petroleum Liquids | GT |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 12 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2011 | other | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | MT10 | Petroleum Liquids | GT |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 12 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2011 | other | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | MT11 | Petroleum Liquids | GT |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 12 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2011 | other | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | MT14 | Petroleum Liquids | GT |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 12 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2011 | other | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | MT15 | Petroleum Liquids | GT |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 12 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2011 | other | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | MT16 | Petroleum Liquids | GT |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OS | X | 12 | 2011 |  |  | N | Electric Utility | 1 | [14 empty] | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2011 | other | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | MT17 | Petroleum Liquids | GT |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OS | X | 12 | 2011 |  |  | N | Electric Utility | 1 | [14 empty] | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2011 | other | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | MT18 | Petroleum Liquids | GT |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 12 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2011 | other | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | MT19 | Petroleum Liquids | GT |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 12 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2011 | other | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | MT20 | Petroleum Liquids | GT |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 12 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2011 | other | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | MT21 | Petroleum Liquids | GT |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 12 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2011 | other | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | MT22 | Petroleum Liquids | GT |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OS | X | 12 | 2011 |  |  | N | Electric Utility | 1 | [14 empty] | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2011 | other | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | MT23 | Petroleum Liquids | GT |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 12 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2011 | other | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | MT24 | Petroleum Liquids | GT |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 12 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2011 | other | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | MT25 | Petroleum Liquids | GT |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 12 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2012 | other | TRUE | 17609 | Southern California Edison Co | 6704 | Pebbly Beach Generating Station Hybrid | CA | Los Angeles | NASB1 | Batteries | BA |  | S | X | X |  |  | 1 |  | 1 | 1 | 0.1 | N |  |  | OP | X | 8 | 2012 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: MWH | [6 empty] | OVER | [23 empty] | N | N
Vintage1960 | hard coal | TRUE | 261 | AGC Division of APGI Inc | 6705 | Warrick | IN | Warrick | 1 | Conventional Steam Coal | ST |  | S | X | X | sige.apgi | sige.apgi | 166.6 | 0.85 | 154 | 155.9 | 40 | N |  |  | OP | X | 4 | 1960 |  |  | Y | IPP CHP | 3 | X X X: T; RC RC RC: BIT; SUB SUB SUB: NG; DFO DFO DFO: NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1964 | hard coal | TRUE | 261 | AGC Division of APGI Inc | 6705 | Warrick | IN | Warrick | 2 | Conventional Steam Coal | ST |  | S | X | X | sige.apgi | sige.apgi | 166.6 | 0.85 | 126 | 127.1 | 40 | N |  |  | OP | X | 1 | 1964 |  |  | Y | IPP CHP | 3 | X X X: T; RC RC RC: BIT; SUB SUB SUB: NG; DFO DFO DFO: NG |  |  |  | N | N |  | OVER | N | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1965 | hard coal | TRUE | 261 | AGC Division of APGI Inc | 6705 | Warrick | IN | Warrick | 3 | Conventional Steam Coal | ST |  | S | X | X | sige.apgi | sige.apgi | 166.6 | 0.85 | 152.9 | 151.3 | 40 | N |  |  | OP | X | 10 | 1965 |  |  | Y | IPP CHP | 3 | X X X: T; RC RC RC: BIT; SUB SUB SUB: NG; DFO DFO DFO: NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1970 | hard coal | TRUE | 261 | AGC Division of APGI Inc | 6705 | Warrick | IN | Warrick | 4 | Conventional Steam Coal | ST |  | J | X | X | sige.war4alcoa | sige.war4alcoa | 323 | 0.85 | 302 | 300.1 | 80 | N |  |  | OP | X | 10 | 1970 |  |  | N | IPP CHP | 3 | X X X: X; RC RC RC: BIT; SUB SUB SUB: NG; DFO DFO DFO: NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1978 | petroleum | TRUE | 7570 | Great River Energy | 6741 | Rock Lake CT | MN | Pine | 1 | Petroleum Liquids | GT |  | S | X | X | GRE.ROCKLAKE | GRE.ROCKLAKE | 25 | 0.85 | 21.6 | 29.4 | 15 | N |  |  | OP | X | 4 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1984 | hard coal | TRUE | 15143 | Platte River Power Authority | 6761 | Rawhide | CO | Larimer | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 293.6 | 0.85 | 280 | 280 | 100 | N |  |  | OP | X | 4 | 1984 | 12 | 2029 | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; DFO DFO DFO: DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage2002 | natural gas peaker | TRUE | 15143 | Platte River Power Authority | 6761 | Rawhide | CO | Larimer | A | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 89.3 | 0.85 | 65 | 65 | 44 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2002 | natural gas peaker | TRUE | 15143 | Platte River Power Authority | 6761 | Rawhide | CO | Larimer | B | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 89.3 | 0.85 | 65 | 65 | 44 | N |  |  | OP | X | 8 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2002 | natural gas peaker | TRUE | 15143 | Platte River Power Authority | 6761 | Rawhide | CO | Larimer | C | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 89.3 | 0.85 | 65 | 65 | 44 | N |  |  | OP | X | 9 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2004 | natural gas peaker | TRUE | 15143 | Platte River Power Authority | 6761 | Rawhide | CO | Larimer | D | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 89.3 | 0.85 | 65 | 65 | 44 | N |  |  | OP | X | 6 | 2004 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2008 | natural gas peaker | TRUE | 15143 | Platte River Power Authority | 6761 | Rawhide | CO | Larimer | F | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 149.6 | 0.85 | 128 | 128 | 65 | N |  |  | OP | X | 6 | 2008 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1981 | hard coal | TRUE | 17177 | City of Sikeston - (MO) | 6768 | Sikeston Power Station | MO | Scott | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 261 | 0.9 | 240 | 240 | 70 | N |  |  | OP | X | 9 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; DFO DFO DFO: DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1982 | hard coal | TRUE | 20447 | Western Farmers Elec Coop, Inc | 6772 | Hugo | OK | Choctaw | 1 | Conventional Steam Coal | ST |  | S | X | X | WFEC_HUGO_PLANT | WFEC_HUGO_PLANT | 446 | 0.85 | 440 | 440 | 180 | N |  |  | OP | X | 4 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; DFO DFO DFO: DFO |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1972 | petroleum | TRUE | 19856 | City of Vineland - (NJ) | 6776 | West Station (NJ) | NJ | Cumberland | 1 | Petroleum Liquids | GT |  | S | X | X | VINELAND 69KV WEST CT |  | 27 | 0.85 | 22.9 | 27.4 | 12 | N |  |  | OP | X | 6 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H |  | N |  |  | N | [18 empty] | N | N | N
Vintage1985 | hydro | TRUE | 50118 | US Army Corps of Engineers | 6789 | St Stephen | SC | Berkeley | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 28 | 0.9 | 28 | 28 | 28 | N |  |  | OP | X | 3 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 50118 | US Army Corps of Engineers | 6789 | St Stephen | SC | Berkeley | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 28 | 0.9 | 28 | 28 | 28 | N |  |  | OP | X | 3 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 50118 | US Army Corps of Engineers | 6789 | St Stephen | SC | Berkeley | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 28 | 0.9 | 28 | 28 | 28 | N |  |  | OP | X | 3 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1968 | natural gas peaker | TRUE | 998 | City of Augusta - (KS) | 6791 | Augusta Electric Plant No 2 | KS | Butler | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 4 | 0.8 | 4 | 4 | 3.6 | N |  |  | OP | X | 10 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1968 | natural gas peaker | TRUE | 998 | City of Augusta - (KS) | 6791 | Augusta Electric Plant No 2 | KS | Butler | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 4 | 0.8 | 4 | 4 | 3.6 | N |  |  | OP | X | 7 | 1968 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1981 | natural gas peaker | TRUE | 998 | City of Augusta - (KS) | 6791 | Augusta Electric Plant No 2 | KS | Butler | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 6 | 0.8 | 6 | 6 | 5.3 | N |  |  | OP | X | 7 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage2005 | natural gas peaker | TRUE | 998 | City of Augusta - (KS) | 6791 | Augusta Electric Plant No 2 | KS | Butler | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 6.7 | 0.8 | 6.1 | 6.1 | 5 | N |  |  | OP | X | 3 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1979 | petroleum | TRUE | 17271 | City & Borough of Sitka - (AK) | 6801 | Jarvis Street | AK | Sitka | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1 | N |  |  | OP | X | 8 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 1H | [23 empty] | N | N
Vintage1979 | petroleum | TRUE | 17271 | City & Borough of Sitka - (AK) | 6801 | Jarvis Street | AK | Sitka | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.8 | 0.8 | 2.8 | 2.8 | 1 | N |  |  | OP | X | 8 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1979 | petroleum | TRUE | 17271 | City & Borough of Sitka - (AK) | 6801 | Jarvis Street | AK | Sitka | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.8 | 0.8 | 2.8 | 2.8 | 1 | N |  |  | OP | X | 8 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage2002 | petroleum | TRUE | 17271 | City & Borough of Sitka - (AK) | 6801 | Jarvis Street | AK | Sitka | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.5 | 0.8 | 4 | 4 | 2.5 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage2014 | petroleum | TRUE | 17271 | City & Borough of Sitka - (AK) | 6801 | Jarvis Street | AK | Sitka | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 13.5 | 0.8 | 13.5 | 13.5 | 10 | N |  |  | OP | X | 8 | 2014 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 1H | [23 empty] | N
Vintage1984 | hard coal | TRUE | 1692 | Big Rivers Electric Corp | 6823 | D B Wilson | KY | Ohio | 1 | Conventional Steam Coal | ST |  | S | X | X | BREC.WILSON1 | BREC.WILSON1 | 509.4 | 0.9 | 417 | 417 | 300 | N |  |  | OP | X | 9 | 1984 |  |  | N | Electric Utility | 1 | X | BIT | DFO | PC |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1978 | petroleum | TRUE | 7570 | Great River Energy | 6824 | St Bonifacius | MN | Carver | 1 | Petroleum Liquids | GT |  | S | X | X | GRE.STBONI | GRE.STBONI | 61.2 | 0.9 | 60.8 | 66 | 10 | N |  |  | OP | X | 6 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 10M | [23 empty] | N | N | N
Vintage1983 | petroleum | TRUE | 9011 | City of Hugoton - (KS) | 7011 | Hugoton 2 | KS | Stevens | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.3 | 0.8 | 4 | 4 | 2.6 | N |  |  | OP | X | 9 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1997 | petroleum | TRUE | 9011 | City of Hugoton - (KS) | 7011 | Hugoton 2 | KS | Stevens | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.2 | 2.2 | 1.5 | N |  |  | OP | X | 6 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: NG |  |  |  | N | N |  | 1H |  |  |  | N | [19 empty] | Y | Y | Y
Vintage1997 | petroleum | TRUE | 9011 | City of Hugoton - (KS) | 7011 | Hugoton 2 | KS | Stevens | 12 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.8 | 2.8 | 2.8 | 1.8 | N |  |  | OP | X | 4 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1998 | natural gas peaker | TRUE | 9011 | City of Hugoton - (KS) | 7011 | Hugoton 2 | KS | Stevens | 13 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.5 | 0.5 | 0.2 | N |  |  | OP | X | 3 | 1998 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1964 | petroleum | TRUE | 9011 | City of Hugoton - (KS) | 7011 | Hugoton 2 | KS | Stevens | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.3 | 0.8 | 2 | 2 | 1.5 | N |  |  | OP | X | 1 | 1964 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: NG |  |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1971 | petroleum | TRUE | 9011 | City of Hugoton - (KS) | 7011 | Hugoton 2 | KS | Stevens | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 0.9 | N |  |  | OP | X | 1 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: NG |  |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1994 | petroleum | TRUE | 9011 | City of Hugoton - (KS) | 7011 | Hugoton 2 | KS | Stevens | 9A | Petroleum Liquids | IC |  | S | X | X |  |  | 4.3 | 0.8 | 4 | 4 | 3.2 | N |  |  | OP | X | 8 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: NG |  |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1982 | hydro | TRUE | 9187 | City of Idaho Falls - (ID) | 7012 | Lower No 1 | ID | Bonneville | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8 | 0.9 | 8 | 8 | 8 | N |  |  | OP | X | 4 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1970 | natural gas steam turbine | TRUE | 20813 | City of Winfield - (KS) | 7013 | East 12th Street | KS | Cowley | 4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 26.5 | 0.85 | 25.8 | 28.6 | 5 | N |  |  | OP | X | 6 | 1970 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2002 | petroleum | TRUE | 20813 | City of Winfield - (KS) | 7013 | East 12th Street | KS | Cowley | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.9 | 1.6 | 1.6 | 0.5 | N |  |  | SB | Y | 6 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1993 | hydro | TRUE | 13037 | City of Mt Pleasant - (UT) | 7015 | Unit 4 | UT | Sanpete | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 0.9 | 1.3 | 0.3 | 0.2 | N |  |  | OP | X | 6 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1986 | natural gas peaker | TRUE | 3355 | City of Chanute | 7018 | Chanute 3 | KS | Neosho | 10 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 7.6 | 0.8 | 6.9 | 6.9 | 4 | N |  |  | OP | X | 8 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | N | N
Vintage1986 | natural gas peaker | TRUE | 3355 | City of Chanute | 7018 | Chanute 3 | KS | Neosho | 11 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 7.6 | 0.8 | 6.9 | 6.9 | 4 | N |  |  | OP | X | 8 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | N | N
Vintage1991 | petroleum | TRUE | 3355 | City of Chanute | 7018 | Chanute 3 | KS | Neosho | 12 | Petroleum Liquids | IC |  | S | X | X |  |  | 6 | 0.8 | 5.5 | 5.5 | 2 | N |  |  | OP | X | 11 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N |  | N
Vintage1991 | petroleum | TRUE | 3355 | City of Chanute | 7018 | Chanute 3 | KS | Neosho | 13 | Petroleum Liquids | IC |  | S | X | X |  |  | 6 | 0.8 | 5.9 | 5.9 | 2 | N |  |  | OP | X | 11 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1985 | natural gas peaker | TRUE | 3355 | City of Chanute | 7018 | Chanute 3 | KS | Neosho | 9 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 7.6 | 0.8 | 6.9 | 6.9 | 4 | N |  |  | OP | X | 10 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1986 | natural gas peaker | TRUE | 17845 | City of Springville - (UT) | 7028 | Whitehead | UT | Utah | K1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 7 | 0.8 | 5.9 | 6.3 | 5 | N |  |  | OP | X | 10 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1986 | natural gas peaker | TRUE | 17845 | City of Springville - (UT) | 7028 | Whitehead | UT | Utah | K2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 7 | 0.8 | 6 | 6.2 | 5 | N |  |  | OP | X | 8 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2000 | natural gas peaker | TRUE | 17845 | City of Springville - (UT) | 7028 | Whitehead | UT | Utah | K3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 7 | 0.8 | 5.9 | 6 | 5 | N |  |  | OP | X | 2 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2002 | natural gas peaker | TRUE | 17845 | City of Springville - (UT) | 7028 | Whitehead | UT | Utah | K4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 5 | 0.8 | 4 | 4.3 | 4 | N |  |  | OP | X | 12 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2016 | natural gas peaker | TRUE | 17845 | City of Springville - (UT) | 7028 | Whitehead | UT | Utah | K6CAT | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 12 | 2016 |  |  | Y | Electric Utility | 1 | [12 empty] | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2016 | natural gas peaker | TRUE | 17845 | City of Springville - (UT) | 7028 | Whitehead | UT | Utah | K7CAT | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 12 | 2016 |  |  | Y | Electric Utility | 1 | [12 empty] | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1990 | lignite | TRUE | 56598 | Major Oak Power, LLC | 7030 | Major Oak Power | TX | Robertson | 1 | Conventional Steam Coal | ST |  | S | X | X | TNP_TNP_O_1 | TNP_TNP_O_1 | 174.6 | 0.9 | 152 | 153 | 95 | N |  |  | OP | X | 9 | 1990 |  |  | N | IPP Non-CHP | 2 | X | LIG | NG | SUB | PC |  |  | NG |  |  |  | N | N |  | OVER | Y |  |  |  | Y | [18 empty] | Y | Y | N
Vintage1991 | lignite | TRUE | 56598 | Major Oak Power, LLC | 7030 | Major Oak Power | TX | Robertson | 2 | Conventional Steam Coal | ST |  | S | X | X | TNP_TNP_O_2 | TNP_TNP_O_2 | 174.6 | 0.9 | 153 | 154 | 95 | N |  |  | OP | X | 10 | 1991 |  |  | N | IPP Non-CHP | 2 | X | LIG | NG | SUB | PC |  |  | NG |  |  |  | N | N |  | OVER | Y |  |  |  | Y | [18 empty] | Y | Y | N
Vintage1970 | petroleum | TRUE | 19876 | Virginia Electric & Power Co | 7032 | Gravel Neck | VA | Surry | 1 | Petroleum Liquids | GT |  | S | X | X |  |  | 16.3 | 0.85 | 12 | 15 | 0 | N |  |  | OP | X | 8 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1970 | petroleum | TRUE | 19876 | Virginia Electric & Power Co | 7032 | Gravel Neck | VA | Surry | 2 | Petroleum Liquids | GT |  | S | X | X |  |  | 23.8 | 0.85 | 16 | 23 | 0 | N |  |  | OP | X | 12 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1989 | natural gas peaker | TRUE | 19876 | Virginia Electric & Power Co | 7032 | Gravel Neck | VA | Surry | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 91.9 | 0.9 | 85 | 98 | 40 | N |  |  | OP | X | 10 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1989 | natural gas peaker | TRUE | 19876 | Virginia Electric & Power Co | 7032 | Gravel Neck | VA | Surry | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 91.9 | 0.9 | 85 | 97 | 40 | N |  |  | OP | X | 7 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1989 | natural gas peaker | TRUE | 19876 | Virginia Electric & Power Co | 7032 | Gravel Neck | VA | Surry | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 91.9 | 0.9 | 85 | 98 | 40 | N |  |  | OP | X | 7 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1989 | natural gas peaker | TRUE | 19876 | Virginia Electric & Power Co | 7032 | Gravel Neck | VA | Surry | 6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 91.9 | 0.9 | 85 | 97 | 40 | N |  |  | OP | X | 11 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1986 | hydro | TRUE | 11135 | City of Logan - (UT) | 7034 | Hydro II | UT | Cache | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.3 | 0.8 | 3.1 | 1.5 | 0.6 | N |  |  | OP | X | 3 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1986 | hydro | TRUE | 11135 | City of Logan - (UT) | 7034 | Hydro II | UT | Cache | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.3 | 0.8 | 3.1 | 1.5 | 0.6 | N |  |  | OP | X | 5 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1967 | petroleum | TRUE | 56815 | NorthWestern Energy (MT wind/thermal) | 7039 | Lake (WY) | WY | Teton | 1 | Petroleum Liquids | IC |  | S | X | X | NA | NA | 2.7 | 0.8 | 2.7 | 2.7 | 2.3 | N |  |  | SB | N | 9 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1988 | hydro | TRUE | 807 | Arkansas Electric Coop Corp | 7040 | Ellis Hydro | AR | Crawford | 1 | Conventional Hydroelectric | HY |  | S | X | X | AECC_HYDRO13 | SWPP | 10.8 | 0.95 | 5 | 5 | 1 | N |  |  | OP | X | 12 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1988 | hydro | TRUE | 807 | Arkansas Electric Coop Corp | 7040 | Ellis Hydro | AR | Crawford | 2 | Conventional Hydroelectric | HY |  | S | X | X | AECC_HYDRO13 | SWPP | 10.8 | 0.95 | 6 | 6 | 1 | N |  |  | OP | X | 12 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1988 | hydro | TRUE | 807 | Arkansas Electric Coop Corp | 7040 | Ellis Hydro | AR | Crawford | 3 | Conventional Hydroelectric | HY |  | S | X | X | AECC_HYDRO13 | SWPP | 10.8 | 0.95 | 6 | 6 | 1 | N |  |  | OP | X | 12 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1991 | hydro | TRUE | 40215 | Cordova Electric Coop, Inc | 7042 | Humpback Creek | AK | Valdez Cordova | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 6 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1991 | hydro | TRUE | 40215 | Cordova Electric Coop, Inc | 7042 | Humpback Creek | AK | Valdez Cordova | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 6 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1991 | hydro | TRUE | 40215 | Cordova Electric Coop, Inc | 7042 | Humpback Creek | AK | Valdez Cordova | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 6 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1985 | hydro | TRUE | 20151 | Washington Electric Coop - (VT) | 7051 | Wrightsville Hydro Plant | VT | Washington | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 9 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 20151 | Washington Electric Coop - (VT) | 7051 | Wrightsville Hydro Plant | VT | Washington | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.9 | 0.2 | 0.2 | 0.2 | N |  |  | OP | X | 9 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 20151 | Washington Electric Coop - (VT) | 7051 | Wrightsville Hydro Plant | VT | Washington | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.9 | 0.4 | 0.4 | 0.4 | N |  |  | OP | X | 9 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1986 | hydro | TRUE | 7601 | Green Mountain Power Corp | 7056 | Bolton Falls | VT | Washington | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.4 | 0.8 | 3.9 | 3.9 | 0.9 | N |  |  | OP | X | 11 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  | 0 | 1H
Vintage1986 | hydro | TRUE | 7601 | Green Mountain Power Corp | 7056 | Bolton Falls | VT | Washington | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.4 | 0.8 | 3.9 | 3.9 | 0.9 | N |  |  | OP | X | 11 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  | 0 | 1H
Vintage1988 | petroleum | TRUE | 4715 | Dahlberg Light & Power Co | 7058 | Solon Diesel | WI | Douglas | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 0.8 | 0.8 | 0.8 | N |  |  | SB | Y | 1 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1988 | petroleum | TRUE | 4715 | Dahlberg Light & Power Co | 7058 | Solon Diesel | WI | Douglas | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 0.8 | 0.8 | 0.8 | N |  |  | SB | Y | 2 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1989 | petroleum | TRUE | 4715 | Dahlberg Light & Power Co | 7058 | Solon Diesel | WI | Douglas | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 0.8 | 0.8 | 0.8 | N |  |  | SB | Y | 4 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1989 | petroleum | TRUE | 4715 | Dahlberg Light & Power Co | 7058 | Solon Diesel | WI | Douglas | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 0.8 | 0.8 | 0.8 | N |  |  | SB | Y | 4 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1989 | petroleum | TRUE | 4715 | Dahlberg Light & Power Co | 7058 | Solon Diesel | WI | Douglas | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 0.8 | 0.8 | 0.8 | N |  |  | SB | Y | 4 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1995 | petroleum | TRUE | 4715 | Dahlberg Light & Power Co | 7058 | Solon Diesel | WI | Douglas | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 0.8 | 0.8 | 0.8 | N |  |  | SB | Y | 12 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1995 | petroleum | TRUE | 4715 | Dahlberg Light & Power Co | 7058 | Solon Diesel | WI | Douglas | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 0.8 | 0.8 | 0.8 | N |  |  | SB | Y | 12 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1995 | petroleum | TRUE | 4715 | Dahlberg Light & Power Co | 7058 | Solon Diesel | WI | Douglas | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 0.8 | 0.8 | 0.8 | N |  |  | SB | Y | 12 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1987 | petroleum | TRUE | 17141 | City of Sibley - (IA) | 7060 | Sibley No Two | IA | Osceola | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 1 | 1 | 1.1 | 1 | N |  |  | OP | X | 12 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: NG |  |  |  | N | N |  | 10M | [23 empty] | Y | N | N
Vintage1991 | other | TRUE | 189 | PowerSouth Energy Cooperative | 7063 | McIntosh (AL) | AL | Washington | 1 | Natural Gas with Compressed Air Storage | CE |  | S | X | X |  |  | 110 | 0.85 | 110 | 110 | 30 | N |  |  | OP | X | 6 | 1991 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage1998 | natural gas peaker | TRUE | 189 | PowerSouth Energy Cooperative | 7063 | McIntosh (AL) | AL | Washington | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 113 | 0.85 | 114 | 120 | 65 | N |  |  | OP | X | 6 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1998 | natural gas peaker | TRUE | 189 | PowerSouth Energy Cooperative | 7063 | McIntosh (AL) | AL | Washington | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 113 | 0.85 | 114 | 120 | 65 | N |  |  | OP | X | 6 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2010 | natural gas peaker | TRUE | 189 | PowerSouth Energy Cooperative | 7063 | McIntosh (AL) | AL | Washington | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 170 | 0.85 | 175 | 224 | 111 | N |  |  | OP | X | 12 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2010 | natural gas peaker | TRUE | 189 | PowerSouth Energy Cooperative | 7063 | McIntosh (AL) | AL | Washington | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 170 | 0.85 | 175 | 224 | 111 | N |  |  | OP | X | 12 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage1988 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 7066 | Stampede | CA | Sierra | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.9 | 3 | 3 | 0 | N |  |  | OP | X | 1 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1988 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 7066 | Stampede | CA | Sierra | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 1 | 0.6 | 0.6 | 0 | N |  |  | OP | X | 1 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1996 | hydro | TRUE | 3255 | California Dept. of Water Resources | 7072 | Mojave Siphon | CA | San Bernardino | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10.9 | 0.95 | 10.8 | 10.8 | 2 | N |  |  | OP | X | 8 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage1996 | hydro | TRUE | 3255 | California Dept. of Water Resources | 7072 | Mojave Siphon | CA | San Bernardino | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10.9 | 0.95 | 10.8 | 10.8 | 2 | N |  |  | OP | X | 8 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage1996 | hydro | TRUE | 3255 | California Dept. of Water Resources | 7072 | Mojave Siphon | CA | San Bernardino | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10.9 | 0.95 | 10.8 | 10.8 | 2 | N |  |  | OP | X | 8 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage1947 | hydro | TRUE | 9191 | Idaho Power Co | 7079 | Upper Salmon B | ID | Twin Falls | 1 | Conventional Hydroelectric | HY |  | S | X | X | US34_1_TOT_B_GEN-APND | US34_1_TOT_B_GEN | 8.2 | 0.92 | 8.8 | 7.9 | 0 | N |  |  | OP | X | 9 | 1947 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | Y | 7 | 2028 | N
Vintage1947 | hydro | TRUE | 9191 | Idaho Power Co | 7079 | Upper Salmon B | ID | Twin Falls | 2 | Conventional Hydroelectric | HY |  | S | X | X | US34_1_TOT_B_GEN-APND | US34_1_TOT_B_GEN | 8.3 | 0.92 | 8.8 | 8.3 | 0 | N |  |  | OP | X | 9 | 1947 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1987 | petroleum | TRUE | 17874 | City of St George | 7080 | St George Red Rock | UT | Washington | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 7 | 0.9 | 7 | 7 | 1 | N |  |  | SB | Y | 5 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 10M | [23 empty] | N | N
Vintage1987 | petroleum | TRUE | 17874 | City of St George | 7080 | St George Red Rock | UT | Washington | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 7 | 0.9 | 7 | 7 | 1 | N |  |  | SB | Y | 5 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 10M | [23 empty] | N | N
Vintage2011 | natural gas combined cycle | TRUE | 13407 | Nevada Power Co | 7082 | Harry Allen | NV | Clark | 5 | Natural Gas Fired Combined Cycle | CT | PB1 | S | X | N |  |  | 167.5 | 0.85 | 151.6 | 164 | 90 | N |  |  | OP | X | 5 | 2011 |  |  | N | Electric Utility | 1 | [14 empty] | 12H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2011 | natural gas combined cycle | TRUE | 13407 | Nevada Power Co | 7082 | Harry Allen | NV | Clark | 6 | Natural Gas Fired Combined Cycle | CT | PB1 | S | X | N |  |  | 167.5 | 0.85 | 151.6 | 164 | 90 | N |  |  | OP | X | 5 | 2011 |  |  | N | Electric Utility | 1 | [14 empty] | 12H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2011 | natural gas combined cycle | TRUE | 13407 | Nevada Power Co | 7082 | Harry Allen | NV | Clark | 7 | Natural Gas Fired Combined Cycle | CA | PB1 | S | Y | X |  |  | 223.5 | 0.85 | 206.8 | 196 | 45 | N |  |  | OP | X | 5 | 2011 |  |  | N | Electric Utility | 1 | [14 empty] | 12H | [23 empty] | N | bar: X X X to RC RC RC
Vintage1995 | natural gas peaker | TRUE | 13407 | Nevada Power Co | 7082 | Harry Allen | NV | Clark | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 101.5 | 0.9 | 72 | 76 | 30 | N |  |  | OP | X | 5 | 1995 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2006 | natural gas peaker | TRUE | 13407 | Nevada Power Co | 7082 | Harry Allen | NV | Clark | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 85 | 0.85 | 72 | 76 | 30 | N |  |  | OP | X | 4 | 2006 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage1992 | hard coal | TRUE | 16604 | City of San Antonio - (TX) | 7097 | J K Spruce | TX | Bexar | 1 | Conventional Steam Coal | ST |  | S | X | X | CALAVER_JKS1 | CALAVER_JKS1 | 566 | 0.9 | 560 | 560 | 122 | N |  |  | OP | X | 12 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; DFO DFO DFO: NG |  |  |  | N | N | 0 | OVER |  | Y |  |  | Y | [15 empty] | N |  |  | N | N | N
Vintage2010 | hard coal | TRUE | 16604 | City of San Antonio - (TX) | 7097 | J K Spruce | TX | Bexar | 2 | Conventional Steam Coal | ST |  | S | X | X | CALAVER_JKS2 | CALAVER_JKS2 | 922.5 | 0.9 | 785 | 785 | 290 | N |  |  | OP | X | 5 | 2010 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; DFO DFO DFO: NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | N |  |  | N | N | N
Vintage2004 | natural gas peaker | TRUE | 8366 | Heber Light & Power Company | 7111 | Heber City | UT | Wasatch | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.4 | 1 | 1.4 | 1.4 | 1.4 | N |  |  | OP | X | 3 | 2004 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2015 | natural gas peaker | TRUE | 8366 | Heber Light & Power Company | 7111 | Heber City | UT | Wasatch | 11 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.9 | 1 | 1.9 | 1.9 | 1.9 | N |  |  | OP | X | 3 | 2015 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2015 | natural gas peaker | TRUE | 8366 | Heber Light & Power Company | 7111 | Heber City | UT | Wasatch | 12 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.3 | 1 | 2.3 | 2.3 | 2.3 | N |  |  | OP | X | 3 | 2015 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2004 | natural gas peaker | TRUE | 8366 | Heber Light & Power Company | 7111 | Heber City | UT | Wasatch | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.4 | 1 | 1.4 | 1.4 | 1.4 | N |  |  | OP | X | 3 | 2004 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2003 | natural gas peaker | TRUE | 8366 | Heber Light & Power Company | 7111 | Heber City | UT | Wasatch | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.9 | 1 | 1.9 | 1.9 | 1.9 | N |  |  | OP | X | 7 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2002 | natural gas peaker | TRUE | 8366 | Heber Light & Power Company | 7111 | Heber City | UT | Wasatch | NA10 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.9 | 1 | 1.9 | 1.9 | 1.9 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | [12 empty] | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 8366 | Heber Light & Power Company | 7111 | Heber City | UT | Wasatch | NA6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.7 | 1 | 0.7 | 0.7 | 0.7 | N |  |  | OP | X | 7 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2003 | natural gas peaker | TRUE | 8366 | Heber Light & Power Company | 7111 | Heber City | UT | Wasatch | NA9 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.9 | 1 | 1.9 | 1.9 | 1.9 | N |  |  | OP | X | 5 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1987 | petroleum | TRUE | 12385 | Metlakatla Power & Light | 7112 | Centennial | AK | Prince of Wales Ketchikan | IC6 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.3 | 0.8 | 3.3 | 3.3 | 0.2 | N |  |  | OP | X | 4 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1990 | hydro | TRUE | 14624 | PUD No 2 of Grant County | 7113 | PEC Headworks | WA | Grant | 1 | Conventional Hydroelectric | HY |  | J | X | X |  |  | 6.6 | 0.95 | 6.6 | 6.6 | 3 | N |  |  | OP | X | 9 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1988 | hydro | TRUE | 19578 | Upper Peninsula Power Company | 7115 | Hoist | MI | Marquette | 2 | Conventional Hydroelectric | HY |  | S | X | X | UPPC.INTEGRATD | UPPC.INTEGRATD | 1.4 | 0.8 | 0.8 | 0.5 | 0 | N |  |  | OP | X | 2 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1988 | hydro | TRUE | 19578 | Upper Peninsula Power Company | 7115 | Hoist | MI | Marquette | 3 | Conventional Hydroelectric | HY |  | S | X | X | UPPC.INTEGRATD | UPPC.INTEGRATD | 2 | 0.8 | 1.2 | 0.8 | 0 | N |  |  | OP | X | 2 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1988 | hydro | TRUE | 19578 | Upper Peninsula Power Company | 7116 | McClure Dam | MI | Marquette | 1 | Conventional Hydroelectric | HY |  | S | X | X | UPPC.INTEGRATD | UPPC.INTEGRATD | 4 | 0.8 | 2.9 | 2.3 | 0 | N |  |  | OP | X | 2 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1988 | hydro | TRUE | 19578 | Upper Peninsula Power Company | 7116 | McClure Dam | MI | Marquette | 2 | Conventional Hydroelectric | HY |  | S | X | X | UPPC.INTEGRATD | UPPC.INTEGRATD | 4 | 0.8 | 2.9 | 2.3 | 0 | N |  |  | OP | X | 2 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1988 | hydro | TRUE | 58149 | Renewable World Energies LLC | 7118 | Cataract (MI) | MI | Marquette | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.8 | 0.6 | 0.3 | 0 | N |  |  | OP | X | 2 | 1988 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage1975 | petroleum | TRUE | 19578 | Upper Peninsula Power Company | 7119 | Gladstone | MI | Delta | 1 | Petroleum Liquids | GT |  | S | X | X | UPPC.GLADSTONE | UPPC.GLADSTONE | 22.6 | 0.9 | 17 | 22.2 | 5 | N |  |  | OP | X | 11 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1991 | other | TRUE | 5416 | Duke Energy Carolinas, LLC | 7125 | Bad Creek | SC | Oconee | 1 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 420 | 0.9 | 420 | 420 | 320 | N |  |  | OP | X | 5 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [7 empty] | 65 | 65 | 6 | 2023
Vintage1991 | other | TRUE | 5416 | Duke Energy Carolinas, LLC | 7125 | Bad Creek | SC | Oconee | 2 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 420 | 0.9 | 420 | 420 | 320 | N |  |  | OP | X | 5 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1991 | other | TRUE | 5416 | Duke Energy Carolinas, LLC | 7125 | Bad Creek | SC | Oconee | 3 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 324 | 0.9 | 340 | 340 | 250 | N |  |  | OP | X | 9 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [7 empty] | 65 | 65 | 9 | 2022
Vintage1991 | other | TRUE | 5416 | Duke Energy Carolinas, LLC | 7125 | Bad Creek | SC | Oconee | 4 | Hydroelectric Pumped Storage | PS |  | S | X | X |  |  | 324 | 0.9 | 340 | 340 | 250 | N |  |  | OP | X | 9 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [7 empty] | 65 | 65 | 6 | 2022
Vintage1994 | hydro | TRUE | 18429 | City of Tacoma - (WA) | 7127 | Wynoochee | WA | Grays Harbor | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 12.8 | 1 | 15.5 | 12.8 | 1 | N |  |  | OP | X | 1 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H
Vintage1988 | hydro | TRUE | 332 | Allegheny Electric Coop Inc | 7128 | William F Matson Generating Station | PA | Huntingdon | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7 | 0.9 | 2.4 | 7 | 2.4 | N |  |  | OP | X | 6 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1988 | hydro | TRUE | 332 | Allegheny Electric Coop Inc | 7128 | William F Matson Generating Station | PA | Huntingdon | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 14.7 | 0.9 | 6 | 14.7 | 6 | N |  |  | OP | X | 6 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1987 | hydro | TRUE | 3255 | California Dept. of Water Resources | 7129 | Thermalito Diverson Dam | CA | Butte | TD1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.4 | 0.9 | 3 | 3 | 0 | N |  |  | OP | X | 7 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage1988 | petroleum | TRUE | 8287 | Hawaii Electric Light Co Inc | 7130 | Puna | HI | Hawaii | 1 | Petroleum Liquids | ST |  | S | X | X |  |  | 15.5 | 0.9 | 14 | 14 | 6 | N |  |  | OP | X | 8 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: RFO; SUB SUB SUB: DFO; DFO DFO DFO: DFO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1992 | petroleum | TRUE | 8287 | Hawaii Electric Light Co Inc | 7130 | Puna | HI | Hawaii | 3 | Petroleum Liquids | GT |  | S | X | X |  |  | 23.6 | 0.9 | 20 | 20 | 7 | N |  |  | OP | X | 8 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1990 | natural gas peaker | TRUE | 11292 | City of Lubbock - (TX) | 7131 | Brandon Station | TX | Lubbock | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 21 | 0.9 | 20 | 21.5 | 20 | N |  |  | OP | X | 7 | 1990 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1991 | hydro | TRUE | 2010 | City of Bountiful | 7132 | Pine View Dam | UT | Weber | NA1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 0.9 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 6 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1993 | hydro | TRUE | 807 | Arkansas Electric Coop Corp | 7135 | Whillock | AR | Conway | 1 | Conventional Hydroelectric | HY |  | S | X | X | EAI.AECCHYDRO9 | EIA | 10.8 | 0.95 | 6 | 6 | 1 | N |  |  | OP | X | 10 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1993 | hydro | TRUE | 807 | Arkansas Electric Coop Corp | 7135 | Whillock | AR | Conway | 2 | Conventional Hydroelectric | HY |  | S | X | X | EAI.AECCHYDRO9 | EIA | 10.8 | 0.95 | 6 | 6 | 1 | N |  |  | OP | X | 10 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1993 | hydro | TRUE | 807 | Arkansas Electric Coop Corp | 7135 | Whillock | AR | Conway | 3 | Conventional Hydroelectric | HY |  | S | X | X | EAI.AECCHYDRO9 | EIA | 10.8 | 0.95 | 5 | 5 | 1 | N |  |  | OP | X | 10 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1989 | natural gas peaker | TRUE | 61358 | Forked River Power, LLC | 7138 | Forked River | NJ | Ocean | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | OYSTERCR14KV FR1 | OYSTERCR14KV FR1 | 38.4 | 0.85 | 34 | 44 | 34 | N |  |  | OP | X | 6 | 1989 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1989 | natural gas peaker | TRUE | 61358 | Forked River Power, LLC | 7138 | Forked River | NJ | Ocean | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | OYSTERCR14KV FR2 | OYSTERCR14KV FR2 | 38.4 | 0.85 | 31 | 41 | 31 | N |  |  | OP | X | 7 | 1989 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1990 | natural gas peaker | TRUE | 12341 | MidAmerican Energy Co | 7145 | Pleasant Hill | IA | Polk | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MEC.PHEC1 | MEC.PHEC1 | 41.4 | 0.9 | 37.3 | 47 | 6 | N |  |  | OP | X | 6 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1990 | natural gas peaker | TRUE | 12341 | MidAmerican Energy Co | 7145 | Pleasant Hill | IA | Polk | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MEC.PHEC2 | MEC.PHEC2 | 41.4 | 0.9 | 38.3 | 47 | 6 | N |  |  | OP | X | 6 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1994 | natural gas peaker | TRUE | 12341 | MidAmerican Energy Co | 7145 | Pleasant Hill | IA | Polk | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MEC.PHEC3 | MEC.PHEC3 | 97 | 0.9 | 81 | 100 | 6 | N |  |  | OP | X | 6 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1989 | petroleum | TRUE | 56505 | National Grid Generation LLC | 7146 | Wading River | NY | Suffolk | 02 | Petroleum Liquids | GT |  | S | X | X | 23547 | 23547 | 79.5 | 0.8 | 76.9 | 96.2 | 66.4 | N |  |  | OP | X | 8 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1989 | petroleum | TRUE | 56505 | National Grid Generation LLC | 7146 | Wading River | NY | Suffolk | 03 | Petroleum Liquids | GT |  | S | X | X | 23601 | 23601 | 79.5 | 0.8 | 81.7 | 99 | 65.9 | N |  |  | OP | X | 8 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 1H | [23 empty] | N | N
Vintage1989 | petroleum | TRUE | 56505 | National Grid Generation LLC | 7146 | Wading River | NY | Suffolk | 1 | Petroleum Liquids | GT |  | S | X | X | 23522 | 23522 | 79.5 | 0.8 | 82 | 101.3 | 68.1 | N |  |  | OP | X | 8 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1903 | hydro | TRUE | 17609 | Southern California Edison Co | 7147 | Mill Creek 3 | CA | San Bernardino | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 1 | 1 | 1 | 0 | N |  |  | OP | X | 3 | 1903 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage1904 | hydro | TRUE | 17609 | Southern California Edison Co | 7147 | Mill Creek 3 | CA | San Bernardino | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 1 | 1 | 1 | 0 | N |  |  | OP | X | 10 | 1904 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage1904 | hydro | TRUE | 17609 | Southern California Edison Co | 7147 | Mill Creek 3 | CA | San Bernardino | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 1 | 1 | 1 | 0 | N |  |  | OP | X | 3 | 1904 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage1986 | hydro | TRUE | 16655 | City of Santa Clara - (CA) | 7151 | Stony Gorge | CA | Glenn | 1 | Conventional Hydroelectric | HY |  | S | X | X | POD_ELKCRK_6_STONYG-APNDPOD_ELKCRK_6_STONYG-APND | POD_ELKCRK_6_STONYG-APND | 2.5 | 0.9 | 2.5 | 2.5 | 0.3 | N |  |  | OP | X | 4 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1986 | hydro | TRUE | 16655 | City of Santa Clara - (CA) | 7151 | Stony Gorge | CA | Glenn | 2 | Conventional Hydroelectric | HY |  | S | X | X | POD_ELKCRK_6_STONYG-APND | POD_ELKCRK_6_STONYG-APND | 2.5 | 0.9 | 2.5 | 2.5 | 0.3 | N |  |  | OP | X | 4 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1989 | natural gas combined cycle | TRUE | 56609 | Calpine Mid-Atlantic Generation LLC | 7153 | Hay Road | DE | New Castle | HR1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y | 50889 | 50889 | 122 | 0.9 | 126 | 126 | 80 | N |  |  | OP | X | 7 | 1989 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1989 | natural gas combined cycle | TRUE | 56609 | Calpine Mid-Atlantic Generation LLC | 7153 | Hay Road | DE | New Castle | HR2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y | 50891 | 50891 | 122 | 0.9 | 126 | 126 | 80 | N |  |  | OP | X | 5 | 1989 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1991 | natural gas combined cycle | TRUE | 56609 | Calpine Mid-Atlantic Generation LLC | 7153 | Hay Road | DE | New Castle | HR3 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y | 50890 | 50890 | 122 | 0.9 | 126 | 126 | 80 | N |  |  | OP | X | 5 | 1991 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1993 | natural gas combined cycle | TRUE | 56609 | Calpine Mid-Atlantic Generation LLC | 7153 | Hay Road | DE | New Castle | HR4 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X | 50892 | 50892 | 200 | 0.9 | 187 | 187 | 45 | N |  |  | OP | X | 5 | 1993 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage2001 | natural gas combined cycle | TRUE | 56609 | Calpine Mid-Atlantic Generation LLC | 7153 | Hay Road | DE | New Castle | HR5 | Natural Gas Fired Combined Cycle | CT | CC2 | S | X | Y | 1048074 | 1048074 | 144 | 0.85 | 128 | 128 | 80 | N |  |  | OP | X | 6 | 2001 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2001 | natural gas combined cycle | TRUE | 56609 | Calpine Mid-Atlantic Generation LLC | 7153 | Hay Road | DE | New Castle | HR6 | Natural Gas Fired Combined Cycle | CT | CC2 | S | X | Y | 1048073 | 1048073 | 144 | 0.85 | 128 | 128 | 80 | N |  |  | OP | X | 7 | 2001 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2001 | natural gas combined cycle | TRUE | 56609 | Calpine Mid-Atlantic Generation LLC | 7153 | Hay Road | DE | New Castle | HR7 | Natural Gas Fired Combined Cycle | CT | CC2 | S | X | Y | 1048072 | 1048072 | 144 | 0.85 | 128 | 128 | 80 | N |  |  | OP | X | 7 | 2001 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2002 | natural gas combined cycle | TRUE | 56609 | Calpine Mid-Atlantic Generation LLC | 7153 | Hay Road | DE | New Castle | HR8 | Natural Gas Fired Combined Cycle | CA | CC2 | S | N | X | 1048075 | 1048075 | 195 | 0.85 | 187 | 187 | 45 | N |  |  | OP | X | 7 | 2002 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1991 | petroleum | TRUE | 9417 | Interstate Power and Light Co | 7155 | Lime Creek | IA | Cerro Gordo | 1 | Petroleum Liquids | GT |  | S | X | X | ALTW.LIMEC1 | ALTW.LIMEC1 | 45.1 | 0.85 | 37.8 | 45.8 | 13 | N |  |  | OP | X | 5 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1991 | petroleum | TRUE | 9417 | Interstate Power and Light Co | 7155 | Lime Creek | IA | Cerro Gordo | 2 | Petroleum Liquids | GT |  | S | X | X | ALTW.LIMEC2 | ALTW.LIMEC2 | 45.1 | 0.85 | 37.8 | 45.8 | 13 | N |  |  | OP | X | 5 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1993 | natural gas peaker | TRUE | 55729 | Duke Energy Kentucky Inc | 7158 | Woodsdale | OH | Butler | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 95.3 | 0.8 | 78 | 94 | 4 | N |  |  | OP | X | 5 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1992 | natural gas peaker | TRUE | 55729 | Duke Energy Kentucky Inc | 7158 | Woodsdale | OH | Butler | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 95.3 | 0.8 | 80 | 94 | 4 | N |  |  | OP | X | 7 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1992 | natural gas peaker | TRUE | 55729 | Duke Energy Kentucky Inc | 7158 | Woodsdale | OH | Butler | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 95.3 | 0.8 | 80 | 94 | 4 | N |  |  | OP | X | 5 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1992 | natural gas peaker | TRUE | 55729 | Duke Energy Kentucky Inc | 7158 | Woodsdale | OH | Butler | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 95.3 | 0.8 | 78 | 94 | 4 | N |  |  | OP | X | 7 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1992 | natural gas peaker | TRUE | 55729 | Duke Energy Kentucky Inc | 7158 | Woodsdale | OH | Butler | GT5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 95.3 | 0.8 | 80 | 94 | 4 | N |  |  | OP | X | 5 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1992 | natural gas peaker | TRUE | 55729 | Duke Energy Kentucky Inc | 7158 | Woodsdale | OH | Butler | GT6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 95.3 | 0.8 | 80 | 94 | 4 | N |  |  | OP | X | 5 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1993 | natural gas peaker | TRUE | 20847 | Wisconsin Electric Power Co | 7159 | Concord | WI | Jefferson | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | WEC.CCDGTC1 | WEC.CCDGTC1 | 95.4 | 0.8 | 91.3 | 100 | 50 | N |  |  | OP | X | 7 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1993 | natural gas peaker | TRUE | 20847 | Wisconsin Electric Power Co | 7159 | Concord | WI | Jefferson | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | WEC.CCDGTC2 | WEC.CCDGTC2 | 95.4 | 0.8 | 90.8 | 100 | 50 | N |  |  | OP | X | 7 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1994 | natural gas peaker | TRUE | 20847 | Wisconsin Electric Power Co | 7159 | Concord | WI | Jefferson | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | WEC.CCDGTC3 | WEC.CCDGTC3 | 95.4 | 0.8 | 90.1 | 100 | 50 | N |  |  | OP | X | 5 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1994 | natural gas peaker | TRUE | 20847 | Wisconsin Electric Power Co | 7159 | Concord | WI | Jefferson | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | WEC.CCDGTC4 | WEC.CCDGTC4 | 95.4 | 0.8 | 92.2 | 100 | 50 | N |  |  | OP | X | 5 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1993 | other | TRUE | 2850 | Central Arizona Water Conservation Dist | 7164 | Waddell | AZ | Maricopa | PG3 | Hydroelectric Pumped Storage | PS |  | W | X | X | n/a | n/a | 10 | 1 | 10 | 10 | 10 | N |  |  | OP | X | 4 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1993 | other | TRUE | 2850 | Central Arizona Water Conservation Dist | 7164 | Waddell | AZ | Maricopa | PG6 | Hydroelectric Pumped Storage | PS |  | W | X | X | n/a | n/a | 10 | 1 | 10 | 10 | 10 | N |  |  | OP | X | 8 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1993 | other | TRUE | 2850 | Central Arizona Water Conservation Dist | 7164 | Waddell | AZ | Maricopa | PG7 | Hydroelectric Pumped Storage | PS |  | W | X | X | n/a | n/a | 10 | 1 | 10 | 10 | 10 | N |  |  | OP | X | 6 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1993 | other | TRUE | 2850 | Central Arizona Water Conservation Dist | 7164 | Waddell | AZ | Maricopa | PS1 | Hydroelectric Pumped Storage | PS |  | W | X | X | n/a | n/a | 10 | 1 | 10 | 10 | 10 | N |  |  | OP | X | 10 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1988 | hydro | TRUE | 13718 | City of North Little Rock - (AR) | 7166 | Murray | AR | Pulaski | 1 | Conventional Hydroelectric | HY |  | S | X | X | EAI.NLRLD | EAI.NLRLD | 22.7 | 0.9 | 21.2 | 21.2 | 4 | N |  |  | OP | X | 10 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1988 | hydro | TRUE | 13718 | City of North Little Rock - (AR) | 7166 | Murray | AR | Pulaski | 2 | Conventional Hydroelectric | HY |  | S | X | X | EAI.NLRLD | EAI.NLRLD | 22.7 | 0.9 | 21.2 | 21.2 | 4 | N |  |  | OP | X | 10 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1988 | hydro | TRUE | 12385 | Metlakatla Power & Light | 7168 | Chester Lake | AK | Prince of Wales Ketchikan | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 0.9 | 1.2 | 1.2 | 0.2 | N |  |  | OP | X | 1 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1997 | petroleum | TRUE | 219 | Alaska Power and Telephone Co | 7169 | Northway | AK | Southeast Fairbanks | 1A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 12 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1997 | petroleum | TRUE | 219 | Alaska Power and Telephone Co | 7169 | Northway | AK | Southeast Fairbanks | 2A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 12 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2007 | petroleum | TRUE | 219 | Alaska Power and Telephone Co | 7169 | Northway | AK | Southeast Fairbanks | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 9 | 2007 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1994 | natural gas peaker | TRUE | 1276 | Barrow Utils & Elec Coop, Inc | 7173 | Barrow | AK | North Slope | 10 | Natural Gas Internal Combustion Engine | IC |  | W | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.5 | N |  |  | OS | X | 11 | 1994 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1996 | natural gas peaker | TRUE | 1276 | Barrow Utils & Elec Coop, Inc | 7173 | Barrow | AK | North Slope | 11 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 4.8 | 0.8 | 4.8 | 5 | 0.5 | N |  |  | OP | X | 11 | 1996 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 1276 | Barrow Utils & Elec Coop, Inc | 7173 | Barrow | AK | North Slope | 12 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 5 | 0.8 | 5 | 5.3 | 0.5 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1977 | natural gas peaker | TRUE | 1276 | Barrow Utils & Elec Coop, Inc | 7173 | Barrow | AK | North Slope | 6 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 2.5 | 0.8 | 2.5 | 3 | 0.5 | N |  |  | OP | X | 2 | 1977 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1980 | natural gas peaker | TRUE | 1276 | Barrow Utils & Elec Coop, Inc | 7173 | Barrow | AK | North Slope | 7 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 2.5 | 0.8 | 2.5 | 3 | 0.5 | N |  |  | OP | X | 12 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1982 | natural gas peaker | TRUE | 1276 | Barrow Utils & Elec Coop, Inc | 7173 | Barrow | AK | North Slope | 8 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 2.5 | 0.8 | 2.5 | 3 | 0.5 | N |  |  | OP | X | 10 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1994 | natural gas peaker | TRUE | 1276 | Barrow Utils & Elec Coop, Inc | 7173 | Barrow | AK | North Slope | 9 | Natural Gas Internal Combustion Engine | IC |  | W | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.5 | N |  |  | OS | X | 11 | 1994 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2016 | petroleum | TRUE | 7833 | Gwitchyaa Zhee Utility Co | 7174 | Gwitchyaa Zhee | AK | Yukon Koyukuk | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.98 | 0.2 | 0.3 | 0.2 | N |  |  | OP | X | 12 | 2016 |  |  | Y | Electric Utility | 1 | X X X: T; RC RC RC: DFO |  |  |  |  | N |  | 10M | [23 empty] | N | N
Vintage2015 | petroleum | TRUE | 7833 | Gwitchyaa Zhee Utility Co | 7174 | Gwitchyaa Zhee | AK | Yukon Koyukuk | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.98 | 0.4 | 0.6 | 0.2 | N |  |  | OP | X | 10 | 2015 |  |  | Y | Electric Utility | 1 | X X X: T; RC RC RC: DFO |  |  |  |  | N |  | 10M | [23 empty] | N
Vintage2016 | petroleum | TRUE | 7833 | Gwitchyaa Zhee Utility Co | 7174 | Gwitchyaa Zhee | AK | Yukon Koyukuk | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.98 | 0.4 | 0.6 | 0.2 | N |  |  | OP | X | 8 | 2016 |  |  | Y | Electric Utility | 1 | X X X: T; RC RC RC: DFO |  |  |  |  | N |  | 10M | [23 empty] | N
Vintage2016 | petroleum | TRUE | 7833 | Gwitchyaa Zhee Utility Co | 7174 | Gwitchyaa Zhee | AK | Yukon Koyukuk | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.98 | 0.2 | 0.3 | 0.2 | N |  |  | OP | X | 12 | 2016 |  |  | Y | Electric Utility | 1 | X X X: T; RC RC RC: DFO |  |  |  |  | N |  | 10M | [23 empty] | N
Vintage1993 | hydro | TRUE | 3990 | Colorado River Indian Irr Proj | 7179 | Headgate Rock | AZ | La Paz | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.5 | 0.9 | 6.5 | 6.5 | 1 | N |  |  | OP | X | 3 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [20 empty] | Y | 1 | 2025 | N
Vintage1993 | hydro | TRUE | 3990 | Colorado River Indian Irr Proj | 7179 | Headgate Rock | AZ | La Paz | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.5 | 0.9 | 6.5 | 6.5 | 1 | N |  |  | OP | X | 8 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [20 empty] | Y | 1 | 2025 | N
Vintage1993 | hydro | TRUE | 3990 | Colorado River Indian Irr Proj | 7179 | Headgate Rock | AZ | La Paz | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.5 | 0.9 | 6.5 | 6.5 | 1 | N |  |  | OP | X | 7 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [20 empty] | Y | 1 | 2025 | N
Vintage1988 | petroleum | TRUE | 4959 | Aniak Light & Power Co Inc | 7182 | Aniak | AK | Bethel | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.2 | 0.3 | 0.1 | N |  |  | OP | X | 7 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2016 | petroleum | TRUE | 4959 | Aniak Light & Power Co Inc | 7182 | Aniak | AK | Bethel | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.9 | 0.6 | 0.6 | 0.3 | N |  |  | OP | X | 7 | 2016 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2018 | petroleum | TRUE | 4959 | Aniak Light & Power Co Inc | 7182 | Aniak | AK | Bethel | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 9 | 2018 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1996 | petroleum | TRUE | 4959 | Aniak Light & Power Co Inc | 7182 | Aniak | AK | Bethel | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 12 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage2012 | petroleum | TRUE | 9188 | I-N-N Electric Coop, Inc | 7183 | Newhalen | AK | Lake and Peninsula | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0 | N |  |  | OP | X | 9 | 2012 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2012 | petroleum | TRUE | 9188 | I-N-N Electric Coop, Inc | 7183 | Newhalen | AK | Lake and Peninsula | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0 | N |  |  | OP | X | 9 | 2012 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2012 | petroleum | TRUE | 9188 | I-N-N Electric Coop, Inc | 7183 | Newhalen | AK | Lake and Peninsula | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0 | N |  |  | OP | X | 9 | 2012 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1998 | hydro | TRUE | 9188 | I-N-N Electric Coop, Inc | 7183 | Newhalen | AK | Lake and Peninsula | H-1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0 | N |  |  | OP | X | 9 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1998 | hydro | TRUE | 9188 | I-N-N Electric Coop, Inc | 7183 | Newhalen | AK | Lake and Peninsula | H-2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0 | N |  |  | OP | X | 9 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H
Vintage1986 | hydro | TRUE | 15783 | City of Redding - (CA) | 7189 | Whiskeytown | CA | Shasta | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.5 | 0.9 | 3.5 | 3.5 | 1 | N |  |  | OP | X | 9 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M |  |  |  |  | N | N | [14 empty] | N |  |  | N
Vintage1992 | hydro | TRUE | 9191 | Idaho Power Co | 7190 | Milner Hydro | ID | Cassia | 1 | Conventional Hydroelectric | HY |  | S | X | X | MLPR_1_TOT_GEN-APND | MLPR_1_TOT_GEN | 46.6 | 0.95 | 34.5 | 28.4 | 0 | N |  |  | OP | X | 12 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1992 | hydro | TRUE | 9191 | Idaho Power Co | 7190 | Milner Hydro | ID | Cassia | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 12.1 | 0.95 | 10.5 | 10.3 | 0 | N |  |  | OP | X | 9 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1992 | hydro | TRUE | 9191 | Idaho Power Co | 7190 | Milner Hydro | ID | Cassia | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 1 | 0.3 | 0.3 | 0 | N |  |  | OP | X | 9 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1986 | hydro | TRUE | 56477 | Tallassee Shoals LLC | 7191 | Tallassee Hydro Project | GA | Clarke | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 0.9 | 2 | 2 | 0.2 | N |  |  | OP | X | 8 | 1986 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 1H | [20 empty] | N |  |  | N
Vintage1986 | hydro | TRUE | 56477 | Tallassee Shoals LLC | 7191 | Tallassee Hydro Project | GA | Clarke | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 8 | 1986 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1989 | hydro | TRUE | 19449 | USACE-Fort Worth District | 7200 | Robert D Willis | TX | Jasper | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4 | 0.9 | 4 | 4 | 0.5 | N |  |  | OA | X | 12 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1989 | hydro | TRUE | 19449 | USACE-Fort Worth District | 7200 | Robert D Willis | TX | Jasper | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4 | 0.9 | 4 | 4 | 0.5 | N |  |  | OA | X | 12 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1993 | natural gas peaker | TRUE | 20856 | Wisconsin Power & Light Co | 7203 | South Fond Du Lac | WI | Fond Du Lac | CT1 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X | ALTE.SFONDDLG1 | ALTE.SFONDDLG1 | 95.4 | 0.8 | 81 | 91.1 | 20 | N |  |  | OP | X | 5 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1994 | natural gas peaker | TRUE | 20856 | Wisconsin Power & Light Co | 7203 | South Fond Du Lac | WI | Fond Du Lac | CT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | ALTE.SFONDDLG2 | ALTE.SFONDDLG2 | 95.4 | 0.8 | 82.8 | 93.1 | 20 | N |  |  | OP | X | 8 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1994 | natural gas peaker | TRUE | 20856 | Wisconsin Power & Light Co | 7203 | South Fond Du Lac | WI | Fond Du Lac | CT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | ALTE.SFONDDLG3 | ALTE.SFONDDLG3 | 95.4 | 0.8 | 82.3 | 92.6 | 20 | N |  |  | OP | X | 8 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1996 | natural gas peaker | TRUE | 20856 | Wisconsin Power & Light Co | 7203 | South Fond Du Lac | WI | Fond Du Lac | CT4 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X | ALTE.SFONDDLG4 | ALTE.SFONDDLG4 | 95.4 | 0.8 | 82.3 | 92.6 | 20 | N |  |  | OP | X | 6 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1996 | natural gas steam turbine | TRUE | 17539 | Dominion Energy South Carolina, Inc | 7210 | Cope | SC | Orangeburg | ST1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 417.3 | 0.85 | 415 | 415 | 110 | N |  |  | OP | X | 1 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: BIT; DFO DFO DFO: DFO | NG |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1990 | natural gas peaker | TRUE | 19876 | Virginia Electric & Power Co | 7212 | Darbytown | VA | Henrico | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 92.1 | 0.9 | 84 | 98 | 40 | N |  |  | OP | X | 5 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1990 | natural gas peaker | TRUE | 19876 | Virginia Electric & Power Co | 7212 | Darbytown | VA | Henrico | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 92.1 | 0.9 | 84 | 97 | 40 | N |  |  | OP | X | 5 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1990 | natural gas peaker | TRUE | 19876 | Virginia Electric & Power Co | 7212 | Darbytown | VA | Henrico | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 92.1 | 0.9 | 84 | 95 | 40 | N |  |  | OP | X | 4 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1990 | natural gas peaker | TRUE | 19876 | Virginia Electric & Power Co | 7212 | Darbytown | VA | Henrico | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 92.1 | 0.9 | 84 | 97 | 40 | N |  |  | OP | X | 4 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO | [6 empty] | 1H | [23 empty] | Y | N | Y
Vintage1995 | hard coal | TRUE | 19876 | Virginia Electric & Power Co | 7213 | Clover | VA | Halifax | 1 | Conventional Steam Coal | ST |  | J | X | X |  |  | 424 | 0.9 | 440 | 443 | 130 | N |  |  | OP | X | 10 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: BIT; DFO DFO DFO: DFO | [6 empty] | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1996 | hard coal | TRUE | 19876 | Virginia Electric & Power Co | 7213 | Clover | VA | Halifax | 2 | Conventional Steam Coal | ST |  | J | X | X |  |  | 424 | 0.9 | 437 | 438 | 130 | N |  |  | OP | X | 3 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: BIT; DFO DFO DFO: DFO | [6 empty] | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1988 | hydro | TRUE | 16655 | City of Santa Clara - (CA) | 7229 | Black Butte | CA | Tehama | 1 | Conventional Hydroelectric | HY |  | S | X | X | BLCKBUTT_7_B1 | BLCKBUTT_7_B1 | 6.1 | 0.9 | 6.1 | 6.1 | 0.5 | N |  |  | OP | X | 9 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1987 | natural gas peaker | TRUE | 16655 | City of Santa Clara - (CA) | 7231 | Gianera | CA | Santa Clara | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | CSCGNRA1_7_N101 | CSCGNRA1_7_N101 | 32.3 | 0.9 | 24.8 | 24.8 | 22 | N |  |  | OP | X | 6 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1986 | natural gas peaker | TRUE | 16655 | City of Santa Clara - (CA) | 7231 | Gianera | CA | Santa Clara | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | CSCGNRA2_7_N101 | CSCGNRA2_7_N101 | 32.3 | 0.9 | 24.8 | 24.8 | 22 | N |  |  | OP | X | 6 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1982 | natural gas peaker | TRUE | 16655 | City of Santa Clara - (CA) | 7232 | Santa Clara Cogen | CA | Santa Clara | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | CSCCOG_6_N001 | CSCCOG_6_N001 | 3.9 | 0.85 | 3.5 | 3.5 | 2.8 | N |  |  | OP | X | 6 | 1982 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X X X to RC RC RC
Vintage1982 | natural gas peaker | TRUE | 16655 | City of Santa Clara - (CA) | 7232 | Santa Clara Cogen | CA | Santa Clara | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | CSCCOG_6_N001 | CSCCOG_6_N001 | 3.9 | 0.85 | 3.5 | 3.5 | 2.8 | N |  |  | OP | X | 6 | 1982 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X X X to RC RC RC
Vintage1997 | hydro | TRUE | 3989 | City of Colorado Springs - (CO) | 7233 | Tesla | CO | El Paso | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 26.6 | 0.95 | 28 | 28 | 0.5 | N |  |  | OP | X | 4 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1994 | natural gas peaker | TRUE | 13781 | Northern States Power Co - Minnesota | 7237 | Angus Anson | SD | Minnehaha | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | NSP ANSON ANSON_2_UNIT | NSP ANSON ANSON_2_UNIT | 119.7 | 0.9 | 90 | 109 | 45 | N |  |  | OP | X | 8 | 1994 | 12 | 2025 | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1994 | natural gas peaker | TRUE | 13781 | Northern States Power Co - Minnesota | 7237 | Angus Anson | SD | Minnehaha | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | NSP ANSON ANSON_3_UNIT | NSP ANSON ANSON_3_UNIT | 119.7 | 0.9 | 90 | 109 | 45 | N |  |  | OP | X | 8 | 1994 | 12 | 2025 | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2005 | natural gas peaker | TRUE | 13781 | Northern States Power Co - Minnesota | 7237 | Angus Anson | SD | Minnehaha | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | NSP ANSON ANSON_4_UNIT | NSP ANSON ANSON_4_UNIT | 166.3 | 0.85 | 147 | 168 | 90 | N |  |  | OP | X | 6 | 2005 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1994 | natural gas peaker | TRUE | 10376 | Kissimmee Utility Authority | 7238 | Cane Island | FL | Osceola | 1 | Natural Gas Fired Combustion Turbine | GT |  | J | X | X |  |  | 32 | 0.8 | 32 | 42 | 10 | N |  |  | OP | X | 11 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO; DFO DFO DFO: NG |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1995 | natural gas combined cycle | TRUE | 10376 | Kissimmee Utility Authority | 7238 | Cane Island | FL | Osceola | 2 | Natural Gas Fired Combined Cycle | CT | UN1 | J | X | Y |  |  | 76 | 0.8 | 76 | 85 | 45 | N |  |  | OP | X | 6 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO; DFO DFO DFO: NG |  |  |  |  | N |  | 1H | [23 empty] | Y | N | Y
Vintage1995 | natural gas combined cycle | TRUE | 10376 | Kissimmee Utility Authority | 7238 | Cane Island | FL | Osceola | 2A | Natural Gas Fired Combined Cycle | CA | UN1 | J | N | X |  |  | 40 | 0.8 | 39 | 40 | 10 | N |  |  | OP | X | 6 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: OTH; DFO DFO DFO: WH |  |  |  | N | N |  | 12H | [23 empty] | N | N
Vintage2002 | natural gas combined cycle | TRUE | 10376 | Kissimmee Utility Authority | 7238 | Cane Island | FL | Osceola | 3 | Natural Gas Fired Combined Cycle | CT | UN2 | J | X | Y |  |  | 152 | 0.85 | 152 | 172 | 90 | N |  |  | OP | X | 1 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO; DFO DFO DFO: NG |  |  |  |  | N |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas combined cycle | TRUE | 10376 | Kissimmee Utility Authority | 7238 | Cane Island | FL | Osceola | 3A | Natural Gas Fired Combined Cycle | CA | UN2 | J | Y | X |  |  | 82.5 | 0.85 | 90 | 90 | 10 | N |  |  | OP | X | 1 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; DFO DFO DFO: WH |  |  |  | N | N |  | 12H | [23 empty] | N |  | N
Vintage2011 | natural gas combined cycle | TRUE | 10376 | Kissimmee Utility Authority | 7238 | Cane Island | FL | Osceola | 4 | Natural Gas Fired Combined Cycle | CT | UN3 | W | X | N |  |  | 180 | 0.85 | 160 | 180 | 78 | N |  |  | OP | X | 7 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2011 | natural gas combined cycle | TRUE | 10376 | Kissimmee Utility Authority | 7238 | Cane Island | FL | Osceola | 4A | Natural Gas Fired Combined Cycle | CA | UN3 | W | Y | X |  |  | 143.5 | 0.85 | 130 | 140 | 10 | N |  |  | OP | X | 7 | 2011 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; DFO DFO DFO: WH |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1996 | other | TRUE | 18454 | Tampa Electric Co | 7242 | Polk | FL | Polk | 1CA | Petroleum Coke | CA | CC1 | S | N | X |  |  | 133.4 | 0.85 | 59 | 59 | 33 | N |  |  | OP | X | 9 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: SGP; SUB SUB SUB: SGC; WC WC WC: NG |  |  |  | Y |  |  | OVER | N | N |  | Y | Y | N | [17 empty] | N | N | N
Vintage1996 | hard coal | TRUE | 18454 | Tampa Electric Co | 7242 | Polk | FL | Polk | 1CT | Coal Integrated Gasification Combined Cycle | CT | CC1 | S | X | N |  |  | 192.9 | 0.86 | 161 | 161 | 89 | N |  |  | OP | X | 9 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: SGC; SUB SUB SUB: NG |  |  |  | Y |  |  | OVER | N | N |  | Y | Y | [18 empty] | Y | N | N
Vintage2000 | natural gas combined cycle | TRUE | 18454 | Tampa Electric Co | 7242 | Polk | FL | Polk | 2 | Natural Gas Fired Combined Cycle | CT | CC2 | S | X | Y |  |  | 175.8 | 0.9 | 150 | 180 | 89 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage2017 | natural gas combined cycle | TRUE | 18454 | Tampa Electric Co | 7242 | Polk | FL | Polk | 2CC | Natural Gas Fired Combined Cycle | CA | CC2 | S | Y | X |  |  | 463 | 0.9 | 461 | 480 | 90 | N |  |  | OP | X | 1 | 2017 |  |  | N | Electric Utility | 1 | [14 empty] | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2002 | natural gas combined cycle | TRUE | 18454 | Tampa Electric Co | 7242 | Polk | FL | Polk | 3 | Natural Gas Fired Combined Cycle | CT | CC2 | S | X | Y |  |  | 175.8 | 0.9 | 150 | 180 | 89 | N |  |  | OP | X | 4 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage2007 | natural gas combined cycle | TRUE | 18454 | Tampa Electric Co | 7242 | Polk | FL | Polk | 4 | Natural Gas Fired Combined Cycle | CT | CC2 | S | X | Y |  |  | 175.8 | 0.85 | 150 | 180 | 89 | N |  |  | OP | X | 3 | 2007 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage2007 | natural gas combined cycle | TRUE | 18454 | Tampa Electric Co | 7242 | Polk | FL | Polk | 5 | Natural Gas Fired Combined Cycle | CT | CC2 | S | X | Y |  |  | 175.8 | 0.85 | 150 | 180 | 89 | N |  |  | OP | X | 4 | 2007 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage1999 | hydro | TRUE | 807 | Arkansas Electric Coop Corp | 7246 | Dam 2 | AR | Desha | 1 | Conventional Hydroelectric | HY |  | S | X | X | EAI.AECCHYDRO2 | EIA | 34.2 | 0.95 | 11 | 11 | 2 | N |  |  | OP | X | 6 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1999 | hydro | TRUE | 807 | Arkansas Electric Coop Corp | 7246 | Dam 2 | AR | Desha | 2 | Conventional Hydroelectric | HY |  | S | X | X | EAI.AECCHYDRO2 | EIA | 34.2 | 0.95 | 12 | 12 | 2 | N |  |  | OP | X | 10 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1999 | hydro | TRUE | 807 | Arkansas Electric Coop Corp | 7246 | Dam 2 | AR | Desha | 3 | Conventional Hydroelectric | HY |  | S | X | X | EAI.AECCHYDRO2 | EIA | 34.2 | 0.95 | 12 | 12 | 2 | N |  |  | OP | X | 8 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1978 | petroleum | TRUE | 12710 | Missouri Basin Muni Power Agny | 7247 | Watertown Power Plant | SD | Codington | 1 | Petroleum Liquids | GT |  | S | X | X |  |  | 67.5 | 0.9 | 50 | 60 | 10 | N |  |  | OP | X | 1 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N |  | N
Vintage1993 | petroleum | TRUE | 213 | Alaska Electric Light & Power Co. | 7250 | Auke Bay | AK | Juneau | 13 | Petroleum Liquids | GT |  | S | X | X |  |  | 2.8 | 0.8 | 2.8 | 2.8 | 0.5 | N |  |  | SB | Y | 8 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1994 | petroleum | TRUE | 213 | Alaska Electric Light & Power Co. | 7250 | Auke Bay | AK | Juneau | 14 | Petroleum Liquids | GT |  | S | X | X |  |  | 30.9 | 0.85 | 23 | 23 | 9 | N |  |  | SB | Y | 12 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1980 | petroleum | TRUE | 213 | Alaska Electric Light & Power Co. | 7250 | Auke Bay | AK | Juneau | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | SB | Y | 9 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1990 | hydro | TRUE | 19099 | TransAlta Centralia Gen LLC | 7259 | Skookumchuck | WA | Thurston | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.94 | 1 | 1 | 0.3 | N |  |  | OP | X | 9 | 1990 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage1990 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 7264 | Miki Basin | HI | Maui | LL1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.6 | N |  |  | OP | X | 4 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1990 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 7264 | Miki Basin | HI | Maui | LL2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.6 | N |  |  | OP | X | 4 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1990 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 7264 | Miki Basin | HI | Maui | LL3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.6 | N |  |  | OP | X | 4 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1990 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 7264 | Miki Basin | HI | Maui | LL4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.6 | N |  |  | OP | X | 4 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N | N | N
Vintage1990 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 7264 | Miki Basin | HI | Maui | LL5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.6 | N |  |  | OP | X | 4 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1990 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 7264 | Miki Basin | HI | Maui | LL6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.6 | N |  |  | OP | X | 4 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N | N | N
Vintage1996 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 7264 | Miki Basin | HI | Maui | LL7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.2 | 0.8 | 2.1 | 2.1 | 0.6 | N |  |  | OP | X | 10 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N | N | N
Vintage1996 | petroleum | TRUE | 11843 | Maui Electric Co Ltd | 7264 | Miki Basin | HI | Maui | LL8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.2 | 0.8 | 2.1 | 2.1 | 0.6 | N |  |  | OP | X | 10 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N | N | N
Vintage2003 | natural gas combined cycle | TRUE | 12745 | Modesto Irrigation District | 7266 | Woodland | CA | Stanislaus | 2 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 37.7 | 0.85 | 33 | 33 | 2 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2003 | natural gas combined cycle | TRUE | 12745 | Modesto Irrigation District | 7266 | Woodland | CA | Stanislaus | 3 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 60.5 | 0.85 | 50 | 50 | 23 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2011 | natural gas peaker | TRUE | 12745 | Modesto Irrigation District | 7266 | Woodland | CA | Stanislaus | 3A | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 8.4 | 0.8 | 8.2 | 8.2 | 4 | N |  |  | OP | X | 7 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2011 | natural gas peaker | TRUE | 12745 | Modesto Irrigation District | 7266 | Woodland | CA | Stanislaus | 3B | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 8.4 | 0.8 | 8.2 | 8.2 | 4 | N |  |  | OP | X | 7 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2011 | natural gas peaker | TRUE | 12745 | Modesto Irrigation District | 7266 | Woodland | CA | Stanislaus | 3C | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 8.4 | 0.8 | 8.2 | 8.2 | 4 | N |  |  | OP | X | 7 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2011 | natural gas peaker | TRUE | 12745 | Modesto Irrigation District | 7266 | Woodland | CA | Stanislaus | 3D | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 8.4 | 0.8 | 8.2 | 8.2 | 4 | N |  |  | OP | X | 7 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2011 | natural gas peaker | TRUE | 12745 | Modesto Irrigation District | 7266 | Woodland | CA | Stanislaus | 3E | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 8.4 | 0.8 | 8.2 | 8.2 | 4 | N |  |  | OP | X | 7 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2011 | natural gas peaker | TRUE | 12745 | Modesto Irrigation District | 7266 | Woodland | CA | Stanislaus | 3F | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 8.4 | 0.8 | 8.2 | 8.2 | 4 | N |  |  | OP | X | 7 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage1993 | natural gas peaker | TRUE | 12745 | Modesto Irrigation District | 7266 | Woodland | CA | Stanislaus | NA1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 50.4 | 0.9 | 45 | 45 | 23 | N |  |  | OP | X | 11 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO; DFO DFO DFO: NG |  |  |  | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage1992 | natural gas peaker | TRUE | 8723 | City of Holland | 7268 | 491 E 48th Street | MI | Allegan | 7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 39.1 | 0.85 | 35 | 39 | 15 | N |  |  | OP | X | 5 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1992 | natural gas peaker | TRUE | 8723 | City of Holland | 7268 | 491 E 48th Street | MI | Allegan | 8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 39.1 | 0.85 | 35 | 39 | 15 | N |  |  | OP | X | 5 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2000 | natural gas peaker | TRUE | 8723 | City of Holland | 7268 | 491 E 48th Street | MI | Allegan | 9 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 83.5 | 0.85 | 75 | 83.5 | 50 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1995 | natural gas peaker | TRUE | 20847 | Wisconsin Electric Power Co | 7270 | Paris (WI) | WI | Kenosha | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | WEC.PARIS01S1 | WEC.PARIS01S1 | 95.4 | 0.8 | 91.4 | 100 | 50 | N |  |  | OP | X | 3 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1995 | natural gas peaker | TRUE | 20847 | Wisconsin Electric Power Co | 7270 | Paris (WI) | WI | Kenosha | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | WEC.PARIS01S2 | WEC.PARIS01S2 | 95.4 | 0.8 | 88.5 | 100 | 50 | N |  |  | OP | X | 3 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1995 | natural gas peaker | TRUE | 20847 | Wisconsin Electric Power Co | 7270 | Paris (WI) | WI | Kenosha | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | WEC.PARIS01S3 | WEC.PARIS01S3 | 95.4 | 0.8 | 94.2 | 100 | 50 | N |  |  | OP | X | 6 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1995 | natural gas peaker | TRUE | 20847 | Wisconsin Electric Power Co | 7270 | Paris (WI) | WI | Kenosha | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | WEC.PARIS01S4 | WEC.PARIS01S4 | 95.4 | 0.8 | 93.7 | 100 | 50 | N |  |  | OP | X | 6 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1995 | natural gas peaker | TRUE | 5416 | Duke Energy Carolinas, LLC | 7277 | Lincoln Combustion | NC | Lincoln | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 109.6 | 0.9 | 73 | 94 | 73 | N |  |  | OP | X | 5 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1995 | natural gas peaker | TRUE | 5416 | Duke Energy Carolinas, LLC | 7277 | Lincoln Combustion | NC | Lincoln | 10 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 109.6 | 0.9 | 73 | 96 | 73 | N |  |  | OP | X | 11 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1995 | natural gas peaker | TRUE | 5416 | Duke Energy Carolinas, LLC | 7277 | Lincoln Combustion | NC | Lincoln | 11 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 109.6 | 0.9 | 73 | 95 | 73 | N |  |  | OP | X | 12 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1995 | natural gas peaker | TRUE | 5416 | Duke Energy Carolinas, LLC | 7277 | Lincoln Combustion | NC | Lincoln | 12 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 109.6 | 0.9 | 73 | 94 | 73 | N |  |  | OP | X | 12 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1996 | natural gas peaker | TRUE | 5416 | Duke Energy Carolinas, LLC | 7277 | Lincoln Combustion | NC | Lincoln | 13 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 109.6 | 0.9 | 72 | 93 | 72 | N |  |  | OP | X | 2 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1996 | natural gas peaker | TRUE | 5416 | Duke Energy Carolinas, LLC | 7277 | Lincoln Combustion | NC | Lincoln | 14 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 109.6 | 0.9 | 72 | 94 | 72 | N |  |  | OP | X | 2 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1996 | natural gas peaker | TRUE | 5416 | Duke Energy Carolinas, LLC | 7277 | Lincoln Combustion | NC | Lincoln | 15 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 109.6 | 0.9 | 73 | 94 | 73 | N |  |  | OP | X | 3 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1996 | natural gas peaker | TRUE | 5416 | Duke Energy Carolinas, LLC | 7277 | Lincoln Combustion | NC | Lincoln | 16 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 109.6 | 0.9 | 73 | 93 | 73 | N |  |  | OP | X | 3 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1995 | natural gas peaker | TRUE | 5416 | Duke Energy Carolinas, LLC | 7277 | Lincoln Combustion | NC | Lincoln | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 109.6 | 0.9 | 74 | 96 | 74 | N |  |  | OP | X | 5 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1995 | natural gas peaker | TRUE | 5416 | Duke Energy Carolinas, LLC | 7277 | Lincoln Combustion | NC | Lincoln | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 109.6 | 0.9 | 73 | 95 | 73 | N |  |  | OP | X | 6 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1995 | natural gas peaker | TRUE | 5416 | Duke Energy Carolinas, LLC | 7277 | Lincoln Combustion | NC | Lincoln | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 109.6 | 0.9 | 73 | 94 | 73 | N |  |  | OP | X | 6 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1995 | natural gas peaker | TRUE | 5416 | Duke Energy Carolinas, LLC | 7277 | Lincoln Combustion | NC | Lincoln | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 109.6 | 0.9 | 72 | 93 | 72 | N |  |  | OP | X | 7 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1995 | natural gas peaker | TRUE | 5416 | Duke Energy Carolinas, LLC | 7277 | Lincoln Combustion | NC | Lincoln | 6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 109.6 | 0.9 | 72 | 93 | 72 | N |  |  | OP | X | 7 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1995 | natural gas peaker | TRUE | 5416 | Duke Energy Carolinas, LLC | 7277 | Lincoln Combustion | NC | Lincoln | 7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 109.6 | 0.9 | 72 | 95 | 72 | N |  |  | OP | X | 9 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1995 | natural gas peaker | TRUE | 5416 | Duke Energy Carolinas, LLC | 7277 | Lincoln Combustion | NC | Lincoln | 8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 109.6 | 0.9 | 72 | 94 | 72 | N |  |  | OP | X | 9 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1995 | natural gas peaker | TRUE | 5416 | Duke Energy Carolinas, LLC | 7277 | Lincoln Combustion | NC | Lincoln | 9 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 109.6 | 0.9 | 71 | 94 | 71 | N |  |  | OP | X | 11 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1988 | hydro | TRUE | 4065 | City of Columbus - (OH) | 7279 | O'Shaughnessy Hydro | OH | Delaware | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 0.9 | 1.3 | 1.3 | 0.2 | N |  |  | OS | X | 9 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M
Vintage1988 | hydro | TRUE | 4065 | City of Columbus - (OH) | 7279 | O'Shaughnessy Hydro | OH | Delaware | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.9 | 0.9 | 3.9 | 3.9 | 0.5 | N |  |  | OS | X | 9 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M
Vintage1990 | natural gas peaker | TRUE | 6949 | City of Gardner - (KS) | 7281 | Gardner Energy Center | KS | Johnson | CT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 19.6 | 0.95 | 13.5 | 14 | 5 | N |  |  | OP | X | 6 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1990 | natural gas peaker | TRUE | 6949 | City of Gardner - (KS) | 7281 | Gardner Energy Center | KS | Johnson | CT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 19.6 | 0.95 | 13.5 | 14 | 5 | N |  |  | OP | X | 5 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1990 | natural gas peaker | TRUE | 14446 | Paragould Light & Water Comm | 7283 | Paragould Turbine | AR | Greene | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | PARAGOULD | PARAGOULD | 3.4 | 0.8 | 3.4 | 3.4 | 3 | N |  |  | OP | X | 8 | 1990 |  |  | N | Electric Utility | 1 | [14 empty] | 1H | [23 empty] | N |  | N | bar: X X X to RC RC RC
Vintage1990 | natural gas peaker | TRUE | 14446 | Paragould Light & Water Comm | 7283 | Paragould Turbine | AR | Greene | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | PARAGOULD | PARAGOULD | 3.4 | 0.8 | 3.4 | 3.4 | 3 | N |  |  | OP | X | 8 | 1990 |  |  | N | Electric Utility | 1 | [14 empty] | 1H | [23 empty] | N |  | N | bar: X X X to RC RC RC
Vintage1990 | natural gas peaker | TRUE | 14446 | Paragould Light & Water Comm | 7283 | Paragould Turbine | AR | Greene | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | PARAGOULD | PARAGOULD | 3.4 | 0.8 | 3.4 | 3.4 | 3 | N |  |  | OP | X | 8 | 1990 |  |  | N | Electric Utility | 1 | [14 empty] | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1990 | natural gas peaker | TRUE | 14446 | Paragould Light & Water Comm | 7283 | Paragould Turbine | AR | Greene | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | PARAGOULD | PARAGOULD | 3.4 | 0.8 | 3.4 | 3.4 | 3 | N |  |  | OP | X | 8 | 1990 |  |  | N | Electric Utility | 1 | [14 empty] | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1991 | petroleum | TRUE | 14446 | Paragould Light & Water Comm | 7283 | Paragould Turbine | AR | Greene | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.2 | 0.2 | 0.2 | N |  |  | SB | Y | 2 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 1H | [23 empty] | N | N
Vintage1991 | natural gas peaker | TRUE | 56606 | Calpine New Jersey Generation LLC | 7288 | Sherman Avenue | NJ | Cumberland | SEHR | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 112.8 | 0.9 | 86.9 | 99 | 78.2 | N |  |  | OP | X | 5 | 1991 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: KER |  |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1989 | natural gas combined cycle | TRUE | 15776 | Reedy Creek Improvement Dist | 7294 | Central Energy Plant | FL | Orange | GTG | Natural Gas Fired Combined Cycle | CT | CC01 | S | X | N | Not Applicable | Not Applicable | 61.5 | 0.8 | 48 | 48 | 2 | N |  |  | SB | Y | 5 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | Y | N | Y
Vintage1989 | natural gas combined cycle | TRUE | 15776 | Reedy Creek Improvement Dist | 7294 | Central Energy Plant | FL | Orange | STG | Natural Gas Fired Combined Cycle | CA | CC01 | S | Y | X | Not Applicable | Not Applicable | 8.5 | 0.8 | 8 | 8 | 1 | N |  |  | SB | Y | 1 | 1989 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC
Vintage1995 | natural gas peaker | TRUE | 5860 | Empire District Electric Co | 7296 | State Line Combined Cycle | MO | Jasper | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | EDESTL4391UN1_ | EDESTL4391UN1_ | 123 | 1 | 94 | 104 | 70 | N |  |  | OP | X | 5 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: JF |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas combined cycle | TRUE | 5860 | Empire District Electric Co | 7296 | State Line Combined Cycle | MO | Jasper | 2-1 | Natural Gas Fired Combined Cycle | CT | CC1 | J | X | N | EDESTL4391UNCT1 | EDESTL4391UNCT1 | 181 | 1 | 175 | 200 | 75 | Y | 11 | 2021 | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N |  | N | bar: X X X to RC RC RC
Vintage1997 | natural gas combined cycle | TRUE | 5860 | Empire District Electric Co | 7296 | State Line Combined Cycle | MO | Jasper | 2-2 | Natural Gas Fired Combined Cycle | CT | CC1 | J | X | N | EDESTL4391UNCT2 | EDESTL4391UNCT2 | 180 | 1 | 175 | 200 | 75 | Y | 5 | 2021 | OP | X | 6 | 1997 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N |  | N | bar: X X X to RC RC RC
Vintage2001 | natural gas combined cycle | TRUE | 5860 | Empire District Electric Co | 7296 | State Line Combined Cycle | MO | Jasper | 2-3 | Natural Gas Fired Combined Cycle | CA | CC1 | J | N | X |  |  | 206.5 | 1 | 186 | 186 | 50 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N |  | N | bar: X X X to RC RC RC
Vintage1999 | natural gas combined cycle | TRUE | 6455 | Duke Energy Florida, LLC | 7302 | Hines Energy Complex | FL | Polk | 1GT | Natural Gas Fired Combined Cycle | CT | E100 | S | X | N |  |  | 173.4 | 0.85 | 161 | 174 | 161 | N |  |  | OP | X | 4 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO; DFO DFO DFO: NG |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1999 | natural gas combined cycle | TRUE | 6455 | Duke Energy Florida, LLC | 7302 | Hines Energy Complex | FL | Polk | 1GT2 | Natural Gas Fired Combined Cycle | CT | E100 | S | X | N |  |  | 173.4 | 0.85 | 167 | 177 | 167 | N |  |  | OP | X | 4 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO; DFO DFO DFO: NG |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1999 | natural gas combined cycle | TRUE | 6455 | Duke Energy Florida, LLC | 7302 | Hines Energy Complex | FL | Polk | 1ST | Natural Gas Fired Combined Cycle | CA | E100 | S | N | X |  |  | 199.7 | 0.85 | 162 | 170 | 162 | N |  |  | OP | X | 4 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO; DFO DFO DFO: NG |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2003 | natural gas combined cycle | TRUE | 6455 | Duke Energy Florida, LLC | 7302 | Hines Energy Complex | FL | Polk | 2GT | Natural Gas Fired Combined Cycle | CT | F110 | S | X | N |  |  | 178.5 | 0.85 | 176 | 179 | 176 | N |  |  | OP | X | 12 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2003 | natural gas combined cycle | TRUE | 6455 | Duke Energy Florida, LLC | 7302 | Hines Energy Complex | FL | Polk | 2GT2 | Natural Gas Fired Combined Cycle | CT | F110 | S | X | N |  |  | 178.5 | 0.85 | 174 | 183 | 174 | N |  |  | OP | X | 12 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2003 | natural gas combined cycle | TRUE | 6455 | Duke Energy Florida, LLC | 7302 | Hines Energy Complex | FL | Polk | 2ST | Natural Gas Fired Combined Cycle | CA | F110 | S | N | X |  |  | 191.3 | 0.85 | 182 | 187 | 182 | N |  |  | OP | X | 12 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2005 | natural gas combined cycle | TRUE | 6455 | Duke Energy Florida, LLC | 7302 | Hines Energy Complex | FL | Polk | 3GT | Natural Gas Fired Combined Cycle | CT | G301 | S | X | N |  |  | 178.5 | 0.85 | 171 | 184 | 171 | N |  |  | OP | X | 11 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2005 | natural gas combined cycle | TRUE | 6455 | Duke Energy Florida, LLC | 7302 | Hines Energy Complex | FL | Polk | 3GT2 | Natural Gas Fired Combined Cycle | CT | G301 | S | X | N |  |  | 178.5 | 0.85 | 176 | 185 | 176 | N |  |  | OP | X | 11 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2005 | natural gas combined cycle | TRUE | 6455 | Duke Energy Florida, LLC | 7302 | Hines Energy Complex | FL | Polk | 3ST | Natural Gas Fired Combined Cycle | CA | G301 | S | N | X |  |  | 204 | 0.85 | 176 | 186 | 176 | N |  |  | OP | X | 11 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2007 | natural gas combined cycle | TRUE | 6455 | Duke Energy Florida, LLC | 7302 | Hines Energy Complex | FL | Polk | 4GT | Natural Gas Fired Combined Cycle | CT | H400 | S | X | N |  |  | 199 | 0.85 | 171 | 179 | 171 | N |  |  | OP | X | 12 | 2007 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2007 | natural gas combined cycle | TRUE | 6455 | Duke Energy Florida, LLC | 7302 | Hines Energy Complex | FL | Polk | 4GT2 | Natural Gas Fired Combined Cycle | CT | H400 | S | X | N |  |  | 199 | 0.85 | 171 | 179 | 171 | N |  |  | OP | X | 12 | 2007 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2007 | natural gas combined cycle | TRUE | 6455 | Duke Energy Florida, LLC | 7302 | Hines Energy Complex | FL | Polk | 4ST | Natural Gas Fired Combined Cycle | CA | H400 | S | N | X |  |  | 212.5 | 0.85 | 174 | 186 | 174 | N |  |  | OP | X | 12 | 2007 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1996 | natural gas peaker | TRUE | 15783 | City of Redding - (CA) | 7307 | Redding Power | CA | Shasta | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 18 | 0.85 | 16 | 17 | 14 | N |  |  | OP | X | 10 | 1996 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H |  | N |  |  | N | [15 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC
Vintage1996 | natural gas peaker | TRUE | 15783 | City of Redding - (CA) | 7307 | Redding Power | CA | Shasta | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 27.9 | 0.9 | 23 | 25 | 16 | N |  |  | OP | X | 4 | 1996 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC
Vintage1996 | natural gas peaker | TRUE | 15783 | City of Redding - (CA) | 7307 | Redding Power | CA | Shasta | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 27.9 | 0.9 | 23 | 25 | 16 | N |  |  | OP | X | 4 | 1996 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC
Vintage1989 | natural gas combined cycle | TRUE | 15783 | City of Redding - (CA) | 7307 | Redding Power | CA | Shasta | 4 | Natural Gas Fired Combined Cycle | CA | 101 | S | N | X |  |  | 26.8 | 0.85 | 27 | 28 | 5 | N |  |  | OP | X | 1 | 1989 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H |  |  |  |  | N | [15 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC
Vintage2002 | natural gas combined cycle | TRUE | 15783 | City of Redding - (CA) | 7307 | Redding Power | CA | Shasta | 5 | Natural Gas Fired Combined Cycle | CT | 101 | S | X | N |  |  | 40 | 0.8 | 41 | 45 | 5 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC
Vintage2011 | natural gas combined cycle | TRUE | 15783 | City of Redding - (CA) | 7307 | Redding Power | CA | Shasta | 6 | Natural Gas Fired Combined Cycle | CT | 101 | S | X | N |  |  | 42.5 | 0.85 | 41 | 46 | 24 | N |  |  | OP | X | 8 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC
Vintage1994 | natural gas combined cycle | TRUE | 15296 | New York Power Authority | 7314 | Richard M Flynn | NY | Suffolk | NA1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 110 | 1 | 87.5 | 104 | 1 | N |  |  | OP | X | 5 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO; DFO DFO DFO: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1994 | natural gas combined cycle | TRUE | 15296 | New York Power Authority | 7314 | Richard M Flynn | NY | Suffolk | NA2 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X |  |  | 60 | 1 | 49.4 | 58.7 | 1 | N |  |  | OP | X | 5 | 1994 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1996 | natural gas peaker | TRUE | 19281 | Turlock Irrigation District | 7315 | Almond Power Plant | CA | Stanislaus | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 49.5 | 0.9 | 49.5 | 49.5 | 16 | N |  |  | OP | X | 4 | 1996 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2012 | natural gas peaker | TRUE | 19281 | Turlock Irrigation District | 7315 | Almond Power Plant | CA | Stanislaus | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 58 | 0.9 | 50 | 58 | 16 | N |  |  | OP | X | 7 | 2012 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2012 | natural gas peaker | TRUE | 19281 | Turlock Irrigation District | 7315 | Almond Power Plant | CA | Stanislaus | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 58 | 0.9 | 50 | 58 | 16 | N |  |  | OP | X | 7 | 2012 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2012 | natural gas peaker | TRUE | 19281 | Turlock Irrigation District | 7315 | Almond Power Plant | CA | Stanislaus | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 58 | 0.9 | 50 | 58 | 16 | N |  |  | OP | X | 7 | 2012 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage1992 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 7317 | Buffalo Bill | WY | Park | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6 | 0.9 | 6 | 6 | 0 | N |  |  | OP | X | 9 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1992 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 7317 | Buffalo Bill | WY | Park | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6 | 0.9 | 6 | 6 | 0 | N |  |  | OP | X | 9 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1992 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 7317 | Buffalo Bill | WY | Park | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6 | 0.9 | 6 | 6 | 0 | N |  |  | OP | X | 9 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1991 | natural gas peaker | TRUE | 54899 | NAES Corporation - (DE) | 7318 | Van Sant Station | DE | Kent | 1 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X | NORTHST 12KV G11 | NORTHST 12KV G11 | 45.1 | 0.85 | 44.4 | 47.2 | 0.5 | N |  |  | OP | X | 5 | 1991 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1995 | natural gas peaker | TRUE | 54888 | NRG Texas Power LLC | 7325 | San Jacinto Steam Electric Station | TX | Harris | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SJS_SJS_G1 | SJS_SJS_G1 | 88.2 | 0.85 | 81 | 81 | 58 | N |  |  | OP | X | 4 | 1995 | 12 | 2031 | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage1995 | natural gas peaker | TRUE | 54888 | NRG Texas Power LLC | 7325 | San Jacinto Steam Electric Station | TX | Harris | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SJS_SJS_G2 | SJS_SJS_G2 | 88.2 | 0.85 | 81 | 81 | 50 | N |  |  | OP | X | 4 | 1995 | 12 | 2031 | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage1992 | natural gas peaker | TRUE | 9234 | Indiana Municipal Power Agency | 7335 | Richmond | IN | Wayne | RCT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 32419337 | 32419337 | 41.4 | 0.85 | 34 | 42 | 17 | N |  |  | OP | X | 5 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | Y | Y
Vintage1992 | natural gas peaker | TRUE | 9234 | Indiana Municipal Power Agency | 7335 | Richmond | IN | Wayne | RCT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 32419339 | 32419339 | 41.4 | 0.85 | 34 | 42 | 17 | N |  |  | OP | X | 5 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | Y | Y
Vintage1992 | natural gas peaker | TRUE | 9234 | Indiana Municipal Power Agency | 7336 | Anderson | IN | Madison | ACT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 32419341 | 32419341 | 41.4 | 0.85 | 34 | 42 | 17 | N |  |  | OP | X | 6 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | Y | Y
Vintage1992 | natural gas peaker | TRUE | 9234 | Indiana Municipal Power Agency | 7336 | Anderson | IN | Madison | ACT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 32419343 | 32419343 | 41.4 | 0.85 | 34 | 42 | 17 | N |  |  | OP | X | 6 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | Y | Y
Vintage2004 | natural gas peaker | TRUE | 9234 | Indiana Municipal Power Agency | 7336 | Anderson | IN | Madison | ACT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 34886963 | 34886963 | 85.9 | 0.85 | 72 | 90 | 36 | N |  |  | OP | X | 6 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | Y | Y
Vintage1993 | hydro | TRUE | 16655 | City of Santa Clara - (CA) | 7338 | Grizzly | CA | Plumas | NA1 | Conventional Hydroelectric | HY |  | S | X | X | GRIZZLYG_7_B1 | GRIZZLYG_7_B1 | 22 | 0.9 | 17.7 | 17.7 | 0 | N |  |  | OP | X | 11 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1989 | natural gas peaker | TRUE | 20315 | City of Wellington - (KS) | 7339 | Wellington 2 | KS | Sumner | 6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 20 | 0.9 | 21 | 21 | 3 | N |  |  | OP | X | 1 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1979 | hard coal | TRUE | 12341 | MidAmerican Energy Co | 7343 | George Neal South | IA | Woodbury | 4 | Conventional Steam Coal | ST |  | J | X | X | MEC.NEALS 4 | MEC NEALS 4 | 695.9 | 0.9 | 650.3 | 650.3 | 200 | N |  |  | OP | X | 7 | 1979 |  |  | Y | Electric Utility | 1 | X X X: T; RC RC RC: RC; SUB SUB SUB: SUB; DFO DFO DFO: DFO |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1994 | natural gas peaker | TRUE | 6455 | Duke Energy Florida, LLC | 7345 | University of Florida | FL | Alachua | P1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 54.2 | 0.9 | 44 | 50 | 40 | N |  |  | OP | X | 1 | 1994 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X X X to RC RC RC
Vintage1995 | natural gas peaker | TRUE | 7140 | Georgia Power Co | 7348 | Robins | GA | Houston | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 91.9 | 0.85 | 80 | 93 | 55 | N |  |  | OP | X | 5 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1995 | natural gas peaker | TRUE | 7140 | Georgia Power Co | 7348 | Robins | GA | Houston | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 91.9 | 0.85 | 80 | 93 | 55 | N |  |  | OP | X | 5 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1995 | natural gas combined cycle | TRUE | 15248 | Portland General Electric Co | 7350 | Coyote Springs | OR | Morrow | 1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | CSP1_5_GNODESTG1 | CSP1_5_COYOTE1 | 208 | 0.95 | 168.3 | 187.2 | 98.8 | N |  |  | OP | X | 11 | 1995 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1995 | natural gas combined cycle | TRUE | 15248 | Portland General Electric Co | 7350 | Coyote Springs | OR | Morrow | 2 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X | CSP1_5_GNODESTG1 | CSP1_5_COYOTE1 | 88 | 0.95 | 75.9 | 83.7 | 61 | N |  |  | OP | X | 11 | 1995 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1991 | hydro | TRUE | 19558 | Homer Electric Assn Inc | 7367 | Bradley Lake | AK | Kenai Peninsula | 1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 63 | 0.95 | 63 | 63 | 63 | N |  |  | OP | X | 6 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1991 | hydro | TRUE | 19558 | Homer Electric Assn Inc | 7367 | Bradley Lake | AK | Kenai Peninsula | 2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 63 | 0.95 | 63 | 63 | 63 | N |  |  | OP | X | 6 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1983 | geothermal | TRUE | 40613 | Northern California Power Agny | 7368 | Geothermal 1 | CA | Sonoma | 1 | Geothermal | ST |  | S | X | X |  |  | 55 | 0.86 | 25 | 26 | 10 | N |  |  | OP | X | 1 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: GEO; DFO DFO DFO: GEO |  |  |  | N | N |  | 12H | [23 empty] | N | N
Vintage1983 | geothermal | TRUE | 40613 | Northern California Power Agny | 7368 | Geothermal 1 | CA | Sonoma | 2 | Geothermal | ST |  | S | X | X |  |  | 55 | 0.86 | 26 | 27 | 10 | N |  |  | OP | X | 1 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: GEO; DFO DFO DFO: GEO |  |  |  | N | N |  | 12H | [23 empty] | N | N
Vintage1985 | geothermal | TRUE | 40613 | Northern California Power Agny | 7369 | Geothermal 2 | CA | Sonoma | 3 | Geothermal | ST |  | S | X | X |  |  | 55 | 0.9 | 25 | 25 | 0 | N |  |  | SB | N | 12 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: GEO; DFO DFO DFO: GEO |  |  |  | N |  |  | OVER | [23 empty] | N
Vintage1986 | geothermal | TRUE | 40613 | Northern California Power Agny | 7369 | Geothermal 2 | CA | Sonoma | 4 | Geothermal | ST |  | S | X | X |  |  | 55 | 0.9 | 40 | 41 | 10 | N |  |  | OP | X | 5 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: GEO; DFO DFO DFO: GEO |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1992 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 7372 | McPhee | CO | Montezuma | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.92 | 1.2 | 1.2 | 0 | N |  |  | OP | X | 12 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1993 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 7373 | Towaoc | CO | Montezuma | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 11.4 | 0.95 | 11.4 | 10.5 | 0 | N |  |  | OP | X | 5 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage2002 | natural gas combined cycle | TRUE | 21554 | Seminole Electric Cooperative Inc | 7380 | Midulla Generating Station | FL | Hardee | CT1 | Natural Gas Fired Combined Cycle | CT | CCU1 | S | X | N |  |  | 181.1 | 0.85 | 179 | 198 | 90 | N |  |  | OP | X | 1 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2002 | natural gas combined cycle | TRUE | 21554 | Seminole Electric Cooperative Inc | 7380 | Midulla Generating Station | FL | Hardee | CT2 | Natural Gas Fired Combined Cycle | CT | CCU1 | S | X | N |  |  | 181.1 | 0.85 | 179 | 198 | 90 | N |  |  | OP | X | 1 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2006 | natural gas peaker | TRUE | 21554 | Seminole Electric Cooperative Inc | 7380 | Midulla Generating Station | FL | Hardee | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 62 | 0.85 | 54 | 62 | 14 | N |  |  | OP | X | 12 | 2006 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2006 | natural gas peaker | TRUE | 21554 | Seminole Electric Cooperative Inc | 7380 | Midulla Generating Station | FL | Hardee | GT5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 62 | 0.85 | 54 | 62 | 14 | N |  |  | OP | X | 12 | 2006 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2006 | natural gas peaker | TRUE | 21554 | Seminole Electric Cooperative Inc | 7380 | Midulla Generating Station | FL | Hardee | GT6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 62 | 0.85 | 54 | 62 | 14 | N |  |  | OP | X | 12 | 2006 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2006 | natural gas peaker | TRUE | 21554 | Seminole Electric Cooperative Inc | 7380 | Midulla Generating Station | FL | Hardee | GT7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 62 | 0.85 | 54 | 62 | 14 | N |  |  | OP | X | 12 | 2006 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2006 | natural gas peaker | TRUE | 21554 | Seminole Electric Cooperative Inc | 7380 | Midulla Generating Station | FL | Hardee | GT8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 62 | 0.85 | 54 | 62 | 14 | N |  |  | OP | X | 12 | 2006 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2002 | natural gas combined cycle | TRUE | 21554 | Seminole Electric Cooperative Inc | 7380 | Midulla Generating Station | FL | Hardee | ST3 | Natural Gas Fired Combined Cycle | CA | CCU1 | S | N | X |  |  | 181.1 | 0.85 | 185 | 187 | 62 | N |  |  | OP | X | 1 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1997 | onshore wind | TRUE | 7601 | Green Mountain Power Corp | 7381 | Searsburg Wind Turbine | VT | Bennington | 1 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 6 |  | 5.2 | 5 | 0.5 | N |  |  | OP | X | 6 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WND |  |  |  | N |  | 11
Vintage1976 | natural gas peaker | TRUE | 15229 | City of Poplar Bluff - (MO) | 7392 | Poplar Bluff Generating Station | MO | Butler | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | POPLARBLUFF |  | 7 | 0.8 | 7 | 7 | 3 | N |  |  | OP | X | 5 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N | 0 | 1H | [23 empty] | N | N | N
Vintage1976 | natural gas peaker | TRUE | 15229 | City of Poplar Bluff - (MO) | 7392 | Poplar Bluff Generating Station | MO | Butler | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | POPLARBLUFF |  | 7 | 0.8 | 7 | 7 | 3 | N |  |  | OP | X | 5 | 1976 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2002 | petroleum | TRUE | 15229 | City of Poplar Bluff - (MO) | 7392 | Poplar Bluff Generating Station | MO | Butler | 3 | Petroleum Liquids | IC |  | S | X | X | POPLARBLUFF |  | 6.7 | 0.8 | 6.6 | 6.6 | 3 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: NG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2002 | petroleum | TRUE | 15229 | City of Poplar Bluff - (MO) | 7392 | Poplar Bluff Generating Station | MO | Butler | 4 | Petroleum Liquids | IC |  | S | X | X | POPLARBLUFF |  | 6.7 | 0.8 | 6.6 | 6.6 | 3 | N |  |  | OA | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: NG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2002 | petroleum | TRUE | 15229 | City of Poplar Bluff - (MO) | 7392 | Poplar Bluff Generating Station | MO | Butler | 5 | Petroleum Liquids | IC |  | S | X | X | POPLARBLUFF |  | 6.7 | 0.8 | 6.6 | 6.6 | 3 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: NG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1984 | hydro | TRUE | 7370 | City of Gonzales - (TX) | 7394 | Gonzales Hydro Plant | TX | Gonzales | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.2 | N |  |  | OS | X | 1 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1984 | hydro | TRUE | 7370 | City of Gonzales - (TX) | 7394 | Gonzales Hydro Plant | TX | Gonzales | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.2 | N |  |  | OS | X | 1 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1984 | hydro | TRUE | 7370 | City of Gonzales - (TX) | 7394 | Gonzales Hydro Plant | TX | Gonzales | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.2 | N |  |  | OS | X | 1 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M |  | N
Vintage1978 | petroleum | TRUE | 3477 | City of Chicopee - (MA) | 7396 | Front Street | MA | Hampden | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2.8 | 2.8 | 1.3 | N |  |  | OP | X | 1 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [20 empty] | Y | 12 | 2024 | N | N | N
Vintage1978 | petroleum | TRUE | 3477 | City of Chicopee - (MA) | 7396 | Front Street | MA | Hampden | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2.8 | 2.8 | 1.3 | N |  |  | OP | X | 1 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [20 empty] | Y | 12 | 2024 | N | N | N
Vintage1978 | petroleum | TRUE | 3477 | City of Chicopee - (MA) | 7396 | Front Street | MA | Hampden | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2.8 | 2.8 | 1.3 | N |  |  | OP | X | 1 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [20 empty] | Y | 12 | 2024 | N | N | N
Vintage1967 | natural gas peaker | TRUE | 3329 | Borough of Chambersburg | 7397 | Falling Spring | PA | Franklin | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | Grand Point | Grand Point | 2 | 0.8 | 2.1 | 2.1 | 1 | N |  |  | OP | X | 12 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1967 | natural gas peaker | TRUE | 3329 | Borough of Chambersburg | 7397 | Falling Spring | PA | Franklin | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | Grand Point | Grand Point | 2 | 0.8 | 2.1 | 2.1 | 1 | N |  |  | OP | X | 12 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2001 | natural gas peaker | TRUE | 3329 | Borough of Chambersburg | 7397 | Falling Spring | PA | Franklin | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | Grand Point | Grand Point | 3.2 | 0.8 | 2.9 | 2.9 | 1 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1980 | natural gas peaker | TRUE | 1366 | City of Bay City - (MI) | 7398 | Water Street Station | MI | Bay | GEN1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 5.7 | 0.8 | 5.5 | 5.5 | 1 | N |  |  | OP | X | 8 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1984 | natural gas peaker | TRUE | 1366 | City of Bay City - (MI) | 7398 | Water Street Station | MI | Bay | GEN2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 6.9 | 0.8 | 6.5 | 6.5 | 1 | N |  |  | OP | X | 10 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1993 | natural gas peaker | TRUE | 1366 | City of Bay City - (MI) | 7399 | Henry Station | MI | Bay | GEN3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 7.7 | 0.9 | 7.5 | 7.5 | 1 | N |  |  | OP | X | 5 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1993 | natural gas peaker | TRUE | 1366 | City of Bay City - (MI) | 7399 | Henry Station | MI | Bay | GEN4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 7.7 | 0.9 | 7.5 | 7.5 | 1 | N |  |  | OP | X | 5 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1983 | petroleum | TRUE | 16560 | City of Salisbury - (MO) | 7400 | Salisbury City of | MO | Chariton | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.9 | 0.8 | 1 | 0.5 | N |  |  | OP | X | 6 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 12H | [23 empty] | N |  | N
Vintage1983 | petroleum | TRUE | 16560 | City of Salisbury - (MO) | 7400 | Salisbury City of | MO | Chariton | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.9 | 0.8 | 1 | 0.5 | N |  |  | OP | X | 6 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 12H | [23 empty] | N |  | N
Vintage1986 | petroleum | TRUE | 16560 | City of Salisbury - (MO) | 7400 | Salisbury City of | MO | Chariton | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.2 | 0.8 | 1.8 | 2 | 1 | N |  |  | OP | X | 6 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 12H | [23 empty] | N |  | N
Vintage1986 | petroleum | TRUE | 16560 | City of Salisbury - (MO) | 7400 | Salisbury City of | MO | Chariton | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.2 | 0.8 | 1.8 | 2 | 1 | N |  |  | OP | X | 6 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 12H | [23 empty] | N |  | N
Vintage1981 | petroleum | TRUE | 17035 | City of Shelbina - (MO) | 7405 | Shelbina Power #1 | MO | Shelby | G1 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 0.3 | N |  |  | OP | X | 1 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  |  | N |  | 10M | [23 empty] | N
Vintage1989 | petroleum | TRUE | 17035 | City of Shelbina - (MO) | 7405 | Shelbina Power #1 | MO | Shelby | G2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 1 | N |  |  | OP | X | 5 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  |  | N |  | 10M | [23 empty] | N
Vintage1992 | petroleum | TRUE | 17035 | City of Shelbina - (MO) | 7406 | Shelbina Power #2 | MO | Shelby | G3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 1 | N |  |  | OP | X | 4 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  |  | N |  | 10M | [23 empty] | N | N | N
Vintage1992 | petroleum | TRUE | 17035 | City of Shelbina - (MO) | 7406 | Shelbina Power #2 | MO | Shelby | G4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 1 | N |  |  | OP | X | 4 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  |  | N |  | 10M | [23 empty] | N | N | N
Vintage1992 | petroleum | TRUE | 17035 | City of Shelbina - (MO) | 7406 | Shelbina Power #2 | MO | Shelby | G5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 1 | N |  |  | OP | X | 4 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  |  | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 17035 | City of Shelbina - (MO) | 7406 | Shelbina Power #2 | MO | Shelby | G6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  |  | N |  | 10M | [23 empty] | N | N | N
Vintage1988 | natural gas peaker | TRUE | 14600 | Payson City Corporation | 7408 | Payson | UT | Utah | 86-1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.6 | 0.8 | 2.6 | 2.6 | 1.8 | N |  |  | OP | X | 6 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 10M | [23 empty] | Y | Y | Y
Vintage1988 | natural gas peaker | TRUE | 14600 | Payson City Corporation | 7408 | Payson | UT | Utah | 86-2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.6 | 0.8 | 2.6 | 2.6 | 1.8 | N |  |  | OP | X | 6 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 10M | [23 empty] | Y | Y | Y
Vintage1995 | natural gas peaker | TRUE | 14600 | Payson City Corporation | 7408 | Payson | UT | Utah | 86-3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2 | 2 | 1.8 | N |  |  | OP | X | 8 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 10M | [23 empty] | Y | Y | Y
Vintage1995 | natural gas peaker | TRUE | 14600 | Payson City Corporation | 7408 | Payson | UT | Utah | 86-4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1.5 | N |  |  | OP | X | 4 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 10M | [23 empty] | Y | Y | Y
Vintage1992 | biomass | TRUE | 40437 | Emerald People's Utility Dist | 7413 | Short Mountain | OR | Lane | 1 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.83 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 2 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: LFG |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1992 | biomass | TRUE | 40437 | Emerald People's Utility Dist | 7413 | Short Mountain | OR | Lane | 2 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.83 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 2 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: LFG |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1993 | biomass | TRUE | 40437 | Emerald People's Utility Dist | 7413 | Short Mountain | OR | Lane | 3 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.83 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 11 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: LFG |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1993 | biomass | TRUE | 40437 | Emerald People's Utility Dist | 7413 | Short Mountain | OR | Lane | 4 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.83 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 11 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: LFG |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1993 | petroleum | TRUE | 219 | Alaska Power and Telephone Co | 7414 | Thorne Bay Plant | AK | Prince of Wales Ketchikan | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 8 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1996 | petroleum | TRUE | 219 | Alaska Power and Telephone Co | 7414 | Thorne Bay Plant | AK | Prince of Wales Ketchikan | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 1 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1985 | petroleum | TRUE | 10622 | City of Lakefield - (MN) | 7415 | Lakefield Utilities | MN | Jackson | 5 | Petroleum Liquids | IC |  | S | X | X | ALTW.MRES |  | 1.2 | 0.8 | 0.9 | 0.9 | 0.8 | N |  |  | OP | X | 2 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 10M | [23 empty] | N
Vintage2003 | petroleum | TRUE | 10622 | City of Lakefield - (MN) | 7415 | Lakefield Utilities | MN | Jackson | 6 | Petroleum Liquids | IC |  | S | X | X | ALTW.MRES |  | 2.2 | 0.8 | 2 | 2 | 1.5 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 10M | [23 empty] | N
Vintage1997 | petroleum | TRUE | 17828 | City of Springfield - (IL) | 7425 | Interstate | IL | Sangamon | 1 | Petroleum Liquids | GT |  | S | X | X | CWLP.INTERSA81 | CWLP.INTERSA81 | 138.6 | 0.9 | 109 | 111 | 75 | N |  |  | OP | X | 9 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: NG |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | Y | N | Y
Vintage1994 | hydro | TRUE | 10944 | PUD No 1 of Lewis County | 7427 | Cowlitz Falls | WA | Lewis | U#1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 35 | 0.9 | 35 | 35 | 12 | N |  |  | OP | X | 6 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1994 | hydro | TRUE | 10944 | PUD No 1 of Lewis County | 7427 | Cowlitz Falls | WA | Lewis | U#2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 35 | 0.9 | 35 | 35 | 12 | N |  |  | OP | X | 6 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1988 | petroleum | TRUE | 6710 | Town of Edenton - (NC) | 7429 | Edenton Generators | NC | Chowan | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 1 | 1.2 | 1.2 | 0.2 | N |  |  | OP | X | 12 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2014 | petroleum | TRUE | 6710 | Town of Edenton - (NC) | 7429 | Edenton Generators | NC | Chowan | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 1 | 1.2 | 1.2 | 0.2 | N |  |  | OP | X | 6 | 2014 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1991 | hydro | TRUE | 13788 | Northern Wasco County PUD | 7431 | Dalles Dam North Fishway Project | OR | Wasco | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.5 | 0.9 | 5 | 5 | 5 | N |  |  | OP | X | 5 | 1991 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1999 | petroleum | TRUE | 14276 | City of Oxford - (KS) | 7432 | Oxford (KS) | KS | Sumner | 1A | Petroleum Liquids | IC |  | S | X | X |  |  | 1.7 | 0.8 | 1.6 | 1.6 | 0.9 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N | 0 | 1H | [20 empty] | N |  |  | N | N | N
Vintage1999 | petroleum | TRUE | 14276 | City of Oxford - (KS) | 7432 | Oxford (KS) | KS | Sumner | 2A | Petroleum Liquids | IC |  | S | X | X |  |  | 1.7 | 0.8 | 1.6 | 1.6 | 0.9 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage2007 | petroleum | TRUE | 14276 | City of Oxford - (KS) | 7432 | Oxford (KS) | KS | Sumner | 3A | Petroleum Liquids | IC |  | S | X | X |  |  | 1.7 | 0.8 | 1.6 | 1.6 | 0.9 | N |  |  | OP | X | 3 | 2007 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1933 | petroleum | TRUE | 19798 | City of Vernon | 7436 | Vernon | CA | Los Angeles | JH1 | Petroleum Liquids | IC |  | S | X | X |  |  | 6 | 0.8 | 3.6 | 4 | 3.6 | N |  |  | OS | X | 9 | 1933 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | OVER | [23 empty] | N | N
Vintage1933 | petroleum | TRUE | 19798 | City of Vernon | 7436 | Vernon | CA | Los Angeles | JH2 | Petroleum Liquids | IC |  | S | X | X |  |  | 6 | 0.8 | 3.6 | 4 | 3.6 | N |  |  | OS | X | 9 | 1933 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | OVER | [23 empty] | N | N
Vintage1933 | petroleum | TRUE | 19798 | City of Vernon | 7436 | Vernon | CA | Los Angeles | JH3 | Petroleum Liquids | IC |  | S | X | X |  |  | 6 | 0.8 | 3.6 | 4.6 | 3.6 | N |  |  | OS | X | 9 | 1933 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | OVER | [23 empty] | N | N
Vintage1933 | petroleum | TRUE | 19798 | City of Vernon | 7436 | Vernon | CA | Los Angeles | JH4 | Petroleum Liquids | IC |  | S | X | X |  |  | 6 | 0.8 | 3.6 | 4 | 3.6 | N |  |  | OS | X | 9 | 1933 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | OVER | [23 empty] | N
Vintage1933 | petroleum | TRUE | 19798 | City of Vernon | 7436 | Vernon | CA | Los Angeles | JH5 | Petroleum Liquids | IC |  | S | X | X |  |  | 6 | 0.8 | 3.6 | 4 | 3.6 | N |  |  | OS | X | 9 | 1933 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | OVER | [23 empty] | N
Vintage1999 | petroleum | TRUE | 6915 | Galena Electric Utility | 7437 | Galena Electric Utility | AK | Yukon Koyukuk | 1A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.4 | N |  |  | OP | X | 6 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2015 | petroleum | TRUE | 6915 | Galena Electric Utility | 7437 | Galena Electric Utility | AK | Yukon Koyukuk | 2A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.3 | N |  |  | OP | X | 8 | 2015 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N | 0 | 10M | [23 empty] | N | N | N
Vintage2009 | petroleum | TRUE | 6915 | Galena Electric Utility | 7437 | Galena Electric Utility | AK | Yukon Koyukuk | 3A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.4 | N |  |  | OP | X | 6 | 2009 | 9 | 2022 | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2004 | petroleum | TRUE | 6915 | Galena Electric Utility | 7437 | Galena Electric Utility | AK | Yukon Koyukuk | 4A | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.5 | N |  |  | OP | X | 5 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2009 | petroleum | TRUE | 6915 | Galena Electric Utility | 7437 | Galena Electric Utility | AK | Yukon Koyukuk | 5A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.4 | N |  |  | OP | X | 6 | 2009 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1996 | petroleum | TRUE | 11560 | City of Manassas - (VA) | 7438 | Church Street Plant | VA | Prince William | C3A | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1 | 1 | 0.3 | N |  |  | OP | X | 6 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1987 | petroleum | TRUE | 11560 | City of Manassas - (VA) | 7438 | Church Street Plant | VA | Prince William | C5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 2 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1987 | petroleum | TRUE | 11560 | City of Manassas - (VA) | 7438 | Church Street Plant | VA | Prince William | C6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 2 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1992 | petroleum | TRUE | 11560 | City of Manassas - (VA) | 7439 | Godwin Drive Plant | VA | Prince William | C10 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 11 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1990 | petroleum | TRUE | 11560 | City of Manassas - (VA) | 7439 | Godwin Drive Plant | VA | Prince William | C7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 5 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1990 | petroleum | TRUE | 11560 | City of Manassas - (VA) | 7439 | Godwin Drive Plant | VA | Prince William | C8 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 5 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1992 | petroleum | TRUE | 11560 | City of Manassas - (VA) | 7439 | Godwin Drive Plant | VA | Prince William | C9 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 11 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1990 | petroleum | TRUE | 11560 | City of Manassas - (VA) | 7440 | VMEA 1 Credit Gen | VA | Prince William | V10 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.6 | 0.8 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 5 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1990 | petroleum | TRUE | 11560 | City of Manassas - (VA) | 7440 | VMEA 1 Credit Gen | VA | Prince William | V3 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.6 | 0.8 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 5 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1990 | petroleum | TRUE | 11560 | City of Manassas - (VA) | 7440 | VMEA 1 Credit Gen | VA | Prince William | V4 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.6 | 0.8 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 5 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1990 | petroleum | TRUE | 11560 | City of Manassas - (VA) | 7440 | VMEA 1 Credit Gen | VA | Prince William | V5 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.6 | 0.8 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 5 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1990 | petroleum | TRUE | 11560 | City of Manassas - (VA) | 7440 | VMEA 1 Credit Gen | VA | Prince William | V6 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.6 | 0.8 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 5 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1990 | petroleum | TRUE | 11560 | City of Manassas - (VA) | 7440 | VMEA 1 Credit Gen | VA | Prince William | V7 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.6 | 0.8 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 5 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1990 | petroleum | TRUE | 11560 | City of Manassas - (VA) | 7440 | VMEA 1 Credit Gen | VA | Prince William | V8 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.6 | 0.8 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 5 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2009 | petroleum | TRUE | 11560 | City of Manassas - (VA) | 7440 | VMEA 1 Credit Gen | VA | Prince William | V9-1 | Petroleum Liquids | IC |  | J | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 0.3 | N |  |  | OP | X | 4 | 2009 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1992 | petroleum | TRUE | 11560 | City of Manassas - (VA) | 7441 | VMEA Peaking Gen | VA | Prince William | V1 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.6 | 0.8 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 11 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1993 | petroleum | TRUE | 11560 | City of Manassas - (VA) | 7441 | VMEA Peaking Gen | VA | Prince William | V11 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.6 | 0.8 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 7 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1993 | petroleum | TRUE | 11560 | City of Manassas - (VA) | 7441 | VMEA Peaking Gen | VA | Prince William | V12 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.6 | 0.8 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 7 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1992 | petroleum | TRUE | 11560 | City of Manassas - (VA) | 7441 | VMEA Peaking Gen | VA | Prince William | V2 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.6 | 0.8 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 11 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1994 | natural gas peaker | TRUE | 15321 | City of Pratt- (KS) | 7447 | Pratt 2 | KS | Pratt | IC2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 8 | 0.9 | 7.6 | 7.6 | 5 | N |  |  | OP | X | 6 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 12H | [23 empty] | Y | Y | Y
Vintage2004 | natural gas peaker | TRUE | 15321 | City of Pratt- (KS) | 7447 | Pratt 2 | KS | Pratt | IC3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 8 | 0.9 | 7.6 | 7.6 | 5 | N |  |  | OP | X | 4 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 12H | [23 empty] | Y | Y | Y
Vintage1996 | natural gas peaker | TRUE | 40613 | Northern California Power Agny | 7449 | Combustion Turbine Project No 2 | CA | San Joaquin | NA1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 50 | 0.95 | 49.3 | 49.9 | 40 | N |  |  | OP | X | 4 | 1996 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1986 | natural gas peaker | TRUE | 40613 | Northern California Power Agny | 7450 | Alameda | CA | Alameda | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 27.4 | 0.95 | 24.9 | 24.9 | 21.8 | N |  |  | OP | X | 5 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1986 | natural gas peaker | TRUE | 40613 | Northern California Power Agny | 7450 | Alameda | CA | Alameda | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 27.4 | 0.95 | 24.9 | 24.9 | 21.8 | N |  |  | OP | X | 5 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1986 | natural gas peaker | TRUE | 40613 | Northern California Power Agny | 7451 | Lodi | CA | San Joaquin | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 27.4 | 0.95 | 25.2 | 25.2 | 23.3 | N |  |  | SB | Y | 2 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1986 | natural gas peaker | TRUE | 16295 | City of Roseville - (CA) | 7452 | Roseville Power Plant #2 | CA | Placer | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 33 |  | 21.2 | 24.2 | 15 | N |  |  | SB | Y | 4 | 1986 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1986 | natural gas peaker | TRUE | 16295 | City of Roseville - (CA) | 7452 | Roseville Power Plant #2 | CA | Placer | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 33 |  | 21.2 | 24.2 | 15 | N |  |  | SB | Y | 5 | 1986 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1994 | natural gas peaker | TRUE | 20169 | Avista Corp | 7456 | Rathdrum | ID | Kootenai | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 83.2 | 0.8 | 66 | 87.5 | 50 | N |  |  | OP | X | 11 | 1994 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC
Vintage1994 | natural gas peaker | TRUE | 20169 | Avista Corp | 7456 | Rathdrum | ID | Kootenai | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 83.2 | 0.8 | 66 | 87.5 | 50 | N |  |  | OP | X | 11 | 1994 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC
Vintage1985 | hydro | TRUE | 918 | City of Aspen- (CO) | 7458 | Basalt | CO | Eagle | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5 | 0.93 | 4.5 | 4.5 | 0.7 | N |  |  | OP | X | 9 | 1985 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage2009 | petroleum | TRUE | 18963 | Inside Passage Elec Coop, Inc | 7462 | Angoon | AK | Skagway Hoonah Angoon | 1A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 8 | 2009 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: JF |  |  |  | N | N |  | 10M |  |  |  | N | [19 empty] | N | N | N
Vintage1998 | petroleum | TRUE | 18963 | Inside Passage Elec Coop, Inc | 7462 | Angoon | AK | Skagway Hoonah Angoon | 2A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 10 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: JF |  |  |  | N | N |  | 10M |  |  |  | N | [19 empty] | N | N | N
Vintage1990 | petroleum | TRUE | 18963 | Inside Passage Elec Coop, Inc | 7462 | Angoon | AK | Skagway Hoonah Angoon | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 5 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: JF |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1997 | petroleum | TRUE | 18963 | Inside Passage Elec Coop, Inc | 7463 | Hoonah | AK | Skagway Hoonah Angoon | 2A | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.1 | N |  |  | OP | X | 7 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: JF |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2012 | petroleum | TRUE | 18963 | Inside Passage Elec Coop, Inc | 7463 | Hoonah | AK | Skagway Hoonah Angoon | 3A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 8 | 2012 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: JF |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2012 | petroleum | TRUE | 18963 | Inside Passage Elec Coop, Inc | 7463 | Hoonah | AK | Skagway Hoonah Angoon | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 8 | 2012 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: JF |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2017 | petroleum | TRUE | 18963 | Inside Passage Elec Coop, Inc | 7464 | Kake | AK | Wrangell Petersburg | 1B | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 9 | 2017 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: JF |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1993 | petroleum | TRUE | 18963 | Inside Passage Elec Coop, Inc | 7464 | Kake | AK | Wrangell Petersburg | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.1 | N |  |  | OP | X | 5 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: JF |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2017 | petroleum | TRUE | 18963 | Inside Passage Elec Coop, Inc | 7464 | Kake | AK | Wrangell Petersburg | 2A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 9 | 2017 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: JF |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2017 | petroleum | TRUE | 18963 | Inside Passage Elec Coop, Inc | 7464 | Kake | AK | Wrangell Petersburg | 3B | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 9 | 2017 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: JF |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2017 | petroleum | TRUE | 18963 | Inside Passage Elec Coop, Inc | 7464 | Kake | AK | Wrangell Petersburg | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 9 | 2017 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: JF |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1959 | petroleum | TRUE | 11481 | City of Madison - (NE) | 7469 | Madison Utilities | NE | Madison | FM1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.9 | 1.7 | 1.7 | 0.1 | N |  |  | OP | X | 12 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1959 | petroleum | TRUE | 11481 | City of Madison - (NE) | 7469 | Madison Utilities | NE | Madison | FM2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1 | 1 | 0.1 | N |  |  | OP | X | 9 | 1959 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1953 | petroleum | TRUE | 11481 | City of Madison - (NE) | 7469 | Madison Utilities | NE | Madison | FM3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 4 | 1953 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2006 | petroleum | TRUE | 11481 | City of Madison - (NE) | 7469 | Madison Utilities | NE | Madison | FM5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.4 | 0.8 | 1 | 1 | 0.1 | N |  |  | OP | X | 3 | 2006 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1989 | petroleum | TRUE | 11626 | City of Marceline - (MO) | 7470 | Marceline | MO | Linn | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.3 | N |  |  | SB | Y | 8 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2002 | petroleum | TRUE | 11626 | City of Marceline - (MO) | 7470 | Marceline | MO | Linn | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 1 | N |  |  | SB | Y | 3 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: NG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2004 | petroleum | TRUE | 11626 | City of Marceline - (MO) | 7470 | Marceline | MO | Linn | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1 | N |  |  | SB | Y | 2 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2004 | petroleum | TRUE | 11626 | City of Marceline - (MO) | 7470 | Marceline | MO | Linn | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1 | N |  |  | SB | Y | 2 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1988 | hydro | TRUE | 16198 | City of Rock Falls - (IL) | 7474 | Upper Sterling | IL | Whiteside | 1 | Conventional Hydroelectric | HY |  | S | X | X | PJM/ComEd.ROCKFALLS | PJM/ComEd.ROCKFALLS | 1.1 | 0.8 | 1 | 1 | 0.5 | N |  |  | OP | X | 6 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1988 | hydro | TRUE | 16198 | City of Rock Falls - (IL) | 7474 | Upper Sterling | IL | Whiteside | 2 | Conventional Hydroelectric | HY |  | S | X | X | PJM/ComEd.ROCKFALLS | PJM/ComEd.ROCKFALLS | 1.1 | 0.8 | 1 | 1 | 0.5 | N |  |  | OP | X | 6 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1987 | petroleum | TRUE | 14164 | City of Orangeburg - (SC) | 7479 | North Road Peak | SC | Orangeburg | EAST | Petroleum Liquids | IC |  | S | X | X |  |  | 7 | 0.9 | 6.5 | 7 | 1 | N |  |  | OP | X | 4 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1987 | petroleum | TRUE | 14164 | City of Orangeburg - (SC) | 7479 | North Road Peak | SC | Orangeburg | WEST | Petroleum Liquids | IC |  | S | X | X |  |  | 7 | 0.9 | 6.5 | 7 | 1 | N |  |  | OP | X | 4 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  |  | N |  | 1H | [23 empty] | N | N | N
Vintage1994 | natural gas peaker | TRUE | 14164 | City of Orangeburg - (SC) | 7480 | Rowesville Rd Plant | SC | Orangeburg | GEN3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 4.8 | 0.9 | 4.2 | 4.8 | 0.5 | N |  |  | OP | X | 6 | 1994 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1994 | natural gas peaker | TRUE | 14164 | City of Orangeburg - (SC) | 7480 | Rowesville Rd Plant | SC | Orangeburg | GEN4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 4.8 | 0.9 | 4.2 | 4.8 | 0.5 | N |  |  | OP | X | 6 | 1994 |  |  | N | Electric Utility | 1 | [12 empty] | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1987 | petroleum | TRUE | 20848 | City of Blue Hill - (NE) | 7481 | City Light & Water | NE | Webster | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.9 | 0.9 | 0.2 | N |  |  | OP | X | 1 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1987 | petroleum | TRUE | 20848 | City of Blue Hill - (NE) | 7481 | City Light & Water | NE | Webster | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 1 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2003 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7482 | NSB Atqasuk Utility | AK | North Slope | NA1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.9 | 0.9 | 0.2 | N |  |  | OP | X | 2 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage2003 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7482 | NSB Atqasuk Utility | AK | North Slope | NA2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.9 | 0.9 | 0.2 | N |  |  | OP | X | 2 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage2003 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7482 | NSB Atqasuk Utility | AK | North Slope | NA3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.3 | N |  |  | OP | X | 2 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1986 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7482 | NSB Atqasuk Utility | AK | North Slope | PG2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 8 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1986 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7482 | NSB Atqasuk Utility | AK | North Slope | PG3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.4 | N |  |  | OP | X | 8 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage2000 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7483 | NSB Kaktovik Utility | AK | North Slope | PG1A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.9 | 0.9 | 0.4 | N |  |  | OP | X | 9 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2000 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7483 | NSB Kaktovik Utility | AK | North Slope | PG2A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.9 | 0.9 | 0.4 | N |  |  | OP | X | 9 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage2000 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7483 | NSB Kaktovik Utility | AK | North Slope | PG3A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 9 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage2000 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7483 | NSB Kaktovik Utility | AK | North Slope | PG4A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 9 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1999 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7484 | NSB Nuiqsut Utility | AK | North Slope | PG1A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.9 | 0.9 | 0.4 | N |  |  | OP | X | 9 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1999 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7484 | NSB Nuiqsut Utility | AK | North Slope | PG2A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.9 | 0.9 | 0.4 | N |  |  | OP | X | 9 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1999 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7484 | NSB Nuiqsut Utility | AK | North Slope | PG3A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 9 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage2013 | natural gas peaker | TRUE | 26616 | North Slope Borough Power & Light | 7484 | NSB Nuiqsut Utility | AK | North Slope | PG3B | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.3 | N |  |  | OP | X | 4 | 2013 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage2008 | natural gas peaker | TRUE | 26616 | North Slope Borough Power & Light | 7484 | NSB Nuiqsut Utility | AK | North Slope | PG5A | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 10 | 2008 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2008 | natural gas peaker | TRUE | 26616 | North Slope Borough Power & Light | 7484 | NSB Nuiqsut Utility | AK | North Slope | PG6A | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 10 | 2008 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2014 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7485 | NSB Point Hope Utility | AK | North Slope | PG1A | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.1 | N |  |  | OP | X | 9 | 2014 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1995 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7485 | NSB Point Hope Utility | AK | North Slope | PG6 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 9 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1995 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7485 | NSB Point Hope Utility | AK | North Slope | PG7 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 9 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage2008 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7485 | NSB Point Hope Utility | AK | North Slope | PG8 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.9 | 0.9 | 0.4 | N |  |  | OP | X | 8 | 2008 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage2013 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7486 | NSB Point Lay Utility | AK | North Slope | PG10 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 7 | 2013 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage2013 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7486 | NSB Point Lay Utility | AK | North Slope | PG7 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 7 | 2013 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage2013 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7486 | NSB Point Lay Utility | AK | North Slope | PG8 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.3 | N |  |  | OP | X | 7 | 2013 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage2013 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7486 | NSB Point Lay Utility | AK | North Slope | PG9 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.3 | N |  |  | OP | X | 7 | 2013 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1994 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7487 | NSB Anaktuvuk Pass | AK | North Slope | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 9 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1994 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7487 | NSB Anaktuvuk Pass | AK | North Slope | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 9 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1994 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7487 | NSB Anaktuvuk Pass | AK | North Slope | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 9 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage2003 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7487 | NSB Anaktuvuk Pass | AK | North Slope | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.9 | 0.9 | 0.4 | N |  |  | OP | X | 12 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage2003 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7487 | NSB Anaktuvuk Pass | AK | North Slope | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.9 | 0.9 | 0.4 | N |  |  | OP | X | 12 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1988 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7488 | NSB Wainwright Utility | AK | North Slope | PG1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 8 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1988 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7488 | NSB Wainwright Utility | AK | North Slope | PG2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 8 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1989 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7488 | NSB Wainwright Utility | AK | North Slope | PG3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 8 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage2001 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7488 | NSB Wainwright Utility | AK | North Slope | PG4A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.9 | 0.9 | 0.4 | N |  |  | OP | X | 10 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage2001 | petroleum | TRUE | 26616 | North Slope Borough Power & Light | 7488 | NSB Wainwright Utility | AK | North Slope | PG5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.9 | 0.9 | 0.4 | N |  |  | OP | X | 10 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1987 | hydro | TRUE | 19397 | City of Ukiah - (CA) | 7489 | Lake Mendocino | CA | Mendocino | G1 | Conventional Hydroelectric | HY |  | S | X | X | N/A | N/A | 1 | 0.9 | 1 | 1 | 0.1 | N |  |  | OP | X | 5 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N |  | N
Vintage1987 | hydro | TRUE | 19397 | City of Ukiah - (CA) | 7489 | Lake Mendocino | CA | Mendocino | G2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 0.1 | N |  |  | OP | X | 5 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N |  | N
Vintage1980 | petroleum | TRUE | 9897 | City of King Cove | 7493 | King Cove | AK | Aleutians East | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.2 | N |  |  | OP | X | 2 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N | N
Vintage1986 | petroleum | TRUE | 9897 | City of King Cove | 7493 | King Cove | AK | Aleutians East | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 1 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N | N
Vintage1992 | petroleum | TRUE | 9897 | City of King Cove | 7493 | King Cove | AK | Aleutians East | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.7 | 0.8 | 0.6 | 0.6 | 0.6 | N |  |  | OP | X | 6 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N | N | N
Vintage1995 | hydro | TRUE | 9897 | City of King Cove | 7493 | King Cove | AK | Aleutians East | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.7 | 0.2 | 0.6 | N |  |  | OP | X | 2 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1980 | petroleum | TRUE | 9897 | City of King Cove | 7493 | King Cove | AK | Aleutians East | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.2 | N |  |  | OP | X | 2 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N | N
Vintage1982 | petroleum | TRUE | 4562 | City of Croswell - (MI) | 7497 | Croswell | MI | Sanilac | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.9 | 0.6 | 0.6 | 0.3 | N |  |  | SB | Y | 11 | 1982 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: NG |  |  |  | N |  |  | 1H | [23 empty] | Y | N | N
Vintage1984 | petroleum | TRUE | 4562 | City of Croswell - (MI) | 7497 | Croswell | MI | Sanilac | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.7 | 0.9 | 0.7 | 0.7 | 0.3 | N |  |  | SB | Y | 11 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: NG |  |  |  | N |  |  | 1H | [23 empty] | Y | N | N
Vintage1988 | petroleum | TRUE | 4562 | City of Croswell - (MI) | 7497 | Croswell | MI | Sanilac | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.9 | 1.2 | 1.2 | 0.6 | N |  |  | SB | Y | 11 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1990 | petroleum | TRUE | 4562 | City of Croswell - (MI) | 7497 | Croswell | MI | Sanilac | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.9 | 1.3 | 1.3 | 0.6 | N |  |  | SB | Y | 11 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: NG |  |  |  | N |  |  | 1H | [23 empty] | Y | N | N
Vintage1996 | petroleum | TRUE | 4562 | City of Croswell - (MI) | 7497 | Croswell | MI | Sanilac | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.9 | 1.3 | 1.3 | 0.6 | N |  |  | SB | Y | 10 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: NG |  |  |  | N |  |  | 1H | [23 empty] | Y | N | N
Vintage2010 | onshore wind | TRUE | 15371 | Town of Princeton - (MA) | 7501 | Princeton Wind Farm | MA | Worcester | 2 | Onshore Wind Turbine | WT |  | S | X | X | WCMASS | WCMASS | 3 |  | 3 | 3 | 0.1 | N |  |  | OP | X | 1 | 2010 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WND |  |  |  | N | N | 2 | 10M | [23 empty] | N
Vintage2010 | petroleum | TRUE | 19454 | City of Unalaska - (AK) | 7502 | Dutch Harbor | AK | Aleutians West | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 5.2 | 0.8 | 4.4 | 4.4 | 3.1 | N |  |  | OP | X | 11 | 2010 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2010 | petroleum | TRUE | 19454 | City of Unalaska - (AK) | 7502 | Dutch Harbor | AK | Aleutians West | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 5.2 | 0.8 | 4.4 | 4.4 | 3.1 | N |  |  | OP | X | 11 | 2010 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2015 | petroleum | TRUE | 19454 | City of Unalaska - (AK) | 7502 | Dutch Harbor | AK | Aleutians West | 12 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.4 | 0.8 | 3.7 | 3.7 | 2.6 | N |  |  | OP | X | 4 | 2015 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2011 | petroleum | TRUE | 19454 | City of Unalaska - (AK) | 7502 | Dutch Harbor | AK | Aleutians West | 13 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.4 | 0.8 | 3.7 | 3.7 | 2.6 | N |  |  | OP | X | 12 | 2011 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2010 | petroleum | TRUE | 19454 | City of Unalaska - (AK) | 7502 | Dutch Harbor | AK | Aleutians West | 15 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.2 | 0.2 | 0.2 | N |  |  | SB | Y | 11 | 2010 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage1989 | petroleum | TRUE | 19454 | City of Unalaska - (AK) | 7502 | Dutch Harbor | AK | Aleutians West | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1 | 1 | 0.6 | N |  |  | OP | X | 11 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1994 | petroleum | TRUE | 19454 | City of Unalaska - (AK) | 7502 | Dutch Harbor | AK | Aleutians West | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1 | 1 | 0.6 | N |  |  | OP | X | 5 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1993 | petroleum | TRUE | 19454 | City of Unalaska - (AK) | 7503 | Unalaska Power Module | AK | Aleutians West | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 11 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1995 | hard coal | TRUE | 19545 | Black Hills Power, Inc. | 7504 | Neil Simpson II | WY | Campbell | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 90 | 0.9 | 80 | 80 | 52 | N |  |  | OP | X | 9 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; SUB SUB SUB: NG; DFO DFO DFO: NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | N |  |  | N | N | N
Vintage2000 | natural gas peaker | TRUE | 19545 | Black Hills Power, Inc. | 7504 | Neil Simpson II | WY | Campbell | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 40 | 0.9 | 34 | 37 | 24.7 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC
Vintage1993 | hydro | TRUE | 61958 | Hydro Sierra Energy, LLC | 7507 | Deadwood Creek | CA | Yuba | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.9 | 1.9 | 2 | 0.1 | N |  |  | OP | X | 12 | 1993 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage1994 | hydro | TRUE | 6013 | Eugene Water & Electric Board | 7508 | Stone Creek | OR | Clackamas | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 12 | 0.9 | 7 | 10.7 | 3 | N |  |  | OP | X | 1 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1997 | hydro | TRUE | 13788 | Northern Wasco County PUD | 7511 | McNary Dam Fish Attraction Project | WA | Benton | 1 | Conventional Hydroelectric | HY |  | J | X | X |  |  | 10 | 0.9 | 9 | 9 | 8.5 | N |  |  | OP | X | 11 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2000 | natural gas combined cycle | TRUE | 16604 | City of San Antonio - (TX) | 7512 | Arthur Von Rosenberg | TX | Bexar | 1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | BRA_AVR_CST1 | BRA_AVR_CST1 | 187.5 | 0.9 | 164 | 176 | 90 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [7 empty] | 10 | 10 | 12 | 2023 | [12 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2000 | natural gas combined cycle | TRUE | 16604 | City of San Antonio - (TX) | 7512 | Arthur Von Rosenberg | TX | Bexar | 2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | BRA_AVR1_CT2 | BRA_AVR1_CT2 | 187.5 | 0.9 | 164 | 176 | 90 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [7 empty] | 10 | 10 | 12 | 2024 | [12 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2000 | natural gas combined cycle | TRUE | 16604 | City of San Antonio - (TX) | 7512 | Arthur Von Rosenberg | TX | Bexar | 3 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | BRA_AVR_CST1 | BRA_AVR_CST1 | 200 | 0.9 | 190 | 197 | 60 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1998 | natural gas peaker | TRUE | 12208 | City of McPherson - (KS) | 7515 | McPherson 3 | KS | McPherson | NA1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 115.6 | 0.9 | 80.2 | 99.9 | 45 | N |  |  | OP | X | 10 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1994 | onshore wind | TRUE | 16534 | Sacramento Municipal Util Dist | 7526 | Solano Wind | CA | Solano | 1 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 13.2 |  | 13.1 | 13.2 | 1 | N |  |  | OP | X | 6 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WND |  |  |  | N | N | 23
Vintage2006 | onshore wind | TRUE | 16534 | Sacramento Municipal Util Dist | 7526 | Solano Wind | CA | Solano | 2 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 24 |  | 24 | 24 | 1 | N |  |  | OP | X | 6 | 2006 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WND |  |  |  | N | N | 8
Vintage2007 | onshore wind | TRUE | 16534 | Sacramento Municipal Util Dist | 7526 | Solano Wind | CA | Solano | 2B | Onshore Wind Turbine | WT |  | S | X | X |  |  | 63 |  | 63 | 63 | 1 | N |  |  | OP | X | 12 | 2007 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WND |  |  |  | N | N | 21
Vintage2012 | onshore wind | TRUE | 16534 | Sacramento Municipal Util Dist | 7526 | Solano Wind | CA | Solano | 3 | Onshore Wind Turbine | WT |  | W | X | X |  |  | 128 |  | 128 | 128 | 1 | N |  |  | OP | X | 4 | 2012 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WND |  |  |  | N | N | 55
Vintage1995 | natural gas peaker | TRUE | 16534 | Sacramento Municipal Util Dist | 7527 | Carson Ice-Gen Project | CA | Sacramento | 1 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 54 | 0.9 | 41.2 | 41.2 | 20 | N |  |  | OP | X | 10 | 1995 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage1995 | natural gas combined cycle | TRUE | 16534 | Sacramento Municipal Util Dist | 7527 | Carson Ice-Gen Project | CA | Sacramento | 2 | Natural Gas Fired Combined Cycle | CA | CC1 | W | Y | X |  |  | 17.5 | 0.85 | 16.6 | 16.6 | 2 | N |  |  | OP | X | 10 | 1995 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X X X to RC RC RC
Vintage1995 | natural gas combined cycle | TRUE | 16534 | Sacramento Municipal Util Dist | 7527 | Carson Ice-Gen Project | CA | Sacramento | CCCT | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N |  |  | 54 | 0.9 | 51.2 | 51.2 | 21 | N |  |  | OP | X | 10 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: OBG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage2000 | natural gas peaker | TRUE | 3046 | Duke Energy Progress - (NC) | 7538 | Wayne County | NC | Wayne | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 195.2 | 0.85 | 169 | 195 | 100 | N |  |  | OP | X | 5 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 3046 | Duke Energy Progress - (NC) | 7538 | Wayne County | NC | Wayne | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 195.2 | 0.85 | 174 | 195 | 100 | N |  |  | OP | X | 5 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 3046 | Duke Energy Progress - (NC) | 7538 | Wayne County | NC | Wayne | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 195.2 | 0.85 | 164 | 195 | 100 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 3046 | Duke Energy Progress - (NC) | 7538 | Wayne County | NC | Wayne | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 195.2 | 0.85 | 162 | 195 | 100 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2009 | natural gas peaker | TRUE | 3046 | Duke Energy Progress - (NC) | 7538 | Wayne County | NC | Wayne | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 198.9 | 0.85 | 153 | 195 | 100 | N |  |  | OP | X | 6 | 2009 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1994 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 7541 | Spirit Mountain | WY | Park | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.5 | 0.9 | 4.5 | 4.5 | 0 | N |  |  | OP | X | 10 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1989 | hydro | TRUE | 14077 | Oklahoma Municipal Power Authority | 7545 | Kaw Hydro | OK | Kay | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 37 | 0.85 | 29.6 | 29.6 | 2 | N |  |  | OP | X | 8 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1966 | natural gas combined cycle | TRUE | 14077 | Oklahoma Municipal Power Authority | 7546 | Ponca City | OK | Kay | 1 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 19.8 | 0.85 | 18.8 | 18.8 | 1.5 | N |  |  | OP | X | 10 | 1966 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage1995 | natural gas combined cycle | TRUE | 14077 | Oklahoma Municipal Power Authority | 7546 | Ponca City | OK | Kay | 3 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 54 | 0.85 | 44.1 | 44.1 | 33 | N |  |  | OP | X | 6 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2003 | natural gas peaker | TRUE | 14077 | Oklahoma Municipal Power Authority | 7546 | Ponca City | OK | Kay | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 60.5 | 0.9 | 43.9 | 43.9 | 33 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage1998 | hydro | TRUE | 20255 | Weber Basin Water Conserv Dist | 7548 | Causey | UT | Weber | 1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.5 | 0.9 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 1 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 12H | [20 empty] | N |  |  | N
Vintage1998 | hydro | TRUE | 20255 | Weber Basin Water Conserv Dist | 7548 | Causey | UT | Weber | 2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.6 | 0.9 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 1 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 12H | [20 empty] | N |  |  | N
Vintage2021 | hydro | TRUE | 20255 | Weber Basin Water Conserv Dist | 7548 | Causey | UT | Weber | MINI | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.1 | 0.8 | 0.1 | 0.1 | 0 | N |  |  | OP | X | 3 | 2021 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M | [20 empty] | N |  |  | N
Vintage1997 | natural gas combined cycle | TRUE | 16534 | Sacramento Municipal Util Dist | 7551 | SCA Cogen 2 | CA | Sacramento | CCST | Natural Gas Fired Combined Cycle | CA | CCC1 | W | Y | X |  |  | 49.8 | 0.9 | 37.6 | 37.6 | 4.5 | N |  |  | OP | X | 3 | 1997 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1997 | natural gas combined cycle | TRUE | 16534 | Sacramento Municipal Util Dist | 7551 | SCA Cogen 2 | CA | Sacramento | CT1A | Natural Gas Fired Combined Cycle | CT | CCC1 | W | X | Y |  |  | 49.8 | 0.9 | 47.6 | 47.6 | 35 | N |  |  | OP | X | 5 | 1997 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1997 | natural gas combined cycle | TRUE | 16534 | Sacramento Municipal Util Dist | 7551 | SCA Cogen 2 | CA | Sacramento | CT1B | Natural Gas Fired Combined Cycle | CT | CCC1 | W | X | Y |  |  | 49.8 | 0.9 | 47.6 | 47.6 | 35 | N |  |  | OP | X | 3 | 1997 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 16534 | Sacramento Municipal Util Dist | 7551 | SCA Cogen 2 | CA | Sacramento | CT1C | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 44 | 0.9 | 43.8 | 47.3 | 20 | N |  |  | OP | X | 4 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage1997 | natural gas combined cycle | TRUE | 16534 | Sacramento Municipal Util Dist | 7552 | SPA Cogen 3 | CA | Sacramento | CCCT | Natural Gas Fired Combined Cycle | CT | CCC1 | W | X | Y |  |  | 118.7 | 0.9 | 119 | 111 | 55 | N |  |  | OP | X | 12 | 1997 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1997 | natural gas combined cycle | TRUE | 16534 | Sacramento Municipal Util Dist | 7552 | SPA Cogen 3 | CA | Sacramento | CCST | Natural Gas Fired Combined Cycle | CA | CCC1 | W | Y | X |  |  | 55.2 | 0.85 | 59 | 53 | 36 | N |  |  | OP | X | 12 | 1997 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1998 | natural gas peaker | TRUE | 13334 | City of Nebraska City | 7555 | Nebraska City # 2 | NE | Otoe | 11 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 4.5 | 0.8 | 4 | 4 | 3.5 | N |  |  | OP | X | 8 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1998 | natural gas peaker | TRUE | 13334 | City of Nebraska City | 7555 | Nebraska City # 2 | NE | Otoe | 12 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 4.5 | 0.8 | 4 | 4 | 3.5 | N |  |  | OP | X | 8 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1998 | petroleum | TRUE | 13334 | City of Nebraska City | 7555 | Nebraska City # 2 | NE | Otoe | 13 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.5 | 0.8 | 4.2 | 4.2 | 3 | N |  |  | OP | X | 11 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1996 | petroleum | FALSE | 56076 | State Farm Insurance | 7556 | State Farm | IL | McLean | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.7 | 0.8 | 1.7 | 1.7 | 0 | N |  |  | SB | Y | 10 | 1996 |  |  | N | Commercial Non-CHP | 4 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1996 | petroleum | FALSE | 56076 | State Farm Insurance | 7556 | State Farm | IL | McLean | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.7 | 0.8 | 1.7 | 1.7 | 0 | N |  |  | SB | Y | 10 | 1996 |  |  | N | Commercial Non-CHP | 4 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1996 | petroleum | FALSE | 56076 | State Farm Insurance | 7556 | State Farm | IL | McLean | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.7 | 0.8 | 1.7 | 1.7 | 0 | N |  |  | SB | Y | 10 | 1996 |  |  | N | Commercial Non-CHP | 4 | X X X: X; RC RC RC: DFO |  |  |  | N | N | 0 | 10M | [23 empty] | N | N | N
Vintage1986 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 7583 | Talcville | NY | St Lawrence | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24044 | 24044 | 1 | 0.8 | 0.7 | 0.7 | 0.4 | N |  |  | OP | X | 1 | 1986 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1986 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 7583 | Talcville | NY | St Lawrence | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24044 | 24044 | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 1 | 1986 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1988 | petroleum | TRUE | 14433 | City of Panora - (IA) | 7584 | Panora | IA | GUTHRIE | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.5 | N |  |  | SB | Y | 1 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1988 | petroleum | TRUE | 14433 | City of Panora - (IA) | 7584 | Panora | IA | GUTHRIE | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.5 | N |  |  | SB | Y | 1 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1993 | petroleum | TRUE | 14433 | City of Panora - (IA) | 7584 | Panora | IA | GUTHRIE | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.5 | N |  |  | SB | Y | 1 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1984 | hydro | TRUE | 17470 | PUD 1 of Snohomish County | 7588 | H M Jackson | WA | Snohomish | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 47.5 | 0.9 | 41 | 44 | 5 | N |  |  | OP | X | 6 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1984 | hydro | TRUE | 17470 | PUD 1 of Snohomish County | 7588 | H M Jackson | WA | Snohomish | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 47.5 | 0.9 | 41 | 44 | 5 | N |  |  | OP | X | 6 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1984 | hydro | TRUE | 17470 | PUD 1 of Snohomish County | 7588 | H M Jackson | WA | Snohomish | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8.4 | 0.9 | 7 | 8 | 0.5 | N |  |  | OP | X | 6 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1984 | hydro | TRUE | 17470 | PUD 1 of Snohomish County | 7588 | H M Jackson | WA | Snohomish | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8.4 | 0.9 | 7 | 8 | 0.5 | N |  |  | OP | X | 6 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1988 | hydro | TRUE | 11204 | Los Alamos County | 7593 | El Vado Dam | NM | Rio Arriba | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8 | 0.9 | 8 | 8 | 1 | N |  |  | OP | X | 5 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage1999 | hydro | TRUE | 40577 | American Mun Power-Ohio, Inc | 7594 | Belleville Dam | WV | Wood | 1 | Conventional Hydroelectric | HY |  | J | X | X | BELLEV12 | BELLEV12 | 21 | 0.9 | 21 | 21 | 3 | N |  |  | OP | X | 6 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1999 | hydro | TRUE | 40577 | American Mun Power-Ohio, Inc | 7594 | Belleville Dam | WV | Wood | 2 | Conventional Hydroelectric | HY |  | J | X | X | BELLEV12 | BELLEV12 | 21 | 0.9 | 21 | 21 | 3 | N |  |  | OP | X | 6 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1998 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7603 | Prospect Municipal | OH | Marion | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | SB | Y | 2 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | natural gas combined cycle | TRUE | 924 | Associated Electric Coop, Inc | 7604 | St Francis Energy Facility | MO | Dunklin | 1 | Natural Gas Fired Combined Cycle | CS |  | S | N | N |  |  | 253.3 | 0.85 | 241 | 241 | 183 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H |  |  |  |  | N | [15 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC
Vintage2001 | natural gas combined cycle | TRUE | 924 | Associated Electric Coop, Inc | 7604 | St Francis Energy Facility | MO | Dunklin | 2 | Natural Gas Fired Combined Cycle | CS |  | S | N | N |  |  | 253.3 | 0.85 | 213 | 220 | 183 | N |  |  | OP | X | 4 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H |  |  |  |  | N |  |  | 7 | 10 | 10 | 2023 | [9 empty] | Y | 10 | 2023 | N | N | N | bar: X X X to RC RC RC
Vintage1997 | natural gas combined cycle | TRUE | 3660 | PUD No 1 of Clark County - (WA) | 7605 | River Road Gen Plant | WA | Clark | 1 | Natural Gas Fired Combined Cycle | CS |  | S | N | N |  |  | 248 | 0.85 | 220 | 248 | 205 | N |  |  | OP | X | 12 | 1997 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [7 empty] | 5 | 7 | 5 | 2023 | [12 empty] | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage1983 | hydro | TRUE | 22776 | Solano Irrigation District | 7646 | Monticello Dam | CA | Solano | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5 | 0.9 | 5 | 5 | 1.6 | N |  |  | OP | X | 6 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | N
Vintage1983 | hydro | TRUE | 22776 | Solano Irrigation District | 7646 | Monticello Dam | CA | Solano | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5 | 0.9 | 5 | 5 | 1.6 | N |  |  | OP | X | 6 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | N
Vintage1983 | hydro | TRUE | 22776 | Solano Irrigation District | 7646 | Monticello Dam | CA | Solano | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 0.9 | 1.5 | 1.5 | 0.7 | N |  |  | OP | X | 6 | 1983 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | N
Vintage1986 | hydro | TRUE | 2439 | City of Bryan - (OH) | 7657 | Auglaize Hydro | OH | Defiance | 1 | Conventional Hydroelectric | HY |  | S | X | X | PJM AEP Dayton | PJM AEP Dayton | 0.7 | 0.8 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 12 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage2004 | hydro | TRUE | 2439 | City of Bryan - (OH) | 7657 | Auglaize Hydro | OH | Defiance | 2A | Conventional Hydroelectric | HY |  | S | X | X | PJM AEP Dayton | PJM AEP Dayton | 0.9 | 0.8 | 1 | 1 | 0.6 | N |  |  | OP | X | 7 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2004 | hydro | TRUE | 2439 | City of Bryan - (OH) | 7657 | Auglaize Hydro | OH | Defiance | 3A | Conventional Hydroelectric | HY |  | S | X | X | PJM AEP Dayton | PJM AEP Dayton | 0.9 | 0.8 | 1 | 1 | 0.6 | N |  |  | OP | X | 6 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1987 | hydro | TRUE | 2439 | City of Bryan - (OH) | 7657 | Auglaize Hydro | OH | Defiance | 4 | Conventional Hydroelectric | HY |  | S | X | X | PJM AEP Dayton | PJM AEP Dayton | 0.5 | 0.8 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 1 | 1987 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1988 | hydro | TRUE | 2439 | City of Bryan - (OH) | 7657 | Auglaize Hydro | OH | Defiance | 5 | Conventional Hydroelectric | HY |  | S | X | X | PJM AEP Dayton | PJM AEP Dayton | 0.5 | 0.8 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 6 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage2004 | hydro | TRUE | 2439 | City of Bryan - (OH) | 7657 | Auglaize Hydro | OH | Defiance | 6 | Conventional Hydroelectric | HY |  | S | X | X | PJM AEP Dayton | PJM AEP Dayton | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 6 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1996 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 7690 | Pennsbury | PA | Bucks | 1 | Landfill Gas | GT |  | S | X | X | FALLS 4 KV PENSBRY1 | FALLS 4 KV PENSBRY1 | 3 | 0.8 | 2 | 2.8 | 1 | N |  |  | OS | X | 9 | 1996 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: LFG; DFO DFO DFO: PG |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1996 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 7690 | Pennsbury | PA | Bucks | 2 | Landfill Gas | GT |  | S | X | X | FALLS 4 KV PENSBRY2 | FALLS 4 KV PENSBRY2 | 3 | 0.8 | 2 | 2.8 | 1 | N |  |  | OS | X | 9 | 1996 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: LFG; DFO DFO DFO: PG |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1999 | natural gas combined cycle | TRUE | 195 | Alabama Power Co | 7697 | Washington County Cogeneration Facility | AL | Washington | 1 | Natural Gas Fired Combined Cycle | CT | G523 | S | X | N |  |  | 82.6 | 0.85 | 75 | 82 | 75 | N |  |  | OP | X | 2 | 1999 |  |  | Y | Electric Utility | 1 | [14 empty] | 12H | [23 empty] | N | bar: X X X to RC RC RC
Vintage1999 | natural gas combined cycle | TRUE | 195 | Alabama Power Co | 7697 | Washington County Cogeneration Facility | AL | Washington | 2 | Natural Gas Fired Combined Cycle | CA | G523 | S | Y | X |  |  | 39.9 | 0.85 | 25 | 25 | 25 | N |  |  | OP | X | 2 | 1999 |  |  | Y | Electric Utility | 1 | [14 empty] | 12H | [23 empty] | N | bar: X X X to RC RC RC
Vintage1999 | natural gas combined cycle | TRUE | 195 | Alabama Power Co | 7698 | General Electric Plastic | AL | Lowndes | 1 | Natural Gas Fired Combined Cycle | CT | G524 | S | X | N |  |  | 82.2 | 0.85 | 74 | 84 | 50 | N |  |  | OP | X | 7 | 1999 |  |  | Y | Electric Utility | 1 | [14 empty] | 12H | [23 empty] | N | bar: X X X to RC RC RC
Vintage1999 | natural gas combined cycle | TRUE | 195 | Alabama Power Co | 7698 | General Electric Plastic | AL | Lowndes | 2 | Natural Gas Fired Combined Cycle | CA | G524 | S | Y | X |  |  | 14.8 | 0.85 | 10.5 | 10.5 | 2 | N |  |  | OP | X | 7 | 1999 |  |  | Y | Electric Utility | 1 | [14 empty] | 12H | [23 empty] | N | bar: X X X to RC RC RC
Vintage1997 | natural gas combined cycle | TRUE | 6455 | Duke Energy Florida, LLC | 7699 | Tiger Bay | FL | Polk | CT1 | Natural Gas Fired Combined Cycle | CT | G200 | S | X | N |  |  | 195.2 | 0.85 | 130 | 160 | 120 | N |  |  | OP | X | 8 | 1997 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1997 | natural gas combined cycle | TRUE | 6455 | Duke Energy Florida, LLC | 7699 | Tiger Bay | FL | Polk | CW1 | Natural Gas Fired Combined Cycle | CA | G200 | S | N | X |  |  | 82.9 | 0.85 | 69 | 70 | 69 | N |  |  | OP | X | 8 | 1997 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2000 | natural gas peaker | TRUE | 17650 | Southern Power Co | 7709 | Dahlberg | GA | Jackson | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 91.9 | 0.85 | 74.8 | 87.1 | 70 | N |  |  | OP | X | 6 | 2000 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 17650 | Southern Power Co | 7709 | Dahlberg | GA | Jackson | 10 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 91.9 | 0.85 | 75.2 | 88.6 | 70 | N |  |  | OP | X | 5 | 2001 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 17650 | Southern Power Co | 7709 | Dahlberg | GA | Jackson | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 91.9 | 0.85 | 74 | 87.4 | 70 | N |  |  | OP | X | 6 | 2000 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 17650 | Southern Power Co | 7709 | Dahlberg | GA | Jackson | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 91.9 | 0.85 | 74.7 | 87.8 | 70 | N |  |  | OP | X | 6 | 2000 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 17650 | Southern Power Co | 7709 | Dahlberg | GA | Jackson | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 91.9 | 0.85 | 73.5 | 86.9 | 70 | N |  |  | OP | X | 6 | 2000 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 17650 | Southern Power Co | 7709 | Dahlberg | GA | Jackson | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 91.9 | 0.85 | 74.7 | 87.7 | 70 | N |  |  | OP | X | 6 | 2000 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 17650 | Southern Power Co | 7709 | Dahlberg | GA | Jackson | 6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 91.9 | 0.85 | 74.9 | 87.7 | 70 | N |  |  | OP | X | 7 | 2000 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 17650 | Southern Power Co | 7709 | Dahlberg | GA | Jackson | 7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 91.9 | 0.85 | 75 | 88 | 70 | N |  |  | OP | X | 6 | 2000 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 17650 | Southern Power Co | 7709 | Dahlberg | GA | Jackson | 8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 91.9 | 0.85 | 74 | 87 | 70 | N |  |  | OP | X | 6 | 2000 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 17650 | Southern Power Co | 7709 | Dahlberg | GA | Jackson | 9 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 91.9 | 0.85 | 74.8 | 88 | 70 | N |  |  | OP | X | 5 | 2001 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas combined cycle | TRUE | 17650 | Southern Power Co | 7710 | H Allen Franklin Combined Cycle | AL | Lee | CT1A | Natural Gas Fired Combined Cycle | CT | G481 | S | X | N |  |  | 203.1 | 0.85 | 177.5 | 188.5 | 115 | N |  |  | OP | X | 6 | 2002 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2002 | natural gas combined cycle | TRUE | 17650 | Southern Power Co | 7710 | H Allen Franklin Combined Cycle | AL | Lee | CT1B | Natural Gas Fired Combined Cycle | CT | G481 | S | X | N |  |  | 203.1 | 0.85 | 177.5 | 188.5 | 115 | N |  |  | OP | X | 6 | 2002 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2002 | natural gas combined cycle | TRUE | 17650 | Southern Power Co | 7710 | H Allen Franklin Combined Cycle | AL | Lee | CT2A | Natural Gas Fired Combined Cycle | CT | G501 | S | X | N |  |  | 203.1 | 0.85 | 177.8 | 190.3 | 125 | N |  |  | OP | X | 6 | 2002 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2002 | natural gas combined cycle | TRUE | 17650 | Southern Power Co | 7710 | H Allen Franklin Combined Cycle | AL | Lee | CT2B | Natural Gas Fired Combined Cycle | CT | G501 | S | X | N |  |  | 203.1 | 0.85 | 177.8 | 190.3 | 125 | N |  |  | OP | X | 6 | 2002 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2008 | natural gas combined cycle | TRUE | 17650 | Southern Power Co | 7710 | H Allen Franklin Combined Cycle | AL | Lee | CT3A | Natural Gas Fired Combined Cycle | CT | G100 | S | X | N |  |  | 203.1 | 0.85 | 182.6 | 196.6 | 109 | N |  |  | OP | X | 5 | 2008 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2008 | natural gas combined cycle | TRUE | 17650 | Southern Power Co | 7710 | H Allen Franklin Combined Cycle | AL | Lee | CT3B | Natural Gas Fired Combined Cycle | CT | G100 | S | X | N |  |  | 203.1 | 0.85 | 182.6 | 196.6 | 109 | N |  |  | OP | X | 5 | 2008 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2002 | natural gas combined cycle | TRUE | 17650 | Southern Power Co | 7710 | H Allen Franklin Combined Cycle | AL | Lee | ST1 | Natural Gas Fired Combined Cycle | CA | G481 | S | Y | X |  |  | 213.3 | 0.85 | 240 | 240 | 120 | N |  |  | OP | X | 6 | 2002 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2002 | natural gas combined cycle | TRUE | 17650 | Southern Power Co | 7710 | H Allen Franklin Combined Cycle | AL | Lee | ST2 | Natural Gas Fired Combined Cycle | CA | G501 | S | Y | X |  |  | 281.9 | 0.85 | 293 | 293 | 130 | N |  |  | OP | X | 6 | 2002 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2008 | natural gas combined cycle | TRUE | 17650 | Southern Power Co | 7710 | H Allen Franklin Combined Cycle | AL | Lee | ST3 | Natural Gas Fired Combined Cycle | CA | G100 | S | Y | X |  |  | 281.9 | 0.85 | 293 | 293 | 112 | N |  |  | OP | X | 5 | 2008 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1998 | natural gas peaker | TRUE | 7801 | Gulf Power Co | 7715 | Pea Ridge | FL | Santa Rosa | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 4.7 | 0.8 | 4 | 4.6 | 4 | N |  |  | OP | X | 4 | 1998 | 4 | 2025 | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1998 | natural gas peaker | TRUE | 7801 | Gulf Power Co | 7715 | Pea Ridge | FL | Santa Rosa | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 4.7 | 0.8 | 4 | 4.6 | 4 | N |  |  | OP | X | 4 | 1998 | 4 | 2025 | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1998 | natural gas peaker | TRUE | 7801 | Gulf Power Co | 7715 | Pea Ridge | FL | Santa Rosa | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 4.7 | 0.8 | 4 | 4.6 | 4 | N |  |  | OP | X | 4 | 1998 | 4 | 2025 | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1998 | petroleum | TRUE | 18642 | Tennessee Valley Authority | 7719 | Meridian | MS | Lauderdale | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.9 | 1.8 | 1.8 | 0 | N |  |  | OP | X | 6 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1998 | petroleum | TRUE | 18642 | Tennessee Valley Authority | 7719 | Meridian | MS | Lauderdale | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.9 | 1.8 | 1.8 | 0 | N |  |  | OP | X | 6 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1998 | petroleum | TRUE | 18642 | Tennessee Valley Authority | 7719 | Meridian | MS | Lauderdale | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.9 | 1.8 | 1.8 | 0 | N |  |  | OP | X | 6 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1998 | petroleum | TRUE | 18642 | Tennessee Valley Authority | 7719 | Meridian | MS | Lauderdale | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.9 | 1.8 | 1.8 | 0 | N |  |  | OP | X | 6 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1998 | petroleum | TRUE | 18642 | Tennessee Valley Authority | 7719 | Meridian | MS | Lauderdale | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.9 | 1.8 | 1.8 | 0 | N |  |  | OP | X | 6 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2000 | natural gas combined cycle | TRUE | 195 | Alabama Power Co | 7721 | Theodore Cogen Facility | AL | Mobile | 1 | Natural Gas Fired Combined Cycle | CT | G525 | S | X | N |  |  | 229 | 0.85 | 166.3 | 180.3 | 160 | N |  |  | OP | X | 12 | 2000 |  |  | Y | Electric Utility | 1 | [14 empty] | 12H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2000 | natural gas combined cycle | TRUE | 195 | Alabama Power Co | 7721 | Theodore Cogen Facility | AL | Mobile | 2 | Natural Gas Fired Combined Cycle | CA | G525 | S | Y | X |  |  | 88.4 | 0.85 | 64.7 | 64.7 | 64.7 | N |  |  | OP | X | 12 | 2000 |  |  | Y | Electric Utility | 1 | [14 empty] | 12H | [23 empty] | N | bar: X X X to RC RC RC
Vintage1996 | nuclear | TRUE | 18642 | Tennessee Valley Authority | 7722 | Watts Bar Nuclear Plant | TN | Rhea | 1 | Nuclear | ST |  | S | X | X |  |  | 1269.9 | 0.9 | 1123 | 1179 | 1123 | N |  |  | OP | X | 5 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NUC |  |  |  | N |  |  | OVER | [23 empty] | N
Vintage2016 | nuclear | TRUE | 18642 | Tennessee Valley Authority | 7722 | Watts Bar Nuclear Plant | TN | Rhea | 2 | Nuclear | ST |  | S | X | X |  |  | 1269.9 | 0.9 | 1122 | 1164 | 1122 | N |  |  | OP | X | 6 | 2016 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NUC |  |  |  | N |  |  | OVER | [23 empty] | N
Vintage1994 | petroleum | TRUE | 10433 | Kodiak Electric Assn Inc | 7723 | Nymans Plant Microgrid | AK | Kodiak Island | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 1 | N |  |  | OP | X | 1 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2000 | petroleum | TRUE | 10433 | Kodiak Electric Assn Inc | 7723 | Nymans Plant Microgrid | AK | Kodiak Island | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 7.5 | 0.9 | 7.3 | 7.4 | 1 | N |  |  | OP | X | 1 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1995 | biomass | TRUE | 14323 | Pacific Northwest Generating Coop | 7725 | Coffin Butte | OR | Benton | 1 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 10 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: LFG |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1995 | biomass | TRUE | 14323 | Pacific Northwest Generating Coop | 7725 | Coffin Butte | OR | Benton | 2 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 10 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: LFG |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1995 | biomass | TRUE | 14323 | Pacific Northwest Generating Coop | 7725 | Coffin Butte | OR | Benton | 3 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 10 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: LFG |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage2007 | biomass | TRUE | 14323 | Pacific Northwest Generating Coop | 7725 | Coffin Butte | OR | Benton | 4 | Landfill Gas | IC |  | S | X | X |  |  | 1.6 | 1 | 1.6 | 1.6 | 0.8 | N |  |  | OP | X | 10 | 2007 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: LFG |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage2007 | biomass | TRUE | 14323 | Pacific Northwest Generating Coop | 7725 | Coffin Butte | OR | Benton | 5 | Landfill Gas | IC |  | S | X | X |  |  | 1.6 | 1 | 1.6 | 1.6 | 0.8 | N |  |  | OP | X | 10 | 2007 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: LFG |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N
Vintage1999 | biomass | TRUE | 63284 | WestRock North Charleston | 7737 | Kapstone | SC | Charleston | 1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 99.2 | 0.85 | 85 | 85 | 25 | N |  |  | OP | X | 4 | 1999 |  |  | Y | IPP CHP | 3 | T | WDS | BIT | BLQ | DFO |  |  | DFO |  |  |  | N | N |  | 12H |  | Y | Y |  | Y | [18 empty] | Y | Y | N
Vintage1999 | natural gas peaker | TRUE | 924 | Associated Electric Coop, Inc | 7749 | Essex | MO | Stoddard | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 121.2 | 0.85 | 96 | 110 | 86 | N |  |  | OP | X | 6 | 1999 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1997 | hydro | TRUE | 219 | Alaska Power and Telephone Co | 7751 | Goat Lake Hydro | AK | Skagway Hoonah Angoon | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4 | 0.8 | 4 | 4 | 1.6 | N |  |  | OP | X | 12 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 1H
Vintage1995 | hydro | TRUE | 219 | Alaska Power and Telephone Co | 7752 | Black Bear Lake | AK | Prince of Wales Ketchikan | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.5 | 0.8 | 4.5 | 4.5 | 1.8 | N |  |  | OP | X | 3 | 1995 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1999 | natural gas peaker | TRUE | 924 | Associated Electric Coop, Inc | 7754 | Nodaway | MO | Nodaway | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 157.8 | 0.85 | 90 | 107 | 65 | N |  |  | OP | X | 6 | 1999 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [20 empty] | Y | 10 | 2023 | N | N | N | bar: X X X to RC RC RC
Vintage1999 | natural gas peaker | TRUE | 924 | Associated Electric Coop, Inc | 7754 | Nodaway | MO | Nodaway | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 157.8 | 0.85 | 88 | 114 | 65 | N |  |  | OP | X | 6 | 1999 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [20 empty] | Y | 10 | 2023 | N | N | N | bar: X X X to RC RC RC
Vintage2000 | natural gas combined cycle | TRUE | 924 | Associated Electric Coop, Inc | 7757 | Chouteau | OK | Mayes | 1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 176 | 0.85 | 145 | 150 | 100 | N |  |  | OP | X | 1 | 2000 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [7 empty] | 14 | 14 | 5 | 2023 | [9 empty] | Y | 5 | 2024 | N | N | N | bar: X X X to RC RC RC
Vintage2000 | natural gas combined cycle | TRUE | 924 | Associated Electric Coop, Inc | 7757 | Chouteau | OK | Mayes | 2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 176 | 0.85 | 148 | 153 | 100 | N |  |  | OP | X | 1 | 2000 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [7 empty] | 14 | 14 | 5 | 2024 | [9 empty] | Y | 5 | 2023 | N | N | N | bar: X X X to RC RC RC
Vintage2000 | natural gas combined cycle | TRUE | 924 | Associated Electric Coop, Inc | 7757 | Chouteau | OK | Mayes | 3 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X |  |  | 182.8 | 0.85 | 149 | 155 | 50 | N |  |  | OP | X | 1 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; DFO DFO DFO: WH |  |  |  | N | N |  | 12H |  |  |  |  | N | [15 empty] | N |  |  | N | N | N
Vintage2011 | natural gas combined cycle | TRUE | 924 | Associated Electric Coop, Inc | 7757 | Chouteau | OK | Mayes | 4 | Natural Gas Fired Combined Cycle | CT | CC2 | S | X | N |  |  | 176 | 0.85 | 158 | 167 | 100 | Y | 10 | 2021 | OP | X | 6 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2011 | natural gas combined cycle | TRUE | 924 | Associated Electric Coop, Inc | 7757 | Chouteau | OK | Mayes | 5 | Natural Gas Fired Combined Cycle | CT | CC2 | S | X | N |  |  | 176 | 0.85 | 156 | 164 | 100 | Y | 10 | 2021 | OP | X | 6 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2011 | natural gas combined cycle | TRUE | 924 | Associated Electric Coop, Inc | 7757 | Chouteau | OK | Mayes | 6 | Natural Gas Fired Combined Cycle | CA | CC2 | S | Y | X |  |  | 182.8 | 0.85 | 144 | 149 | 50 | N |  |  | OP | X | 6 | 2011 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H |  |  |  |  | N | [18 empty] | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2000 | petroleum | TRUE | 20214 | Waverly Municipal Elec Utility | 7758 | South Plant | IA | Bremer | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.9 | 1.9 | 0.5 | N |  |  | OP | X | 5 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage2000 | petroleum | TRUE | 20214 | Waverly Municipal Elec Utility | 7758 | South Plant | IA | Bremer | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.9 | 1.9 | 0.5 | N |  |  | OP | X | 5 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage2000 | petroleum | TRUE | 20214 | Waverly Municipal Elec Utility | 7758 | South Plant | IA | Bremer | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.9 | 1.9 | 0.5 | N |  |  | OP | X | 5 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage2000 | petroleum | TRUE | 20214 | Waverly Municipal Elec Utility | 7758 | South Plant | IA | Bremer | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.9 | 1.9 | 0.5 | N |  |  | OP | X | 5 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N |  | N
Vintage2000 | petroleum | TRUE | 20214 | Waverly Municipal Elec Utility | 7758 | South Plant | IA | Bremer | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.9 | 1.9 | 0.5 | N |  |  | OP | X | 5 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N |  | N
Vintage2000 | petroleum | TRUE | 20214 | Waverly Municipal Elec Utility | 7758 | South Plant | IA | Bremer | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.9 | 1.9 | 0.5 | N |  |  | OP | X | 5 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N |  | N
Vintage2000 | natural gas peaker | TRUE | 9273 | Indianapolis Power & Light Co | 7759 | Georgetown | IN | Marion | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | IPL.16GEOR11G | IPL.16GEOR11G | 85 | 0.85 | 79 | 89.4 | 40 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2000 | natural gas peaker | TRUE | 9273 | Indianapolis Power & Light Co | 7759 | Georgetown | IN | Marion | GT2 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X | IPL.16GEOR22G | IPL.16GEOR22G | 85 | 0.85 | 79 | 89.4 | 40 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2000 | natural gas peaker | TRUE | 9273 | Indianapolis Power & Light Co | 7759 | Georgetown | IN | Marion | GT3 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X | IPL.16GEOR33G | IPL.16GEOR33G | 85 | 0.85 | 79.2 | 89.6 | 40 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 9273 | Indianapolis Power & Light Co | 7759 | Georgetown | IN | Marion | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | IPL.16GEOR44G | IPL.16GEOR44G | 85 | 0.85 | 79.2 | 89.6 | 40 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage1999 | natural gas peaker | TRUE | 56491 | Tilton Energy LLC | 7760 | Tilton | IL | Vermilion | 1 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X | Tilton 138 kv TEC1 Gen | AEP Tilton 1 CT | 47 | 0.85 | 45.5 | 50 | 18 | N |  |  | OP | X | 6 | 1999 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1999 | natural gas peaker | TRUE | 56491 | Tilton Energy LLC | 7760 | Tilton | IL | Vermilion | 2 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X | Tilton 138 kv TEC2 Gen | AEP Tilton 2 CT | 47 | 0.85 | 45.5 | 50 | 18 | N |  |  | OP | X | 6 | 1999 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1999 | natural gas peaker | TRUE | 56491 | Tilton Energy LLC | 7760 | Tilton | IL | Vermilion | 3 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X | Tilton 138 Kv TEC3 Gen | AEP Tilton 3 CT | 47 | 0.85 | 46 | 50 | 18 | N |  |  | OP | X | 6 | 1999 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1999 | natural gas peaker | TRUE | 56491 | Tilton Energy LLC | 7760 | Tilton | IL | Vermilion | 4 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X | Tilton 138 KV TEC4 Gen | AEP Tilton 4 CT | 47 | 0.85 | 46.1 | 50 | 18 | N |  |  | OP | X | 6 | 1999 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N |  |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 15470 | Duke Energy Indiana, LLC | 7763 | Henry County | IN | Henry | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | CP/Comm Pricing | CP/Comm Pricing | 60.5 | 0.85 | 40 | 40 | 25 | N |  |  | OP | X | 7 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 15470 | Duke Energy Indiana, LLC | 7763 | Henry County | IN | Henry | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | CP/Comm Pricing | CP/Comm Pricing | 60.5 | 0.85 | 43 | 47 | 25 | N |  |  | OP | X | 7 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 15470 | Duke Energy Indiana, LLC | 7763 | Henry County | IN | Henry | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | CP/Comm Pricing | CP/Comm Pricing | 60.5 | 0.85 | 43 | 47 | 25 | N |  |  | OP | X | 7 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2000 | natural gas peaker | TRUE | 59421 | SEPG Operating Services, LLC MPC | 7764 | MPC Generating | GA | Walton | 1 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 185.4 | 0.9 | 147.5 | 169 | 110 | N |  |  | OP | X | 1 | 2000 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 59421 | SEPG Operating Services, LLC MPC | 7764 | MPC Generating | GA | Walton | 2 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 200.7 | 0.9 | 155 | 182 | 110 | N |  |  | OP | X | 1 | 2001 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1999 | petroleum | TRUE | 5957 | City of Erie - (KS) | 7766 | Erie Energy Center | KS | Neosho | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 1.5 | N |  |  | OP | X | 10 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 5957 | City of Erie - (KS) | 7766 | Erie Energy Center | KS | Neosho | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 1.5 | N |  |  | OP | X | 10 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 5957 | City of Erie - (KS) | 7766 | Erie Energy Center | KS | Neosho | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 1.5 | N |  |  | OP | X | 10 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 5957 | City of Erie - (KS) | 7766 | Erie Energy Center | KS | Neosho | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 1.5 | N |  |  | OP | X | 10 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 5957 | City of Erie - (KS) | 7766 | Erie Energy Center | KS | Neosho | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 1.5 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 5957 | City of Erie - (KS) | 7766 | Erie Energy Center | KS | Neosho | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 1.5 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 5957 | City of Erie - (KS) | 7766 | Erie Energy Center | KS | Neosho | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 1.5 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 5957 | City of Erie - (KS) | 7766 | Erie Energy Center | KS | Neosho | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 1.5 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 17874 | City of St George | 7767 | Bloomington Power Plant | UT | Washington | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.7 | 0.9 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 3 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 10M | [23 empty] | N | N
Vintage1999 | petroleum | TRUE | 17874 | City of St George | 7767 | Bloomington Power Plant | UT | Washington | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.7 | 0.9 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 3 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 10M | [23 empty] | N | N
Vintage1999 | petroleum | TRUE | 17874 | City of St George | 7767 | Bloomington Power Plant | UT | Washington | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.7 | 0.9 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 3 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 10M | [23 empty] | N
Vintage1999 | petroleum | TRUE | 17874 | City of St George | 7767 | Bloomington Power Plant | UT | Washington | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.7 | 0.9 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 3 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 10M | [23 empty] | N
Vintage1999 | petroleum | TRUE | 17874 | City of St George | 7767 | Bloomington Power Plant | UT | Washington | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.7 | 0.9 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 3 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 10M | [23 empty] | N | N
Vintage1999 | petroleum | TRUE | 17874 | City of St George | 7767 | Bloomington Power Plant | UT | Washington | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.7 | 0.9 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 3 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 10M | [23 empty] | N | N
Vintage1999 | natural gas peaker | TRUE | 17690 | SOWEGA Power LLC | 7768 | Sowega Power | GA | Mitchell | CTG2 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 49.8 | 0.85 | 48.5 | 48.5 | 37 | N |  |  | OP | X | 6 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1999 | natural gas peaker | TRUE | 17690 | SOWEGA Power LLC | 7768 | Sowega Power | GA | Mitchell | CTG3 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 49.8 | 0.85 | 48.5 | 48.5 | 37 | N |  |  | OP | X | 6 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 16179 | Rochelle Municipal Utilities | 7770 | 1515 S Caron Road | IL | Ogle | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 4.2 | 0.8 | 3 | 3.5 | 2 | N |  |  | OP | X | 5 | 2000 |  |  | N | Electric Utility | 1 | [14 empty] | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2011 | onshore wind | TRUE | 58190 | Bluestem LLC | 7771 | Springview | NE | Keya Paha | 3 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 1.5 |  | 1.5 | 1.5 | 1.5 | N |  |  | OP | X | 6 | 2011 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WND |  |  |  | N | N | 1
Vintage2011 | onshore wind | TRUE | 58190 | Bluestem LLC | 7771 | Springview | NE | Keya Paha | 4 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 1.5 |  | 1.5 | 1.5 | 1.5 | N |  |  | OP | X | 6 | 2011 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WND |  |  |  | N | N | 1 |  |  |  |  | N
Vintage2000 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7774 | Cleveland Peaking | OH | Cuyahoga | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2000 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7774 | Cleveland Peaking | OH | Cuyahoga | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2000 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7774 | Cleveland Peaking | OH | Cuyahoga | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2000 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7774 | Cleveland Peaking | OH | Cuyahoga | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7774 | Cleveland Peaking | OH | Cuyahoga | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7774 | Cleveland Peaking | OH | Cuyahoga | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1999 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7775 | Versailles Peaking | OH | Darke | 1 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 6 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7775 | Versailles Peaking | OH | Darke | 2 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 6 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7775 | Versailles Peaking | OH | Darke | 3 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 6 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7776 | Napoleon Peaking | OH | Henry | 4 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7776 | Napoleon Peaking | OH | Henry | 5 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7776 | Napoleon Peaking | OH | Henry | 6 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7777 | Dover Peaking | OH | Tuscarawas | 1 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7777 | Dover Peaking | OH | Tuscarawas | 2 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7777 | Dover Peaking | OH | Tuscarawas | 3 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7777 | Dover Peaking | OH | Tuscarawas | 4 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1999 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7777 | Dover Peaking | OH | Tuscarawas | 5 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1999 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7777 | Dover Peaking | OH | Tuscarawas | 6 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1999 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7778 | Orrville Peaking | OH | Wayne | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7778 | Orrville Peaking | OH | Wayne | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7778 | Orrville Peaking | OH | Wayne | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7779 | Bryan Peaking | OH | Williams | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7779 | Bryan Peaking | OH | Williams | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7779 | Bryan Peaking | OH | Williams | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7779 | Bryan Peaking | OH | Williams | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1999 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7779 | Bryan Peaking | OH | Williams | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1999 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7779 | Bryan Peaking | OH | Williams | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1999 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7780 | Jackson Cntr Peaking | OH | Shelby | 1 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 6 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7781 | Arcanum Peaking | OH | Darke | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 6 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2000 | natural gas peaker | TRUE | 40577 | American Mun Power-Ohio, Inc | 7782 | Hamilton Peaking | OH | Butler | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 32 | 0.85 | 29 | 32 | 29 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2000 | natural gas peaker | TRUE | 40577 | American Mun Power-Ohio, Inc | 7783 | Bowling Green Peaking | OH | Wood | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 32 | 0.85 | 29 | 32 | 29 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1994 | natural gas combined cycle | TRUE | 58651 | Allegany Generating Station, LLC | 7784 | Allegany Cogen | NY | Allegany | 1 | Natural Gas Fired Combined Cycle | CT | CC01 | S | X | N | 23514 | 23514 | 42 | 0.9 | 40 | 40 | 27 | N |  |  | OP | X | 6 | 1994 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1994 | natural gas combined cycle | TRUE | 58651 | Allegany Generating Station, LLC | 7784 | Allegany Cogen | NY | Allegany | 2 | Natural Gas Fired Combined Cycle | CA | CC01 | S | Y | X | 23514 | 23514 | 25 | 0.9 | 20 | 20 | 10 | N |  |  | OP | X | 6 | 1994 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1989 | hydro | TRUE | 11204 | Los Alamos County | 7789 | Abiquiu Dam | NM | Rio Arriba | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.3 | 0.9 | 6.9 | 6.9 | 1 | N |  |  | OP | X | 4 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage1989 | hydro | TRUE | 11204 | Los Alamos County | 7789 | Abiquiu Dam | NM | Rio Arriba | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.3 | 0.9 | 6.9 | 6.9 | 1 | N |  |  | OP | X | 4 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage2011 | hydro | TRUE | 11204 | Los Alamos County | 7789 | Abiquiu Dam | NM | Rio Arriba | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.85 | 3 | 3 | 0.5 | N |  |  | OP | X | 5 | 2011 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage1986 | hard coal | TRUE | 40230 | Deseret Generation & Tran Coop | 7790 | Bonanza | UT | Uintah | 1 | Conventional Steam Coal | ST |  | J | X | X |  |  | 499.5 | 0.995 | 458 | 458 | 210 | N |  |  | OP | X | 5 | 1986 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: BIT; DFO DFO DFO: DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage2000 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7791 | Montpelier | OH | Williams | 1 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2000 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7791 | Montpelier | OH | Williams | 2 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2000 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7791 | Montpelier | OH | Williams | 3 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2000 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7791 | Montpelier | OH | Williams | 4 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7791 | Montpelier | OH | Williams | 5 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7791 | Montpelier | OH | Williams | 6 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1999 | natural gas peaker | TRUE | 11571 | Manitowoc Public Utilities | 7795 | Custer Energy Center | WI | Manitowoc | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | WPS.CUSTEGEN1 |  | 24.5 | 0.8 | 22 | 24 | 9.8 | N |  |  | OP | X | 6 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO; DFO DFO DFO: NG | DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1997 | petroleum | TRUE | 11560 | City of Manassas - (VA) | 7797 | Dominion/Lo Mar | VA | Prince William | DOM1 | Petroleum Liquids | GT |  | J | X | X |  |  | 12 | 0.8 | 9 | 9 | 3 | N |  |  | OP | X | 8 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1997 | petroleum | TRUE | 11560 | City of Manassas - (VA) | 7797 | Dominion/Lo Mar | VA | Prince William | DOM2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.7 | 1.7 | 0.3 | N |  |  | OP | X | 8 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1997 | petroleum | TRUE | 11560 | City of Manassas - (VA) | 7797 | Dominion/Lo Mar | VA | Prince William | LOM1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.7 | 1.7 | 0.3 | N |  |  | OP | X | 8 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1997 | petroleum | TRUE | 11560 | City of Manassas - (VA) | 7797 | Dominion/Lo Mar | VA | Prince William | LOM2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.7 | 1.7 | 0.3 | N |  |  | OP | X | 8 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1997 | petroleum | TRUE | 11560 | City of Manassas - (VA) | 7797 | Dominion/Lo Mar | VA | Prince William | LOM3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.7 | 1.7 | 0.3 | N |  |  | OP | X | 8 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1996 | petroleum | TRUE | 11560 | City of Manassas - (VA) | 7798 | Gateway Gen | VA | Prince William | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.7 | 1.7 | 0.3 | N |  |  | OP | X | 3 | 1996 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2009 | petroleum | TRUE | 11560 | City of Manassas - (VA) | 7798 | Gateway Gen | VA | Prince William | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.7 | 1.7 | 0.3 | N |  |  | OP | X | 6 | 2009 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2000 | natural gas peaker | TRUE | 11479 | Madison Gas & Electric Co | 7799 | West Marinette 34 | WI | Marinette | 34 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MGE.WMARIN034 | MGE.WMARIN034 | 83 | 0.85 | 68.7 | 68.7 | 50 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 3046 | Duke Energy Progress - (NC) | 7805 | Sherwood H Smith Jr Energy Complex | NC | Richmond | 001 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 199.4 | 0.85 | 157 | 192 | 100 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO | [6 empty] | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 3046 | Duke Energy Progress - (NC) | 7805 | Sherwood H Smith Jr Energy Complex | NC | Richmond | 002 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 199.4 | 0.85 | 156 | 192 | 100 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO | [6 empty] | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 3046 | Duke Energy Progress - (NC) | 7805 | Sherwood H Smith Jr Energy Complex | NC | Richmond | 003 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 199.4 | 0.85 | 155 | 192 | 100 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO | [6 empty] | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 3046 | Duke Energy Progress - (NC) | 7805 | Sherwood H Smith Jr Energy Complex | NC | Richmond | 004 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 199.4 | 0.85 | 159 | 192 | 100 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO | [6 empty] | 1H | [23 empty] | Y | N | Y
Vintage2011 | natural gas combined cycle | TRUE | 3046 | Duke Energy Progress - (NC) | 7805 | Sherwood H Smith Jr Energy Complex | NC | Richmond | 10 | Natural Gas Fired Combined Cycle | CT | 2 | S | X | Y |  |  | 191.2 | 0.85 | 178 | 215 | 178 | N |  |  | OP | X | 6 | 2011 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO | [6 empty] | 12H | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 3046 | Duke Energy Progress - (NC) | 7805 | Sherwood H Smith Jr Energy Complex | NC | Richmond | 6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 199.4 | 0.85 | 145 | 192 | 100 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO | [6 empty] | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas combined cycle | TRUE | 3046 | Duke Energy Progress - (NC) | 7805 | Sherwood H Smith Jr Energy Complex | NC | Richmond | 7 | Natural Gas Fired Combined Cycle | CT | 1 | S | X | Y |  |  | 199.4 | 0.85 | 152 | 193 | 152 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO | [6 empty] | 12H | [23 empty] | Y | N | Y
Vintage2002 | natural gas combined cycle | TRUE | 3046 | Duke Energy Progress - (NC) | 7805 | Sherwood H Smith Jr Energy Complex | NC | Richmond | 8 | Natural Gas Fired Combined Cycle | CT | 1 | S | X | Y |  |  | 199.4 | 0.85 | 152 | 193 | 152 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO | [6 empty] | 12H | [23 empty] | Y | N | Y
Vintage2011 | natural gas combined cycle | TRUE | 3046 | Duke Energy Progress - (NC) | 7805 | Sherwood H Smith Jr Energy Complex | NC | Richmond | 9 | Natural Gas Fired Combined Cycle | CT | 2 | S | X | Y |  |  | 191.2 | 0.85 | 178 | 215 | 178 | N |  |  | OP | X | 6 | 2011 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO | [6 empty] | 12H | [23 empty] | Y | N | Y
Vintage2002 | natural gas combined cycle | TRUE | 3046 | Duke Energy Progress - (NC) | 7805 | Sherwood H Smith Jr Energy Complex | NC | Richmond | ST4 | Natural Gas Fired Combined Cycle | CA | 1 | S | N | X |  |  | 195.5 | 0.85 | 171 | 184 | 171 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO | [6 empty] | 12H | [23 empty] | Y | N | Y
Vintage2011 | natural gas combined cycle | TRUE | 3046 | Duke Energy Progress - (NC) | 7805 | Sherwood H Smith Jr Energy Complex | NC | Richmond | ST5 | Natural Gas Fired Combined Cycle | CA | 2 | S | Y | X |  |  | 271.1 | 0.85 | 252 | 250 | 252 | N |  |  | OP | X | 6 | 2011 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO | [6 empty] | 12H | [23 empty] | Y | N | Y
Vintage2020 | natural gas peaker | TRUE | 16873 | Village of Sebewaing - (MI) | 7806 | Pine Street | MI | Huron | 7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | CONS.MPPA | MISO-CONS.MPPA | 4.4 | 0.95 | 4.4 | 4.4 | 2.2 | N |  |  | OP | X | 2 | 2020 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage2020 | natural gas peaker | TRUE | 16873 | Village of Sebewaing - (MI) | 7806 | Pine Street | MI | Huron | 8 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | CONS.MPPA | MISO-CONS.MPPA | 3.3 | 0.95 | 3.3 | 3.3 | 1.6 | N |  |  | OP | X | 3 | 2020 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage1994 | hydro | TRUE | 7977 | City of Hamilton - (OH) | 7807 | Hamilton Hydro | OH | Butler | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.1 | 0.9 | 1 | 1 | 0.3 | N |  |  | OP | X | 5 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1994 | hydro | TRUE | 7977 | City of Hamilton - (OH) | 7807 | Hamilton Hydro | OH | Butler | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.1 | 0.9 | 1 | 1 | 0.3 | N |  |  | OP | X | 5 | 1994 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage2004 | petroleum | TRUE | 792 | City of Argyle - (WI) | 7810 | Argyle | WI | Lafayette | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.2 | 0.8 | 2 | 2 | 0.5 | N |  |  | SB | Y | 7 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage2000 | natural gas peaker | TRUE | 13994 | Oglethorpe Power Corporation | 7813 | Sewell Creek Energy | GA | Polk | 1 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 121 | 0.85 | 97.2 | 109.1 | 65 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2000 | natural gas peaker | TRUE | 13994 | Oglethorpe Power Corporation | 7813 | Sewell Creek Energy | GA | Polk | 2 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 121 | 0.85 | 98.6 | 112.1 | 65 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2000 | natural gas peaker | TRUE | 13994 | Oglethorpe Power Corporation | 7813 | Sewell Creek Energy | GA | Polk | 3 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 164 | 0.85 | 129.8 | 147.4 | 69 | N |  |  | OP | X | 9 | 2000 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2000 | natural gas peaker | TRUE | 13994 | Oglethorpe Power Corporation | 7813 | Sewell Creek Energy | GA | Polk | 4 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 164 | 0.85 | 126.7 | 142.8 | 69 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2003 | petroleum | TRUE | 59159 | Central Electric Power | 7814 | Webb Forging | SC | Union | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.9 | 0.8 | 2.4 | 2.4 | 2 | N |  |  | OP | X | 7 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2003 | petroleum | TRUE | 59159 | Central Electric Power | 7814 | Webb Forging | SC | Union | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.9 | 0.8 | 2.4 | 2.4 | 2 | N |  |  | OP | X | 7 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | natural gas peaker | TRUE | 40307 | Prairie Power, Inc | 7818 | Alsey | IL | Scott | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | AMIL.ALSEYCTG1 |  | 30 | 0.9 | 30 | 34.7 | 6 | N |  |  | OP | X | 6 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | natural gas peaker | TRUE | 40307 | Prairie Power, Inc | 7818 | Alsey | IL | Scott | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | AMIL.ALSEYCTG2 |  | 30 | 0.9 | 30 | 34.7 | 6 | N |  |  | OP | X | 8 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | natural gas peaker | TRUE | 40307 | Prairie Power, Inc | 7818 | Alsey | IL | Scott | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | AMIL.ALSEYCTG3 |  | 20 | 0.9 | 19.3 | 20.3 | 12 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1999 | natural gas peaker | TRUE | 40307 | Prairie Power, Inc | 7818 | Alsey | IL | Scott | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | AMIL.ALSEYCTG4 |  | 20 | 0.9 | 18 | 19.4 | 12 | N |  |  | OP | X | 8 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1999 | natural gas peaker | TRUE | 40307 | Prairie Power, Inc | 7818 | Alsey | IL | Scott | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | AMIL.ALSEYCTG5 |  | 25 | 0.9 | 25 | 26.7 | 12 | N |  |  | OP | X | 6 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2016 | natural gas peaker | TRUE | 40307 | Prairie Power, Inc | 7818 | Alsey | IL | Scott | 6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | AMIL.ALSEYCTG6 |  | 48 | 0.85 | 42 | 45 | 20 | N |  |  | OP | X | 12 | 2016 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1949 | hydro | TRUE | 20847 | Wisconsin Electric Power Co | 7820 | Big Quinnesec 92 | MI | Dickinson | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8 | 0.9 | 8 | 8 | 5.4 | N |  |  | OP | X | 11 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1949 | hydro | TRUE | 20847 | Wisconsin Electric Power Co | 7820 | Big Quinnesec 92 | MI | Dickinson | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8 | 0.9 | 8 | 8 | 5.3 | N |  |  | OP | X | 12 | 1949 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1914 | hydro | TRUE | 20847 | Wisconsin Electric Power Co | 7821 | Big Quinnesec 61 | MI | Dickinson | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 1 | 2.2 | 2.2 | 0.5 | N |  |  | OP | X | 5 | 1914 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1914 | hydro | TRUE | 20847 | Wisconsin Electric Power Co | 7821 | Big Quinnesec 61 | MI | Dickinson | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 1 | 2.2 | 2.2 | 0.5 | N |  |  | OP | X | 5 | 1914 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1940 | hydro | TRUE | 10056 | City of Kaukauna | 7822 | Kaukauna City Hydro | WI | Outagamie | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.9 | 2.4 | 2.4 | 0.2 | N |  |  | OP | X | 12 | 1940 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [5 empty] | 0 | 10M | [23 empty] | N
Vintage1942 | hydro | TRUE | 10056 | City of Kaukauna | 7822 | Kaukauna City Hydro | WI | Outagamie | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.9 | 2.4 | 2.4 | 0.2 | N |  |  | OP | X | 10 | 1942 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [5 empty] | 0 | 10M | [23 empty] | N
Vintage1979 | natural gas peaker | TRUE | 9216 | Imperial Irrigation District | 7824 | Rockwood | CA | Imperial | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 24.9 | 0.85 | 21.2 | 21.1 | 1.5 | N |  |  | OP | X | 6 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1980 | petroleum | TRUE | 9216 | Imperial Irrigation District | 7824 | Rockwood | CA | Imperial | 2 | Petroleum Liquids | GT |  | S | X | X |  |  | 24.9 | 0.85 | 21.1 | 21.9 | 1.5 | N |  |  | OP | X | 4 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2001 | natural gas peaker | TRUE | 807 | Arkansas Electric Coop Corp | 7825 | Fulton (AR) | AR | Hempstead | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | AECC_FULTON | SWPP | 154.8 | 0.9 | 153 | 153 | 125 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 17650 | Southern Power Co | 7826 | Rowan | NC | Rowan | 001 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 199.4 | 0.85 | 156.4 | 185.2 | 95 | N |  |  | OP | X | 4 | 2001 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 17650 | Southern Power Co | 7826 | Rowan | NC | Rowan | 002 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 199.4 | 0.85 | 162.9 | 184.4 | 95 | N |  |  | OP | X | 4 | 2001 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 17650 | Southern Power Co | 7826 | Rowan | NC | Rowan | 003 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 199.4 | 0.85 | 156.1 | 184.6 | 95 | N |  |  | OP | X | 5 | 2001 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2003 | natural gas combined cycle | TRUE | 17650 | Southern Power Co | 7826 | Rowan | NC | Rowan | 4 | Natural Gas Fired Combined Cycle | CT | G102 | S | X | N |  |  | 199.4 | 0.85 | 155.5 | 188.5 | 58 | N |  |  | OP | X | 6 | 2003 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2003 | natural gas combined cycle | TRUE | 17650 | Southern Power Co | 7826 | Rowan | NC | Rowan | 5 | Natural Gas Fired Combined Cycle | CT | G102 | S | X | N |  |  | 199.4 | 0.85 | 155.5 | 188.5 | 58 | N |  |  | OP | X | 6 | 2003 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2003 | natural gas combined cycle | TRUE | 17650 | Southern Power Co | 7826 | Rowan | NC | Rowan | STG | Natural Gas Fired Combined Cycle | CA | G102 | S | N | X |  |  | 195 | 0.85 | 188 | 188 | 59 | N |  |  | OP | X | 6 | 2003 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2000 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7827 | Shelby North | OH | Richland | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2000 | petroleum | TRUE | 17043 | City of Shelby - (OH) | 7828 | Shelby South | OH | Richland | 1 | Petroleum Liquids | IC |  | S | X | X | AEP | AEP | 1.8 | 0.8 | 1.8 | 1.8 | 0.2 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | natural gas peaker | TRUE | 13994 | Oglethorpe Power Corporation | 7829 | Smarr Energy Center | GA | Monroe | 1 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 121 | 0.85 | 96 | 109.1 | 65 | N |  |  | OP | X | 6 | 1999 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage1999 | natural gas peaker | TRUE | 13994 | Oglethorpe Power Corporation | 7829 | Smarr Energy Center | GA | Monroe | 2 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 121 | 0.85 | 95.6 | 109.1 | 65 | N |  |  | OP | X | 6 | 1999 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2000 | petroleum | TRUE | 38084 | Great Lakes Energy Coop | 7831 | Beaver Island | MI | Charlevoix | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1 | 1 | 0.4 | N |  |  | SB | Y | 9 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2000 | petroleum | TRUE | 38084 | Great Lakes Energy Coop | 7831 | Beaver Island | MI | Charlevoix | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1 | 1 | 0.4 | N |  |  | SB | Y | 9 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2001 | petroleum | TRUE | 38084 | Great Lakes Energy Coop | 7831 | Beaver Island | MI | Charlevoix | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.8 | 0.8 | 0.3 | N |  |  | SB | Y | 1 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2001 | natural gas combined cycle | TRUE | 17543 | South Carolina Public Service Authority | 7834 | John S Rainey | SC | Anderson | CT1A | Natural Gas Fired Combined Cycle | CT | PB1 | S | X | N |  |  | 165 | 0.85 | 150 | 170 | 120 | N |  |  | OP | X | 9 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2001 | natural gas combined cycle | TRUE | 17543 | South Carolina Public Service Authority | 7834 | John S Rainey | SC | Anderson | CT1B | Natural Gas Fired Combined Cycle | CT | PB1 | S | X | N |  |  | 165 | 0.85 | 150 | 170 | 120 | N |  |  | OP | X | 9 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 17543 | South Carolina Public Service Authority | 7834 | John S Rainey | SC | Anderson | CT2A | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 165 | 0.85 | 146 | 180 | 20 | N |  |  | OP | X | 3 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 17543 | South Carolina Public Service Authority | 7834 | John S Rainey | SC | Anderson | CT2B | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 165 | 0.85 | 146 | 180 | 20 | N |  |  | OP | X | 5 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2004 | natural gas peaker | TRUE | 17543 | South Carolina Public Service Authority | 7834 | John S Rainey | SC | Anderson | CT3A | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 84 | 0.85 | 75 | 90 | 10 | N |  |  | OP | X | 1 | 2004 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2004 | natural gas peaker | TRUE | 17543 | South Carolina Public Service Authority | 7834 | John S Rainey | SC | Anderson | CT3B | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 84 | 0.85 | 75 | 90 | 10 | N |  |  | OP | X | 1 | 2004 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2004 | natural gas peaker | TRUE | 17543 | South Carolina Public Service Authority | 7834 | John S Rainey | SC | Anderson | CT4A | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 84 | 0.85 | 75 | 90 | 10 | N |  |  | OP | X | 1 | 2004 |  |  | N | Electric Utility | 1 | [12 empty] | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2001 | natural gas combined cycle | TRUE | 17543 | South Carolina Public Service Authority | 7834 | John S Rainey | SC | Anderson | ST1S | Natural Gas Fired Combined Cycle | CA | PB1 | S | N | X |  |  | 190 | 0.85 | 160 | 190 | 120 | N |  |  | OP | X | 9 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2003 | natural gas peaker | TRUE | 56386 | Essential Power Rock Springs LLC | 7835 | Essential Power Rock Springs LLC | MD | Cecil | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | ROCKSPRI-CT1 | ROCKSPRI-CT1 | 198.9 | 0.85 | 167.5 | 167.5 | 100 | N |  |  | OP | X | 6 | 2003 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2003 | natural gas peaker | TRUE | 56386 | Essential Power Rock Springs LLC | 7835 | Essential Power Rock Springs LLC | MD | Cecil | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | ROCKSPRI-CT2 | ROCKSPRI-CT2 | 175.9 | 0.85 | 166.5 | 166.5 | 100 | N |  |  | OP | X | 6 | 2003 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2003 | natural gas peaker | TRUE | 56386 | Essential Power Rock Springs LLC | 7835 | Essential Power Rock Springs LLC | MD | Cecil | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | ROCKSPRI-CT3 | ROCKSPRI-CT3 | 198.9 | 0.85 | 169 | 169 | 100 | N |  |  | OP | X | 6 | 2003 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2003 | natural gas peaker | TRUE | 56386 | Essential Power Rock Springs LLC | 7835 | Essential Power Rock Springs LLC | MD | Cecil | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | ROCKSPRI-CT4 | ROCK-SPRI-CT4 | 198.9 | 0.85 | 169 | 169 | 100 | N |  |  | OP | X | 6 | 2003 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N |  | N | bar: X X X to RC RC RC
Vintage2004 | natural gas peaker | TRUE | 40229 | Old Dominion Electric Coop | 7836 | Marsh Run Generation Facility | VA | Fauquier | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 34887875 | 34887875 | 171.1 | 0.85 | 161 | 192 | 96 | N |  |  | OP | X | 9 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage2004 | natural gas peaker | TRUE | 40229 | Old Dominion Electric Coop | 7836 | Marsh Run Generation Facility | VA | Fauquier | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 34887877 | 34887877 | 171.1 | 0.85 | 159.3 | 192 | 96 | N |  |  | OP | X | 9 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage2004 | natural gas peaker | TRUE | 40229 | Old Dominion Electric Coop | 7836 | Marsh Run Generation Facility | VA | Fauquier | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 34887879 | 34887879 | 171.1 | 0.85 | 161 | 192 | 96 | N |  |  | OP | X | 9 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage2003 | natural gas peaker | TRUE | 40229 | Old Dominion Electric Coop | 7837 | Louisa Generation Facility | VA | Louisa | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 93354021 | 93354021 | 84.5 | 0.85 | 76.5 | 92 | 46 | N |  |  | OP | X | 8 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage2003 | natural gas peaker | TRUE | 40229 | Old Dominion Electric Coop | 7837 | Louisa Generation Facility | VA | Louisa | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 93354023 | 93354023 | 84.5 | 0.85 | 77 | 92 | 46 | N |  |  | OP | X | 8 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage2003 | natural gas peaker | TRUE | 40229 | Old Dominion Electric Coop | 7837 | Louisa Generation Facility | VA | Louisa | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 93354025 | 93354025 | 84.5 | 0.85 | 77.3 | 92 | 46 | N |  |  | OP | X | 8 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage2003 | natural gas peaker | TRUE | 40229 | Old Dominion Electric Coop | 7837 | Louisa Generation Facility | VA | Louisa | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 93354027 | 93354027 | 84.5 | 0.85 | 77.2 | 92 | 46 | N |  |  | OP | X | 8 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage2003 | natural gas peaker | TRUE | 40229 | Old Dominion Electric Coop | 7837 | Louisa Generation Facility | VA | Louisa | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 34887991 | 34887991 | 171.1 | 0.85 | 158 | 187 | 95 | N |  |  | OP | X | 8 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 19876 | Virginia Electric & Power Co | 7838 | Remington | VA | Fauquier | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 178.5 | 0.85 | 153 | 187 | 90 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO | [6 empty] | 1H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 19876 | Virginia Electric & Power Co | 7838 | Remington | VA | Fauquier | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 170 | 0.85 | 151 | 187 | 90 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO | [6 empty] | 1H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 19876 | Virginia Electric & Power Co | 7838 | Remington | VA | Fauquier | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 178.5 | 0.85 | 152 | 187 | 90 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO | [6 empty] | 1H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 19876 | Virginia Electric & Power Co | 7838 | Remington | VA | Fauquier | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 178.5 | 0.85 | 152 | 188 | 90 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO | [6 empty] | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 19876 | Virginia Electric & Power Co | 7839 | Ladysmith | VA | Caroline | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 178.5 | 0.85 | 151 | 183 | 90 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO | [6 empty] | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 19876 | Virginia Electric & Power Co | 7839 | Ladysmith | VA | Caroline | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 178.5 | 0.85 | 151 | 183 | 90 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO | [6 empty] | 1H | [23 empty] | Y | N | Y
Vintage2008 | natural gas peaker | TRUE | 19876 | Virginia Electric & Power Co | 7839 | Ladysmith | VA | Caroline | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 178.5 | 0.85 | 161 | 183 | 90 | N |  |  | OP | X | 6 | 2008 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO | [6 empty] | 1H | [23 empty] | Y | N | Y
Vintage2008 | natural gas peaker | TRUE | 19876 | Virginia Electric & Power Co | 7839 | Ladysmith | VA | Caroline | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 178.5 | 0.85 | 160 | 183 | 90 | N |  |  | OP | X | 6 | 2008 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO | [6 empty] | 1H | [23 empty] | Y | N | Y
Vintage2009 | natural gas peaker | TRUE | 19876 | Virginia Electric & Power Co | 7839 | Ladysmith | VA | Caroline | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 178.5 | 0.85 | 160 | 183 | 90 | N |  |  | OP | X | 4 | 2009 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage2000 | petroleum | TRUE | 4329 | Copper Valley Elec Assn, Inc | 7841 | Valdez Cogen | AK | Valdez Cordova | 1 | Petroleum Liquids | GT |  | S | X | X |  |  | 5.3 | 0.8 | 5.1 | 5.3 | 1 | N |  |  | OP | X | 4 | 2000 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2000 | natural gas peaker | TRUE | 17697 | Southwestern Electric Coop Inc - (IL) | 7842 | Freedom Power Project | IL | Fayette | CT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | AMIL.SWECCTG1 | AMIL.SWECCTG1 | 71 | 0.9 | 45 | 45 | 20 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | [11 empty] | N | N | 0 | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 7570 | Great River Energy | 7843 | Pleasant Valley (MN) | MN | Mower | 11 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | GRE.PVLYGR1 | GRE,PVLYGR1 | 167.5 | 0.85 | 151.1 | 177.6 | 40 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO | [6 empty] | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 7570 | Great River Energy | 7843 | Pleasant Valley (MN) | MN | Mower | 12 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | GRE.PVLYGR2 | GRE.PVLYGR2 | 167.5 | 0.85 | 148.7 | 178.3 | 40 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO | [6 empty] | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 7570 | Great River Energy | 7843 | Pleasant Valley (MN) | MN | Mower | 13 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | GREPVLYGR3 | GRE.PVLYGR3 | 132.8 | 0.9 | 114.4 | 128.6 | 65 | N |  |  | OP | X | 5 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO | [6 empty] | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 12667 | Minnesota Municipal Power Agny | 7844 | Minnesota River | MN | Carver | UOO1 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X | NSP.MINRVR1 | NSP.MINRVR1 | 49 | 0.8 | 39 | 39 | 1 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage2010 | natural gas combined cycle | TRUE | 18642 | Tennessee Valley Authority | 7845 | Lagoon Creek | TN | Haywood | CTG1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 173.4 | 0.9 | 160 | 190 | 78.2 | N |  |  | OP | X | 9 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage2010 | natural gas combined cycle | TRUE | 18642 | Tennessee Valley Authority | 7845 | Lagoon Creek | TN | Haywood | CTG2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 173.4 | 0.9 | 160 | 190 | 78.2 | N |  |  | OP | X | 9 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 7845 | Lagoon Creek | TN | Haywood | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 84.5 | 0.9 | 73.9 | 94.3 | 60 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 7845 | Lagoon Creek | TN | Haywood | GT10 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 86.2 | 0.9 | 72.7 | 92.8 | 60 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 7845 | Lagoon Creek | TN | Haywood | GT11 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 86.2 | 0.9 | 72.7 | 92.8 | 60 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 7845 | Lagoon Creek | TN | Haywood | GT12 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 86.2 | 0.9 | 72.7 | 92.8 | 60 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 7845 | Lagoon Creek | TN | Haywood | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 84.5 | 0.9 | 73.9 | 94.3 | 60 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 7845 | Lagoon Creek | TN | Haywood | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 84.5 | 0.9 | 73.9 | 94.3 | 60 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 7845 | Lagoon Creek | TN | Haywood | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 84.5 | 0.9 | 73.9 | 94.3 | 60 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 7845 | Lagoon Creek | TN | Haywood | GT5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 84.5 | 0.9 | 73.9 | 94.3 | 60 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 7845 | Lagoon Creek | TN | Haywood | GT6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 84.5 | 0.9 | 73.9 | 94.3 | 60 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 7845 | Lagoon Creek | TN | Haywood | GT7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 84.5 | 0.9 | 73.9 | 94.3 | 60 | N |  |  | OP | X | 7 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 7845 | Lagoon Creek | TN | Haywood | GT8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 84.5 | 0.9 | 73.9 | 94.3 | 60 | N |  |  | OP | X | 7 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 7845 | Lagoon Creek | TN | Haywood | GT9 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 86.2 | 0.9 | 72.7 | 92.8 | 60 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2010 | natural gas combined cycle | TRUE | 18642 | Tennessee Valley Authority | 7845 | Lagoon Creek | TN | Haywood | STG1 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 257.6 | 0.9 | 205 | 235 | 96.8 | N |  |  | OP | X | 9 | 2010 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 9617 | JEA | 7846 | Brandy Branch | FL | Duval | 001 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | FRCC | FRCC | 185 | 0.9 | 178.6 | 191.2 | 85 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas combined cycle | TRUE | 9617 | JEA | 7846 | Brandy Branch | FL | Duval | 002 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | FRCC | FRCC | 185 | 0.9 | 189.8 | 211.1 | 65 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2001 | natural gas combined cycle | TRUE | 9617 | JEA | 7846 | Brandy Branch | FL | Duval | 003 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | FRCC | FRCC | 185 | 0.9 | 189.8 | 211.1 | 65 | N |  |  | OP | X | 10 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2005 | natural gas combined cycle | TRUE | 9617 | JEA | 7846 | Brandy Branch | FL | Duval | 004 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | FRCC | FRCC | 228.1 | 0.85 | 185 | 190 | 65 | N |  |  | OP | X | 2 | 2005 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2001 | petroleum | TRUE | 4305 | City of Coon Rapids | 7847 | Coon Rapids II | IA | Carroll | 1 | Petroleum Liquids | IC |  | S | X | X | WAUECOONRPMUUNCOONRAPIDS_RA |  | 1.8 | 0.95 | 1.7 | 1.8 | 0.2 | N |  |  | SB | Y | 10 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage2001 | petroleum | TRUE | 4305 | City of Coon Rapids | 7847 | Coon Rapids II | IA | Carroll | 2 | Petroleum Liquids | IC |  | S | X | X | WAUECOONRPMUUNCOONRAPIDS_RA |  | 1.8 | 0.95 | 1.7 | 1.8 | 0.2 | N |  |  | SB | Y | 10 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage2001 | petroleum | TRUE | 4305 | City of Coon Rapids | 7847 | Coon Rapids II | IA | Carroll | 3 | Petroleum Liquids | IC |  | S | X | X | WAUECOONRPMUUNCOONRAPIDS_RA |  | 1.8 | 0.95 | 1.7 | 1.8 | 0.2 | N |  |  | SB | Y | 10 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage2002 | natural gas peaker | TRUE | 924 | Associated Electric Coop, Inc | 7848 | Holden | MO | Johnson | 11 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 107.1 | 0.85 | 90 | 113 | 69 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 924 | Associated Electric Coop, Inc | 7848 | Holden | MO | Johnson | 12 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 107.1 | 0.85 | 89 | 107 | 69 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 924 | Associated Electric Coop, Inc | 7848 | Holden | MO | Johnson | 13 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 107.1 | 0.85 | 88 | 115 | 69 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2000 | petroleum | TRUE | 12341 | MidAmerican Energy Co | 7849 | Knoxville Industrial | IA | Marion | 1 | Petroleum Liquids | IC |  | S | X | X | MEC.KNOXIN 1 | MEC.KNOXIN 1 | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 12341 | MidAmerican Energy Co | 7849 | Knoxville Industrial | IA | Marion | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 12341 | MidAmerican Energy Co | 7849 | Knoxville Industrial | IA | Marion | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 12341 | MidAmerican Energy Co | 7849 | Knoxville Industrial | IA | Marion | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N | N
Vintage2000 | petroleum | TRUE | 12341 | MidAmerican Energy Co | 7849 | Knoxville Industrial | IA | Marion | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N | N
Vintage2000 | petroleum | TRUE | 12341 | MidAmerican Energy Co | 7849 | Knoxville Industrial | IA | Marion | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N | N
Vintage2000 | petroleum | TRUE | 12341 | MidAmerican Energy Co | 7849 | Knoxville Industrial | IA | Marion | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N | N
Vintage2000 | petroleum | TRUE | 12341 | MidAmerican Energy Co | 7849 | Knoxville Industrial | IA | Marion | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 12341 | MidAmerican Energy Co | 7850 | Shenandoah | IA | Page | 1 | Petroleum Liquids | IC |  | S | X | X | MEC.SHENDO 1 | MEC.SHENDO 1 | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 12341 | MidAmerican Energy Co | 7850 | Shenandoah | IA | Page | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 12341 | MidAmerican Energy Co | 7850 | Shenandoah | IA | Page | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 12341 | MidAmerican Energy Co | 7850 | Shenandoah | IA | Page | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 12341 | MidAmerican Energy Co | 7850 | Shenandoah | IA | Page | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 12341 | MidAmerican Energy Co | 7850 | Shenandoah | IA | Page | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 12341 | MidAmerican Energy Co | 7850 | Shenandoah | IA | Page | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 12341 | MidAmerican Energy Co | 7850 | Shenandoah | IA | Page | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 12341 | MidAmerican Energy Co | 7850 | Shenandoah | IA | Page | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 12341 | MidAmerican Energy Co | 7850 | Shenandoah | IA | Page | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 12341 | MidAmerican Energy Co | 7851 | Waterloo Lundquist | IA | Black Hawk | 1 | Petroleum Liquids | IC |  | S | X | X | MEC.LUNDQS 1 | MEC.LUNDQS 1 | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N |  | N
Vintage2000 | petroleum | TRUE | 12341 | MidAmerican Energy Co | 7851 | Waterloo Lundquist | IA | Black Hawk | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N |  | N
Vintage2000 | petroleum | TRUE | 12341 | MidAmerican Energy Co | 7851 | Waterloo Lundquist | IA | Black Hawk | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N |  | N
Vintage2000 | petroleum | TRUE | 12341 | MidAmerican Energy Co | 7851 | Waterloo Lundquist | IA | Black Hawk | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 12341 | MidAmerican Energy Co | 7851 | Waterloo Lundquist | IA | Black Hawk | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 12341 | MidAmerican Energy Co | 7851 | Waterloo Lundquist | IA | Black Hawk | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 12341 | MidAmerican Energy Co | 7851 | Waterloo Lundquist | IA | Black Hawk | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 12341 | MidAmerican Energy Co | 7851 | Waterloo Lundquist | IA | Black Hawk | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 12341 | MidAmerican Energy Co | 7851 | Waterloo Lundquist | IA | Black Hawk | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | OP | X | 4 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1998 | petroleum | TRUE | 5056 | City of Denison - (IA) | 7853 | West Receiving | IA | Crawford | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.4 | N |  |  | OP | X | 4 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 16198 | City of Rock Falls - (IL) | 7854 | Avenue A Generator Sets | IL | Whiteside | 1 | Petroleum Liquids | IC |  | S | X | X | PJM/ComEd.ROCKFALLS | PJM/ComEd.ROCKFALLS | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | SB | Y | 9 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2000 | petroleum | TRUE | 16198 | City of Rock Falls - (IL) | 7854 | Avenue A Generator Sets | IL | Whiteside | 2 | Petroleum Liquids | IC |  | S | X | X | PJM/ComEd.ROCKFALLS | PJM/ComEd.ROCKFALLS | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | SB | Y | 9 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | onshore wind | TRUE | 12894 | City of Moorhead - (MN) | 7855 | Moorhead Wind Turbine | MN | Clay | 8 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 0.7 |  | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 5 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WND |  |  |  | N | N | 1 | [24 empty] | N
Vintage2001 | onshore wind | TRUE | 12894 | City of Moorhead - (MN) | 7855 | Moorhead Wind Turbine | MN | Clay | 9 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 0.7 |  | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 9 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WND |  |  |  | N | N | 1 | [24 empty] | N
Vintage2002 | petroleum | TRUE | 7626 | City of Greenfield - (IA) | 7856 | North Generation Plant | IA | Adair | 1 | Petroleum Liquids | IC |  | S | X | X | ALTW.ALTW | ALTW.ALTW | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 1 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2002 | petroleum | TRUE | 7626 | City of Greenfield - (IA) | 7856 | North Generation Plant | IA | Adair | 2 | Petroleum Liquids | IC |  | S | X | X | ALTW.ALTW | ALTW.ALTW | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 1 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2011 | petroleum | TRUE | 7626 | City of Greenfield - (IA) | 7856 | North Generation Plant | IA | Adair | 3 | Petroleum Liquids | IC |  | S | X | X | ALTW.ALTW | ALTW.ALTW | 2.2 | 0.8 | 2.2 | 2.2 | 0.6 | N |  |  | OP | X | 11 | 2011 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2011 | petroleum | TRUE | 7626 | City of Greenfield - (IA) | 7856 | North Generation Plant | IA | Adair | 4 | Petroleum Liquids | IC |  | S | X | X | ALTW.ALTW | ALTW.ALTW | 2.2 | 0.8 | 2.2 | 2.2 | 0.6 | N |  |  | OP | X | 11 | 2011 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2001 | petroleum | TRUE | 18231 | City of Stuart - (IA) | 7857 | Gilliam South | IA | Adair | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.9 | 1.7 | 1.8 | 0.5 | N |  |  | OP | X | 2 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2012 | petroleum | TRUE | 18231 | City of Stuart - (IA) | 7857 | Gilliam South | IA | Adair | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.9 | 2.3 | 2.3 | 0.5 | N |  |  | OP | X | 4 | 2012 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1974 | natural gas peaker | TRUE | 12159 | Midwest Electric Power Inc | 7858 | MEPI GT Facility | IL | Massac | 1 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X | GLH.EEI7B1 | GLH.EEI7B1 | 64.5 | 0.9 | 55 | 56 | 20 | N |  |  | OP | X | 10 | 1974 | 8 | 2022 | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1974 | natural gas peaker | TRUE | 12159 | Midwest Electric Power Inc | 7858 | MEPI GT Facility | IL | Massac | 2 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X | GLH.EEI7B1 | GLH.EEI7B1 | 64.5 | 0.9 | 55 | 56 | 20 | N |  |  | OP | X | 10 | 1974 | 8 | 2022 | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1974 | natural gas peaker | TRUE | 12159 | Midwest Electric Power Inc | 7858 | MEPI GT Facility | IL | Massac | 3 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X | GLH.EEI7B1 | GLH.EEI7B1 | 64.5 | 0.9 | 55 | 56 | 20 | N |  |  | OP | X | 10 | 1974 | 8 | 2022 | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2000 | natural gas peaker | TRUE | 12159 | Midwest Electric Power Inc | 7858 | MEPI GT Facility | IL | Massac | 4 | Natural Gas Fired Combustion Turbine | GT |  | J | X | X | GLH.EEI7B1 | GLH.EEI7B1 | 54 | 0.8 | 37 | 43 | 5 | N |  |  | OP | X | 7 | 2000 | 8 | 2022 | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2000 | natural gas peaker | TRUE | 12159 | Midwest Electric Power Inc | 7858 | MEPI GT Facility | IL | Massac | 5 | Natural Gas Fired Combustion Turbine | GT |  | J | X | X | GLH.EEI7B1 | GLH.EEI7B1 | 54 | 0.8 | 37 | 43 | 5 | N |  |  | OP | X | 7 | 2000 | 8 | 2022 | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2002 | petroleum | TRUE | 17035 | City of Shelbina - (MO) | 7860 | Shelbina Power #3 | MO | Shelby | G7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 4 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 10M | [23 empty] | N |  | N
Vintage2002 | petroleum | TRUE | 17035 | City of Shelbina - (MO) | 7860 | Shelbina Power #3 | MO | Shelby | G8 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 4 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 10M | [23 empty] | N |  | N
Vintage2001 | hydro | TRUE | 40215 | Cordova Electric Coop, Inc | 7862 | Power Creek | AK | Valdez Cordova | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.8 | 2.8 | 2.7 | 0.1 | N |  |  | OP | X | 11 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage2001 | hydro | TRUE | 40215 | Cordova Electric Coop, Inc | 7862 | Power Creek | AK | Valdez Cordova | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.8 | 2.8 | 2.7 | 0.1 | N |  |  | OP | X | 11 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage2001 | natural gas peaker | TRUE | 4716 | Dairyland Power Coop | 7863 | Elk Mound | WI | Chippewa | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | DPC.EKM1 | DPC.DPC | 35.5 | 0.8 | 30.7 | 40.4 | 20.7 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 4716 | Dairyland Power Coop | 7863 | Elk Mound | WI | Chippewa | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | DPC.EKM2 | DPC.DPC | 35.5 | 0.8 | 33.9 | 44.3 | 21.1 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | petroleum | TRUE | 5563 | City of Earlville - (IA) | 7865 | Earlville | IA | Delaware | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.98 | 1.8 | 1.8 | 0 | N |  |  | OP | X | 7 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N | N | N
Vintage2013 | hydro | TRUE | 15500 | Puget Sound Energy Inc | 7867 | Snoqualmie 2 | WA | King | 6A | Conventional Hydroelectric | HY |  | S | X | X |  |  | 14.4 | 0.95 | 12.6 | 12.6 | 5.2 | N |  |  | OP | X | 2 | 2013 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1957 | hydro | TRUE | 15500 | Puget Sound Energy Inc | 7867 | Snoqualmie 2 | WA | King | 7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 24.3 | 0.9 | 21 | 21 | 5 | N |  |  | OP | X | 1 | 1957 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1967 | petroleum | TRUE | 56505 | National Grid Generation LLC | 7869 | Glenwood Landing | NY | Nassau | GT1 | Petroleum Liquids | GT |  | S | X | X | 23712 | 23712 | 16 | 0.85 | 12.6 | 17.6 | 10 | N |  |  | SB | Y | 4 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: KER |  |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage2002 | natural gas peaker | TRUE | 56505 | National Grid Generation LLC | 7869 | Glenwood Landing | NY | Nassau | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 24219 | 24219 | 53 | 0.9 | 42.6 | 47 | 37 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: KER |  |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 56505 | National Grid Generation LLC | 7869 | Glenwood Landing | NY | Nassau | GT5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 24220 | 24220 | 53 | 0.9 | 42.5 | 47 | 37 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: KER |  |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1993 | natural gas combined cycle | TRUE | 15500 | Puget Sound Energy Inc | 7870 | Encogen | WA | Whatcom | CTG1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 39.4 | 0.9 | 34.5 | 42.2 | 21 | N |  |  | OP | X | 3 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1993 | natural gas combined cycle | TRUE | 15500 | Puget Sound Energy Inc | 7870 | Encogen | WA | Whatcom | CTG2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 39.4 | 0.9 | 34.5 | 42.2 | 21 | N |  |  | OP | X | 3 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1993 | natural gas combined cycle | TRUE | 15500 | Puget Sound Energy Inc | 7870 | Encogen | WA | Whatcom | CTG3 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 39.4 | 0.9 | 34.5 | 42.2 | 22 | N |  |  | OP | X | 3 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1993 | natural gas combined cycle | TRUE | 15500 | Puget Sound Energy Inc | 7870 | Encogen | WA | Whatcom | STG | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X |  |  | 58.2 | 0.9 | 55.9 | 55.9 | 30 | N |  |  | OP | X | 4 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2002 | natural gas peaker | TRUE | 25422 | National Power Coop Inc | 7872 | Robert P Mone Plant | OH | Van Wert | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 32419345 | 32419345 | 198 | 0.85 | 145 | 180 | 100 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N | 0 | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 25422 | National Power Coop Inc | 7872 | Robert P Mone Plant | OH | Van Wert | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 32419347 | 32419347 | 198 | 0.85 | 145 | 180 | 100 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N | 0 | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 25422 | National Power Coop Inc | 7872 | Robert P Mone Plant | OH | Van Wert | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 32419349 | 32419349 | 198 | 0.85 | 145 | 180 | 100 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N | 0 | 1H | [23 empty] | Y | N | Y
Vintage2003 | natural gas combined cycle | TRUE | 18454 | Tampa Electric Co | 7873 | H L Culbreath Bayside Power Station | FL | Hillsborough | 1A | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 189.9 | 0.9 | 156 | 183 | 78 | N |  |  | OP | X | 4 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [7 empty] | 12 | 16 | 1 | 2023 | [12 empty] | N | bar: X X X to RC RC RC
Vintage2003 | natural gas combined cycle | TRUE | 18454 | Tampa Electric Co | 7873 | H L Culbreath Bayside Power Station | FL | Hillsborough | 1B | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 189.9 | 0.9 | 156 | 183 | 78 | N |  |  | OP | X | 4 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [7 empty] | 12 | 16 | 1 | 2023 | [12 empty] | N | bar: X X X to RC RC RC
Vintage2003 | natural gas combined cycle | TRUE | 18454 | Tampa Electric Co | 7873 | H L Culbreath Bayside Power Station | FL | Hillsborough | 1C | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 189.9 | 0.9 | 156 | 183 | 78 | N |  |  | OP | X | 4 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [7 empty] | 12 | 16 | 1 | 2023 | [12 empty] | N | bar: X X X to RC RC RC
Vintage1965 | natural gas combined cycle | TRUE | 18454 | Tampa Electric Co | 7873 | H L Culbreath Bayside Power Station | FL | Hillsborough | 1ST | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X |  |  | 239.4 | 0.85 | 233 | 243 | 47 | N |  |  | OP | X | 11 | 1965 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [7 empty] | 12 | 16 | 1 | 2023 | [12 empty] | N | N | bar: X X X to RC RC RC
Vintage2004 | natural gas combined cycle | TRUE | 18454 | Tampa Electric Co | 7873 | H L Culbreath Bayside Power Station | FL | Hillsborough | 2A | Natural Gas Fired Combined Cycle | CT | CC2 | S | X | Y |  |  | 189.9 | 0.9 | 156 | 183 | 78 | N |  |  | OP | X | 1 | 2004 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [7 empty] | 14 | 16 | 1 | 2024 | [12 empty] | N | N | bar: X X X to RC RC RC
Vintage2004 | natural gas combined cycle | TRUE | 18454 | Tampa Electric Co | 7873 | H L Culbreath Bayside Power Station | FL | Hillsborough | 2B | Natural Gas Fired Combined Cycle | CT | CC2 | S | X | Y |  |  | 189.9 | 0.9 | 156 | 183 | 78 | N |  |  | OP | X | 1 | 2004 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [7 empty] | 14 | 16 | 1 | 2024 | [12 empty] | N | N | bar: X X X to RC RC RC
Vintage2004 | natural gas combined cycle | TRUE | 18454 | Tampa Electric Co | 7873 | H L Culbreath Bayside Power Station | FL | Hillsborough | 2C | Natural Gas Fired Combined Cycle | CT | CC2 | S | X | Y |  |  | 189.9 | 0.9 | 156 | 183 | 78 | N |  |  | OP | X | 1 | 2004 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [7 empty] | 14 | 16 | 1 | 2024 | [12 empty] | N | bar: X X X to RC RC RC
Vintage2004 | natural gas combined cycle | TRUE | 18454 | Tampa Electric Co | 7873 | H L Culbreath Bayside Power Station | FL | Hillsborough | 2D | Natural Gas Fired Combined Cycle | CT | CC2 | S | X | Y |  |  | 189.9 | 0.9 | 156 | 183 | 78 | N |  |  | OP | X | 1 | 2004 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [7 empty] | 14 | 16 | 1 | 2024 | [12 empty] | N | bar: X X X to RC RC RC
Vintage1967 | natural gas combined cycle | TRUE | 18454 | Tampa Electric Co | 7873 | H L Culbreath Bayside Power Station | FL | Hillsborough | 2ST | Natural Gas Fired Combined Cycle | CA | CC2 | S | N | X |  |  | 445.7 | 0.9 | 305 | 315 | 52 | N |  |  | OP | X | 10 | 1967 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [7 empty] | 14 | 16 | 1 | 2024 | [12 empty] | N | bar: X X X to RC RC RC
Vintage2009 | natural gas peaker | TRUE | 18454 | Tampa Electric Co | 7873 | H L Culbreath Bayside Power Station | FL | Hillsborough | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 69.9 | 0.85 | 56 | 61 | 14 | N |  |  | OP | X | 7 | 2009 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2009 | natural gas peaker | TRUE | 18454 | Tampa Electric Co | 7873 | H L Culbreath Bayside Power Station | FL | Hillsborough | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 69.9 | 0.85 | 56 | 61 | 14 | N |  |  | OP | X | 7 | 2009 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 10M | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage2009 | natural gas peaker | TRUE | 18454 | Tampa Electric Co | 7873 | H L Culbreath Bayside Power Station | FL | Hillsborough | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 69.9 | 0.85 | 56 | 61 | 14 | N |  |  | OP | X | 4 | 2009 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 10M | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage2009 | natural gas peaker | TRUE | 18454 | Tampa Electric Co | 7873 | H L Culbreath Bayside Power Station | FL | Hillsborough | 6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 69.9 | 0.85 | 56 | 61 | 14 | N |  |  | OP | X | 4 | 2009 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 10M | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage2000 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7874 | Edgerton | OH | Williams | 1 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 8 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage2000 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7874 | Edgerton | OH | Williams | 2 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 8 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1998 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7878 | Wellington | OH | Lorain | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 1 | N |  |  | SB | Y | 2 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2000 | petroleum | TRUE | 15293 | Powell Valley Electric Coop | 7883 | Powell Valley | TN | Hancock | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.9 | 1.8 | 1.8 | 0.4 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 15293 | Powell Valley Electric Coop | 7883 | Powell Valley | TN | Hancock | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.9 | 1.8 | 1.8 | 0.4 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 15293 | Powell Valley Electric Coop | 7883 | Powell Valley | TN | Hancock | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.9 | 1.8 | 1.8 | 0.4 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 15293 | Powell Valley Electric Coop | 7883 | Powell Valley | TN | Hancock | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.9 | 1.8 | 1.8 | 0.4 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage2000 | petroleum | TRUE | 15293 | Powell Valley Electric Coop | 7883 | Powell Valley | TN | Hancock | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.9 | 1.8 | 1.8 | 0.4 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage2000 | petroleum | TRUE | 15293 | Powell Valley Electric Coop | 7883 | Powell Valley | TN | Hancock | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.9 | 1.8 | 1.8 | 0.4 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage2000 | petroleum | TRUE | 15293 | Powell Valley Electric Coop | 7883 | Powell Valley | TN | Hancock | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.9 | 1.8 | 1.8 | 0.4 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 15293 | Powell Valley Electric Coop | 7883 | Powell Valley | TN | Hancock | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.9 | 1.8 | 1.8 | 0.4 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 15293 | Powell Valley Electric Coop | 7883 | Powell Valley | TN | Hancock | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.9 | 1.8 | 1.8 | 0.4 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 15293 | Powell Valley Electric Coop | 7883 | Powell Valley | TN | Hancock | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.9 | 1.8 | 1.8 | 0.4 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 15293 | Powell Valley Electric Coop | 7883 | Powell Valley | TN | Hancock | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.9 | 1.8 | 1.8 | 0.4 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2000 | petroleum | FALSE | 4775 | Dakota Magic Casino | 7884 | Dakota Magic | ND | Richland | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.1 | N |  |  | SB | Y | 2 | 2000 |  |  | N | Commercial Non-CHP | 4 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N | N
Vintage1999 | onshore wind | TRUE | 11479 | Madison Gas & Electric Co | 7886 | Wind Turbine | WI | Kewaunee | 1 | Onshore Wind Turbine | WT |  | S | X | X | MGE.LRRGTOT | MGE.LRRGTOT | 11 |  | 0.7 | 0.7 |  | N |  |  | OP | X | 6 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WND |  |  |  | N | N | 17 | [21 empty] | N |  |  | N
Vintage2004 | natural gas combined cycle | TRUE | 11018 | Lincoln Electric System | 7887 | Terry Bundy Generating Station | NE | Lancaster | 1 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | LES84_BLUFPLT1 | LES_TBGS_CC1 | 28.2 | 0.9 | 27.3 | 28.6 | 10 | N |  |  | OP | X | 8 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 12H |  |  |  |  | N | [18 empty] | N |  | N
Vintage2003 | natural gas combined cycle | TRUE | 11018 | Lincoln Electric System | 7887 | Terry Bundy Generating Station | NE | Lancaster | 2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y | LES84_BLUFPLT1 | LES_TBGS_CC1 | 60.5 | 0.85 | 46 | 48 | 20 | N |  |  | OP | X | 10 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2004 | natural gas combined cycle | TRUE | 11018 | Lincoln Electric System | 7887 | Terry Bundy Generating Station | NE | Lancaster | 3 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y | LES84_BLUFPLT1 | LES_TBGS_CC1 | 60.5 | 0.85 | 45.2 | 48 | 20 | N |  |  | OP | X | 4 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2003 | natural gas peaker | TRUE | 11018 | Lincoln Electric System | 7887 | Terry Bundy Generating Station | NE | Lancaster | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | LES84_BLUFUNSALT_VALLEY_4_RA__ | LES_TBGS_CT4 | 60.5 | 0.85 | 45.4 | 48 | 20 | N |  |  | OP | X | 8 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2004 | petroleum | TRUE | 11018 | Lincoln Electric System | 7887 | Terry Bundy Generating Station | NE | Lancaster | BSU | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.6 | 1.6 | 0 | N |  |  | OP | X | 7 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N |  | N
Vintage2014 | biomass | TRUE | 11018 | Lincoln Electric System | 7887 | Terry Bundy Generating Station | NE | Lancaster | LFG1 | Landfill Gas | IC |  | S | X | X | LES84_BLUFUNTBGS_LFG_G1_RA | LES_LFG_1 | 1.6 | 0.8 | 1.6 | 1.6 | 1.1 | N |  |  | OP | X | 1 | 2014 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: LFG |  |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage2014 | biomass | TRUE | 11018 | Lincoln Electric System | 7887 | Terry Bundy Generating Station | NE | Lancaster | LFG2 | Landfill Gas | IC |  | S | X | X | LES84_BLUFUNTBGS_LFG_G1_RA | LES_LFG_1 | 1.6 | 0.8 | 1.6 | 1.6 | 1.1 | N |  |  | OP | X | 1 | 2014 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: LFG |  |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage2014 | biomass | TRUE | 11018 | Lincoln Electric System | 7887 | Terry Bundy Generating Station | NE | Lancaster | LFG3 | Landfill Gas | IC |  | S | X | X | LES84_BLUFUNTBGS_LFG_G1_RA | LES_LFG_1 | 1.6 | 0.8 | 1.6 | 1.6 | 1.1 | N |  |  | OP | X | 1 | 2014 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: LFG |  |  |  | N | N |  | 1H | [23 empty] | N |  | N
Vintage2003 | natural gas combined cycle | TRUE | 17650 | Southern Power Co | 7897 | E B Harris Electric Generating Plant | AL | Autauga | CT1A | Natural Gas Fired Combined Cycle | CT | G103 | S | X | N |  |  | 185 | 0.85 | 182.6 | 194.9 | 125 | N |  |  | OP | X | 6 | 2003 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2003 | natural gas combined cycle | TRUE | 17650 | Southern Power Co | 7897 | E B Harris Electric Generating Plant | AL | Autauga | CT1B | Natural Gas Fired Combined Cycle | CT | G103 | S | X | N |  |  | 185 | 0.85 | 182.6 | 194.9 | 125 | N |  |  | OP | X | 6 | 2003 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2003 | natural gas combined cycle | TRUE | 17650 | Southern Power Co | 7897 | E B Harris Electric Generating Plant | AL | Autauga | CT2A | Natural Gas Fired Combined Cycle | CT | G104 | S | X | N |  |  | 185 | 0.85 | 178.3 | 192.5 | 125 | N |  |  | OP | X | 6 | 2003 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2003 | natural gas combined cycle | TRUE | 17650 | Southern Power Co | 7897 | E B Harris Electric Generating Plant | AL | Autauga | CT2B | Natural Gas Fired Combined Cycle | CT | G104 | S | X | N |  |  | 185 | 0.85 | 178.3 | 192.5 | 125 | N |  |  | OP | X | 6 | 2003 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2003 | natural gas combined cycle | TRUE | 17650 | Southern Power Co | 7897 | E B Harris Electric Generating Plant | AL | Autauga | ST1 | Natural Gas Fired Combined Cycle | CA | G103 | S | Y | X |  |  | 282 | 0.9 | 293 | 293 | 130 | N |  |  | OP | X | 6 | 2003 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2003 | natural gas combined cycle | TRUE | 17650 | Southern Power Co | 7897 | E B Harris Electric Generating Plant | AL | Autauga | ST2 | Natural Gas Fired Combined Cycle | CA | G104 | S | Y | X |  |  | 282 | 0.9 | 300 | 300 | 130 | N |  |  | OP | X | 6 | 2003 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2000 | petroleum | TRUE | 13464 | Village of New Knoxville - (OH) | 7898 | New Knoxville | OH | Auglaize | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1 | 1 | 0.2 | N |  |  | OS | X | 9 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage2004 | natural gas combined cycle | TRUE | 1015 | Austin Energy | 7900 | Sand Hill | TX | Travis | 5A | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 198 | 0.85 | 161 | 180 | 92 | N |  |  | OP | X | 9 | 2004 |  |  | N | Electric Utility | 1 | [14 empty] | 12H | [23 empty] | N |  | N | bar: X X X to RC RC RC
Vintage2004 | natural gas combined cycle | TRUE | 1015 | Austin Energy | 7900 | Sand Hill | TX | Travis | 5C | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 190 | 0.85 | 151 | 164 | 55 | N |  |  | OP | X | 9 | 2004 |  |  | N | Electric Utility | 1 | [14 empty] | 12H | [23 empty] | N |  | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 1015 | Austin Energy | 7900 | Sand Hill | TX | Travis | SH1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 51.4 | 0.85 | 47.3 | 47.3 | 12 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | [14 empty] | 10M | [23 empty] | N |  | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 1015 | Austin Energy | 7900 | Sand Hill | TX | Travis | SH2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 51.4 | 0.85 | 47.3 | 47.3 | 12 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | [14 empty] | 10M | [23 empty] | N |  | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 1015 | Austin Energy | 7900 | Sand Hill | TX | Travis | SH3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 51.4 | 0.85 | 47.3 | 47.3 | 12 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | [14 empty] | 10M | [23 empty] | N |  | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 1015 | Austin Energy | 7900 | Sand Hill | TX | Travis | SH4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 51.4 | 0.85 | 47.3 | 47.3 | 12 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | [14 empty] | 10M | [23 empty] | N |  | N | bar: X X X to RC RC RC
Vintage2010 | natural gas peaker | TRUE | 1015 | Austin Energy | 7900 | Sand Hill | TX | Travis | SH6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 51.4 | 0.9 | 47.3 | 47.3 | 15 | N |  |  | OP | X | 6 | 2010 |  |  | N | Electric Utility | 1 | [14 empty] | 10M | [23 empty] | N |  | N | bar: X X X to RC RC RC
Vintage2010 | natural gas peaker | TRUE | 1015 | Austin Energy | 7900 | Sand Hill | TX | Travis | SH7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 51.4 | 0.9 | 47.3 | 47.3 | 12 | N |  |  | OP | X | 6 | 2010 |  |  | N | Electric Utility | 1 | [14 empty] | 10M | [23 empty] | N |  | N | bar: X X X to RC RC RC
Vintage1985 | lignite | TRUE | 17698 | Southwestern Electric Power Co | 7902 | Pirkey | TX | Harrison | 1 | Conventional Steam Coal | ST |  | J | X | X |  |  | 721 | 0.9 | 650 | 650 | 300 | N |  |  | OP | X | 1 | 1985 | 3 | 2023 | N | Electric Utility | 1 | X | LIG | NG | SUB |  |  |  | NG |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage2002 | natural gas peaker | TRUE | 17833 | City Utilities of Springfield - (MO) | 7903 | McCartney | MO | Greene | MGS1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SPRM_MCCT1 |  | 58.9 | 0.85 | 50 | 50 | 30 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage2002 | natural gas peaker | TRUE | 17833 | City Utilities of Springfield - (MO) | 7903 | McCartney | MO | Greene | MSG2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SPRM_MCCT2 |  | 58.9 | 0.85 | 50 | 50 | 30 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X X X to RC RC RC
Vintage1984 | hydro | TRUE | 10325 | Kings River Conservation Dist | 7907 | Pine Flat | CA | Fresno | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 55 | 0.95 | 55 | 55 | 5 | N |  |  | OP | X | 1 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N | 0 | 1H | [20 empty] | N |  |  | N
Vintage1984 | hydro | TRUE | 10325 | Kings River Conservation Dist | 7907 | Pine Flat | CA | Fresno | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 55 | 0.95 | 55 | 55 | 5 | N |  |  | OP | X | 1 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1984 | hydro | TRUE | 10325 | Kings River Conservation Dist | 7907 | Pine Flat | CA | Fresno | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 55 | 0.95 | 55 | 55 | 5 | N |  |  | OP | X | 4 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage2001 | natural gas peaker | TRUE | 15296 | New York Power Authority | 7909 | Vernon Boulevard | NY | Queens | VG02 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 47 | 1 | 40 | 40 | 1 | N |  |  | OP | X | 8 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 15296 | New York Power Authority | 7909 | Vernon Boulevard | NY | Queens | VG03 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 47 | 1 | 39.9 | 39.9 | 1 | N |  |  | OP | X | 8 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 15296 | New York Power Authority | 7910 | Joseph J Seymour Power Project | NY | Kings | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 47 | 1 | 40 | 40 | 1 | N |  |  | OP | X | 7 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 15296 | New York Power Authority | 7910 | Joseph J Seymour Power Project | NY | Kings | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 47 | 1 | 39.9 | 39.9 | 1 | N |  |  | OP | X | 7 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage1921 | hydro | TRUE | 64145 | Kern and Tule Hydro LLC | 7911 | Kern Canyon | CA | Kern | 1 | Conventional Hydroelectric | HY |  | S | X | X | KRNCNYN_6_N001 | KRNCNYN_6_N001 | 11.5 | 0.9 | 11.5 | 11.5 | 0 | N |  |  | OS | X | 8 | 1921 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2001 | natural gas peaker | TRUE | 15296 | New York Power Authority | 7912 | Brentwood | NY | Suffolk | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 47 | 1 | 46 | 46 | 1 | N |  |  | OP | X | 7 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 15296 | New York Power Authority | 7913 | Hell Gate | NY | Bronx | HG01 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 47 | 1 | 39.9 | 39.9 | 1 | N |  |  | OP | X | 7 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 15296 | New York Power Authority | 7913 | Hell Gate | NY | Bronx | HG02 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 47 | 1 | 40 | 40 | 1 | N |  |  | OP | X | 7 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 15296 | New York Power Authority | 7914 | Harlem River Yard | NY | Bronx | HR01 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 47 | 1 | 39.9 | 39.9 | 1 | N |  |  | OP | X | 7 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 15296 | New York Power Authority | 7914 | Harlem River Yard | NY | Bronx | HR02 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 47 | 1 | 40 | 40 | 1 | N |  |  | OP | X | 7 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 15296 | New York Power Authority | 7915 | North 1st | NY | Kings | N01 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 47 | 1 | 46 | 46 | 1 | N |  |  | OP | X | 8 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage2002 | natural gas peaker | TRUE | 13994 | Oglethorpe Power Corporation | 7916 | Talbot County Energy | GA | Talbot | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 121 | 0.85 | 97 | 114 | 70 | N |  |  | OP | X | 5 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2002 | natural gas peaker | TRUE | 13994 | Oglethorpe Power Corporation | 7916 | Talbot County Energy | GA | Talbot | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 121 | 0.85 | 95.8 | 114 | 70 | N |  |  | OP | X | 4 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2002 | natural gas peaker | TRUE | 13994 | Oglethorpe Power Corporation | 7916 | Talbot County Energy | GA | Talbot | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 121 | 0.85 | 96.2 | 114 | 70 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2002 | natural gas peaker | TRUE | 13994 | Oglethorpe Power Corporation | 7916 | Talbot County Energy | GA | Talbot | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 121 | 0.85 | 97.3 | 114 | 70 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2003 | natural gas peaker | TRUE | 13994 | Oglethorpe Power Corporation | 7916 | Talbot County Energy | GA | Talbot | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 121 | 0.85 | 96.5 | 114 | 70 | N |  |  | OP | X | 5 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2003 | natural gas peaker | TRUE | 13994 | Oglethorpe Power Corporation | 7916 | Talbot County Energy | GA | Talbot | 6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 121 | 0.85 | 96.3 | 114 | 70 | N |  |  | OP | X | 5 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2003 | natural gas combined cycle | TRUE | 13994 | Oglethorpe Power Corporation | 7917 | Chattahoochee Energy Facility | GA | Heard | 1 | Natural Gas Fired Combined Cycle | CT | 2224 | S | X | N |  |  | 176 | 0.85 | 145.5 | 169.5 | 65 | N |  |  | OP | X | 2 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage2003 | natural gas combined cycle | TRUE | 13994 | Oglethorpe Power Corporation | 7917 | Chattahoochee Energy Facility | GA | Heard | 2 | Natural Gas Fired Combined Cycle | CT | 2224 | S | X | N |  |  | 176 | 0.85 | 141.5 | 167.5 | 130 | N |  |  | OP | X | 2 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage2003 | natural gas combined cycle | TRUE | 13994 | Oglethorpe Power Corporation | 7917 | Chattahoochee Energy Facility | GA | Heard | 3 | Natural Gas Fired Combined Cycle | CA | 2224 | S | Y | X |  |  | 187.7 | 0.85 | 179 | 189 | 130 | N |  |  | OP | X | 2 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage2001 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7918 | Galion | OH | Crawford | 1 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2001 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7918 | Galion | OH | Crawford | 2 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2001 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7918 | Galion | OH | Crawford | 3 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 7 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2001 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7919 | Seville | OH | Medina | 1 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2001 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7919 | Seville | OH | Medina | 2 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2001 | petroleum | TRUE | 40577 | American Mun Power-Ohio, Inc | 7919 | Seville | OH | Medina | 3 | Petroleum Liquids | IC |  | J | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.8 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2001 | petroleum | TRUE | 19062 | City of Traer - (IA) | 7920 | Traer South | IA | Tama | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 1.6 | N |  |  | SB | Y | 4 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage2001 | petroleum | TRUE | 11611 | City of Maquoketa - (IA) | 7921 | Maquoketa 2 | IA | Jackson | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.95 | 1.2 | 1.2 | 0.6 | N |  |  | SB | Y | 7 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2001 | petroleum | TRUE | 11611 | City of Maquoketa - (IA) | 7921 | Maquoketa 2 | IA | Jackson | 12 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.95 | 1.3 | 1.3 | 0.6 | N |  |  | SB | Y | 7 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2002 | petroleum | TRUE | 11611 | City of Maquoketa - (IA) | 7921 | Maquoketa 2 | IA | Jackson | 13 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.95 | 1.3 | 1.3 | 0.6 | N |  |  | SB | Y | 6 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2002 | petroleum | TRUE | 11611 | City of Maquoketa - (IA) | 7921 | Maquoketa 2 | IA | Jackson | 14 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.95 | 1.3 | 1.3 | 0.6 | N |  |  | SB | Y | 6 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2000 | petroleum | TRUE | 241 | Albertville Municipal Utilities Board | 7924 | Albertville | AL | Marshall | DG1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 0.9 | 0.9 | 0.3 | N |  |  | OP | X | 2 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage2000 | petroleum | TRUE | 241 | Albertville Municipal Utilities Board | 7924 | Albertville | AL | Marshall | DG2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 0.9 | 0.9 | 0.3 | N |  |  | OP | X | 2 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage2000 | petroleum | TRUE | 241 | Albertville Municipal Utilities Board | 7924 | Albertville | AL | Marshall | DG3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 0.9 | 0.9 | 0.3 | N |  |  | OP | X | 2 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage2000 | petroleum | TRUE | 241 | Albertville Municipal Utilities Board | 7924 | Albertville | AL | Marshall | DG4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 0.9 | 0.9 | 0.3 | N |  |  | OP | X | 2 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage2001 | natural gas peaker | TRUE | 7570 | Great River Energy | 7925 | Lakefield Junction | MN | Martin | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | GRE.LKFLGR1 | GRE.LKFLGR1 | 89.3 | 0.85 | 77.5 | 91.7 | 45 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 7570 | Great River Energy | 7925 | Lakefield Junction | MN | Martin | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | GRE.LKFLGR2 | GRE.LKFLGR2 | 89.3 | 0.85 | 77.7 | 91.7 | 45 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 7570 | Great River Energy | 7925 | Lakefield Junction | MN | Martin | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | GRE.LKFLGR3 | GRE,LKFLGR3 | 89.3 | 0.85 | 77.3 | 91.7 | 45 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 7570 | Great River Energy | 7925 | Lakefield Junction | MN | Martin | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | GRE.LKFLGR4 | GRE.LKFLGR4 | 89.3 | 0.85 | 77.7 | 91.7 | 45 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  |  | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 7570 | Great River Energy | 7925 | Lakefield Junction | MN | Martin | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | GRE.LKFLGR5 | GRE.LKFLGR5 | 89.3 | 0.85 | 78 | 91.7 | 45 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  |  | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 7570 | Great River Energy | 7925 | Lakefield Junction | MN | Martin | 6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | GRE.LKFLGR6 | GRE.LKFLGR6 | 89.3 | 0.85 | 77.4 | 91.7 | 45 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  |  | N |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | petroleum | TRUE | 7570 | Great River Energy | 7925 | Lakefield Junction | MN | Martin | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | SB | N | 4 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  |  | N |  | 10M | [23 empty] | N | N
Vintage2002 | petroleum | TRUE | 18204 | City of Strawberry Point | 7926 | South Strawberry | IA | Clayton | 1A | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 1 | 1.8 | 1.8 | 1.8 | N |  |  | SB | Y | 1 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage2002 | petroleum | TRUE | 18204 | City of Strawberry Point | 7926 | South Strawberry | IA | Clayton | 2A | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 1 | 1.8 | 1.8 | 1.8 | N |  |  | SB | Y | 1 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2000 | onshore wind | TRUE | 18642 | Tennessee Valley Authority | 7927 | Buffalo Mountain | TN | Anderson | 1 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 0.6 |  | 0.7 | 0.7 | 0 | N |  |  | OP | X | 10 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WND |  |  |  | N |  | 1
Vintage2000 | onshore wind | TRUE | 18642 | Tennessee Valley Authority | 7927 | Buffalo Mountain | TN | Anderson | 2 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 0.6 |  | 0.7 | 0.7 | 0 | N |  |  | OP | X | 10 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WND |  |  |  | N |  | 1
Vintage2000 | onshore wind | TRUE | 18642 | Tennessee Valley Authority | 7927 | Buffalo Mountain | TN | Anderson | 3 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 0.6 |  | 0.7 | 0.7 | 0 | N |  |  | OP | X | 10 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WND |  |  |  | N |  | 1
Vintage2003 | natural gas peaker | TRUE | 10000 | Evergy Metro | 7928 | Osawatomie | KS | Miami | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | KCPLPAOLAUNOSA1 | PAOLAUNOSA1 | 102 | 0.85 | 75.7 |  | 50 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2003 | natural gas peaker | TRUE | 10000 | Evergy Metro | 7929 | West Gardner | KS | Johnson | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | KCPLBULLCRK5UNWGR1 | BULLCRK5UNWGR1 | 102 | 0.85 | 79.5 |  | 30 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2003 | natural gas peaker | TRUE | 10000 | Evergy Metro | 7929 | West Gardner | KS | Johnson | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | KCPLBULLCRK5UNWGR2 | BULLCRK5UNWGR2 | 102 | 0.85 | 78.6 |  | 30 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2003 | natural gas peaker | TRUE | 10000 | Evergy Metro | 7929 | West Gardner | KS | Johnson | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | KCPLBULLCRK5UNWGR3 | BULLCRK5UNWGR3 | 102 | 0.85 | 77.3 |  | 30 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2003 | natural gas peaker | TRUE | 10000 | Evergy Metro | 7929 | West Gardner | KS | Johnson | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | KCPLBULLCRK5UNWGR4 | BULLCRK5UNWGR4 | 102 | 0.85 | 77.5 |  | 30 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2002 | natural gas peaker | TRUE | 16440 | City of Russell - (KS) | 7930 | Russell Energy Center | KS | Russell | T-1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | KMEA_EMP2_RUSS1 | KMEA_EMP2_RUSS2 | 7.5 | 0.8 | 6 | 7.9 | 4.7 | N |  |  | OP | X | 2 | 2002 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2002 | natural gas peaker | TRUE | 16440 | City of Russell - (KS) | 7930 | Russell Energy Center | KS | Russell | T-2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | KMEA_EMP2_RUSS1 | KMEA_EMP2_RUSS2 | 7.5 | 0.8 | 6 | 7.9 | 4.7 | N |  |  | OP | X | 2 | 2002 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2003 | natural gas combined cycle | TRUE | 20169 | Avista Corp | 7931 | Coyote Springs II | OR | Morrow | 1 | Natural Gas Fired Combined Cycle | CT | U2CT | S | X | N |  |  | 170 | 0.85 | 173 | 207 | 65 | N |  |  | OP | X | 7 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2003 | natural gas combined cycle | TRUE | 20169 | Avista Corp | 7931 | Coyote Springs II | OR | Morrow | 2 | Natural Gas Fired Combined Cycle | CA | U2CT | S | Y | X |  |  | 117 | 0.9 | 117 | 117 | 57 | N |  |  | OP | X | 7 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2001 | natural gas peaker | TRUE | 20910 | Wolverine Power Supply Coop | 7932 | Gaylord - Wolverine | MI | Otsego | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | CONS.GYRD1WPSC |  | 23.4 | 0.8 | 20.2 | 27.1 | 11.7 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 20910 | Wolverine Power Supply Coop | 7932 | Gaylord - Wolverine | MI | Otsego | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | CONS.GYRD2WPSC |  | 23.4 | 0.8 | 20.2 | 27.1 | 11.7 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 20910 | Wolverine Power Supply Coop | 7932 | Gaylord - Wolverine | MI | Otsego | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | CONS.GYRD3WPSC |  | 23.4 | 0.8 | 20.2 | 27.1 | 11.7 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2001 | petroleum | TRUE | 16198 | City of Rock Falls - (IL) | 7934 | Industrial Park | IL | Whiteside | 3 | Petroleum Liquids | IC |  | S | X | X | PJM/ComEd.ROCKFALLS | PJM/ComEd.ROCKFALLS | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 7 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2001 | petroleum | TRUE | 16198 | City of Rock Falls - (IL) | 7934 | Industrial Park | IL | Whiteside | 4 | Petroleum Liquids | IC |  | S | X | X | PJM/ComEd.ROCKFALLS | PJM/ComEd.ROCKFALLS | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 7 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2001 | petroleum | TRUE | 16198 | City of Rock Falls - (IL) | 7934 | Industrial Park | IL | Whiteside | 5 | Petroleum Liquids | IC |  | S | X | X | PJM/ComEd.ROCKFALLS | PJM/ComEd.ROCKFALLS | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 7 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2002 | petroleum | TRUE | 16198 | City of Rock Falls - (IL) | 7934 | Industrial Park | IL | Whiteside | 6 | Petroleum Liquids | IC |  | S | X | X | PJM/ComEd.ROCKFALLS | PJM/ComEd.ROCKFALLS | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2002 | petroleum | TRUE | 16198 | City of Rock Falls - (IL) | 7934 | Industrial Park | IL | Whiteside | 7 | Petroleum Liquids | IC |  | S | X | X | PJM/ComEd.ROCKFALLS | PJM/ComEd.ROCKFALLS | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2011 | petroleum | TRUE | 16198 | City of Rock Falls - (IL) | 7934 | Industrial Park | IL | Whiteside | 8 | Petroleum Liquids | IC |  | S | X | X | PJM/ComEd.ROCKFALLS | PJM/ComEd.ROCKFALLS | 2.2 | 0.8 | 2.2 | 2.2 | 0.5 | N |  |  | OP | X | 7 | 2011 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  |  | N |  | 10M | [23 empty] | N | N | N
Vintage2011 | petroleum | TRUE | 16198 | City of Rock Falls - (IL) | 7934 | Industrial Park | IL | Whiteside | 9 | Petroleum Liquids | IC |  | S | X | X | PJM/ComEd.ROCKFALLS | PJM/ComEd.ROCKFALLS | 2.2 | 0.8 | 2.2 | 2.2 | 0.5 | N |  |  | OP | X | 7 | 2011 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  |  | N |  | 10M | [23 empty] | N | N | N
Vintage2000 | petroleum | TRUE | 19150 | Trenton Municipal Utilities - (MO) | 7935 | Trenton South | MO | Grundy | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 0.7 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 19150 | Trenton Municipal Utilities - (MO) | 7935 | Trenton South | MO | Grundy | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 0.7 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 19150 | Trenton Municipal Utilities - (MO) | 7935 | Trenton South | MO | Grundy | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 0.7 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2000 | petroleum | TRUE | 19150 | Trenton Municipal Utilities - (MO) | 7935 | Trenton South | MO | Grundy | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 0.7 | N |  |  | OP | X | 7 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2004 | petroleum | TRUE | 19150 | Trenton Municipal Utilities - (MO) | 7935 | Trenton South | MO | Grundy | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.7 | N |  |  | OP | X | 4 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2004 | petroleum | TRUE | 19150 | Trenton Municipal Utilities - (MO) | 7935 | Trenton South | MO | Grundy | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.7 | N |  |  | OP | X | 4 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2004 | petroleum | TRUE | 19150 | Trenton Municipal Utilities - (MO) | 7935 | Trenton South | MO | Grundy | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.7 | N |  |  | OP | X | 4 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2002 | onshore wind | TRUE | 20160 | Energy Northwest | 7936 | Nine Canyon | WA | Benton | 1 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 95.9 |  | 95 | 95 | 0 | N |  |  | OP | X | 9 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WND |  |  |  | N |  | 63 | [24 empty] | N
Vintage2002 | petroleum | TRUE | 40229 | Old Dominion Electric Coop | 7940 | Ponton Diesel Generating Facility | VA | Amelia | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.2 | N |  |  | SB | Y | 12 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N
Vintage2002 | petroleum | TRUE | 40229 | Old Dominion Electric Coop | 7940 | Ponton Diesel Generating Facility | VA | Amelia | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.2 | N |  |  | SB | Y | 12 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N
Vintage2002 | petroleum | TRUE | 40229 | Old Dominion Electric Coop | 7941 | Nottoway Diesel Generating Facility | VA | Southampton | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.2 | N |  |  | SB | Y | 11 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N
Vintage2002 | petroleum | TRUE | 40229 | Old Dominion Electric Coop | 7941 | Nottoway Diesel Generating Facility | VA | Southampton | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.2 | N |  |  | SB | Y | 11 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N
Vintage2001 | hydro | TRUE | 12397 | Metropolitan Water District of S CA | 7942 | Diamond Valley Lake | CA | Riverside | 10 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.3 | 0.9 | 3.3 | 3.3 | 2 | N |  |  | OP | X | 12 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage2001 | hydro | TRUE | 12397 | Metropolitan Water District of S CA | 7942 | Diamond Valley Lake | CA | Riverside | 11 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.3 | 0.9 | 3.3 | 3.3 | 2 | N |  |  | OP | X | 12 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage2001 | hydro | TRUE | 12397 | Metropolitan Water District of S CA | 7942 | Diamond Valley Lake | CA | Riverside | 12 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.3 | 0.9 | 3.3 | 3.3 | 2 | N |  |  | OP | X | 12 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage2001 | hydro | TRUE | 12397 | Metropolitan Water District of S CA | 7942 | Diamond Valley Lake | CA | Riverside | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.3 | 0.9 | 3.3 | 3.3 | 2 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage2001 | hydro | TRUE | 12397 | Metropolitan Water District of S CA | 7942 | Diamond Valley Lake | CA | Riverside | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.3 | 0.9 | 3.3 | 3.3 | 2 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage2001 | hydro | TRUE | 12397 | Metropolitan Water District of S CA | 7942 | Diamond Valley Lake | CA | Riverside | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.3 | 0.9 | 3.3 | 3.3 | 2 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage2001 | hydro | TRUE | 12397 | Metropolitan Water District of S CA | 7942 | Diamond Valley Lake | CA | Riverside | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.3 | 0.9 | 3.3 | 3.3 | 2 | N |  |  | OP | X | 12 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage2001 | hydro | TRUE | 12397 | Metropolitan Water District of S CA | 7942 | Diamond Valley Lake | CA | Riverside | 7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.3 | 0.9 | 3.3 | 3.3 | 2 | N |  |  | OP | X | 12 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage2001 | hydro | TRUE | 12397 | Metropolitan Water District of S CA | 7942 | Diamond Valley Lake | CA | Riverside | 8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.3 | 0.9 | 3.3 | 3.3 | 2 | N |  |  | OP | X | 12 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT | [6 empty] | 10M
Vintage2004 | natural gas combined cycle | TRUE | 13100 | Municipal Electric Authority | 7946 | Wansley Unit 9 | GA | Heard | CT1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 183.6 | 0.85 | 139 | 165.1 | 110 | N |  |  | OP | X | 6 | 2004 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2004 | natural gas combined cycle | TRUE | 13100 | Municipal Electric Authority | 7946 | Wansley Unit 9 | GA | Heard | CT2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 183.6 | 0.85 | 140.1 | 167.9 | 110 | N |  |  | OP | X | 6 | 2004 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2004 | natural gas combined cycle | TRUE | 13100 | Municipal Electric Authority | 7946 | Wansley Unit 9 | GA | Heard | ST1 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 226.9 | 0.85 | 199.2 | 212.6 | 65 | N |  |  | OP | X | 6 | 2004 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2003 | natural gas peaker | TRUE | 14232 | Otter Tail Power Co | 7947 | Solway CT | MN | Beltrami | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | OTP.SLWAY01 | OTP.SLWAY01 | 50 | 0.85 | 44 | 48 | 15 | N |  |  | OP | X | 5 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2005 | petroleum | TRUE | 14232 | Otter Tail Power Co | 7947 | Solway CT | MN | Beltrami | D1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 0.1 | N |  |  | OP | X | 8 | 2005 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2005 | natural gas peaker | TRUE | 9267 | Hoosier Energy R E C, Inc | 7948 | Lawrence County Station | IN | Lawrence | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | HE.07LCPGEN1 | HE.07LCPGEN1 | 67 | 0.85 | 43.8 | 50 | 20 | N |  |  | OP | X | 5 | 2005 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2005 | natural gas peaker | TRUE | 9267 | Hoosier Energy R E C, Inc | 7948 | Lawrence County Station | IN | Lawrence | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | HE.07LCPGEN2 | HE.07LCPGEN2 | 67 | 0.85 | 43.8 | 50 | 20 | N |  |  | OP | X | 5 | 2005 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2005 | natural gas peaker | TRUE | 9267 | Hoosier Energy R E C, Inc | 7948 | Lawrence County Station | IN | Lawrence | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | HE.07LCPGEN3 | HE.07LCPGEN3 | 67 | 0.85 | 43.8 | 50 | 20 | N |  |  | OP | X | 5 | 2005 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2005 | natural gas peaker | TRUE | 9267 | Hoosier Energy R E C, Inc | 7948 | Lawrence County Station | IN | Lawrence | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | HE.07LCPGEN4 | HE.07LCPGEN4 | 67 | 0.85 | 43.8 | 50 | 20 | N |  |  | OP | X | 5 | 2005 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2005 | natural gas peaker | TRUE | 9267 | Hoosier Energy R E C, Inc | 7948 | Lawrence County Station | IN | Lawrence | 5 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X | HE.07LCPGEN5 | HE.07LCPGEN5 | 67 | 0.85 | 43.8 | 50 | 20 | N |  |  | OP | X | 5 | 2005 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2005 | natural gas peaker | TRUE | 9267 | Hoosier Energy R E C, Inc | 7948 | Lawrence County Station | IN | Lawrence | 6 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X | HE.07LCPGEN6 | HE.07LCPGEN6 | 67 | 0.85 | 43.8 | 50 | 20 | N |  |  | OP | X | 5 | 2005 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2008 | natural gas peaker | TRUE | 9191 | Idaho Power Co | 7953 | Evander Andrews Power Complex | ID | Elmore | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | DNPR_GNODE011 | DNPR_2_G011 | 179.1 | 0.9 | 170.2 | 172.7 | 125.3 | N |  |  | OP | X | 2 | 2008 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 9191 | Idaho Power Co | 7953 | Evander Andrews Power Complex | ID | Elmore | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | DNPR_GNODE012 | DNPR_2_G012 | 45.9 | 0.9 | 42.8 | 28.8 | 31 | N |  |  | OP | X | 9 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 9191 | Idaho Power Co | 7953 | Evander Andrews Power Complex | ID | Elmore | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | DNPR_GNODE013 | DNPR_2_G013 | 45.9 | 0.9 | 42.2 | 32.6 | 29.3 | N |  |  | OP | X | 9 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2001 | petroleum | TRUE | 56152 | New Smyrna Beach Utilities Commission | 7954 | Field Street | FL | Volusia | 1 | Petroleum Liquids | GT |  | S | X | X |  |  | 24 | 0.9 | 22 | 24 | 12 | N |  |  | OS | X | 5 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 12H | [23 empty] | N | N | N
Vintage2001 | petroleum | TRUE | 56152 | New Smyrna Beach Utilities Commission | 7954 | Field Street | FL | Volusia | 2 | Petroleum Liquids | GT |  | S | X | X |  |  | 24 | 0.9 | 22 | 24 | 12 | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 12H | [23 empty] | N | N | N
Vintage2002 | biomass | TRUE | 14127 | Omaha Public Power District | 7955 | Elk City Station | NE | Douglas | 1 | Landfill Gas | IC |  | S | X | X | ELK_CITY_1 |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | N |  |  | OP | X | 4 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: LFG |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2002 | biomass | TRUE | 14127 | Omaha Public Power District | 7955 | Elk City Station | NE | Douglas | 2 | Landfill Gas | IC |  | S | X | X | ELK_CITY_1 |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | N |  |  | OP | X | 4 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: LFG |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2002 | biomass | TRUE | 14127 | Omaha Public Power District | 7955 | Elk City Station | NE | Douglas | 3 | Landfill Gas | IC |  | S | X | X | ELK_CITY_1 |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | N |  |  | OP | X | 4 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: LFG |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2002 | biomass | TRUE | 14127 | Omaha Public Power District | 7955 | Elk City Station | NE | Douglas | 4 | Landfill Gas | IC |  | S | X | X | ELK_CITY_1 |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | N |  |  | OP | X | 4 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: LFG |  |  |  |  | N |  | 10M | [23 empty] | N
Vintage2006 | biomass | TRUE | 14127 | Omaha Public Power District | 7955 | Elk City Station | NE | Douglas | 5 | Landfill Gas | IC |  | S | X | X | ELK_CITY_2 |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | N |  |  | OP | X | 6 | 2006 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: LFG |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2006 | biomass | TRUE | 14127 | Omaha Public Power District | 7955 | Elk City Station | NE | Douglas | 6 | Landfill Gas | IC |  | S | X | X | ELK_CITY_2 |  | 0.8 | 0.8 | 0.7 | 0.7 | 0.7 | N |  |  | OP | X | 6 | 2006 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: LFG |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2006 | biomass | TRUE | 14127 | Omaha Public Power District | 7955 | Elk City Station | NE | Douglas | 7 | Landfill Gas | IC |  | S | X | X | ELK_CITY_2 |  | 0.8 | 0.8 | 0.7 | 0.7 | 0.7 | N |  |  | OP | X | 8 | 2006 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: LFG |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2009 | biomass | TRUE | 14127 | Omaha Public Power District | 7955 | Elk City Station | NE | Douglas | 8 | Landfill Gas | IC |  | S | X | X | ELK_CITY_2 |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | N |  |  | OP | X | 8 | 2009 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: LFG |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2003 | petroleum | TRUE | 59159 | Central Electric Power | 7957 | Sediver | SC | York | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.9 | 0.8 | 2.4 | 2.4 | 2 | N |  |  | OP | X | 7 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2001 | biomass | TRUE | 17543 | South Carolina Public Service Authority | 7958 | Horry Land Fill Gas Site | SC | Horry | HG1 | Landfill Gas | IC |  | S | X | X |  |  | 1 | 1 | 1.1 | 1.1 | 0.5 | N |  |  | OP | X | 8 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: LFG |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2001 | biomass | TRUE | 17543 | South Carolina Public Service Authority | 7958 | Horry Land Fill Gas Site | SC | Horry | HG2 | Landfill Gas | IC |  | S | X | X |  |  | 1 | 1 | 1.1 | 1.1 | 0.5 | N |  |  | OP | X | 8 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: LFG |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2003 | biomass | TRUE | 17543 | South Carolina Public Service Authority | 7958 | Horry Land Fill Gas Site | SC | Horry | HG3 | Landfill Gas | IC |  | S | X | X |  |  | 1.1 | 1 | 1.1 | 1.1 | 0.5 | N |  |  | OP | X | 3 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: LFG |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2002 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 7960 | Kemper County | MS | Kemper | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 93 | 0.9 | 73.3 | 93.6 | 60 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 7960 | Kemper County | MS | Kemper | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 93 | 0.9 | 73.3 | 93.6 | 60 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 7960 | Kemper County | MS | Kemper | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 93 | 0.9 | 73.3 | 93.6 | 60 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 18642 | Tennessee Valley Authority | 7960 | Kemper County | MS | Kemper | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 93 | 0.9 | 73.3 | 93.6 | 60 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 5084 | Delaware Municipal Electric Corp | 7962 | Warren F Sam Beasley Generation Station | DE | Kent | 001 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | Clayton 13 KV G1 |  | 45 | 0.85 | 48 | 48 | 2 | N |  |  | OP | X | 4 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2012 | natural gas peaker | TRUE | 5084 | Delaware Municipal Electric Corp | 7962 | Warren F Sam Beasley Generation Station | DE | Kent | 002 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | Clayton 13 KV G2 |  | 51 | 0.85 | 50 | 50 | 2 | N |  |  | OP | X | 11 | 2012 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 19436 | Union Electric Co - (MO) | 7964 | Peno Creek | MO | Pike | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | AMMO.PENOCTG1 | AMMO.PENOCTG1 | 60 | 0.85 | 47 | 58 | 38 | N |  |  | OP | X | 5 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 10M | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 19436 | Union Electric Co - (MO) | 7964 | Peno Creek | MO | Pike | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | AMMO.PENOCTG2 | AMMO.PENOCTG2 | 60 | 0.85 | 47 | 58 | 38 | N |  |  | OP | X | 5 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 10M | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 19436 | Union Electric Co - (MO) | 7964 | Peno Creek | MO | Pike | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | AMMO.PENOCTG3 | AMMO.PENOCTG3 | 60 | 0.85 | 47 | 58 | 38 | N |  |  | OP | X | 5 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 10M | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 19436 | Union Electric Co - (MO) | 7964 | Peno Creek | MO | Pike | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | AMMO.PENOCTG4 | AMMOCTG4 | 60 | 0.85 | 47 | 58 | 38 | N |  |  | OP | X | 5 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 10M | [23 empty] | Y | N | Y
Vintage1998 | onshore wind | TRUE | 11018 | Lincoln Electric System | 7965 | Salt Valley Wind Plant | NE | Lancaster | G1 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 0.6 |  | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 12 | 1998 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WND |  |  |  | N | N | 1
Vintage1999 | onshore wind | TRUE | 11018 | Lincoln Electric System | 7965 | Salt Valley Wind Plant | NE | Lancaster | G2 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 0.6 |  | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 10 | 1999 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WND |  |  |  | N | N | 1
Vintage2000 | onshore wind | TRUE | 309 | City of Algona - (IA) | 7966 | Iowa Distributed Wind Generation Project | IA | Kossuth | IDWG | Onshore Wind Turbine | WT |  | S | X | X | WAUEALGONAMUNALGONA_1_UNIT_RA | WAUEALGONAMUNALGONA_1_UNIT_RA | 2.3 |  | 2.3 | 2.3 | 0.1 | N |  |  | OP | X | 6 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WND |  |  |  | N | N | 3 | [24 empty] | N
Vintage2002 | natural gas peaker | TRUE | 15473 | Public Service Co of NM | 7967 | Lordsburg Generating | NM | Hidalgo | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 44 | 0.9 | 41.3 | 42.7 | 10 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2002 | natural gas peaker | TRUE | 15473 | Public Service Co of NM | 7967 | Lordsburg Generating | NM | Hidalgo | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 44 | 0.9 | 41.3 | 42.7 | 10 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2003 | petroleum | TRUE | 14645 | City of Pella - (IA) | 7971 | Pella Peaking | IA | Marion | 10 | Petroleum Liquids | IC |  | S | X | X | MEC.MRES.PELLA | MEC.MRES.PELLA | 2 | 0.98 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2003 | petroleum | TRUE | 14645 | City of Pella - (IA) | 7971 | Pella Peaking | IA | Marion | 11 | Petroleum Liquids | IC |  | S | X | X | MEC.MRES.PELLA | MEC.MRES.PELLA | 2 | 0.98 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2003 | petroleum | TRUE | 14645 | City of Pella - (IA) | 7971 | Pella Peaking | IA | Marion | 12 | Petroleum Liquids | IC |  | S | X | X | MEC.MRES.PELLA | MEC.MRES.PELLA | 2 | 0.98 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2003 | petroleum | TRUE | 14645 | City of Pella - (IA) | 7971 | Pella Peaking | IA | Marion | 13 | Petroleum Liquids | IC |  | S | X | X | MEC.MRES.PELLA | MEC.MRES.PELLA | 2 | 0.98 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2003 | petroleum | TRUE | 14645 | City of Pella - (IA) | 7971 | Pella Peaking | IA | Marion | 14 | Petroleum Liquids | IC |  | S | X | X | MEC.MRES.PELLA | MEC.MRES.PELLA | 2 | 0.98 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2003 | petroleum | TRUE | 14645 | City of Pella - (IA) | 7971 | Pella Peaking | IA | Marion | 15 | Petroleum Liquids | IC |  | S | X | X | MEC.MRES.PELLA | MEC.MRES.PELLA | 2 | 0.98 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2003 | petroleum | TRUE | 14645 | City of Pella - (IA) | 7971 | Pella Peaking | IA | Marion | 16 | Petroleum Liquids | IC |  | S | X | X | MEC.MRES.PELLA | MEC.MRES.PELLA | 2 | 0.98 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2003 | petroleum | TRUE | 14645 | City of Pella - (IA) | 7971 | Pella Peaking | IA | Marion | 3 | Petroleum Liquids | IC |  | S | X | X | MEC.MRES.PELLA | MEC.MRES.PELLA | 2 | 0.98 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2003 | petroleum | TRUE | 14645 | City of Pella - (IA) | 7971 | Pella Peaking | IA | Marion | 4 | Petroleum Liquids | IC |  | S | X | X | MEC.MRES.PELLA | MEC.MRES.PELLA | 2 | 0.98 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2003 | petroleum | TRUE | 14645 | City of Pella - (IA) | 7971 | Pella Peaking | IA | Marion | 5 | Petroleum Liquids | IC |  | S | X | X | MEC.MRES.PELLA | MEC.MRES.PELLA | 2 | 0.98 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2003 | petroleum | TRUE | 14645 | City of Pella - (IA) | 7971 | Pella Peaking | IA | Marion | 6 | Petroleum Liquids | IC |  | S | X | X | MEC.MRES.PELLA | MEC.MRES.PELLA | 2 | 0.98 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2003 | petroleum | TRUE | 14645 | City of Pella - (IA) | 7971 | Pella Peaking | IA | Marion | 7 | Petroleum Liquids | IC |  | S | X | X | MEC.MRES.PELLA | MEC.MRES.PELLA | 2 | 0.98 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2003 | petroleum | TRUE | 14645 | City of Pella - (IA) | 7971 | Pella Peaking | IA | Marion | 8 | Petroleum Liquids | IC |  | S | X | X | MEC.MRES.PELLA | MEC.MRES.PELLA | 2 | 0.98 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2003 | petroleum | TRUE | 14645 | City of Pella - (IA) | 7971 | Pella Peaking | IA | Marion | 9 | Petroleum Liquids | IC |  | S | X | X | MEC.MRES.PELLA | MEC.MRES.PELLA | 2 | 0.98 | 1.8 | 1.8 | 1 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2002 | natural gas peaker | TRUE | 20910 | Wolverine Power Supply Coop | 7972 | Sumpter | MI | Wayne | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | DECO.JUDD11 |  | 85 | 0.83 | 77 | 93.9 | 45 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage2002 | natural gas peaker | TRUE | 20910 | Wolverine Power Supply Coop | 7972 | Sumpter | MI | Wayne | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | DECO.JUDD12 |  | 85 | 0.83 | 77.5 | 94.2 | 45 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage2002 | natural gas peaker | TRUE | 20910 | Wolverine Power Supply Coop | 7972 | Sumpter | MI | Wayne | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | DECO.JUDD13 |  | 85 | 0.83 | 76.6 | 93.1 | 45 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage2002 | natural gas peaker | TRUE | 20910 | Wolverine Power Supply Coop | 7972 | Sumpter | MI | Wayne | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | DECO.JUDD14 |  | 85 | 0.83 | 77.3 | 93.8 | 45 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage2002 | petroleum | TRUE | 9961 | Kansas Electric Power Coop Inc | 7973 | Sharpe | KS | Coffey | 1 | Petroleum Liquids | IC |  | S | X | X | WR.SHARPE.KEPC | WR.SHARPE.KEPC | 2 | 0.8 | 2 | 2 | 0.3 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2002 | petroleum | TRUE | 9961 | Kansas Electric Power Coop Inc | 7973 | Sharpe | KS | Coffey | 10 | Petroleum Liquids | IC |  | S | X | X | WR.SHARPE.KEPC | WR.SHARPE.KEPC | 2 | 0.8 | 2 | 2 | 0.3 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2002 | petroleum | TRUE | 9961 | Kansas Electric Power Coop Inc | 7973 | Sharpe | KS | Coffey | 2 | Petroleum Liquids | IC |  | S | X | X | WR.SHARPE.KEPC | WR.SHARPE.KEPC | 2 | 0.8 | 2 | 2 | 0.3 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2002 | petroleum | TRUE | 9961 | Kansas Electric Power Coop Inc | 7973 | Sharpe | KS | Coffey | 3 | Petroleum Liquids | IC |  | S | X | X | WR.SHARPE.KEPC | WR.SHARPE.KEPC | 2 | 0.8 | 2 | 2 | 0.3 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2002 | petroleum | TRUE | 9961 | Kansas Electric Power Coop Inc | 7973 | Sharpe | KS | Coffey | 4 | Petroleum Liquids | IC |  | S | X | X | WR.SHARPE.KEPC | WR.SHARPE.KEPC | 2 | 0.8 | 2 | 2 | 0.3 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2002 | petroleum | TRUE | 9961 | Kansas Electric Power Coop Inc | 7973 | Sharpe | KS | Coffey | 5 | Petroleum Liquids | IC |  | S | X | X | WR.SHARPE.KEPC | WR.SHARPE.KEPC | 2 | 0.8 | 2 | 2 | 0.3 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2002 | petroleum | TRUE | 9961 | Kansas Electric Power Coop Inc | 7973 | Sharpe | KS | Coffey | 6 | Petroleum Liquids | IC |  | S | X | X | WR.SHARPE.KEPC | WR.SHARPE.KEPC | 2 | 0.8 | 2 | 2 | 0.3 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2002 | petroleum | TRUE | 9961 | Kansas Electric Power Coop Inc | 7973 | Sharpe | KS | Coffey | 7 | Petroleum Liquids | IC |  | S | X | X | WR.SHARPE.KEPC | WR.SHARPE.KEPC | 2 | 0.8 | 2 | 2 | 0.3 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2002 | petroleum | TRUE | 9961 | Kansas Electric Power Coop Inc | 7973 | Sharpe | KS | Coffey | 8 | Petroleum Liquids | IC |  | S | X | X | WR.SHARPE.KEPC | WR.SHARPE.KEPC | 2 | 0.8 | 2 | 2 | 0.3 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2002 | petroleum | TRUE | 9961 | Kansas Electric Power Coop Inc | 7973 | Sharpe | KS | Coffey | 9 | Petroleum Liquids | IC |  | S | X | X | WR.SHARPE.KEPC | WR.SHARPE.KEPC | 2 | 0.8 | 2 | 2 | 0.3 | N |  |  | OP | X | 7 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2001 | onshore wind | TRUE | 1307 | Basin Electric Power Coop | 7974 | Chamberlain Wind Project | SD | Brule | WTC1 | Onshore Wind Turbine | WT |  | S | X | X | WAUELAKPLATUNCHAMBERLAIN_RA | WAUE.BEPM.CHAMBERLAIN | 1.3 |  | 1.3 | 1.3 | 0 | N |  |  | OP | X | 11 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WND |  |  |  | N | N | 1 | [24 empty] | N
Vintage2001 | onshore wind | TRUE | 1307 | Basin Electric Power Coop | 7974 | Chamberlain Wind Project | SD | Brule | WTC2 | Onshore Wind Turbine | WT |  | S | X | X | WAUELAKPLATUNCHAMBERLAIN_RA | WAUE.BEPM.CHAMBERLAIN | 1.3 |  | 1.3 | 1.3 | 0 | N |  |  | OP | X | 11 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WND |  |  |  | N | N | 1 | [24 empty] | N
Vintage2003 | natural gas peaker | TRUE | 30151 | Tri-State G & T Assn, Inc | 7975 | Pyramid | NM | Hidalgo | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 46.5 | 0.85 | 39.5 | 45.6 | 25 | N |  |  | OP | X | 3 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2003 | natural gas peaker | TRUE | 30151 | Tri-State G & T Assn, Inc | 7975 | Pyramid | NM | Hidalgo | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 46.5 | 0.85 | 39.5 | 45.6 | 25 | N |  |  | OP | X | 3 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2003 | natural gas peaker | TRUE | 30151 | Tri-State G & T Assn, Inc | 7975 | Pyramid | NM | Hidalgo | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 46.5 | 0.85 | 39.5 | 45.6 | 25 | N |  |  | OP | X | 5 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2003 | natural gas peaker | TRUE | 30151 | Tri-State G & T Assn, Inc | 7975 | Pyramid | NM | Hidalgo | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 46.5 | 0.85 | 39.5 | 45.6 | 25 | N |  |  | OP | X | 4 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage2003 | petroleum | TRUE | 13095 | City of Mulvane - (KS) | 7976 | Mulvane 2 | KS | Sedgwick | 10 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.1 | 0.8 | 3.8 | 3.8 | 1.5 | N |  |  | OP | X | 9 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | N |  | N
Vintage2003 | petroleum | TRUE | 13095 | City of Mulvane - (KS) | 7976 | Mulvane 2 | KS | Sedgwick | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 4.1 | 0.8 | 3.8 | 3.8 | 1.5 | N |  |  | OS | X | 9 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | N |  | N
Vintage2003 | petroleum | TRUE | 13095 | City of Mulvane - (KS) | 7976 | Mulvane 2 | KS | Sedgwick | 9 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.4 | N |  |  | OP | X | 9 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | N |  | N
Vintage2003 | petroleum | TRUE | 7494 | City of Granite Falls - (MN) | 7977 | Granite Falls 2 | MN | Yellow Medicine | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | SB | Y | 5 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2003 | petroleum | TRUE | 7494 | City of Granite Falls - (MN) | 7977 | Granite Falls 2 | MN | Yellow Medicine | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | SB | Y | 5 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2003 | petroleum | TRUE | 7494 | City of Granite Falls - (MN) | 7977 | Granite Falls 2 | MN | Yellow Medicine | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 2 | N |  |  | SB | Y | 5 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2002 | natural gas peaker | TRUE | 5416 | Duke Energy Carolinas, LLC | 7981 | Mill Creek (SC) | SC | Cherokee | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 99.9 | 0.85 | 71 | 94 | 71 | N |  |  | OP | X | 12 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 5416 | Duke Energy Carolinas, LLC | 7981 | Mill Creek (SC) | SC | Cherokee | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 99.9 | 0.85 | 70 | 94 | 70 | N |  |  | OP | X | 12 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 5416 | Duke Energy Carolinas, LLC | 7981 | Mill Creek (SC) | SC | Cherokee | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 99.9 | 0.85 | 71 | 95 | 71 | N |  |  | OP | X | 12 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 5416 | Duke Energy Carolinas, LLC | 7981 | Mill Creek (SC) | SC | Cherokee | 4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 99.9 | 0.85 | 70 | 94 | 70 | N |  |  | OP | X | 12 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2003 | natural gas peaker | TRUE | 5416 | Duke Energy Carolinas, LLC | 7981 | Mill Creek (SC) | SC | Cherokee | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 99.9 | 0.85 | 69 | 94 | 69 | N |  |  | OP | X | 5 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2003 | natural gas peaker | TRUE | 5416 | Duke Energy Carolinas, LLC | 7981 | Mill Creek (SC) | SC | Cherokee | 6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 99.9 | 0.85 | 71 | 92 | 71 | N |  |  | OP | X | 5 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2003 | natural gas peaker | TRUE | 5416 | Duke Energy Carolinas, LLC | 7981 | Mill Creek (SC) | SC | Cherokee | 7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 99.9 | 0.85 | 70 | 95 | 70 | N |  |  | OP | X | 5 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2003 | natural gas peaker | TRUE | 5416 | Duke Energy Carolinas, LLC | 7981 | Mill Creek (SC) | SC | Cherokee | 8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 99.9 | 0.85 | 71 | 93 | 71 | N |  |  | OP | X | 5 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2003 | petroleum | TRUE | 15793 | Redwood Falls Public Util Comm | 7982 | South Generation | MN | Redwood | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.2 | 0.8 | 2 | 2 | 0.1 | N |  |  | OP | X | 3 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N | N | N
Vintage2003 | petroleum | TRUE | 15793 | Redwood Falls Public Util Comm | 7982 | South Generation | MN | Redwood | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.2 | 0.8 | 2 | 2 | 0.1 | N |  |  | OP | X | 3 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N | N | N
Vintage2003 | petroleum | TRUE | 15793 | Redwood Falls Public Util Comm | 7982 | South Generation | MN | Redwood | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.2 | 0.8 | 2.2 | 2 | 0.1 | N |  |  | OP | X | 3 | 2003 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N | N | N
Vintage2002 | natural gas peaker | TRUE | 40582 | Michigan Public Power Agency | 7984 | Kalkaska CT #1 | MI | Kalkaska | 001 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | CONS.KALK | CONS.KALK | 60.5 | 0.85 | 48.3 | 61.4 | 20 | N |  |  | OP | X | 12 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2003 | natural gas combined cycle | TRUE | 12341 | MidAmerican Energy Co | 7985 | Greater Des Moines | IA | Polk | GT1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | MEC.CC.GDM1&2 | MEC.CC.GDM1&2 | 190.4 | 0.85 | 155.7 | 197.6 | 120 | Y | 1 | 2021 | OP | X | 5 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | OVER | [23 empty] | N | bar: X X X to RC RC RC
Vintage2003 | natural gas combined cycle | TRUE | 12341 | MidAmerican Energy Co | 7985 | Greater Des Moines | IA | Polk | GT2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | MEC.CC.GDM1&2 | MEC.CC.GDM1& 2 | 190.4 | 0.85 | 149.4 | 202.4 | 120 | Y | 1 | 2021 | OP | X | 5 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | OVER | [23 empty] | N | bar: X X X to RC RC RC
Vintage2004 | natural gas combined cycle | TRUE | 12341 | MidAmerican Energy Co | 7985 | Greater Des Moines | IA | Polk | ST1 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X | MEC.CC.GDM1&2 | MEC.CC.GDM1&2 | 195.5 | 0.85 | 174.8 | 178 | 55 | N |  |  | OP | X | 12 | 2004 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | OVER | [23 empty] | N | bar: X X X to RC RC RC
Vintage2002 | natural gas peaker | TRUE | 2507 | City of Burbank Water and Power | 7987 | Lake One | CA | Los Angeles | L1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 60.5 | 0.85 | 48 | 48 | 10 | N |  |  | OP | X | 6 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC
Vintage2003 | natural gas peaker | TRUE | 17568 | Cooperative Energy | 7988 | Silver Creek | MS | Jefferson Davis | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SME.SLVRCRK_1 |  | 83.5 | 0.85 | 75 | 83.5 | 53 | N |  |  | OP | X | 6 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage2004 | natural gas peaker | TRUE | 17568 | Cooperative Energy | 7988 | Silver Creek | MS | Jefferson Davis | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SME.SLVRCRK_2 |  | 83.5 | 0.85 | 75 | 83.5 | 53 | N |  |  | OP | X | 6 | 2004 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage2005 | natural gas peaker | TRUE | 17568 | Cooperative Energy | 7988 | Silver Creek | MS | Jefferson Davis | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SME.SLVRCRK_3 |  | 83.5 | 0.85 | 75 | 83.5 | 53 | N |  |  | OP | X | 6 | 2005 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage2003 | natural gas peaker | TRUE | 17568 | Cooperative Energy | 7989 | Sylvarena | MS | Smith | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SME.SYLV_1 |  | 47 | 0.85 | 43 | 47 | 24 | N |  |  | OP | X | 7 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2003 | natural gas peaker | TRUE | 17568 | Cooperative Energy | 7989 | Sylvarena | MS | Smith | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SME.SYLV_2 |  | 47 | 0.85 | 43 | 47 | 24 | N |  |  | OP | X | 7 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2003 | natural gas peaker | TRUE | 17568 | Cooperative Energy | 7989 | Sylvarena | MS | Smith | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SME.SYLV_3 |  | 47 | 0.85 | 43 | 47 | 24 | N |  |  | OP | X | 7 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | bar: X X X to RC RC RC
Vintage2002 | petroleum | TRUE | 406 | City of Altamont - (IL) | 7990 | Altamont | IL | Effingham | 1 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | SB | Y | 1 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2002 | petroleum | TRUE | 406 | City of Altamont - (IL) | 7990 | Altamont | IL | Effingham | 2 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | SB | Y | 1 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2002 | petroleum | TRUE | 406 | City of Altamont - (IL) | 7990 | Altamont | IL | Effingham | 3 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | SB | Y | 1 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2006 | petroleum | TRUE | 406 | City of Altamont - (IL) | 7990 | Altamont | IL | Effingham | 4 | Petroleum Liquids | IC |  | S | X | X | AMIL.IP.IMEA | AMIL.IP.IMEA | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | SB | Y | 11 | 2006 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N |  | N
Vintage2005 | natural gas combined cycle | TRUE | 11479 | Madison Gas & Electric Co | 7991 | West Campus Cogeneration Facility | WI | Dane | 1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | MGE.CC.WCCF | MGE.CC.WCCF | 54 | 0.9 | 28.4 | 28.4 | 27 | N |  |  | OP | X | 4 | 2005 |  |  | Y | Electric Utility | 1 | X X X: T; RC RC RC: NG; SUB SUB SUB: DFO; DFO DFO DFO: NG | DFO |  |  | N | N |  | 12H | [20 empty] | N |  |  | Y | N | Y
Vintage2005 | natural gas combined cycle | TRUE | 11479 | Madison Gas & Electric Co | 7991 | West Campus Cogeneration Facility | WI | Dane | CT2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | MGE.CC.WCCF | MGE.CC.WCCF | 54 | 0.9 | 32 | 32 | 27 | N |  |  | OP | X | 4 | 2005 |  |  | Y | Electric Utility | 1 | X X X: T; RC RC RC: NG; SUB SUB SUB: DFO; DFO DFO DFO: NG | DFO |  |  | N | N |  | 12H | [20 empty] | N |  |  | Y | N | Y
Vintage2005 | natural gas combined cycle | TRUE | 11479 | Madison Gas & Electric Co | 7991 | West Campus Cogeneration Facility | WI | Dane | STG1 | Natural Gas Fired Combined Cycle | CA | CC1 | J | Y | X | MGE.CC.WCCF | MGE.CC.WCCF | 61.3 | 0.9 | 67.8 | 67.8 | 11 | N |  |  | OP | X | 4 | 2005 |  |  | Y | Electric Utility | 1 | X X X: T; RC RC RC: NG; SUB SUB SUB: DFO; DFO DFO DFO: NG | DFO |  |  | N | N |  | 12H | [20 empty] | N |  |  | Y | N | Y
Vintage2002 | petroleum | TRUE | 56146 | Black Hills Colorado Electric, LLC | 7995 | Airport Industrial | CO | Pueblo | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 2 | N |  |  | OP | X | 1 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage2002 | petroleum | TRUE | 56146 | Black Hills Colorado Electric, LLC | 7995 | Airport Industrial | CO | Pueblo | IC2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 2 | N |  |  | OP | X | 1 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage2002 | petroleum | TRUE | 56146 | Black Hills Colorado Electric, LLC | 7995 | Airport Industrial | CO | Pueblo | IC3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 2 | N |  |  | OP | X | 1 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage2002 | petroleum | TRUE | 56146 | Black Hills Colorado Electric, LLC | 7995 | Airport Industrial | CO | Pueblo | IC4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 2 | N |  |  | OP | X | 1 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage2001 | petroleum | TRUE | 10623 | City of Lakeland - (FL) | 7997 | Winston | FL | Polk | WD01 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 12 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage2001 | petroleum | TRUE | 10623 | City of Lakeland - (FL) | 7997 | Winston | FL | Polk | WD02 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 12 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage2001 | petroleum | TRUE | 10623 | City of Lakeland - (FL) | 7997 | Winston | FL | Polk | WD03 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 12 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage2001 | petroleum | TRUE | 10623 | City of Lakeland - (FL) | 7997 | Winston | FL | Polk | WD04 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 12 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage2001 | petroleum | TRUE | 10623 | City of Lakeland - (FL) | 7997 | Winston | FL | Polk | WD05 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 12 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage2001 | petroleum | TRUE | 10623 | City of Lakeland - (FL) | 7997 | Winston | FL | Polk | WD06 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 12 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage2001 | petroleum | TRUE | 10623 | City of Lakeland - (FL) | 7997 | Winston | FL | Polk | WD07 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 12 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage2001 | petroleum | TRUE | 10623 | City of Lakeland - (FL) | 7997 | Winston | FL | Polk | WD08 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 12 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage2001 | petroleum | TRUE | 10623 | City of Lakeland - (FL) | 7997 | Winston | FL | Polk | WD09 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 12 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage2001 | petroleum | TRUE | 10623 | City of Lakeland - (FL) | 7997 | Winston | FL | Polk | WD10 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 12 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage2001 | petroleum | TRUE | 10623 | City of Lakeland - (FL) | 7997 | Winston | FL | Polk | WD11 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 12 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage2001 | petroleum | TRUE | 10623 | City of Lakeland - (FL) | 7997 | Winston | FL | Polk | WD12 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 12 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage2001 | petroleum | TRUE | 10623 | City of Lakeland - (FL) | 7997 | Winston | FL | Polk | WD13 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 12 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage2001 | petroleum | TRUE | 10623 | City of Lakeland - (FL) | 7997 | Winston | FL | Polk | WD14 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 12 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage2001 | petroleum | TRUE | 10623 | City of Lakeland - (FL) | 7997 | Winston | FL | Polk | WD15 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 12 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage2001 | petroleum | TRUE | 10623 | City of Lakeland - (FL) | 7997 | Winston | FL | Polk | WD16 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 12 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage2001 | petroleum | TRUE | 10623 | City of Lakeland - (FL) | 7997 | Winston | FL | Polk | WD17 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 12 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage2001 | petroleum | TRUE | 10623 | City of Lakeland - (FL) | 7997 | Winston | FL | Polk | WD18 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 12 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage2001 | petroleum | TRUE | 10623 | City of Lakeland - (FL) | 7997 | Winston | FL | Polk | WD19 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 12 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage2001 | petroleum | TRUE | 10623 | City of Lakeland - (FL) | 7997 | Winston | FL | Polk | WD20 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 12 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage2008 | natural gas combined cycle | TRUE | 49893 | Invenergy Services LLC | 7999 | Grays Harbor Energy Facility | WA | Grays Harbor | CT1 | Natural Gas Fired Combined Cycle | CT | CC01 | S | X | N |  |  | 198.9 | 0.85 | 151 | 188 | 100 | N |  |  | OP | X | 5 | 2008 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2008 | natural gas combined cycle | TRUE | 49893 | Invenergy Services LLC | 7999 | Grays Harbor Energy Facility | WA | Grays Harbor | CT2 | Natural Gas Fired Combined Cycle | CT | CC01 | S | X | N |  |  | 198.9 | 0.85 | 153 | 190 | 100 | N |  |  | OP | X | 5 | 2008 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2008 | natural gas combined cycle | TRUE | 49893 | Invenergy Services LLC | 7999 | Grays Harbor Energy Facility | WA | Grays Harbor | ST1 | Natural Gas Fired Combined Cycle | CA | CC01 | S | Y | X |  |  | 317.1 | 0.85 | 291 | 291 | 100 | N |  |  | OP | X | 5 | 2008 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2005 | natural gas combined cycle | TRUE | 13337 | Nebraska Public Power District | 8000 | Beatrice | NE | Gage | CT1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | NPPD_BPS | NPPD_BPS | 76.6 | 0.85 | 69 | 69 | 0 | N |  |  | OP | X | 1 | 2005 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2005 | natural gas combined cycle | TRUE | 13337 | Nebraska Public Power District | 8000 | Beatrice | NE | Gage | CT2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | NPPD_BPS | NPPD_BPS | 76.6 | 0.85 | 68 | 68 | 0 | N |  |  | OP | X | 1 | 2005 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2005 | natural gas combined cycle | TRUE | 13337 | Nebraska Public Power District | 8000 | Beatrice | NE | Gage | ST1 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | NPPD_BPS | NPPD_BPS | 93.9 | 0.85 | 83 | 83 | 0 | N |  |  | OP | X | 1 | 2005 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1974 | natural gas steam turbine | TRUE | 62032 | Granite Shore Power | 8002 | Newington | NH | Rockingham | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | 4002 Z_NewHampshire |  | 414 | 0.9 | 400.2 | 400.2 | 60 | N |  |  | OP | X | 6 | 1974 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: RFO; DFO DFO DFO: DFO |  |  |  | N |  |  | OVER | [23 empty] | Y | Y | Y
Vintage1974 | hydro | TRUE | 54765 | Bear Swamp Power Company LLC | 8004 | Fife Brook | MA | Berkshire | GEN1 | Conventional Hydroelectric | HY |  | J | X | X |  |  | 11.2 | 0.9 | 11.2 | 11.2 | 3 | N |  |  | OP | X | 10 | 1974 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage1974 | other | TRUE | 54765 | Bear Swamp Power Company LLC | 8005 | Bear Swamp | MA | Berkshire | GEN1 | Hydroelectric Pumped Storage | PS |  | J | X | X |  |  | 300 | 0.9 | 300 | 300 | 220 | N |  |  | OP | X | 9 | 1974 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M | [7 empty] | 33 | 33 | 11 | 2022
Vintage1974 | other | TRUE | 54765 | Bear Swamp Power Company LLC | 8005 | Bear Swamp | MA | Berkshire | GEN2 | Hydroelectric Pumped Storage | PS |  | J | X | X |  |  | 300 | 0.9 | 333 | 333 | 220 | Y | 11 | 2021 | OP | X | 10 | 1974 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage1974 | natural gas steam turbine | TRUE | 5511 | CCI Roseton LLC | 8006 | Roseton Generating Facility | NY | Orange | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | 23587 | 23587 | 621 | 0.9 | 599 | 614.7 | 140 | N |  |  | OP | X | 12 | 1974 |  |  | N | IPP Non-CHP | 2 | X | NG | RFO | DFO |  |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1974 | natural gas steam turbine | TRUE | 5511 | CCI Roseton LLC | 8006 | Roseton Generating Facility | NY | Orange | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | 23588 | 23588 | 621 | 0.9 | 605.7 | 605.7 | 140 | N |  |  | OP | X | 9 | 1974 |  |  | N | IPP Non-CHP | 2 | X | NG | RFO | DFO |  |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1974 | other | TRUE | 56505 | National Grid Generation LLC | 8007 | Holtsville | NY | Suffolk | 1 | Petroleum Liquids | GT |  | S | X | X | 23690 | 23690 | 56.7 | 0.9 | 55.5 | 62.1 | 37.6 | N |  |  | OP | X | 7 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: KER |  |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage1975 | other | TRUE | 56505 | National Grid Generation LLC | 8007 | Holtsville | NY | Suffolk | 10 | Petroleum Liquids | GT |  | S | X | X | 23699 | 23699 | 56.7 | 0.9 | 54.1 | 65.6 | 40.1 | N |  |  | OP | X | 7 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: KER |  |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage1974 | other | TRUE | 56505 | National Grid Generation LLC | 8007 | Holtsville | NY | Suffolk | 2 | Petroleum Liquids | GT |  | S | X | X | 23691 | 23691 | 56.7 | 0.9 | 55.6 | 61.3 | 35.1 | N |  |  | OP | X | 7 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: KER |  |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage1974 | other | TRUE | 56505 | National Grid Generation LLC | 8007 | Holtsville | NY | Suffolk | 3 | Petroleum Liquids | GT |  | S | X | X | 23692 | 23692 | 56.7 | 0.9 | 51 | 64.8 | 35.8 | N |  |  | OP | X | 7 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: KER |  |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage1974 | other | TRUE | 56505 | National Grid Generation LLC | 8007 | Holtsville | NY | Suffolk | 4 | Petroleum Liquids | GT |  | S | X | X | 23693 | 23693 | 56.7 | 0.9 | 52.4 | 64.3 | 35.9 | N |  |  | OP | X | 7 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: KER |  |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage1974 | other | TRUE | 56505 | National Grid Generation LLC | 8007 | Holtsville | NY | Suffolk | 5 | Petroleum Liquids | GT |  | S | X | X | 23694 | 23694 | 56.7 | 0.9 | 53.4 | 65 | 40.3 | N |  |  | OP | X | 7 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: KER |  |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage1975 | other | TRUE | 56505 | National Grid Generation LLC | 8007 | Holtsville | NY | Suffolk | 6 | Petroleum Liquids | GT |  | S | X | X | 23695 | 23695 | 56.7 | 0.9 | 50.4 | 65.4 | 38.5 | N |  |  | OP | X | 7 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: KER |  |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage1975 | other | TRUE | 56505 | National Grid Generation LLC | 8007 | Holtsville | NY | Suffolk | 7 | Petroleum Liquids | GT |  | S | X | X | 23696 | 23696 | 56.7 | 0.9 | 49.2 | 64.8 | 36.8 | N |  |  | OP | X | 7 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: KER |  |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage1975 | other | TRUE | 56505 | National Grid Generation LLC | 8007 | Holtsville | NY | Suffolk | 8 | Petroleum Liquids | GT |  | S | X | X | 23697 | 23697 | 56.7 | 0.9 | 55.4 | 66.8 | 41.8 | N |  |  | OP | X | 7 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: KER |  |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage1975 | other | TRUE | 56505 | National Grid Generation LLC | 8007 | Holtsville | NY | Suffolk | 9 | Petroleum Liquids | GT |  | S | X | X | 23698 | 23698 | 56.7 | 0.9 | 55.3 | 69.1 | 40.4 | N |  |  | OP | X | 7 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: KER |  |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage1974 | natural gas peaker | TRUE | 56606 | Calpine New Jersey Generation LLC | 8008 | Mickleton Station | NJ | Gloucester | MICK | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 71.2 | 0.9 | 63.7 | 78 | 57.3 | N |  |  | OP | X | 6 | 1974 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N |  |  | 1H | [23 empty] | N |  | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 13137 | City of Murray - (UT) | 8010 | Murray Turbine | UT | Salt Lake | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 14 | 1 | 12 | 13 | 7 | N |  |  | OP | X | 6 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 13137 | City of Murray - (UT) | 8010 | Murray Turbine | UT | Salt Lake | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 14 | 1 | 12 | 13 | 7 | N |  |  | OP | X | 10 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC
Vintage2002 | natural gas peaker | TRUE | 13137 | City of Murray - (UT) | 8010 | Murray Turbine | UT | Salt Lake | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 14 | 1 | 12 | 13 | 7 | N |  |  | OP | X | 1 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC
Vintage1974 | petroleum | TRUE | 6035 | Exelon Power | 8012 | Croydon CT Generating Station | PA | Bucks | 11 | Petroleum Liquids | GT |  | S | X | X | CROYDON 13 KV UNIT11 | CROYDON 13 KV UNIT11 | 68.3 | 0.9 | 49 | 64 | 10 | N |  |  | OP | X | 6 | 1974 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1974 | petroleum | TRUE | 6035 | Exelon Power | 8012 | Croydon CT Generating Station | PA | Bucks | 12 | Petroleum Liquids | GT |  | S | X | X | CROYDON 13 KV UNIT12 | CROYDON 13 KV UNIT12 | 68.3 | 0.9 | 49 | 64 | 10 | N |  |  | OP | X | 6 | 1974 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1974 | petroleum | TRUE | 6035 | Exelon Power | 8012 | Croydon CT Generating Station | PA | Bucks | 21 | Petroleum Liquids | GT |  | S | X | X | CROYDON 13 KV UNIT21 | CROYDON 13 KV UNIT21 | 68.3 | 0.9 | 49 | 64 | 10 | N |  |  | OP | X | 6 | 1974 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1974 | petroleum | TRUE | 6035 | Exelon Power | 8012 | Croydon CT Generating Station | PA | Bucks | 22 | Petroleum Liquids | GT |  | S | X | X | CROYDON 13 KV UNIT22 | CROYDON 13 KV UNIT22 | 68.3 | 0.9 | 49 | 64 | 10 | N |  |  | OP | X | 6 | 1974 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1974 | petroleum | TRUE | 6035 | Exelon Power | 8012 | Croydon CT Generating Station | PA | Bucks | 31 | Petroleum Liquids | GT |  | S | X | X | CROYDON 13 KV UNIT31 | CROYDON 13 KV UNIT31 | 68.3 | 0.9 | 49 | 64 | 10 | N |  |  | OP | X | 8 | 1974 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1974 | petroleum | TRUE | 6035 | Exelon Power | 8012 | Croydon CT Generating Station | PA | Bucks | 32 | Petroleum Liquids | GT |  | S | X | X | CROYDON 13 KV UNIT32 | CROYDON 13 KV UNIT32 | 68.3 | 0.9 | 48 | 64 | 10 | N |  |  | OP | X | 8 | 1974 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1974 | petroleum | TRUE | 6035 | Exelon Power | 8012 | Croydon CT Generating Station | PA | Bucks | 41 | Petroleum Liquids | GT |  | S | X | X | CROYDON 13 KV UNIT41 | CROYDON 13 KV UNIT41 | 68.3 | 0.9 | 49 | 64 | 10 | N |  |  | OP | X | 7 | 1974 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1974 | petroleum | TRUE | 6035 | Exelon Power | 8012 | Croydon CT Generating Station | PA | Bucks | 42 | Petroleum Liquids | GT |  | S | X | X | CROYDON 13 KV UNIT42 | CROYDON 13 KV UNIT42 | 68.3 | 0.9 | 49 | 64 | 10 | N |  |  | OP | X | 7 | 1974 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage2002 | petroleum | TRUE | 13697 | North Central Power Co Inc | 8013 | Winter | WI | Sawyer | IC 1 | Petroleum Liquids | IC |  | S | X | X | nsp.ncpload | nsp.ncpload | 2.8 | 0.8 | 2.8 | 2.8 | 0.1 | N |  |  | OP | X | 8 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage2002 | petroleum | TRUE | 13697 | North Central Power Co Inc | 8013 | Winter | WI | Sawyer | IC 2 | Petroleum Liquids | IC |  | S | X | X | nsp.ncpload | nsp.ncpload | 2.8 | 0.8 | 2.8 | 2.8 | 0.1 | N |  |  | OP | X | 8 | 2002 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage2001 | natural gas peaker | TRUE | 14446 | Paragould Light & Water Comm | 8015 | Paragould Reciprocating | AR | Greene | 011 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PARAGOULD | PARAGOULD | 6.4 | 0.8 | 6 | 6 | 6 | N |  |  | OP | X | 7 | 2001 |  |  | N | Electric Utility | 1 | [12 empty] | N |  | 12H | [23 empty] | N |  | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 14446 | Paragould Light & Water Comm | 8015 | Paragould Reciprocating | AR | Greene | 021 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PARAGOULD | PARAGOULD | 6.4 | 0.8 | 6 | 6 | 6 | N |  |  | OP | X | 7 | 2001 |  |  | N | Electric Utility | 1 | [12 empty] | N |  | 12H | [23 empty] | N |  | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 14446 | Paragould Light & Water Comm | 8015 | Paragould Reciprocating | AR | Greene | 031 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PARAGOULD | PARAGOULD | 6.4 | 0.8 | 6 | 6 | 6 | N |  |  | OP | X | 7 | 2001 |  |  | N | Electric Utility | 1 | [12 empty] | N |  | 12H | [23 empty] | N |  | N | bar: X X X to RC RC RC
Vintage1973 | petroleum | TRUE | 17828 | City of Springfield - (IL) | 8016 | Factory | IL | Sangamon | 1 | Petroleum Liquids | GT |  | S | X | X | CWLP.FACTOR91 | CWLP.FACTOR91 | 26.6 | 0.9 | 16.8 | 19 | 1 | N |  |  | OP | X | 8 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage2004 | petroleum | TRUE | 1148 | City of Baldwin City- (KS) | 8020 | Baldwin City Plant No 2 | KS | Douglas | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.2 | 0.8 | 3 | 3 | 1 | N |  |  | OP | X | 8 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2004 | petroleum | TRUE | 1148 | City of Baldwin City- (KS) | 8020 | Baldwin City Plant No 2 | KS | Douglas | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.2 | 0.8 | 3 | 3 | 1 | N |  |  | OP | X | 8 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 20169 | Avista Corp | 8022 | Boulder Park | WA | Spokane | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 4.1 | 0.8 | 4.1 | 4.1 | 4.1 | N |  |  | OP | X | 5 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2002 | natural gas peaker | TRUE | 20169 | Avista Corp | 8022 | Boulder Park | WA | Spokane | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 4.1 | 0.8 | 4.1 | 4.1 | 4.1 | N |  |  | OP | X | 5 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2002 | natural gas peaker | TRUE | 20169 | Avista Corp | 8022 | Boulder Park | WA | Spokane | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 4.1 | 0.8 | 4.1 | 4.1 | 4.1 | N |  |  | OP | X | 5 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2002 | natural gas peaker | TRUE | 20169 | Avista Corp | 8022 | Boulder Park | WA | Spokane | 4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 4.1 | 0.8 | 4.1 | 4.1 | 4.1 | N |  |  | OP | X | 5 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2002 | natural gas peaker | TRUE | 20169 | Avista Corp | 8022 | Boulder Park | WA | Spokane | 5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 4.1 | 0.8 | 4.1 | 4.1 | 4.1 | N |  |  | OP | X | 5 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2002 | natural gas peaker | TRUE | 20169 | Avista Corp | 8022 | Boulder Park | WA | Spokane | 6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 4.1 | 0.8 | 4.1 | 4.1 | 4.1 | N |  |  | OP | X | 5 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage1975 | hard coal | TRUE | 20856 | Wisconsin Power & Light Co | 8023 | Columbia (WI) | WI | Columbia | 1 | Conventional Steam Coal | ST |  | J | X | X | ALTE.COLUMBIA1 | ALTE.COLUMBIA1 | 556 | 0.9 | 579.3 | 582.3 | 130 | N |  |  | OP | X | 5 | 1975 | 12 | 2023 | N | Electric Utility | 1 | X | RC | DFO | BIT | SUB |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | N |  |  | N | N
Vintage1978 | hard coal | TRUE | 20856 | Wisconsin Power & Light Co | 8023 | Columbia (WI) | WI | Columbia | 2 | Conventional Steam Coal | ST |  | J | X | X | ALTE.COLUMBIA2 | ALTE.COLUMBIA2 | 556 | 0.9 | 572.5 | 580.3 | 130 | N |  |  | OP | X | 5 | 1978 | 12 | 2024 | N | Electric Utility | 1 | X | RC | DFO | BIT | SUB |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | N |  |  | N | N
Vintage2002 | natural gas peaker | TRUE | 1307 | Basin Electric Power Coop | 8026 | Hartzog | WY | Campbell | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 7.5 | 0.8 | 5 | 6 | 0.5 | N |  |  | OP | X | 8 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2002 | natural gas peaker | TRUE | 1307 | Basin Electric Power Coop | 8026 | Hartzog | WY | Campbell | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 7.5 | 0.8 | 5 | 6 | 0.5 | N |  |  | OP | X | 8 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2002 | natural gas peaker | TRUE | 1307 | Basin Electric Power Coop | 8026 | Hartzog | WY | Campbell | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 7.5 | 0.8 | 5 | 6 | 0.5 | N |  |  | OP | X | 8 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1974 | petroleum | TRUE | 13781 | Northern States Power Co - Minnesota | 8027 | Blue Lake | MN | Scott | 1 | Petroleum Liquids | GT |  | S | X | X | NSP BLUE_LK BLUE_L_1_UNIT | NSP BLUE_LK BLUE_L_1_UNIT | 56.7 | 0.9 | 39 | 50 | 19 | N |  |  | OP | X | 3 | 1974 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1974 | petroleum | TRUE | 13781 | Northern States Power Co - Minnesota | 8027 | Blue Lake | MN | Scott | 2 | Petroleum Liquids | GT |  | S | X | X | NSP BLUE_LK BLUE_L_2_UNIT | NSP BLUE_LK BLUE_L_2_UNIT | 56.7 | 0.9 | 39 | 50 | 19 | N |  |  | OP | X | 3 | 1974 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1974 | petroleum | TRUE | 13781 | Northern States Power Co - Minnesota | 8027 | Blue Lake | MN | Scott | 3 | Petroleum Liquids | GT |  | S | X | X | NSP BLUE_LK BLUE_L_3_UNIT | NSP BLUE_LK BLUE_L_3_UNIT | 56.7 | 0.9 | 36 | 46 | 19 | N |  |  | OP | X | 3 | 1974 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1974 | petroleum | TRUE | 13781 | Northern States Power Co - Minnesota | 8027 | Blue Lake | MN | Scott | 4 | Petroleum Liquids | GT |  | S | X | X | NSP BLUE_LK BLUE_L_4_UNIT | NSP BLUE_LK BLUE_L_4_UNIT | 56.7 | 0.9 | 39 | 48 | 32 | N |  |  | OP | X | 4 | 1974 | 12 | 2023 | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2005 | natural gas peaker | TRUE | 13781 | Northern States Power Co - Minnesota | 8027 | Blue Lake | MN | Scott | 7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | NSP BLUE_LK BLUE_L_7_UNIT | NSP BLUE_LK BLUE_L_7_UNIT | 166.3 | 0.85 | 150 | 174 | 100 | N |  |  | OP | X | 6 | 2005 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2005 | natural gas peaker | TRUE | 13781 | Northern States Power Co - Minnesota | 8027 | Blue Lake | MN | Scott | 8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | NSP BLUE_LK BLUE_L_8_UNIT | NSP BLUE_LK BLUE_L_8_UNIT | 166.3 | 0.85 | 150 | 177 | 100 | N |  |  | OP | X | 6 | 2005 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2002 | natural gas peaker | TRUE | 1307 | Basin Electric Power Coop | 8028 | Arvada | WY | Sheridan | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 7.5 | 0.8 | 5 | 6 | 0.5 | N |  |  | OP | X | 9 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2002 | natural gas peaker | TRUE | 1307 | Basin Electric Power Coop | 8028 | Arvada | WY | Sheridan | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 7.5 | 0.8 | 5 | 6 | 0.5 | N |  |  | OP | X | 9 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1974 | natural gas peaker | TRUE | 12341 | MidAmerican Energy Co | 8029 | Sycamore (IA) | IA | Polk | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MEC.SYCAMO 1 | MEC.SYCAMO 1 | 78.8 | 0.9 | 71.5 | 95 | 6 | N |  |  | OP | X | 8 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1974 | natural gas peaker | TRUE | 12341 | MidAmerican Energy Co | 8029 | Sycamore (IA) | IA | Polk | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MEC.SYCAMO 2 | MEC.SYCAMO 2 | 78.8 | 0.9 | 72.7 | 95 | 6 | N |  |  | OP | X | 11 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage2002 | natural gas peaker | TRUE | 1307 | Basin Electric Power Coop | 8030 | Barber Creek | WY | Campbell | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 7.5 | 0.8 | 5 | 6 | 0.5 | N |  |  | OP | X | 9 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2002 | natural gas peaker | TRUE | 1307 | Basin Electric Power Coop | 8030 | Barber Creek | WY | Campbell | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 7.5 | 0.8 | 5 | 6 | 0.5 | N |  |  | OP | X | 9 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2002 | natural gas peaker | TRUE | 1307 | Basin Electric Power Coop | 8030 | Barber Creek | WY | Campbell | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 7.5 | 0.8 | 5 | 6 | 0.5 | N |  |  | OP | X | 9 | 2002 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2004 | natural gas combined cycle | TRUE | 9417 | Interstate Power and Light Co | 8031 | Emery Station | IA | Cerro Gordo | 11 | Natural Gas Fired Combined Cycle | CT | G821 | S | X | Y | ALTW.CC.EMERY1 | ALTW.CC.EMERY1 | 173.4 | 0.85 | 150.3 | 177.3 | 95 | N |  |  | OP | X | 5 | 2004 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC
Vintage2004 | natural gas combined cycle | TRUE | 9417 | Interstate Power and Light Co | 8031 | Emery Station | IA | Cerro Gordo | 12 | Natural Gas Fired Combined Cycle | CT | G821 | S | X | Y | ALTW.CC.EMERY2 | ALTW.CC.EMERY2 | 173.4 | 0.85 | 152.1 | 179.4 | 95 | N |  |  | OP | X | 5 | 2004 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC
Vintage2004 | natural gas combined cycle | TRUE | 9417 | Interstate Power and Light Co | 8031 | Emery Station | IA | Cerro Gordo | ST1 | Natural Gas Fired Combined Cycle | CA | G821 | S | Y | X |  |  | 256 | 0.85 | 239.9 | 256.1 | 63 | N |  |  | OP | X | 5 | 2004 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC
Vintage1974 | natural gas peaker | TRUE | 13809 | NorthWestern Energy - (SD) | 8034 | Yankton | SD | Yankton | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  | WAUE_NWPS_NTWK | 2.2 | 0.8 | 2.2 | 2.2 | 1 | N |  |  | SB | Y | 8 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1974 | petroleum | TRUE | 13809 | NorthWestern Energy - (SD) | 8034 | Yankton | SD | Yankton | 2 | Petroleum Liquids | IC |  | S | X | X |  | WAUE_NWPS_NTWK | 2.7 | 0.8 | 2.8 | 2.8 | 1.2 | N |  |  | SB | Y | 8 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1975 | natural gas peaker | TRUE | 13809 | NorthWestern Energy - (SD) | 8034 | Yankton | SD | Yankton | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  | WAUE_NWPS_NTWK | 6.5 | 0.8 | 6.5 | 6.5 | 3 | N |  |  | SB | Y | 3 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1963 | petroleum | TRUE | 13809 | NorthWestern Energy - (SD) | 8034 | Yankton | SD | Yankton | 4 | Petroleum Liquids | IC |  | S | X | X |  | WAUE_NWPS_NTWK | 2 | 0.8 | 2 | 2 | 0.9 | N |  |  | SB | Y | 2 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1974 | nuclear | TRUE | 13337 | Nebraska Public Power District | 8036 | Cooper Nuclear Station | NE | Nemaha | 1 | Nuclear | ST |  | S | X | X | NPPD_COOPR | NPPD_COOPR | 801 | 0.85 | 770 | 770 | 0 | N |  |  | OP | X | 3 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NUC; DFO DFO DFO: NUC |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1974 | natural gas peaker | TRUE | 18315 | Sunflower Electric Power Corp | 8037 | Clifton | KS | Washington | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MKECCLIFTON_UN1 | MKECCLIFTON_UN1 | 85 | 0.9 | 75.6 | 75.6 | 10 | N |  |  | OP | X | 12 | 1974 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1974 | petroleum | TRUE | 18315 | Sunflower Electric Power Corp | 8037 | Clifton | KS | Washington | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 2.5 | N |  |  | SB | Y | 8 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1974 | hard coal | TRUE | 5416 | Duke Energy Carolinas, LLC | 8042 | Belews Creek | NC | Stokes | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 1245.6 | 0.9 | 1110 | 1110 | 300 | N |  |  | OP | X | 8 | 1974 |  |  | N | Electric Utility | 1 | X | BIT | NG | DFO |  |  |  | NG |  |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | Y | Y | N
Vintage1975 | hard coal | TRUE | 5416 | Duke Energy Carolinas, LLC | 8042 | Belews Creek | NC | Stokes | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 1245.6 | 0.9 | 1110 | 1110 | 675 | N |  |  | OP | X | 12 | 1975 |  |  | N | Electric Utility | 1 | X | BIT | NG | DFO |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | Y | N
Vintage1974 | natural gas steam turbine | TRUE | 6455 | Duke Energy Florida, LLC | 8048 | Anclote | FL | Pasco | 1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 556.2 | 0.9 | 508 | 521 | 80 | N |  |  | OP | X | 10 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: RFO; DFO DFO DFO: DFO | NG |  |  | N | N |  | OVER | [23 empty] | Y | N | Y
Vintage1978 | natural gas steam turbine | TRUE | 6455 | Duke Energy Florida, LLC | 8048 | Anclote | FL | Pasco | 2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 556.2 | 0.9 | 505 | 514 | 80 | N |  |  | OP | X | 10 | 1978 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: RFO; DFO DFO DFO: DFO | NG |  |  | N | N |  | OVER | [23 empty] | Y | N | Y
Vintage1974 | petroleum | TRUE | 6455 | Duke Energy Florida, LLC | 8049 | Intercession City | FL | Osceola | P1 | Petroleum Liquids | GT |  | S | X | X |  |  | 56.7 | 0.9 | 45 | 61 | 30 | N |  |  | OP | X | 5 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1993 | natural gas peaker | TRUE | 6455 | Duke Energy Florida, LLC | 8049 | Intercession City | FL | Osceola | P10 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 103.5 | 0.85 | 74 | 86 | 40 | N |  |  | OP | X | 10 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1997 | petroleum | TRUE | 6455 | Duke Energy Florida, LLC | 8049 | Intercession City | FL | Osceola | P11 | Petroleum Liquids | GT |  | J | X | X |  |  | 148.5 | 0.9 | 140 | 161 | 60 | N |  |  | OP | X | 1 | 1997 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage2000 | natural gas peaker | TRUE | 6455 | Duke Energy Florida, LLC | 8049 | Intercession City | FL | Osceola | P12 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 98.2 | 0.85 | 73 | 89 | 50 | N |  |  | OP | X | 12 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 6455 | Duke Energy Florida, LLC | 8049 | Intercession City | FL | Osceola | P13 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 98.2 | 0.85 | 73 | 91 | 50 | N |  |  | OP | X | 12 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 6455 | Duke Energy Florida, LLC | 8049 | Intercession City | FL | Osceola | P14 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 98.2 | 0.85 | 73 | 90 | 50 | N |  |  | OP | X | 12 | 2000 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1974 | petroleum | TRUE | 6455 | Duke Energy Florida, LLC | 8049 | Intercession City | FL | Osceola | P2 | Petroleum Liquids | GT |  | S | X | X |  |  | 56.7 | 0.9 | 46 | 60 | 30 | N |  |  | OP | X | 5 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1974 | petroleum | TRUE | 6455 | Duke Energy Florida, LLC | 8049 | Intercession City | FL | Osceola | P3 | Petroleum Liquids | GT |  | S | X | X |  |  | 56.7 | 0.9 | 46 | 61 | 30 | N |  |  | OP | X | 5 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1974 | petroleum | TRUE | 6455 | Duke Energy Florida, LLC | 8049 | Intercession City | FL | Osceola | P4 | Petroleum Liquids | GT |  | S | X | X |  |  | 56.7 | 0.9 | 46 | 62 | 30 | N |  |  | OP | X | 5 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1974 | petroleum | TRUE | 6455 | Duke Energy Florida, LLC | 8049 | Intercession City | FL | Osceola | P5 | Petroleum Liquids | GT |  | S | X | X |  |  | 56.7 | 0.9 | 45 | 59 | 30 | N |  |  | OP | X | 5 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1974 | petroleum | TRUE | 6455 | Duke Energy Florida, LLC | 8049 | Intercession City | FL | Osceola | P6 | Petroleum Liquids | GT |  | S | X | X |  |  | 56.7 | 0.9 | 47 | 60 | 30 | N |  |  | OP | X | 5 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1993 | natural gas peaker | TRUE | 6455 | Duke Energy Florida, LLC | 8049 | Intercession City | FL | Osceola | P7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 103.5 | 0.85 | 78 | 90 | 40 | N |  |  | OP | X | 10 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1993 | natural gas peaker | TRUE | 6455 | Duke Energy Florida, LLC | 8049 | Intercession City | FL | Osceola | P8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 103.5 | 0.85 | 77 | 88 | 40 | N |  |  | OP | X | 10 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1993 | natural gas peaker | TRUE | 6455 | Duke Energy Florida, LLC | 8049 | Intercession City | FL | Osceola | P9 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 103.5 | 0.85 | 77 | 88 | 40 | N |  |  | OP | X | 10 | 1993 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 15296 | New York Power Authority | 8053 | Pouch | NY | Richmond | N01 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 47 | 1 | 45.1 | 46 | 1 | N |  |  | OP | X | 8 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1975 | natural gas steam turbine | TRUE | 12685 | Entergy Mississippi LLC | 8054 | Gerald Andrus | MS | Washington | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | EES.G_ANDRUS1 | EES.G_ANDRUS1 | 781.4 | 0.9 | 706.5 | 725 | 205 | N |  |  | OP | X | 1 | 1975 | 6 | 2035 | N | Electric Utility | 1 | [8 empty] | DFO |  |  | N |  |  | OVER | [23 empty] | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage1974 | nuclear | TRUE | 814 | Entergy Arkansas LLC | 8055 | Arkansas Nuclear One | AR | Pope | 1 | Nuclear | ST |  | S | X | X | EAI.ANO1 | EAI.ANO1 | 902.5 | 0.9 | 833.3 | 852 | 250 | N |  |  | OP | X | 12 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NUC; DFO DFO DFO: DFO | [6 empty] | OVER | [23 empty] | N
Vintage1980 | nuclear | TRUE | 814 | Entergy Arkansas LLC | 8055 | Arkansas Nuclear One | AR | Pope | 2 | Nuclear | ST |  | S | X | X | EAI.ANO2 | EAIANO2 | 942.5 | 0.95 | 984.5 | 1002 | 250 | N |  |  | OP | X | 3 | 1980 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NUC | [6 empty] | OVER | [23 empty] | N
Vintage1975 | natural gas steam turbine | TRUE | 11241 | Entergy Louisiana LLC | 8056 | Waterford 1 & 2 | LA | St Charles | 1 | Natural Gas Steam Turbine | ST |  | S | X | X | EES.WATRFD1 | EES.WATRFD1 | 445.5 | 0.9 | 409.5 | 411.1 | 125 | N |  |  | OP | X | 7 | 1975 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: RFO; DFO DFO DFO: NG |  |  |  | N |  |  | OVER | [23 empty] | Y | Y | Y
Vintage1975 | natural gas steam turbine | TRUE | 11241 | Entergy Louisiana LLC | 8056 | Waterford 1 & 2 | LA | St Charles | 2 | Natural Gas Steam Turbine | ST |  | S | X | X | EES.WATRFD2 | EES.WATRFD2 | 445.5 | 0.9 | 422.4 | 426.4 | 125 | N |  |  | OP | X | 10 | 1975 | 6 | 2024 | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: RFO; DFO DFO DFO: NG |  |  |  | N |  |  | OVER | [23 empty] | Y | Y | Y
Vintage2009 | petroleum | TRUE | 11241 | Entergy Louisiana LLC | 8056 | Waterford 1 & 2 | LA | St Charles | 4 | Petroleum Liquids | GT |  | S | X | X | EES.WATRFD4_CT | EES.WATRFD4_CT | 41 | 0.95 | 32.1 | 35.7 | 31.9 | N |  |  | SB | Y | 9 | 2009 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; DFO DFO DFO: DFO |  |  |  | N |  |  | 12H | [23 empty] | N
Vintage1973 | natural gas combined cycle | TRUE | 15474 | Public Service Co of Oklahoma | 8059 | Comanche (OK) | OK | Comanche | 1G1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 85 | 0.9 | 78 | 78 | 30 | N |  |  | OP | X | 12 | 1973 |  |  | N | Electric Utility | 1 | [12 empty] | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1973 | natural gas combined cycle | TRUE | 15474 | Public Service Co of Oklahoma | 8059 | Comanche (OK) | OK | Comanche | 1G2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 85 | 0.9 | 78 | 78 | 30 | N |  |  | OP | X | 8 | 1973 |  |  | N | Electric Utility | 1 | [12 empty] | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1974 | natural gas combined cycle | TRUE | 15474 | Public Service Co of Oklahoma | 8059 | Comanche (OK) | OK | Comanche | 1S | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X |  |  | 120 | 0.9 | 104 | 114 | 34 | N |  |  | OP | X | 2 | 1974 |  |  | N | Electric Utility | 1 | [12 empty] | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1962 | petroleum | TRUE | 15474 | Public Service Co of Oklahoma | 8059 | Comanche (OK) | OK | Comanche | IC1 | Petroleum Liquids | IC |  | S | X | X |  |  | 4 | 0.85 | 4 | 4 | 2 | N |  |  | OS | X | 5 | 1962 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 1H | [23 empty] | N | N | N
Vintage1990 | natural gas peaker | TRUE | 55983 | Luminant Generation Company LLC | 8063 | DeCordova Steam Electric Station | TX | Hood | CT1 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 89.4 | 0.9 | 69 | 88 | 60 | N |  |  | OP | X | 3 | 1990 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1990 | natural gas peaker | TRUE | 55983 | Luminant Generation Company LLC | 8063 | DeCordova Steam Electric Station | TX | Hood | CT2 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 89.4 | 0.9 | 68 | 87 | 60 | N |  |  | OP | X | 3 | 1990 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1990 | natural gas peaker | TRUE | 55983 | Luminant Generation Company LLC | 8063 | DeCordova Steam Electric Station | TX | Hood | CT3 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 89.4 | 0.9 | 68 | 86 | 60 | N |  |  | OP | X | 3 | 1990 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1990 | natural gas peaker | TRUE | 55983 | Luminant Generation Company LLC | 8063 | DeCordova Steam Electric Station | TX | Hood | CT4 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 89.4 | 0.9 | 69 | 86 | 60 | N |  |  | OP | X | 3 | 1990 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1974 | hard coal | TRUE | 14354 | PacifiCorp | 8066 | Jim Bridger | WY | Sweetwater | 1 | Conventional Steam Coal | ST |  | J | X | X |  |  | 608.3 | 0.95 | 531 | 531 | 50 | N |  |  | OP | X | 11 | 1974 | 12 | 2037 | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; SUB SUB SUB: DFO; DFO DFO DFO: DFO |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [15 empty] | Y | 12 | 2025 | N
Vintage1975 | hard coal | TRUE | 14354 | PacifiCorp | 8066 | Jim Bridger | WY | Sweetwater | 2 | Conventional Steam Coal | ST |  | J | X | X |  |  | 617 | 0.95 | 539 | 539 | 40 | N |  |  | OP | X | 12 | 1975 | 12 | 2037 | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; SUB SUB SUB: DFO; DFO DFO DFO: DFO |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [15 empty] | Y | 12 | 2025 | N
Vintage1976 | hard coal | TRUE | 14354 | PacifiCorp | 8066 | Jim Bridger | WY | Sweetwater | 3 | Conventional Steam Coal | ST |  | J | X | X |  |  | 608.3 | 0.95 | 523 | 523 | 65 | N |  |  | OP | X | 9 | 1976 | 12 | 2037 | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; SUB SUB SUB: DFO; DFO DFO DFO: DFO |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1979 | hard coal | TRUE | 14354 | PacifiCorp | 8066 | Jim Bridger | WY | Sweetwater | 4 | Conventional Steam Coal | ST |  | J | X | X |  |  | 608.3 | 0.96 | 526 | 526 | 80 | N |  |  | OP | X | 11 | 1979 | 12 | 2037 | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; SUB SUB SUB: DFO; DFO DFO DFO: DFO |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1972 | natural gas peaker | TRUE | 15466 | Public Service Co of Colorado | 8067 | Fort Lupton | CO | Weld | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 50.4 | 0.9 | 44 | 50 | 10 | N |  |  | OP | X | 4 | 1972 | 12 | 2026 | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1972 | natural gas peaker | TRUE | 15466 | Public Service Co of Colorado | 8067 | Fort Lupton | CO | Weld | 2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 50.4 | 0.9 | 44 | 50 | 10 | N |  |  | OP | X | 4 | 1972 | 12 | 2026 | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1974 | natural gas combined cycle | TRUE | 16572 | Salt River Project | 8068 | Santan | AZ | Maricopa | ST1 | Natural Gas Fired Combined Cycle | CS |  | S | N | N |  |  | 103.5 | 0.9 | 92 | 103.5 | 80 | N |  |  | OP | X | 10 | 1974 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage1974 | natural gas combined cycle | TRUE | 16572 | Salt River Project | 8068 | Santan | AZ | Maricopa | ST2 | Natural Gas Fired Combined Cycle | CS |  | S | N | N |  |  | 103.5 | 0.9 | 92 | 103.5 | 80 | N |  |  | OP | X | 12 | 1974 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage1974 | natural gas combined cycle | TRUE | 16572 | Salt River Project | 8068 | Santan | AZ | Maricopa | ST3 | Natural Gas Fired Combined Cycle | CS |  | S | N | N |  |  | 103.5 | 0.9 | 92 | 103.5 | 80 | N |  |  | OP | X | 10 | 1974 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage1975 | natural gas combined cycle | TRUE | 16572 | Salt River Project | 8068 | Santan | AZ | Maricopa | ST4 | Natural Gas Fired Combined Cycle | CS |  | S | N | N |  |  | 103.5 | 0.9 | 92 | 103.5 | 80 | N |  |  | OP | X | 5 | 1975 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2005 | natural gas combined cycle | TRUE | 16572 | Salt River Project | 8068 | Santan | AZ | Maricopa | ST5A | Natural Gas Fired Combined Cycle | CT | STS5 | S | X | Y |  |  | 153.8 | 0.85 | 151 | 203 | 90 | N |  |  | OP | X | 4 | 2005 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [20 empty] | Y | 12 | 2023 | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2005 | natural gas combined cycle | TRUE | 16572 | Salt River Project | 8068 | Santan | AZ | Maricopa | ST5B | Natural Gas Fired Combined Cycle | CT | STS5 | S | X | Y |  |  | 153.8 | 0.85 | 151 | 200 | 90 | N |  |  | OP | X | 4 | 2005 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [20 empty] | Y | 12 | 2023 | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2005 | natural gas combined cycle | TRUE | 16572 | Salt River Project | 8068 | Santan | AZ | Maricopa | ST5S | Natural Gas Fired Combined Cycle | CA | STS5 | S | Y | X |  |  | 314.5 | 0.85 | 280 | 318 | 60 | N |  |  | OP | X | 4 | 2005 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2006 | natural gas combined cycle | TRUE | 16572 | Salt River Project | 8068 | Santan | AZ | Maricopa | ST6A | Natural Gas Fired Combined Cycle | CT | STS6 | S | X | Y |  |  | 153.8 | 0.85 | 151 | 195 | 90 | N |  |  | OP | X | 3 | 2006 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [20 empty] | Y | 12 | 2024 | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage2006 | natural gas combined cycle | TRUE | 16572 | Salt River Project | 8068 | Santan | AZ | Maricopa | ST6S | Natural Gas Fired Combined Cycle | CA | STS6 | S | Y | X |  |  | 136.1 | 0.85 | 126 | 135 | 45 | N |  |  | OP | X | 3 | 2006 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage1977 | hard coal | TRUE | 14354 | PacifiCorp | 8069 | Huntington | UT | Emery | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 541.3 | 0.92 | 459 | 459 | 60 | N |  |  | OP | X | 6 | 1977 | 12 | 2036 | N | Electric Utility | 1 | X X X: X; RC RC RC: BIT; SUB SUB SUB: DFO; DFO DFO DFO: DFO |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1974 | hard coal | TRUE | 14354 | PacifiCorp | 8069 | Huntington | UT | Emery | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 496 | 0.9 | 450 | 450 | 60 | N |  |  | OP | X | 7 | 1974 | 12 | 2036 | N | Electric Utility | 1 | X X X: X; RC RC RC: BIT; SUB SUB SUB: DFO; DFO DFO DFO: DFO |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1974 | natural gas combined cycle | TRUE | 15248 | Portland General Electric Co | 8073 | Beaver | OR | Columbia | 1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y | BRP1_2_GNODE1-7 | BRP1_2_BEAVER1-7 | 68.3 | 0.9 | 55.3 | 63 | 5 | N |  |  | OP | X | 8 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1974 | natural gas combined cycle | TRUE | 15248 | Portland General Electric Co | 8073 | Beaver | OR | Columbia | 2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y | BRP1_2_GNODE1-7 | BRP1_2_BEAVER1-7 | 68.3 | 0.9 | 55.3 | 63 | 5 | N |  |  | OP | X | 8 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1974 | natural gas combined cycle | TRUE | 15248 | Portland General Electric Co | 8073 | Beaver | OR | Columbia | 3 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y | BRP1_2_GNODE1-7 | BRP1_2_BEAVER1-7 | 68.3 | 0.9 | 55.3 | 63 | 5 | N |  |  | OP | X | 8 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1974 | natural gas combined cycle | TRUE | 15248 | Portland General Electric Co | 8073 | Beaver | OR | Columbia | 4 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y | BRP1_2_GNODE1-7 | BRP1_2_BEAVER1-7 | 68.3 | 0.9 | 55.3 | 63 | 5 | N |  |  | OP | X | 8 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1974 | natural gas combined cycle | TRUE | 15248 | Portland General Electric Co | 8073 | Beaver | OR | Columbia | 5 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y | BRP1_2_GNODE1-7 | BRP1_2_BEAVER1-7 | 68.3 | 0.9 | 55.3 | 63 | 5 | N |  |  | OP | X | 8 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1974 | natural gas combined cycle | TRUE | 15248 | Portland General Electric Co | 8073 | Beaver | OR | Columbia | 6 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y | BRP1_2_GNODE1-7 | BRP1_2_BEAVER1-7 | 68.3 | 0.9 | 55.3 | 63 | 5 | N |  |  | OP | X | 8 | 1974 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1977 | natural gas combined cycle | TRUE | 15248 | Portland General Electric Co | 8073 | Beaver | OR | Columbia | 7 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X | BRP1_2_GNODE1-7 | BRP1_2_BEAVER1-7 | 176.4 | 0.9 | 137 | 139 | 10 | N |  |  | OP | X | 11 | 1977 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage2001 | natural gas peaker | TRUE | 15248 | Portland General Electric Co | 8073 | Beaver | OR | Columbia | 8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | BRP1_2_GNODE8 |  | 24.5 | 0.9 | 24 | 24 | 17 | N |  |  | OP | X | 8 | 2001 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X X X to RC RC RC
Vintage1974 | natural gas peaker | TRUE | 63844 | Ellwood Power, LLC | 8076 | Ellwood | CA | Santa Barbara | 01 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | GOLETA_6_ELLWOD | GOLETA_6_N100 | 58 | 0.9 | 54 | 54 | 54 | N |  |  | OP | X | 8 | 1974 | 1 | 2024 | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | bar: X X X to RC RC RC
Vintage1989 | petroleum | TRUE | 8287 | Hawaii Electric Light Co Inc | 8083 | Keahole | HI | Hawaii | 2 | Petroleum Liquids | GT |  | S | X | X |  |  | 17.6 | 0.9 | 15.9 | 15.9 | 5 | N |  |  | OP | X | 11 | 1989 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1984 | petroleum | TRUE | 8287 | Hawaii Electric Light Co Inc | 8083 | Keahole | HI | Hawaii | 21 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 11 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1984 | petroleum | TRUE | 8287 | Hawaii Electric Light Co Inc | 8083 | Keahole | HI | Hawaii | 22 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 11 | 1984 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1988 | petroleum | TRUE | 8287 | Hawaii Electric Light Co Inc | 8083 | Keahole | HI | Hawaii | 23 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 3 | 1988 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2009 | petroleum | TRUE | 8287 | Hawaii Electric Light Co Inc | 8083 | Keahole | HI | Hawaii | 7 | Petroleum Liquids | CA | CC1 | S | N | X |  |  | 18 | 0.9 | 16 | 16 | 3.5 | N |  |  | OP | X | 6 | 2009 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2004 | petroleum | TRUE | 8287 | Hawaii Electric Light Co Inc | 8083 | Keahole | HI | Hawaii | CT4 | Petroleum Liquids | CT | CC1 | S | X | Y |  |  | 23 | 0.9 | 19.8 | 21.6 | 7 | N |  |  | OP | X | 5 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2004 | petroleum | TRUE | 8287 | Hawaii Electric Light Co Inc | 8083 | Keahole | HI | Hawaii | CT5 | Petroleum Liquids | CT | CC1 | S | X | Y |  |  | 23 | 0.9 | 19.8 | 21.6 | 7 | N |  |  | OP | X | 6 | 2004 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1965 | petroleum | TRUE | 17834 | City of Springfield - (CO) | 8100 | Springfield (CO) | CO | Baca | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 1 | 1.2 | 1.2 | 1 | N |  |  | SB | Y | 8 | 1965 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: NG |  |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1950 | petroleum | TRUE | 17834 | City of Springfield - (CO) | 8100 | Springfield (CO) | CO | Baca | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.2 | 1 | 0.2 | 0.2 | 0.1 | N |  |  | SB | Y | 8 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: NG |  |  |  | N | N |  | 1H | N | [22 empty] | Y | Y | Y
Vintage1950 | petroleum | TRUE | 17834 | City of Springfield - (CO) | 8100 | Springfield (CO) | CO | Baca | IC4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 1 | 0.5 | 0.5 | 0.4 | N |  |  | SB | Y | 9 | 1950 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: NG |  |  |  | N | N |  | 1H | N | [22 empty] | Y | Y | Y
Vintage1960 | petroleum | TRUE | 17834 | City of Springfield - (CO) | 8100 | Springfield (CO) | CO | Baca | IC5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 1 | 0.8 | 0.8 | 0.7 | N |  |  | SB | Y | 9 | 1960 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO; SUB SUB SUB: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1974 | hard coal | TRUE | 61135 | Gavin Power, LLC | 8102 | Gavin Power, LLC | OH | Gallia | 1 | Conventional Steam Coal | ST |  | W | X | X |  |  | 1300 | 0.9 | 1330 | 1330 | 485 | N |  |  | OP | X | 10 | 1974 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: RC; SUB SUB SUB: BIT; DFO DFO DFO: DFO |  |  |  | N | N |  | OVER |  | Y |  |  |  | Y |  | 18 | 18 | 6 | 2022 | [12 empty] | N | N | N
Vintage1975 | hard coal | TRUE | 61135 | Gavin Power, LLC | 8102 | Gavin Power, LLC | OH | Gallia | 2 | Conventional Steam Coal | ST |  | W | X | X |  |  | 1300 | 0.9 | 1361 | 1361 | 485 | Y | 6 | 2021 | OP | X | 7 | 1975 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: RC; SUB SUB SUB: BIT; DFO DFO DFO: DFO |  |  |  | N | N |  | OVER |  | Y |  |  |  | Y | [17 empty] | N | N | N
Vintage2007 | petroleum | TRUE | 7969 | City of Halstad - (MN) | 8105 | Halstad | MN | Norman | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.9 | 1.9 | 1.6 | N |  |  | SB | Y | 9 | 2007 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2007 | petroleum | TRUE | 7969 | City of Halstad - (MN) | 8105 | Halstad | MN | Norman | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.9 | 1.9 | 1.6 | N |  |  | SB | Y | 9 | 2007 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2001 | natural gas peaker | TRUE | 18947 | City of Tipton - (IA) | 8106 | Tipton | IA | Cedar | 1A | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1.6 | N |  |  | OP | X | 2 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1971 | natural gas peaker | TRUE | 18947 | City of Tipton - (IA) | 8106 | Tipton | IA | Cedar | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.2 | 1.2 | 0.9 | N |  |  | OP | X | 4 | 1971 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage2011 | petroleum | TRUE | 18947 | City of Tipton - (IA) | 8106 | Tipton | IA | Cedar | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1.4 | N |  |  | OP | X | 1 | 2011 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  |  | N |  | 10M | [23 empty] | N | N | N
Vintage2011 | petroleum | TRUE | 18947 | City of Tipton - (IA) | 8106 | Tipton | IA | Cedar | 6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1.4 | N |  |  | OP | X | 1 | 2011 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  |  | N |  | 10M | [23 empty] | N | N | N
Vintage2019 | petroleum | TRUE | 18947 | City of Tipton - (IA) | 8106 | Tipton | IA | Cedar | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1.5 | N |  |  | OP | X | 1 | 2019 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  |  | N |  | 10M | [20 empty] | N |  |  | N | N
Vintage1973 | petroleum | TRUE | 8847 | City of Hopkinton - (IA) | 8108 | Hopkinton | IA | Delaware | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.4 | N |  |  | OP | X | 9 | 1973 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2011 | petroleum | TRUE | 8847 | City of Hopkinton - (IA) | 8108 | Hopkinton | IA | Delaware | CAT | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.2 | 2.2 | 0.4 | N |  |  | OP | X | 9 | 2011 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1963 | natural gas peaker | TRUE | 17946 | City of Stanberry - (MO) | 8110 | Stanberry | MO | Gentry | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.5 | N |  |  | SB | Y | 7 | 1963 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  |  | N |  | 1H | [23 empty] | Y | N | Y
Vintage1967 | natural gas peaker | TRUE | 17946 | City of Stanberry - (MO) | 8110 | Stanberry | MO | Gentry | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.5 | N |  |  | SB | Y | 10 | 1967 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  |  | N |  | 1H | [23 empty] | Y | N | Y
Vintage1958 | petroleum | TRUE | 17946 | City of Stanberry - (MO) | 8110 | Stanberry | MO | Gentry | IC5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.1 | N |  |  | SB | Y | 8 | 1958 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO | [6 empty] | 10M | [23 empty] | N | N | N
Vintage1979 | natural gas peaker | TRUE | 17946 | City of Stanberry - (MO) | 8110 | Stanberry | MO | Gentry | IC6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.8 | 0.955 | 1.8 | 1.8 | 0.7 | N |  |  | SB | Y | 1 | 1979 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO | [6 empty] | 1H | [23 empty] | Y | N | Y
Vintage1980 | hard coal | TRUE | 3989 | City of Colorado Springs - (CO) | 8219 | Ray D Nixon | CO | El Paso | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 207 | 0.9 | 208 | 208 | 110 | N |  |  | OP | X | 4 | 1980 | 12 | 2029 | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; DFO DFO DFO: DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | N |  |  | N | N | N
Vintage1999 | natural gas peaker | TRUE | 3989 | City of Colorado Springs - (CO) | 8219 | Ray D Nixon | CO | El Paso | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 37.8 | 0.85 | 30 | 32 | 20 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC
Vintage1999 | natural gas peaker | TRUE | 3989 | City of Colorado Springs - (CO) | 8219 | Ray D Nixon | CO | El Paso | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 37.8 | 0.85 | 30 | 32 | 20 | N |  |  | OP | X | 7 | 1999 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC
Vintage1981 | lignite | TRUE | 14232 | Otter Tail Power Co | 8222 | Coyote | ND | Mercer | 1 | Conventional Steam Coal | ST |  | J | X | X | OTP.COYOT1 | OTP.COYOT1 | 450 | 0.9 | 429 | 429 | 200 | N |  |  | OP | X | 5 | 1981 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: LIG; DFO DFO DFO: DFO |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N
Vintage1985 | hard coal | TRUE | 24211 | Tucson Electric Power Co | 8223 | Springerville | AZ | Apache | 1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 424.8 | 0.9 | 381 | 381 | 100 | N |  |  | OP | X | 6 | 1985 | 1 | 2027 | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; SUB SUB SUB: RC; DFO DFO DFO: DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | Y |  |  | N | N | N
Vintage1990 | hard coal | TRUE | 24211 | Tucson Electric Power Co | 8223 | Springerville | AZ | Apache | 2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 424.8 | 0.9 | 406 | 406 | 100 | N |  |  | OP | X | 6 | 1990 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: SUB; SUB SUB SUB: RC; DFO DFO DFO: DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage2006 | hard coal | TRUE | 24211 | Tucson Electric Power Co | 8223 | Springerville | AZ | Apache | 3 | Conventional Steam Coal | ST |  | W | X | X |  |  | 458.1 | 0.9 | 417 | 417 | 100 | N |  |  | OP | X | 7 | 2006 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: RC; DFO DFO DFO: DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage2009 | hard coal | TRUE | 24211 | Tucson Electric Power Co | 8223 | Springerville | AZ | Apache | 4 | Conventional Steam Coal | ST |  | W | X | X |  |  | 458.1 | 0.9 | 415 | 415 | 130 | N |  |  | OP | X | 12 | 2009 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: RC; DFO DFO DFO: DFO |  |  |  | N | N |  | OVER | N | Y |  |  | Y | [18 empty] | N | N | N
Vintage2001 | solar pv | TRUE | 24211 | Tucson Electric Power Co | 8223 | Springerville | AZ | Apache | SGSS | Solar Photovoltaic | PV |  | S | X | X |  |  | 3.7 |  | 3.7 | 3.7 |  | N |  |  | OP | X | 5 | 2001 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: SUN |  |  |  | N | N | [25 empty] | N
Vintage2010 | solar pv | TRUE | 24211 | Tucson Electric Power Co | 8223 | Springerville | AZ | Apache | SGSS1 | Solar Photovoltaic | PV |  | S | X | X |  |  | 1.4 |  | 1.4 | 1.4 |  | N |  |  | OP | X | 12 | 2010 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: SUN |  |  |  | N | N | [25 empty] | N
Vintage2014 | solar pv | TRUE | 24211 | Tucson Electric Power Co | 8223 | Springerville | AZ | Apache | WMS | Solar Photovoltaic | PV |  | S | X | X |  |  | 8.3 |  | 8.3 | 8.3 |  | N |  |  | OP | X | 12 | 2014 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: SUN |  |  |  | N | N | [25 empty] | N
Vintage1981 | hard coal | TRUE | 17166 | Sierra Pacific Power Co | 8224 | North Valmy | NV | Humboldt | 1 | Conventional Steam Coal | ST |  | J | X | X |  |  | 277.2 | 0.9 | 254 | 254 | 90 | N |  |  | OP | X | 12 | 1981 | 12 | 2025 | N | Electric Utility | 1 | X X X: X; RC RC RC: BIT; SUB SUB SUB: SUB; DFO DFO DFO: DFO |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1985 | hard coal | TRUE | 17166 | Sierra Pacific Power Co | 8224 | North Valmy | NV | Humboldt | 2 | Conventional Steam Coal | ST |  | J | X | X |  |  | 289.8 | 0.9 | 268 | 268 | 90 | N |  |  | OP | X | 5 | 1985 | 12 | 2025 | N | Electric Utility | 1 | X X X: X; RC RC RC: BIT; SUB SUB SUB: SUB; DFO DFO DFO: DFO |  |  |  | N |  |  | OVER |  | Y |  |  | Y | [18 empty] | N
Vintage1970 | other | TRUE | 59524 | Seneca Generation LLC | 8225 | Seneca Generation LLC | PA | Warren | 1 | Hydroelectric Pumped Storage | PS |  | S | X | X | SENECA 13KV GEN1 | SENECA 13KV GEN1 | 205.9 | 0.9 | 234 | 234 | 75 | N |  |  | OP | X | 6 | 1970 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1970 | other | TRUE | 59524 | Seneca Generation LLC | 8225 | Seneca Generation LLC | PA | Warren | 2 | Hydroelectric Pumped Storage | PS |  | S | X | X | SENECA 13KV GEN2 | SENECA 13KV GEN2 | 205.9 | 0.9 | 218 | 218 | 75 | N |  |  | OP | X | 6 | 1970 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1970 | hydro | TRUE | 59524 | Seneca Generation LLC | 8225 | Seneca Generation LLC | PA | Warren | 3 | Conventional Hydroelectric | HY |  | S | X | X | SENECA 13KV GEN3 | SENECA 13KV GEN3 | 26.1 | 0.9 | 30 | 30 | 30 | N |  |  | OP | X | 6 | 1970 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1970 | hard coal | TRUE | 14165 | GenOn Power Midwest, LP | 8226 | Cheswick Power Plant | PA | Allegheny | 1 | Conventional Steam Coal | ST |  | S | X | X | 38367993 | CHESWICK 24 KV UNIT1 | 637 | 0.91 | 565 | 565 | 130 | N |  |  | OP | X | 6 | 1970 | 3 | 2022 | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: BIT; SUB SUB SUB: NG; DFO DFO DFO: NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | N |  |  | Y | Y | N
Vintage1936 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 8902 | Hoover Dam (AZ) | AZ | Mohave | A0 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 2.7 | 2.7 | 0 | N |  |  | OP | X | 9 | 1936 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage1941 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 8902 | Hoover Dam (AZ) | AZ | Mohave | A1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 130 | 0.8 | 130 | 130 | 0 | N |  |  | OP | X | 10 | 1941 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage1942 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 8902 | Hoover Dam (AZ) | AZ | Mohave | A2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 130 | 0.98 | 130 | 130 | 0 | N |  |  | OP | X | 7 | 1942 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage1952 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 8902 | Hoover Dam (AZ) | AZ | Mohave | A3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 130 | 0.98 | 130 | 130 | 0 | N |  |  | OP | X | 9 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage1952 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 8902 | Hoover Dam (AZ) | AZ | Mohave | A4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 130 | 0.98 | 130 | 130 | 0 | N |  |  | OP | X | 5 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage1943 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 8902 | Hoover Dam (AZ) | AZ | Mohave | A5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 127 | 0.97 | 127 | 127 | 0 | N |  |  | OP | X | 1 | 1943 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage1939 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 8902 | Hoover Dam (AZ) | AZ | Mohave | A6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 130 | 0.98 | 130 | 130 | 0 | N |  |  | OP | X | 9 | 1939 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage1939 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 8902 | Hoover Dam (AZ) | AZ | Mohave | A7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 130 | 0.98 | 130 | 130 | 0 | N |  |  | OP | X | 6 | 1939 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage1937 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 8902 | Hoover Dam (AZ) | AZ | Mohave | A8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 61.5 | 0.98 | 61.5 | 61.5 | 0 | N |  |  | OP | X | 8 | 1937 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage1952 | hydro | TRUE | 2518 | U S Bureau of Reclamation | 8902 | Hoover Dam (AZ) | AZ | Mohave | A9 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 68.5 | 0.98 | 68.5 | 68.5 | 0 | N |  |  | OP | X | 4 | 1952 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage1967 | natural gas peaker | TRUE | 54863 | U S Power Generating Company LLC | 8906 | Astoria Generating Station | NY | Queens | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 15 | 1 | 13.6 | 19.3 | 12 | N |  |  | OP | X | 7 | 1967 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N |  |  | 1H | [23 empty] | N | N | bar: X X X to RC RC RC
Vintage1954 | natural gas steam turbine | TRUE | 54863 | U S Power Generating Company LLC | 8906 | Astoria Generating Station | NY | Queens | 2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 180 | 1 | 172.4 | 169 | 60 | N |  |  | OP | X | 3 | 1954 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N |  |  | OVER | [23 empty] | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage1958 | natural gas steam turbine | TRUE | 54863 | U S Power Generating Company LLC | 8906 | Astoria Generating Station | NY | Queens | 3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 376 | 1 | 371.3 | 370 | 75 | N |  |  | OP | X | 9 | 1958 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: RFO; DFO DFO DFO: NG | RFO |  |  | N |  |  | OVER | [23 empty] | Y | Y | Y
Vintage1961 | natural gas steam turbine | TRUE | 54863 | U S Power Generating Company LLC | 8906 | Astoria Generating Station | NY | Queens | 4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 387 | 1 | 379.4 | 376.2 | 75 | N |  |  | OS | X | 12 | 1961 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: RFO; DFO DFO DFO: NG | RFO |  |  | N |  |  | OVER | [23 empty] | Y | Y | Y
Vintage1962 | natural gas steam turbine | TRUE | 54863 | U S Power Generating Company LLC | 8906 | Astoria Generating Station | NY | Queens | ST5 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 387 | 1 | 375.1 | 375.3 | 75 | N |  |  | OP | X | 5 | 1962 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: NG; SUB SUB SUB: RFO; DFO DFO DFO: NG | RFO |  |  | N |  |  | OVER | [23 empty] | Y | Y | Y
Vintage1962 | natural gas peaker | TRUE | 8973 | Town of Hudson - (MA) | 9038 | Cherry Street | MA | Middlesex | 10 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.2 | 0.8 | 1.9 | 1.9 | 0.5 | N |  |  | OP | X | 12 | 1962 | 5 | 2030 | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1962 | natural gas peaker | TRUE | 8973 | Town of Hudson - (MA) | 9038 | Cherry Street | MA | Middlesex | 11 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.2 | 0.8 | 1.9 | 1.9 | 0.5 | N |  |  | OP | X | 12 | 1962 | 5 | 2030 | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1972 | natural gas peaker | TRUE | 8973 | Town of Hudson - (MA) | 9038 | Cherry Street | MA | Middlesex | 12 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 5.6 | 0.8 | 4.9 | 4.9 | 0.5 | N |  |  | OP | X | 10 | 1972 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1951 | petroleum | TRUE | 8973 | Town of Hudson - (MA) | 9038 | Cherry Street | MA | Middlesex | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.3 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 5 | 1951 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1956 | natural gas peaker | TRUE | 8973 | Town of Hudson - (MA) | 9038 | Cherry Street | MA | Middlesex | 8 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 4 | 0.8 | 3.4 | 3.4 | 0.5 | N |  |  | OP | X | 3 | 1956 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: NG; SUB SUB SUB: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | N | N
Vintage1992 | hydro | TRUE | 20169 | Avista Corp | 9095 | Monroe Street | WA | Spokane | 6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 14.8 | 0.9 | 15 | 15 | 1 | N |  |  | OP | X | 12 | 1992 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1922 | hydro | TRUE | 20169 | Avista Corp | 9096 | Upper Falls | WA | Spokane | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10 | 0.85 | 10.2 | 10.2 | 1 | N |  |  | OP | X | 4 | 1922 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M | [20 empty] | N |  |  | N
Vintage1964 | natural gas peaker | TRUE | 11479 | Madison Gas & Electric Co | 9674 | Nine Springs | WI | Dane | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 16.2 | 0.85 | 13.1 | 13.1 | 3 | N |  |  | OP | X | 12 | 1964 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X X X to RC RC RC
Vintage1970 | hydro | TRUE | 16868 | City of Seattle - (WA) | 9842 | Newhalem | WA | Whatcom | 20 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.3 | 0.92 | 2.3 | 2.3 | 0 | N |  |  | OS | X | 2 | 1970 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1893 | hydro | TRUE | 8776 | City of Holyoke Gas and Electric Dept. | 9864 | Cabot Holyoke | MA | Hampden | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.6 | 0.6 | 0.6 | N |  |  | OP | X | 1 | 1893 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1938 | hydro | TRUE | 8776 | City of Holyoke Gas and Electric Dept. | 9864 | Cabot Holyoke | MA | Hampden | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.6 | 0.6 | 0.4 | N |  |  | OP | X | 1 | 1938 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1939 | hydro | TRUE | 8776 | City of Holyoke Gas and Electric Dept. | 9864 | Cabot Holyoke | MA | Hampden | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.3 | N |  |  | OP | X | 1 | 1939 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1907 | hydro | TRUE | 8776 | City of Holyoke Gas and Electric Dept. | 9864 | Cabot Holyoke | MA | Hampden | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.5 | 0.5 | 0.4 | N |  |  | OP | X | 1 | 1907 |  |  | N | Electric Utility | 1 | X X X: X; RC RC RC: WAT |  |  |  | N | N |  | 10M
Vintage1976 | natural gas steam turbine | FALSE | 63637 | Molson Coors USA LLC | 10003 | Colorado Energy Nations Company | CO | Jefferson | GEN1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 7.5 | 0.8 | 10 | 10 | 3 | N |  |  | OP | X | 9 | 1976 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H |  | N |  |  | N | [18 empty] | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage1977 | natural gas steam turbine | FALSE | 63637 | Molson Coors USA LLC | 10003 | Colorado Energy Nations Company | CO | Jefferson | GEN2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 7.5 | 0.8 | 10 | 10 | 3 | N |  |  | OP | X | 5 | 1977 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H |  | N |  |  | N | [18 empty] | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage1983 | natural gas steam turbine | FALSE | 63637 | Molson Coors USA LLC | 10003 | Colorado Energy Nations Company | CO | Jefferson | GEN3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 20 | 0.8 | 20 | 20 | 3 | N |  |  | OP | X | 6 | 1983 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H |  | N |  |  | N | [18 empty] | N | N | N | bar: X X X to RC RC RC; DFO DFO DFO
Vintage1978 | other | FALSE | 9383 | Mosaic Fertilizer LLC | 10004 | Mosaic South Pierce Operations | FL | Polk | TG1 | All Other | ST |  | S | X | X |  |  | 7.5 | 0.9 | 4 | 4 | 2 | N |  |  | OP | X | 1 | 1978 |  |  | Y | Industrial CHP | 7 | X X X: B; RC RC RC: WH; DFO DFO DFO: NG |  |  |  | N |  |  | OVER | [23 empty] | N | N
Vintage1992 | other | FALSE | 9383 | Mosaic Fertilizer LLC | 10004 | Mosaic South Pierce Operations | FL | Polk | TG2 | All Other | ST |  | S | X | X |  |  | 38 | 0.85 | 33 | 33 | 2 | N |  |  | OP | X | 1 | 1992 |  |  | Y | Industrial CHP | 7 | X X X: B; RC RC RC: WH; DFO DFO DFO: NG |  |  |  | N |  |  | OVER | [23 empty] | N | N
Vintage1988 | onshore wind | TRUE | 9397 | International Turbine Res Inc | 10005 | Dinosaur Point | CA | Merced | WTGS | Onshore Wind Turbine | WT |  | S | X | X |  |  | 17.4 |  | 17 | 16 | 15 | N |  |  | OP | X | 5 | 1988 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WND |  |  |  | N | N | 161 | [16 empty] | WT | WND | 90 | 9 | 2024 | N
Vintage1983 | natural gas peaker | FALSE | 1194 | Baptist Memorial Hospital | 10008 | Baptist Medical Center | FL | Duval | TG-2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 2.5 | 0.8 | 2.2 | 2.5 | 0.5 | N |  |  | OP | X | 12 | 1983 |  |  | Y | Commercial CHP | 5 | X X X: T; RC RC RC: NG; SUB SUB SUB: DFO; DFO DFO DFO: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1986 | natural gas peaker | FALSE | 1194 | Baptist Memorial Hospital | 10008 | Baptist Medical Center | FL | Duval | TG-3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3 | 0.8 | 2.7 | 3 | 0.5 | N |  |  | OP | X | 3 | 1986 |  |  | Y | Commercial CHP | 5 | X X X: T; RC RC RC: NG; SUB SUB SUB: DFO; DFO DFO DFO: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1993 | natural gas peaker | FALSE | 1194 | Baptist Memorial Hospital | 10008 | Baptist Medical Center | FL | Duval | TG-4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.5 | 0.9 | 3.2 | 3.5 | 0.5 | N |  |  | OP | X | 3 | 1993 |  |  | Y | Commercial CHP | 5 | X X X: T; RC RC RC: NG; SUB SUB SUB: DFO; DFO DFO DFO: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1989 | municipal solid waste | TRUE | 4435 | Covanta Energy Co | 10013 | Covanta Hennepin Energy | MN | Hennepin | GEN1 | Municipal Solid Waste | ST |  | W | X | X |  |  | 39.5 | 0.85 | 33.7 | 33.7 | 6 | N |  |  | OP | X | 10 | 1989 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: MSW; DFO DFO DFO: NG |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1988 | hydro | TRUE | 1932 | Boise-Kuna Irrigation District | 10014 | Lucky Peak Power Plant Project | ID | Ada | U131 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 45 | 0.9 | 36.2 | 19.2 | 0 | N |  |  | OP | X | 10 | 1988 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage1988 | hydro | TRUE | 1932 | Boise-Kuna Irrigation District | 10014 | Lucky Peak Power Plant Project | ID | Ada | U132 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 45 | 0.9 | 36.2 | 19.2 | 0 | N |  |  | OP | X | 10 | 1988 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage1988 | hydro | TRUE | 1932 | Boise-Kuna Irrigation District | 10014 | Lucky Peak Power Plant Project | ID | Ada | U133 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 11.2 | 0.9 | 10.6 | 10.3 | 0 | N |  |  | OP | X | 10 | 1988 |  |  | N | IPP Non-CHP | 2 | X X X: X; RC RC RC: WAT |  |  |  | N |  |  | 10M
Vintage1954 | biomass | TRUE | 17465 | WestRock-West Point Mill | 10017 | WestRock-West Point Mill | VA | King William | GEN8 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 5 | 0.8 | 5 | 5 | 1.8 | N |  |  | OS | X | 1 | 1954 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | BIT | SLW | DFO | NG |  |  |  | N | N |  | OVER |  | Y |  | Y | Y | [18 empty] | Y | Y | N
Vintage1960 | biomass | TRUE | 17465 | WestRock-West Point Mill | 10017 | WestRock-West Point Mill | VA | King William | GEN9 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 10 | 0.8 | 10 | 10 | 4 | N |  |  | OP | X | 10 | 1960 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | BIT | SLW | DFO | NG |  |  |  | N | N |  | OVER |  | Y |  | Y | Y | [18 empty] | Y | Y | N
Vintage1968 | biomass | TRUE | 17465 | WestRock-West Point Mill | 10017 | WestRock-West Point Mill | VA | King William | GN10 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 25 | 0.85 | 25 | 25 | 7 | N |  |  | OP | X | 12 | 1968 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | BIT | SLW | DFO | NG |  |  |  | N | N |  | OVER |  | Y |  | Y | Y | [18 empty] | Y | Y | N
Vintage1977 | biomass | TRUE | 17465 | WestRock-West Point Mill | 10017 | WestRock-West Point Mill | VA | King William | GN11 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 15 | 0.85 | 15 | 15 | 7 | N |  |  | OP | X | 8 | 1977 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | SLW | DFO | BIT | NG |  |  |  | N | N |  | OVER |  | Y |  | Y | Y | [18 empty] | Y | Y | N
Vintage1985 | biomass | TRUE | 17465 | WestRock-West Point Mill | 10017 | WestRock-West Point Mill | VA | King William | GN12 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 46 | 0.85 | 46 | 46 | 10 | N |  |  | OP | X | 10 | 1985 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | SLW | DFO | BIT | NG |  |  |  | N | N |  | OVER |  | Y |  | Y | Y | [18 empty] | Y | Y | N
Vintage2006 | geothermal | TRUE | 34691 | Ormat Nevada Inc | 10018 | Desert Peak Power Plant | NV | Lyon | GEN2 | Geothermal | BT |  | W | X | X |  |  | 15 | 0.8 | 10 | 15 | 10 | N |  |  | OP | X | 6 | 2006 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: GEO |  |  |  | N |  |  | OVER | [23 empty] | N
Vintage2006 | geothermal | TRUE | 34691 | Ormat Nevada Inc | 10018 | Desert Peak Power Plant | NV | Lyon | OEC2 | Geothermal | BT |  | W | X | X |  |  | 11 | 0.8 | 7.3 | 11 | 7.3 | N |  |  | OP | X | 6 | 2006 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: GEO |  |  |  | N |  |  | OVER | [23 empty] | N
Vintage2016 | natural gas peaker | FALSE | 4558 | Cutrale Citrus Juices USA Inc | 10020 | Cutrale Citrus Juices USA I | FL | Lake | GEN3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 4.1 | 0.8 | 4.3 | 3.9 | 1.5 | N |  |  | OP | X | 1 | 2016 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X T T T T T to WAT BLQ BLQ BLQ BLQ BLQ
Vintage1968 | natural gas steam turbine | FALSE | 5624 | RED-Rochester, LLC | 10025 | RED-Rochester, LLC | NY | Monroe | 17TG | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 15 | 0.8 | 15 | 15 | 4 | N |  |  | OP | X | 12 | 1968 |  |  | Y | Industrial CHP | 7 | B | NG | RFO | DFO |  |  |  | RFO |  |  |  | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage1964 | natural gas steam turbine | FALSE | 5624 | RED-Rochester, LLC | 10025 | RED-Rochester, LLC | NY | Monroe | 41TG | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 25.6 | 0.8 | 25.6 | 25.6 | 5 | N |  |  | OP | X | 5 | 1964 |  |  | Y | Industrial CHP | 7 | X T T T T T: B; WAT BLQ BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG NG: DFO; WAT NG NG NG NG NG: DFO |  |  |  | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage1967 | natural gas steam turbine | FALSE | 5624 | RED-Rochester, LLC | 10025 | RED-Rochester, LLC | NY | Monroe | 42TG | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 25.6 | 0.8 | 25.6 | 25.6 | 5 | N |  |  | OP | X | 8 | 1967 |  |  | Y | Industrial CHP | 7 | X T T T T T: B; WAT BLQ BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG NG: DFO; WAT NG NG NG NG NG: DFO |  |  |  | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage1969 | natural gas steam turbine | FALSE | 5624 | RED-Rochester, LLC | 10025 | RED-Rochester, LLC | NY | Monroe | 43TG | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 25.6 | 0.8 | 25.6 | 25.6 | 5 | N |  |  | OP | X | 4 | 1969 |  |  | Y | Industrial CHP | 7 | X T T T T T: B; WAT BLQ BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG NG: DFO; WAT NG NG NG NG NG: DFO |  |  |  | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage1987 | natural gas steam turbine | FALSE | 5624 | RED-Rochester, LLC | 10025 | RED-Rochester, LLC | NY | Monroe | 44TG | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 25.6 | 0.8 | 25.6 | 25.6 | 5 | N |  |  | OP | X | 8 | 1987 |  |  | Y | Industrial CHP | 7 | X T T T T T: B; WAT BLQ BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG NG: DFO; WAT NG NG NG NG NG: DFO |  |  |  | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage2015 | natural gas steam turbine | FALSE | 5624 | RED-Rochester, LLC | 10025 | RED-Rochester, LLC | NY | Monroe | 75TG | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 3 | 0.9 | 2.2 | 2.2 | 0.4 | N |  |  | OP | X | 4 | 2015 |  |  | Y | Industrial CHP | 7 | X T T T T T: B; WAT BLQ BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG NG: RFO; WAT NG NG NG NG NG: RFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | N
Vintage1957 | hydro | FALSE | 5624 | RED-Rochester, LLC | 10025 | RED-Rochester, LLC | NY | Monroe | KPR1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 6 | 1957 |  |  | N | Industrial CHP | 7 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 12H | [23 empty] | N
Vintage2008 | biomass | TRUE | 5901 | Encina Joint Powers Authority | 10026 | Encina Water Pollution Control | CA | San Diego | EG10 | Other Waste Biomass | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 11 | 2008 |  |  | N | Commercial Non-CHP | 4 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: OBG; WAT NG NG NG NG NG: NG |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | N
Vintage2008 | biomass | TRUE | 5901 | Encina Joint Powers Authority | 10026 | Encina Water Pollution Control | CA | San Diego | EG20 | Other Waste Biomass | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 11 | 2008 |  |  | N | Commercial Non-CHP | 4 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: OBG; WAT NG NG NG NG NG: NG |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | N
Vintage2009 | biomass | TRUE | 5901 | Encina Joint Powers Authority | 10026 | Encina Water Pollution Control | CA | San Diego | EG30 | Other Waste Biomass | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 1 | 2009 |  |  | N | Commercial Non-CHP | 4 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: OBG; WAT NG NG NG NG NG: NG |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | N
Vintage2009 | biomass | TRUE | 5901 | Encina Joint Powers Authority | 10026 | Encina Water Pollution Control | CA | San Diego | EG40 | Other Waste Biomass | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 4 | 2009 |  |  | N | Commercial Non-CHP | 4 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: OBG; WAT NG NG NG NG NG: NG |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | N
Vintage2017 | solar pv | FALSE | 7049 | General Electric Aircraft Engines | 10029 | General Electric Aircraft Engines | MA | Essex | PV | Solar Photovoltaic | PV |  | W | X | X |  |  | 2.1 |  | 2.1 | 2.1 |  | N |  |  | OP | X | 5 | 2017 |  |  | N | Industrial Non-CHP | 6 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: SUN | [27 empty] | N |  |  | N
Vintage1985 | natural gas combined cycle | TRUE | 7860 | Energy Center Dover LLC | 10030 | Energy Center Dover | DE | Kent | COG1 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | Kent 13kv -DoverST1 (GF1) | Kent 13kv -DoverST1 | 18 | 0.9 | 15 | 15 | 5 | N |  |  | OP | X | 5 | 1985 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T T T to WAT BLQ BLQ BLQ BLQ BLQ; WAT NG NG NG NG NG
Vintage2001 | natural gas combined cycle | TRUE | 7860 | Energy Center Dover LLC | 10030 | Energy Center Dover | DE | Kent | KD-1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | Kent 13kv -DoverCT1 (KD1) | Kent 13kv - DoverCT1 | 50 | 0.85 | 44 | 50 | 30 | N |  |  | OP | X | 6 | 2001 |  |  | N | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T T T to WAT BLQ BLQ BLQ BLQ BLQ
Vintage2001 | natural gas peaker | TRUE | 7860 | Energy Center Dover LLC | 10030 | Energy Center Dover | DE | Kent | KD-2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | Kent 13kv -DoverCT2 (KD2) | Kent 13kv -DoverCT2 | 50 | 0.85 | 44 | 50 | 30 | N |  |  | OP | X | 6 | 2001 |  |  | N | IPP CHP | 3 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG NG: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1987 | natural gas combined cycle | TRUE | 3028 | Calpine Gilroy Cogen LP | 10034 | Gilroy Power Plant | CA | Santa Clara | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 90 | 1 | 85 | 85 | 85 | N |  |  | OP | X | 10 | 1987 |  |  | Y | IPP CHP | 3 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | N | bar: X T T T T T to WAT BLQ BLQ BLQ BLQ BLQ
Vintage1987 | natural gas combined cycle | TRUE | 3028 | Calpine Gilroy Cogen LP | 10034 | Gilroy Power Plant | CA | Santa Clara | GEN2 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X |  |  | 40 | 1 | 30 | 35 | 20 | N |  |  | OP | X | 10 | 1987 |  |  | Y | IPP CHP | 3 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | N | bar: X T T T T T to WAT BLQ BLQ BLQ BLQ BLQ
Vintage1989 | hydro | TRUE | 56590 | Silverstreet Hydro | 10036 | Hillsborough Hosiery | NH | Hillsborough | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 1 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 12 | 1989 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT | [5 empty] | 0 | 10M
Vintage1989 | hydro | TRUE | 56590 | Silverstreet Hydro | 10036 | Hillsborough Hosiery | NH | Hillsborough | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 1 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 12 | 1989 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT | [6 empty] | 10M
Vintage2008 | natural gas peaker | FALSE | 10077 | Kaweah Delta Hospital | 10042 | Kaweah Delta District Hospital | CA | Tulare | KDHT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.5 | 0.8 | 3.5 | 3.5 | 1.6 | N |  |  | OP | X | 10 | 2008 |  |  | N | Commercial Non-CHP | 4 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | bar: X T T T T T to WAT BLQ BLQ BLQ BLQ BLQ
Vintage1994 | hard coal | TRUE | 63046 | Logan Generating Company LP | 10043 | Logan Generating Plant | NJ | Gloucester | GEN1 | Conventional Steam Coal | ST |  | W | X | X | 49790 | 49790 | 242.3 | 0.9 | 219 | 219 | 50 | N |  |  | OP | X | 9 | 1994 |  |  | Y | IPP CHP | 3 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: BIT; WAT NG NG NG NG NG: DFO; WAT NG NG NG NG NG: DFO |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N
Vintage1984 | hydro | TRUE | 54696 | Little Mac Power Company | 10049 | Little Mac Project | ID | Twin Falls | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0 | N |  |  | OP | X | 5 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage1984 | hydro | TRUE | 54696 | Little Mac Power Company | 10049 | Little Mac Project | ID | Twin Falls | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0 | N |  |  | OP | X | 5 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1984 | hydro | TRUE | 54696 | Little Mac Power Company | 10049 | Little Mac Project | ID | Twin Falls | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0 | N |  |  | OP | X | 5 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1984 | hydro | TRUE | 54696 | Little Mac Power Company | 10049 | Little Mac Project | ID | Twin Falls | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0 | N |  |  | OP | X | 5 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage2009 | biomass | TRUE | 11079 | Little Rock Water Reclamation Authority | 10050 | Fourche Creek Wastewater | AR | Pulaski | 4 | Other Waste Biomass | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 0.8 | N |  |  | OP | X | 12 | 2009 |  |  | Y | Commercial CHP | 5 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: OBG; WAT NG NG NG NG NG: NG; WAT NG NG NG NG NG: OBG |  |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1985 | hydro | TRUE | 49753 | Brooks Energy, LLC | 10051 | Lockville Hydropower | NC | Chatham | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 1 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1985 | hydro | TRUE | 49753 | Brooks Energy, LLC | 10051 | Lockville Hydropower | NC | Chatham | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 1 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1986 | biomass | TRUE | 54788 | DG Fairhaven Power LLC | 10052 | Fairhaven Power | CA | Humboldt | GEN1 | Wood/Wood Waste Biomass | ST |  | W | X | X |  |  | 18.8 | 0.95 | 16 | 16 | 1 | N |  |  | OA | X | 9 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WDS; WAT NG NG NG NG NG: NG; WAT NG NG NG NG NG: NG |  |  |  | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage1984 | petroleum | FALSE | 7075 | General Electric Co | 10058 | General Electric Diesel Engine Plant | PA | Mercer | REGN | Petroleum Liquids | IC |  | S | X | X |  |  | 4.4 | 0.8 | 4.3 | 4.2 | 0 | N |  |  | OP | X | 6 | 1984 |  |  | N | Industrial Non-CHP | 6 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: DFO |  |  |  | N |  |  | 10M | [23 empty] | N | N | N
Vintage1984 | hydro | FALSE | 7080 | Aclara Meters LLC | 10059 | General Electric Great Falls Upper Hydro | NH | Strafford | 1575 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 1 | 1.6 | 1.6 | 0.4 | N |  |  | OS | X | 12 | 1984 | 8 | 2023 | N | Industrial Non-CHP | 6 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1988 | hydro | FALSE | 7080 | Aclara Meters LLC | 10059 | General Electric Great Falls Upper Hydro | NH | Strafford | 500 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.88 | 0.5 | 0.5 | 0.2 | N |  |  | OS | X | 8 | 1988 | 8 | 2023 | N | Industrial Non-CHP | 6 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1989 | natural gas combined cycle | FALSE | 11401 | Mars Wrigley Confectionery US, LLC | 10061 | Mars Wrigley Confectionery US, LLC | NJ | WARREN | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 10.9 | 0.8 | 8.8 | 10.7 | 6 | N |  |  | OP | X | 5 | 1989 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N | 0 | 1H | [23 empty] | N | N | N | bar: X T T T T T to WAT BLQ BLQ BLQ BLQ BLQ
Vintage1984 | natural gas combined cycle | FALSE | 11401 | Mars Wrigley Confectionery US, LLC | 10061 | Mars Wrigley Confectionery US, LLC | NJ | WARREN | GEN2 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X |  |  | 1.4 | 0.8 | 0.7 | 1.2 | 0.5 | N |  |  | OP | X | 10 | 1984 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T T T to WAT BLQ BLQ BLQ BLQ BLQ
Vintage1981 | municipal solid waste | TRUE | 50085 | Covanta Southeast Florida Renewable Ltd | 10062 | Miami Dade County Resource Recovery Fac | FL | Miami Dade | GEN1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 38.5 | 0.85 | 35.8 | 36.2 | 5 | N |  |  | OP | X | 12 | 1981 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: MSW; WAT NG NG NG NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1981 | municipal solid waste | TRUE | 50085 | Covanta Southeast Florida Renewable Ltd | 10062 | Miami Dade County Resource Recovery Fac | FL | Miami Dade | GEN2 | Municipal Solid Waste | ST |  | S | X | X |  |  | 38.5 | 0.85 | 35.8 | 36.2 | 5 | N |  |  | OP | X | 12 | 1981 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: MSW; WAT NG NG NG NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1989 | hydro | TRUE | 11943 | McCallum Enterprises I LP | 10063 | Derby Hydro | CT | Fairfield | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4 | 1 | 4 | 4 | 2.5 | N |  |  | OP | X | 1 | 1989 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1989 | hydro | TRUE | 11943 | McCallum Enterprises I LP | 10063 | Derby Hydro | CT | Fairfield | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4 | 1 | 4 | 4 | 2.5 | N |  |  | OP | X | 1 | 1989 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M
Vintage1989 | hydro | TRUE | 11943 | McCallum Enterprises I LP | 10063 | Derby Hydro | CT | Fairfield | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 1 | 0.3 | 0.3 | 0.2 | N |  |  | SB | Y | 1 | 1989 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 10M
Vintage1989 | hydro | TRUE | 11943 | McCallum Enterprises I LP | 10063 | Derby Hydro | CT | Fairfield | GEN4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 1 | 0.3 | 0.3 | 0.2 | N |  |  | SB | Y | 1 | 1989 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 10M
Vintage1985 | hydro | TRUE | 12401 | Merimil Ltd Partnership | 10066 | Lockwood Hydroelectric Facility | ME | Kennebec | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.9 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 10 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M
Vintage1985 | hydro | TRUE | 12401 | Merimil Ltd Partnership | 10066 | Lockwood Hydroelectric Facility | ME | Kennebec | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.9 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 10 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M
Vintage1985 | hydro | TRUE | 12401 | Merimil Ltd Partnership | 10066 | Lockwood Hydroelectric Facility | ME | Kennebec | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.9 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 10 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M
Vintage1985 | hydro | TRUE | 12401 | Merimil Ltd Partnership | 10066 | Lockwood Hydroelectric Facility | ME | Kennebec | GEN4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.9 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 10 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M
Vintage1985 | hydro | TRUE | 12401 | Merimil Ltd Partnership | 10066 | Lockwood Hydroelectric Facility | ME | Kennebec | GEN5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.9 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 10 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M
Vintage1985 | hydro | TRUE | 12401 | Merimil Ltd Partnership | 10066 | Lockwood Hydroelectric Facility | ME | Kennebec | GEN6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.9 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 10 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M
Vintage1988 | hydro | TRUE | 12401 | Merimil Ltd Partnership | 10066 | Lockwood Hydroelectric Facility | ME | Kennebec | GEN7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.9 | 2.2 | 2.2 | 0.1 | N |  |  | OP | X | 10 | 1988 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M
Vintage1985 | hydro | TRUE | 5164 | Denver City & County-Foothills | 10070 | Foothills Hydro Plant | CO | Douglas | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.1 | 0.88 | 3.1 | 3.1 | 0.4 | N |  |  | OP | X | 5 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1982 | other | FALSE | 55727 | Orion Engineered Carbons | 10072 | Engineered Carbons Borger Cogen | TX | Hutchinson | GEN1 | Other Gases | ST |  | S | X | X | NA ( behind the meter ) | NA ( behind the meter ) | 20 | 1 | 18.8 | 18.8 | 5 | N |  |  | OP | X | 10 | 1982 |  |  | N | Industrial Non-CHP | 6 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: OG; WAT NG NG NG NG NG: NG; WAT NG NG NG NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1957 | hard coal | TRUE | 12647 | ALLETE, Inc. | 10075 | Taconite Harbor Energy Center | MN | Cook | GEN1 | Conventional Steam Coal | ST |  | S | X | X | MP.TACHB1 | MP.TACHB1 | 84 | 0.9 | 79 | 79 | 32 | N |  |  | SB | Y | 1 | 1957 | 3 | 2023 | N | Electric Utility | 1 | X | SUB | DFO | BIT |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | N |  |  | N
Vintage1957 | hard coal | TRUE | 12647 | ALLETE, Inc. | 10075 | Taconite Harbor Energy Center | MN | Cook | GEN2 | Conventional Steam Coal | ST |  | S | X | X | MP.TACHB2 | MP.TACHB2 | 84 | 0.9 | 75.9 | 75.9 | 32 | N |  |  | SB | Y | 1 | 1957 | 3 | 2023 | N | Electric Utility | 1 | X | SUB | DFO | BIT |  |  |  | DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [15 empty] | N |  |  | N
Vintage1986 | hydro | TRUE | 5068 | Denver City & County of | 10081 | Strontia Springs Hydro Plant | CO | Douglas | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.9 | 1 | 1 | 0.5 | N |  |  | OP | X | 7 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 1H | [7 empty] | 373 | 373 | 10 | 2024 | [12 empty] | N
Vintage2003 | biomass | TRUE | 11217 | Los Angeles County Sanitation | 10091 | Total Energy Facilities | CA | Los Angeles | G2 | Other Waste Biomass | CT | CC1 | S | X | Y |  |  | 9.9 | 0.9 | 8 | 9 | 5 | N |  |  | OP | X | 2 | 2003 |  |  | Y | Commercial CHP | 5 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: OBG; WAT NG NG NG NG NG: NG; WAT WDS WDS WDS WDS WDS: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2001 | biomass | TRUE | 11217 | Los Angeles County Sanitation | 10091 | Total Energy Facilities | CA | Los Angeles | G3 | Other Waste Biomass | CT | CC1 | S | X | Y |  |  | 9.9 | 0.9 | 8 | 9 | 5 | N |  |  | OP | X | 12 | 2001 |  |  | Y | Commercial CHP | 5 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: OBG; WAT NG NG NG NG NG: NG; WAT WDS WDS WDS WDS WDS: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1986 | biomass | TRUE | 11217 | Los Angeles County Sanitation | 10091 | Total Energy Facilities | CA | Los Angeles | GEN1 | Other Waste Biomass | CT | CC1 | S | X | Y |  |  | 9.9 | 0.9 | 8 | 9 | 5 | N |  |  | OP | X | 1 | 1986 |  |  | Y | Commercial CHP | 5 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: OBG; WAT NG NG NG NG NG: NG; WAT WDS WDS WDS WDS WDS: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1986 | biomass | TRUE | 11217 | Los Angeles County Sanitation | 10091 | Total Energy Facilities | CA | Los Angeles | GEN4 | Other Waste Biomass | CA | CC1 | S | N | X |  |  | 8.7 | 0.9 | 7.4 | 7.4 | 2 | N |  |  | OP | X | 11 | 1986 |  |  | Y | Commercial CHP | 5 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: OBG; WAT NG NG NG NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1982 | petroleum | FALSE | 58553 | PAR Petroleum | 10093 | Tesoro Hawaii | HI | Honolulu | GEN1 | Petroleum Liquids | GT |  | S | X | X |  |  | 20 | 0.8 | 20 | 20 | 5 | N |  |  | OP | X | 12 | 1982 |  |  | Y | Industrial CHP | 7 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: WO; WAT NG NG NG NG NG: JF; WAT WDS WDS WDS WDS WDS: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | N
Vintage1992 | natural gas combined cycle | TRUE | 50160 | Pedricktown Cogeneration Company LP | 10099 | Pedricktown Cogeneration Company LP | NJ | Salem | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | 71856717 | 71856717 | 95.2 | 0.9 | 112.8 | 112.6 | 105 | N |  |  | OP | X | 3 | 1992 | 5 | 2022 | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG NG: DFO |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | Y | N | Y
Vintage1992 | natural gas combined cycle | TRUE | 50160 | Pedricktown Cogeneration Company LP | 10099 | Pedricktown Cogeneration Company LP | NJ | Salem | GEN2 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | 71856717 | 71856717 | 45 | 0.85 |  |  |  | N |  |  | OP | X | 3 | 1992 | 5 | 2022 | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG NG: DFO |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | Y | N | Y
Vintage2000 | natural gas peaker | FALSE | 6636 | Foss Manufacturing Company LLC | 10108 | Hampton Facility | NH | Rockingham | GEN8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 5 | 0.8 | 3.8 | 5 | 1.2 | N |  |  | OP | X | 1 | 2000 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T T T to WAT BLQ BLQ BLQ BLQ BLQ
Vintage1985 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 10109 | Stevens Mills Dam | NH | Merrimack | 1G | Conventional Hydroelectric | HY |  | W | X | X | 4392 | 4392 | 0.2 | 0.9 | 0.2 | 0.2 | 0.2 | N |  |  | OP | X | 1 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT | [6 empty] | 10M
Vintage1985 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 10109 | Stevens Mills Dam | NH | Merrimack | 3G | Conventional Hydroelectric | HY |  | W | X | X | 4392 | 4392 | 1.7 | 0.9 | 1.8 | 1.8 | 0.3 | N |  |  | OP | X | 1 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT | [6 empty] | 10M
Vintage1986 | natural gas peaker | FALSE | 15743 | Frito-Lay Inc | 10110 | Frito-Lay Cogen Plant | CA | Kern | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 6 | 0.8 | 5.5 | 5.9 | 0.5 | N |  |  | OS | X | 3 | 1986 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H |  |  |  |  | N | [18 empty] | N | N | N | bar: X T T T T T to WAT BLQ BLQ BLQ BLQ BLQ
Vintage1988 | hard coal | TRUE | 7199 | Gilberton Power Co | 10113 | John B Rich Memorial Power Station | PA | Schuylkill | GEN1 | Conventional Steam Coal | ST |  | S | X | X | 50600 | 50600 | 88.4 | 0.85 | 80 | 80 | 50 | N |  |  | OP | X | 2 | 1988 |  |  | Y | IPP CHP | 3 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: WC; WAT NG NG NG NG NG: DFO; WAT NG NG NG NG NG: DFO |  |  |  | N | N |  | OVER | Y |  |  |  | Y | [18 empty] | Y | N | N
Vintage2016 | natural gas peaker | FALSE | 7726 | Sharp Grossmont Hospital | 10115 | Grossmont Hospital | CA | San Diego | GEN3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 4.5 | 0.83 | 4.2 | 4.4 | 2.2 | N |  |  | OP | X | 5 | 2016 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N | 0 | 1H |  |  |  |  | N | [18 empty] | N | N | bar: X T T T T T to WAT BLQ BLQ BLQ BLQ BLQ
Vintage1987 | hydro | TRUE | 9357 | Hampshire Paper Co Inc | 10116 | Hampshire Paper | NY | St Lawrence | 05 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.4 | 0.9 | 1.8 | 2.7 | 0.4 | N |  |  | OP | X | 5 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 1H | [20 empty] | N |  |  | N |  | N
Vintage2006 | municipal solid waste | TRUE | 8181 | Harrisburg Authority | 10118 | Harrisburg Facility | PA | Dauphin | GEN3 | Municipal Solid Waste | ST |  | W | X | X |  |  | 24.1 | 1 | 16.7 | 16.7 | 4 | N |  |  | OP | X | 4 | 2006 |  |  | Y | IPP CHP | 3 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: MSW; WAT NG NG NG NG NG: NG; WAT NG NG NG NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1980 | biomass | TRUE | 8486 | PInova Inc | 10120 | PInova Inc | GA | Glynn | GEN5 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 7.1 | 1 | 7.1 | 7.1 | 1 | N |  |  | OP | X | 1 | 1980 |  |  | Y | Industrial CHP | 7 | T | WDS | NG | OBL | RFO |  |  | WDS | NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1988 | hydro | TRUE | 8596 | High Shoals Hydro | 10121 | High Shoals Hydro (GA) | GA | Morgan | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.4 | 1 | 1.4 | 1.4 | 0.1 | N |  |  | OP | X | 11 | 1988 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT | [6 empty] | 10M
Vintage2002 | natural gas peaker | FALSE | 62860 | COE Bridgewater LLC c/o Thor Equities, LLC | 10122 | CIP II/AR Bridgewater Holdings - NJCOE | NJ | Somerset | 02 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | N/A | N/A | 5 | 0.9 | 4.1 | 4.2 | 2 | N |  |  | OP | X | 11 | 2002 |  |  | Y | Commercial CHP | 5 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG NG: DFO |  |  |  | N | N |  | 1H |  |  |  |  | N | [15 empty] | N |  |  | Y | N | Y
Vintage2004 | natural gas peaker | FALSE | 60557 | PB Nutclif Master, LLC | 10123 | Hoffmann LaRoche | NJ | Essex | TG01 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 5.3 | 0.9 | 4.1 | 5.3 | 2.8 | N |  |  | OP | X | 5 | 2004 |  |  | Y | Industrial CHP | 7 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG NG: DFO; WAT NG NG NG NG NG: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2004 | natural gas peaker | FALSE | 60557 | PB Nutclif Master, LLC | 10123 | Hoffmann LaRoche | NJ | Essex | TG03 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 5.3 | 0.9 | 4.1 | 5.3 | 2.8 | N |  |  | OP | X | 5 | 2004 |  |  | Y | Industrial CHP | 7 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG NG: DFO; WAT NG NG NG NG NG: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1987 | hydro | TRUE | 59136 | Ampersand Hollow Dam Hydro LLC | 10124 | Hollow Dam Power Partnership | NY | St Lawrence | HY1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OS | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N |  |  | 10M
Vintage1987 | hydro | TRUE | 59136 | Ampersand Hollow Dam Hydro LLC | 10124 | Hollow Dam Power Partnership | NY | St Lawrence | HY2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N |  |  | 10M
Vintage1983 | hydro | FALSE | 8787 | Humboldt Bay Mun Water Dist | 10128 | Gosselin Hydro Plant | CA | Trinity | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.85 | 0.1 | 0.3 | 0.1 | N |  |  | OP | X | 6 | 1983 |  |  | N | Commercial Non-CHP | 4 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1983 | hydro | FALSE | 8787 | Humboldt Bay Mun Water Dist | 10128 | Gosselin Hydro Plant | CA | Trinity | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.85 | 0.1 | 0.3 | 0.1 | N |  |  | OP | X | 6 | 1983 |  |  | N | Commercial Non-CHP | 4 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1988 | natural gas peaker | FALSE | 9335 | Indiana University of Penn | 10129 | Indiana University of Pennsylvania | PA | Indiana | GEN1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 6.1 | 0.9 | 6 | 6 | 0.5 | N |  |  | OP | X | 3 | 1988 |  |  | Y | Commercial CHP | 5 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG NG: DFO; WAT NG NG NG NG NG: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1988 | natural gas peaker | FALSE | 9335 | Indiana University of Penn | 10129 | Indiana University of Pennsylvania | PA | Indiana | GEN2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 6.1 | 0.9 | 6 | 6 | 0.5 | N |  |  | OP | X | 3 | 1988 |  |  | Y | Commercial CHP | 5 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG NG: DFO; WAT NG NG NG NG NG: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1988 | natural gas peaker | FALSE | 9335 | Indiana University of Penn | 10129 | Indiana University of Pennsylvania | PA | Indiana | GEN3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 6.1 | 0.9 | 6 | 6 | 0.5 | N |  |  | OP | X | 3 | 1988 |  |  | Y | Commercial CHP | 5 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG NG: DFO; WAT NG NG NG NG NG: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1988 | natural gas peaker | FALSE | 9335 | Indiana University of Penn | 10129 | Indiana University of Pennsylvania | PA | Indiana | GEN4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 6.1 | 0.9 | 6 | 6 | 0.5 | N |  |  | OP | X | 3 | 1988 |  |  | Y | Commercial CHP | 5 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG NG: DFO; WAT NG NG NG NG NG: DFO |  |  |  | N | N |  | 10M | [23 empty] | Y | Y | Y
Vintage1989 | hydro | TRUE | 7601 | Green Mountain Power Corp | 10137 | Deweys Mill | VT | Windsor | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 1 | 2.4 | 2.3 | 0.1 | N |  |  | OP | X | 6 | 1989 |  |  | N | Electric Utility | 1 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1989 | hydro | TRUE | 7601 | Green Mountain Power Corp | 10137 | Deweys Mill | VT | Windsor | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 1 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 6 | 1989 |  |  | N | Electric Utility | 1 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1985 | hydro | TRUE | 9370 | Hydrodynamics Inc | 10138 | South Dry Creek Hydro | MT | Carbon | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.95 | 2 |  | 0.2 | N |  |  | OP | X | 9 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N |  |  | 1H
Vintage1990 | hydro | TRUE | 9439 | Isabella Partners | 10139 | Isabella Hydro Project | CA | Kern | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.9 | 0.95 | 5.9 | 5.9 | 0.5 | N |  |  | OP | X | 12 | 1990 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 1H
Vintage1990 | hydro | TRUE | 9439 | Isabella Partners | 10139 | Isabella Hydro Project | CA | Kern | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.9 | 0.95 | 5.9 | 5.9 | 0.5 | N |  |  | OP | X | 12 | 1990 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 1H
Vintage1986 | hydro | TRUE | 1751 | Birch Power Co | 10140 | Birch Creek Power | ID | Clark | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.6 | 1 | 2.6 | 2.6 | 0.2 | N |  |  | OP | X | 4 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT | [5 empty] | 0 | 10M
Vintage1995 | hard coal | TRUE | 9379 | Inter-Power/AhlCon Partners, L.P. | 10143 | Colver Green Energy | PA | Cambria | COLV | Conventional Steam Coal | ST |  | S | X | X | Glory | Glory | 118 | 0.9 | 110 | 110 | 77 | N |  |  | OP | X | 2 | 1995 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WC; WAT NG NG NG NG NG: PG; WAT NG NG NG NG NG: PG |  |  |  | N | N |  | OVER | Y |  |  |  | Y | [18 empty] | N | N | N
Vintage2004 | biomass | TRUE | 17164 | Sierra Pacific Industries | 10144 | Sierra Pacific Lincoln Facility | CA | Placer | GEN4 | Wood/Wood Waste Biomass | ST |  | S | X | X | SPILINCF_7_N002 | SPILINCF_7_N002 | 19.2 | 0.85 | 17.5 | 16.9 | 1 | N |  |  | OP | X | 3 | 2004 |  |  | Y | Industrial CHP | 7 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: WDS; WAT NG NG NG NG NG: NG |  |  |  | N |  |  | 12H | [23 empty] | N | N | N
Vintage1957 | natural gas steam turbine | FALSE | 49967 | Decorative Panels International, Inc. | 10149 | Decorative Panels Intl | MI | Alpena | GEN1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 7.5 | 0.8 | 7 | 7.5 | 1 | N |  |  | OP | X | 11 | 1957 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H |  | N | [21 empty] | N | N | N | bar: X T T T T T to WAT BLQ BLQ BLQ BLQ BLQ; WAT NG NG NG NG NG
Vintage1992 | hard coal | TRUE | 563 | American Bituminous Power LP | 10151 | Grant Town Power Plant | WV | Marion | GEN1 | Conventional Steam Coal | ST |  | S | X | X | 5021728 | 5021728 | 95.7 | 1 | 80 | 80 | 32 | N |  |  | OP | X | 7 | 1992 |  |  | N | IPP Non-CHP | 2 | X | WC | NG | BIT | TDF | PC |  | NG |  |  |  | N | N | 0 | OVER | Y |  |  |  | Y | [18 empty] | Y | Y | N
Vintage1985 | hydro | TRUE | 503 | American Hydro Power Company | 10152 | Warrior Ridge Hydro | PA | Huntingdon | L-1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 1 | 0.7 | 0.7 | 0.2 | N |  |  | OP | X | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 503 | American Hydro Power Company | 10152 | Warrior Ridge Hydro | PA | Huntingdon | L-2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 1 | 0.7 | 0.7 | 0.2 | N |  |  | OP | X | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 503 | American Hydro Power Company | 10152 | Warrior Ridge Hydro | PA | Huntingdon | L-4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 1 | 0.7 | 0.7 | 0.2 | N |  |  | OP | X | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 503 | American Hydro Power Company | 10152 | Warrior Ridge Hydro | PA | Huntingdon | L-5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 1 | 0.7 | 0.7 | 0.2 | N |  |  | OP | X | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1985 | natural gas peaker | FALSE | 54769 | INEOS USA LLC | 10154 | Power Island | TX | Brazoria | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 41 | 0.85 | 30 | 38 | 29 | N |  |  | OP | X | 11 | 1985 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T T T to WAT BLQ BLQ BLQ BLQ BLQ
Vintage2020 | natural gas peaker | FALSE | 54769 | INEOS USA LLC | 10154 | Power Island | TX | Brazoria | GEN2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 50 | 0.85 | 40 | 50 | 20 | N |  |  | OP | X | 1 | 2020 |  |  | Y | Industrial CHP | 7 | [14 empty] | 1H | [23 empty] | N | N | N | bar: X T T T T T to WAT BLQ BLQ BLQ BLQ BLQ
Vintage2020 | natural gas peaker | FALSE | 54769 | INEOS USA LLC | 10154 | Power Island | TX | Brazoria | GEN3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 50 | 0.85 | 40 | 50 | 20 | N |  |  | OP | X | 2 | 2020 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T T T to WAT BLQ BLQ BLQ BLQ BLQ
Vintage1993 | hydro | TRUE | 756 | Appomattox River Associates LP | 10155 | Brasfield | VA | Chesterfield | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.9 | 0.99 | 2.9 | 2.9 | 0.3 | N |  |  | OP | X | 9 | 1993 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 12H | [20 empty] | N |  |  | N |  | N
Vintage1990 | natural gas combined cycle | TRUE | 20323 | Wellhead Services, Inc | 10156 | Fresno Cogen Partners | CA | Fresno | GEN2 | Natural Gas Fired Combined Cycle | CA | CC1 | J | N | X |  |  | 10 | 0.8 | 6 | 6.5 | 1.5 | N |  |  | OP | X | 1 | 1990 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X T T T T T to WAT BLQ BLQ BLQ BLQ BLQ
Vintage2001 | natural gas peaker | TRUE | 20323 | Wellhead Services, Inc | 10156 | Fresno Cogen Partners | CA | Fresno | GEN3 | Natural Gas Fired Combustion Turbine | GT |  | J | X | X |  |  | 18.6 | 0.85 | 18.6 | 18.6 | 14 | N |  |  | OP | X | 8 | 2001 |  |  | N | IPP CHP | 3 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X T T T T T to WAT BLQ BLQ BLQ BLQ BLQ
Vintage2004 | natural gas combined cycle | TRUE | 20323 | Wellhead Services, Inc | 10156 | Fresno Cogen Partners | CA | Fresno | GEN4 | Natural Gas Fired Combined Cycle | CT | CC1 | J | X | N |  |  | 52.2 | 0.85 | 52.2 | 52.2 | 1.5 | N |  |  | OP | X | 1 | 2004 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X T T T T T to WAT BLQ BLQ BLQ BLQ BLQ
Vintage1986 | hydro | TRUE | 5093 | Desert Water Agency | 10162 | Whitewater Hydro Plant | CA | Riverside | WWHI | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 0.9 | 1.3 | 1.3 | 0.8 | N |  |  | SB | Y | 4 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 1H | [20 empty] | Y | 3 | 2022 | N
Vintage1983 | petroleum | FALSE | 54705 | Seadrift Coke L P | 10167 | Seadrift Coke LP | TX | Calhoun | GEN1 | Petroleum Coke | ST |  | S | X | X | South Zone Node | South Zone Node | 7.6 | 1 | 7.6 | 7.6 | 1 | N |  |  | OP | X | 11 | 1983 |  |  | Y | Industrial CHP | 7 | X T T T T T: B; WAT BLQ BLQ BLQ BLQ BLQ: PC; WAT NG NG NG NG NG: NG | OG |  |  | N | N |  | OVER |  |  |  | Y | Y | [15 empty] | N |  |  | N | N | N
Vintage1989 | natural gas combined cycle | TRUE | 3084 | Carson Cogeneration Co | 10169 | Carson Cogeneration | CA | Los Angeles | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | J | X | N | ICEGEN_7_B1 | ICEGEN_7_B1 | 45.3 | 1 | 41.3 | 41.1 | 28 | N |  |  | OP | X | 12 | 1989 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | bar: X T T T T T to WAT BLQ BLQ BLQ BLQ BLQ
Vintage1990 | natural gas combined cycle | TRUE | 3084 | Carson Cogeneration Co | 10169 | Carson Cogeneration | CA | Los Angeles | GEN2 | Natural Gas Fired Combined Cycle | CA | CC1 | J | N | X | ICEGEN_7_B1 | ICEGEN_7_B1 | 10.5 | 1 | 8 | 8.1 | 8 | N |  |  | OP | X | 1 | 1990 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | bar: X T T T T T to WAT BLQ BLQ BLQ BLQ BLQ
Vintage1985 | hydro | TRUE | 63985 | Hydroland Omega LLC | 10173 | Cherokee Falls | SC | CHEROKEE | T-1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 4.3 | 1 | 1 | 2 | 0.1 | N |  |  | OP | X | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage2000 | petroleum | FALSE | 3476 | DTE San Diego COGEN Inc. | 10175 | Childrens Hospital | CA | San Diego | 0799 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.2 | N |  |  | SB | N | 4 | 2000 |  |  | N | Commercial CHP | 5 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2004 | natural gas peaker | FALSE | 3476 | DTE San Diego COGEN Inc. | 10175 | Childrens Hospital | CA | San Diego | 1711 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 4.8 | 0.9 | 4.8 | 4.8 | 2.8 | N |  |  | OP | X | 12 | 2004 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | bar: X T T T T T to WAT BLQ BLQ BLQ BLQ BLQ
Vintage2010 | petroleum | FALSE | 3476 | DTE San Diego COGEN Inc. | 10175 | Childrens Hospital | CA | San Diego | 5083 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.1 | N |  |  | OP | X | 10 | 2010 |  |  | N | Commercial CHP | 5 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N
Vintage2010 | petroleum | FALSE | 3476 | DTE San Diego COGEN Inc. | 10175 | Childrens Hospital | CA | San Diego | 5084 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.1 | N |  |  | OP | X | 10 | 2010 |  |  | N | Commercial CHP | 5 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N
Vintage2010 | petroleum | FALSE | 3476 | DTE San Diego COGEN Inc. | 10175 | Childrens Hospital | CA | San Diego | 5085 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.1 | N |  |  | OP | X | 10 | 2010 |  |  | N | Commercial CHP | 5 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N
Vintage1979 | other | TRUE | 11724 | Massachusetts Bay Trans Auth | 10176 | M Street Jet | MA | Suffolk | NO.6 | Petroleum Liquids | GT |  | S | X | X | NEMASSBOST | NEMASSBOST | 69 | 0.9 | 50 | 68 | 5 | N |  |  | OP | X | 5 | 1979 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: KER; WAT NG NG NG NG NG: KER |  |  |  | N | N | 0 | 10M | [23 empty] | N | N | N
Vintage1985 | biomass | TRUE | 19068 | Colorado Energy Nations Company, LLC | 10180 | Metro Wastewater Reclamation District | CO | Denver | 1 | Other Waste Biomass | IC |  | W | X | X |  |  | 2 | 0.85 | 1.2 | 1.2 | 0.6 | N |  |  | OS | X | 4 | 1985 |  |  | Y | IPP CHP | 3 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: OBG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1985 | biomass | TRUE | 19068 | Colorado Energy Nations Company, LLC | 10180 | Metro Wastewater Reclamation District | CO | Denver | 2 | Other Waste Biomass | IC |  | W | X | X |  |  | 2 | 0.85 | 1.2 | 1.2 | 0.6 | N |  |  | OS | X | 4 | 1985 |  |  | Y | IPP CHP | 3 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: OBG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1985 | biomass | TRUE | 19068 | Colorado Energy Nations Company, LLC | 10180 | Metro Wastewater Reclamation District | CO | Denver | 3 | Other Waste Biomass | IC |  | W | X | X |  |  | 2 | 0.85 | 1.2 | 1.2 | 0.6 | N |  |  | SB | Y | 4 | 1985 |  |  | Y | IPP CHP | 3 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: OBG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1985 | biomass | TRUE | 19068 | Colorado Energy Nations Company, LLC | 10180 | Metro Wastewater Reclamation District | CO | Denver | 4 | Other Waste Biomass | IC |  | W | X | X |  |  | 2 | 0.85 | 1.2 | 1.2 | 0.6 | N |  |  | SB | Y | 4 | 1985 |  |  | Y | IPP CHP | 3 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: OBG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2000 | biomass | TRUE | 19068 | Colorado Energy Nations Company, LLC | 10180 | Metro Wastewater Reclamation District | CO | Denver | 5 | Other Waste Biomass | GT |  | W | X | X |  |  | 3.5 | 0.95 | 2.5 | 3.1 | 0.6 | N |  |  | OP | X | 8 | 2000 |  |  | Y | IPP CHP | 3 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: OBG; WAT NG NG NG NG NG: NG; WAT NG NG NG NG NG: PG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage2000 | biomass | TRUE | 19068 | Colorado Energy Nations Company, LLC | 10180 | Metro Wastewater Reclamation District | CO | Denver | 6 | Other Waste Biomass | GT |  | W | X | X |  |  | 3.5 | 0.95 | 2.5 | 3.1 | 0.6 | N |  |  | OP | X | 9 | 2000 |  |  | Y | IPP CHP | 3 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: OBG; WAT NG NG NG NG NG: NG; WAT NG NG NG NG NG: PG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1988 | hydro | FALSE | 12374 | Metropolitan Sewerage District | 10181 | Metropolitan Sewerage District | NC | Buncombe | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.9 | 0.8 | 0.8 | 0.8 | N |  |  | SB | Y | 9 | 1988 |  |  | N | Commercial Non-CHP | 4 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1988 | hydro | FALSE | 12374 | Metropolitan Sewerage District | 10181 | Metropolitan Sewerage District | NC | Buncombe | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.9 | 0.8 | 0.8 | 0.8 | N |  |  | OP | X | 9 | 1988 |  |  | N | Commercial Non-CHP | 4 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1988 | hydro | FALSE | 12374 | Metropolitan Sewerage District | 10181 | Metropolitan Sewerage District | NC | Buncombe | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.9 | 0.8 | 0.8 | 0.8 | N |  |  | OP | X | 9 | 1988 |  |  | N | Commercial Non-CHP | 4 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 61979 | City of Nashua, NH | 10183 | Mine Falls Generating Station | NH | Hillsborough | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 0.9 | 1.5 | 1.5 | 0.4 | N |  |  | OP | X | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 61979 | City of Nashua, NH | 10183 | Mine Falls Generating Station | NH | Hillsborough | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 0.9 | 1.7 | 1.7 | 0.4 | N |  |  | OP | X | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1988 | natural gas peaker | FALSE | 62903 | Silicon Hills Campus, LLC | 10184 | Central Utility Plant | TX | Travis | EG1 | Natural Gas Internal Combustion Engine | IC | 1 | S | X | X |  |  | 6 | 0.8 | 3.6 | 4.1 | 1.8 | N |  |  | SB | Y | 7 | 1988 |  |  | Y | Commercial CHP | 5 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG NG: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1988 | natural gas peaker | FALSE | 62903 | Silicon Hills Campus, LLC | 10184 | Central Utility Plant | TX | Travis | EG2 | Natural Gas Internal Combustion Engine | IC | 1 | S | X | X |  |  | 6 | 0.8 | 2.5 | 2.4 | 1.8 | N |  |  | SB | Y | 7 | 1988 |  |  | Y | Commercial CHP | 5 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG NG: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1988 | natural gas steam turbine | FALSE | 62903 | Silicon Hills Campus, LLC | 10184 | Central Utility Plant | TX | Travis | TG1 | Natural Gas Steam Turbine | ST | 1 | S | X | X |  |  | 2.3 | 0.85 | 2.2 | 2.3 | 0.2 | N |  |  | SB | Y | 7 | 1988 |  |  | Y | Commercial CHP | 5 | X T T T T T: B; WAT BLQ BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG NG: DFO; WAT NG NG NG NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1983 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 10186 | Anson Abenaki Hydros | ME | Somerset | AB1 | Conventional Hydroelectric | HY |  | W | X | X | 4136 |  | 3 | 0.95 | 2.2 | 2.2 | 1 | N |  |  | OP | X | 5 | 1983 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1980 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 10186 | Anson Abenaki Hydros | ME | Somerset | AB2 | Conventional Hydroelectric | HY |  | W | X | X | 4136 |  | 2.7 | 0.95 | 2.2 | 2.2 | 1 | N |  |  | OP | X | 9 | 1980 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1983 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 10186 | Anson Abenaki Hydros | ME | Somerset | AB3 | Conventional Hydroelectric | HY |  | W | X | X | 4136 |  | 3 | 0.95 | 2.2 | 2.2 | 1 | N |  |  | OP | X | 4 | 1983 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1983 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 10186 | Anson Abenaki Hydros | ME | Somerset | AB4 | Conventional Hydroelectric | HY |  | W | X | X | 4136 |  | 3 | 0.95 | 2.2 | 2.2 | 1 | N |  |  | OP | X | 4 | 1983 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT | [5 empty] | 0 | 10M
Vintage1961 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 10186 | Anson Abenaki Hydros | ME | Somerset | AB5 | Conventional Hydroelectric | HY |  | W | X | X | 4136 |  | 2.5 | 0.95 | 2.2 | 2.2 | 1 | N |  |  | OP | X | 7 | 1961 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT | [5 empty] | 0 | 10M
Vintage2008 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 10186 | Anson Abenaki Hydros | ME | Somerset | AB6 | Conventional Hydroelectric | HY |  | W | X | X | 4136 |  | 3 | 0.95 | 2.6 | 2.6 | 2.1 | N |  |  | OP | X | 4 | 2008 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT |  |  |  | N |  |  | 10M
Vintage1950 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 10186 | Anson Abenaki Hydros | ME | Somerset | AB7 | Conventional Hydroelectric | HY |  | W | X | X | 4136 |  | 2.5 | 0.95 | 2.2 | 2.2 | 1 | N |  |  | OP | X | 1 | 1950 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT | [5 empty] | 0 | 10M
Vintage1989 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 10186 | Anson Abenaki Hydros | ME | Somerset | AB8 | Conventional Hydroelectric | HY |  | W | X | X | 4136 |  | 0.3 | 1 | 0.3 | 0.3 | 0.2 | N |  |  | OP | X | 8 | 1989 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT | [5 empty] | 0 | 10M
Vintage1984 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 10186 | Anson Abenaki Hydros | ME | Somerset | AN1 | Conventional Hydroelectric | HY |  | W | X | X | 4136 |  | 1.8 | 1 | 1.8 | 1.8 | 0.6 | N |  |  | OP | X | 9 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT | [5 empty] | 0 | 10M
Vintage1984 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 10186 | Anson Abenaki Hydros | ME | Somerset | AN2 | Conventional Hydroelectric | HY |  | W | X | X | 4136 |  | 1.8 | 1 | 1.8 | 1.8 | 0.6 | N |  |  | OP | X | 9 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT | [5 empty] | 0 | 10M
Vintage1984 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 10186 | Anson Abenaki Hydros | ME | Somerset | AN3 | Conventional Hydroelectric | HY |  | W | X | X | 4136 |  | 1.8 | 1 | 1.8 | 1.8 | 0.6 | N |  |  | OP | X | 9 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT | [5 empty] | 0 | 10M
Vintage1984 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 10186 | Anson Abenaki Hydros | ME | Somerset | AN4 | Conventional Hydroelectric | HY |  | W | X | X | 4136 |  | 1.8 | 1 | 1.8 | 1.8 | 0.6 | N |  |  | OP | X | 9 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT | [5 empty] | 0 | 10M
Vintage1984 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 10186 | Anson Abenaki Hydros | ME | Somerset | AN5 | Conventional Hydroelectric | HY |  | W | X | X | 4136 |  | 1.8 | 1 | 1.8 | 1.8 | 0.6 | N |  |  | OP | X | 9 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT | [5 empty] | 0 | 10M
Vintage2015 | natural gas peaker | FALSE | 4558 | Cutrale Citrus Juices USA Inc | 10188 | Cutrale Citrus Juices USA II | FL | Polk | GEN6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 4.1 | 0.8 | 4.3 | 3.9 | 1.5 | N |  |  | OP | X | 6 | 2015 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X T T T T T to WAT BLQ BLQ BLQ BLQ BLQ
Vintage2015 | natural gas peaker | FALSE | 4558 | Cutrale Citrus Juices USA Inc | 10188 | Cutrale Citrus Juices USA II | FL | Polk | GEN7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 4.1 | 0.8 | 4.3 | 3.9 | 1.5 | N |  |  | OP | X | 12 | 2015 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: X T T T T T to WAT BLQ BLQ BLQ BLQ BLQ
Vintage1992 | natural gas combined cycle | TRUE | 60741 | Fortistar Castleton Power | 10190 | Castleton Energy Center | NY | Rensselaer | GEN1 | Natural Gas Fired Combined Cycle | CT | CCCC | S | X | N |  |  | 47 | 0.9 | 67.7 | 76.6 | 50 | N |  |  | OP | X | 2 | 1992 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG NG: DFO | [6 empty] | 12H | [20 empty] | N |  |  | Y | Y | Y
Vintage1992 | natural gas combined cycle | TRUE | 60741 | Fortistar Castleton Power | 10190 | Castleton Energy Center | NY | Rensselaer | GEN2 | Natural Gas Fired Combined Cycle | CA | CCCC | W | Y | X |  |  | 25 | 0.9 |  |  | 0 | N |  |  | OP | X | 2 | 1992 |  |  | N | IPP Non-CHP | 2 | [14 empty] | 12H | [20 empty] | N |  |  | N | N | N | bar: X T T T T T to WAT BLQ BLQ BLQ BLQ BLQ
Vintage1984 | onshore wind | TRUE | 2719 | CalWind Resources Inc | 10191 | Tehachapi Wind Resource I | CA | Kern | EXIS | Onshore Wind Turbine | WT |  | S | X | X | SP15 | SP15 | 8.7 |  | 8.7 | 8.7 | 0 | N |  |  | OP | X | 12 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WND |  |  |  | N | N | 134 | [21 empty] | N |  |  | N
Vintage1990 | petroleum | FALSE | 3453 | Island Energy Services | 10194 | Hawaii Cogen | HI | Honolulu | GEN1 | Petroleum Liquids | GT |  | W | X | X |  |  | 3 | 0.8 | 3.2 | 3.2 | 2 | N |  |  | OS | X | 8 | 1990 |  |  | Y | Industrial CHP | 7 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: WO; WAT NG NG NG NG NG: OG |  |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1990 | petroleum | FALSE | 3453 | Island Energy Services | 10194 | Hawaii Cogen | HI | Honolulu | GEN2 | Petroleum Liquids | GT |  | W | X | X |  |  | 3 | 0.8 | 3.2 | 3.2 | 2 | N |  |  | OS | X | 8 | 1990 |  |  | Y | Industrial CHP | 7 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: WO; WAT NG NG NG NG NG: OG |  |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1990 | petroleum | FALSE | 3453 | Island Energy Services | 10194 | Hawaii Cogen | HI | Honolulu | GEN3 | Petroleum Liquids | GT |  | W | X | X |  |  | 3 | 0.8 | 3.2 | 3.2 | 2 | N |  |  | OS | X | 8 | 1990 |  |  | Y | Industrial CHP | 7 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: WO; WAT NG NG NG NG NG: OG |  |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage2011 | petroleum | FALSE | 3453 | Island Energy Services | 10194 | Hawaii Cogen | HI | Honolulu | GEN4 | Petroleum Liquids | GT |  | W | X | X |  |  | 3.2 | 0.8 | 3.2 | 3.2 | 2 | N |  |  | OS | X | 6 | 2011 |  |  | Y | Industrial CHP | 7 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: WO; WAT NG NG NG NG NG: OG |  |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1984 | natural gas peaker | FALSE | 50122 | CF Industries Nitrogen LLC | 10195 | CF Industries Yazoo City Complex | MS | Yazoo | EXIS | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | U EES MSCHEM G1 | U EES MSCHEM G1 | 25 | 0.8 | 20 | 22 | 1 | N |  |  | OP | X | 7 | 1984 |  |  | Y | Industrial CHP | 7 | [11 empty] | N |  |  | 12H | [23 empty] | N | bar: X T T T T T to WAT BLQ BLQ BLQ BLQ BLQ; WAT NG NG NG NG NG
Vintage1987 | hydro | TRUE | 60023 | EONY Generation Limited | 10196 | Moose River | NY | Lewis | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 12.6 | 0.9 | 12.4 | 12.2 | 2.5 | N |  |  | OP | X | 11 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT | [6 empty] | 1H
Vintage1986 | hydro | TRUE | 60023 | EONY Generation Limited | 10197 | Philadlephia | NY | Jefferson | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.6 | 0.9 | 3.3 | 3.3 | 0.6 | N |  |  | OP | X | 10 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: WAT | [6 empty] | 1H
Vintage1968 | other | FALSE | 9436 | Mosaic Phosphates Co. | 10198 | Mosaic Phosphates Uncle Sam | LA | St James | GEN2 | All Other | ST |  | S | X | X |  |  | 11 | 0.8 | 11 | 11 | 4 | N |  |  | OP | X | 1 | 1968 |  |  | Y | Industrial CHP | 7 | X T T T T T: B; WAT BLQ BLQ BLQ BLQ BLQ: WH; WAT NG NG NG NG NG: NG; WAT NG NG NG NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage2016 | other | FALSE | 9436 | Mosaic Phosphates Co. | 10198 | Mosaic Phosphates Uncle Sam | LA | St James | GEN3 | All Other | ST |  | S | X | X |  |  | 15 | 0.85 | 15 | 15 | 4 | N |  |  | OP | X | 8 | 2016 |  |  | Y | Industrial CHP | 7 | X T T T T T: B; WAT BLQ BLQ BLQ BLQ BLQ: WH; WAT NG NG NG NG NG: NG; WAT NG NG NG NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1988 | biomass | TRUE | 9686 | WestRock, Fernandina Beach | 10202 | Fernandina Beach Mill | FL | Nassau | GEN5 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 37.4 | 0.85 | 30 | 30 | 2.5 | N |  |  | OP | X | 1 | 1988 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | BIT | DFO |  | NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | N | [17 empty] | Y | Y | N
Vintage1982 | biomass | TRUE | 9686 | WestRock, Fernandina Beach | 10202 | Fernandina Beach Mill | FL | Nassau | GEN6 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 59.5 | 0.8 | 50 | 50 | 2.5 | N |  |  | OP | X | 9 | 1982 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | BIT | DFO |  | NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | N | [17 empty] | Y | Y | N
Vintage1988 | other | FALSE | 3102 | Mosaic Company | 10204 | Mosaic Co Tampa Facility | FL | Hillsborough | GEN1 | All Other | ST |  | S | X | X |  |  | 37.8 | 0.85 | 34.4 | 34.4 | 2 | N |  |  | OP | X | 8 | 1988 |  |  | Y | Industrial CHP | 7 | [11 empty] | N |  |  | OVER | [23 empty] | N | N | bar: X T T T T T to WAT BLQ BLQ BLQ BLQ BLQ; WAT NG NG NG NG NG
Vintage1999 | other | FALSE | 3102 | Mosaic Company | 10204 | Mosaic Co Tampa Facility | FL | Hillsborough | GEN3 | All Other | ST |  | S | X | X |  |  | 34.6 | 0.8 | 33.6 | 33.6 | 4 | N |  |  | OP | X | 11 | 1999 |  |  | Y | Industrial CHP | 7 | [11 empty] | N |  |  | OVER | [23 empty] | N | N | bar: X T T T T T to WAT BLQ BLQ BLQ BLQ BLQ; WAT NG NG NG NG NG
Vintage1989 | natural gas peaker | FALSE | 11161 | Loma Linda University | 10206 | Loma Linda University Cogen | CA | San Bernardino | GEN1 | Natural Gas Fired Combustion Turbine | GT | ST01 | S | X | X |  |  | 5.2 | 0.8 | 4.8 | 4.8 | 2.4 | N |  |  | OP | X | 11 | 1989 |  |  | Y | Commercial CHP | 5 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG NG: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1989 | natural gas peaker | FALSE | 11161 | Loma Linda University | 10206 | Loma Linda University Cogen | CA | San Bernardino | GEN2 | Natural Gas Fired Combustion Turbine | GT | ST01 | S | X | X |  |  | 5.2 | 0.8 | 4.8 | 4.8 | 2.4 | N |  |  | OP | X | 11 | 1989 |  |  | Y | Commercial CHP | 5 | X T T T T T: T; WAT BLQ BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG NG: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1986 | petroleum | FALSE | 11161 | Loma Linda University | 10206 | Loma Linda University Cogen | CA | San Bernardino | GEN4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.7 | 0.8 | 1.7 | 1.7 | 0.9 | N |  |  | SB | N | 6 | 1986 |  |  | N | Commercial CHP | 5 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2018 | petroleum | FALSE | 11161 | Loma Linda University | 10206 | Loma Linda University Cogen | CA | San Bernardino | GEN5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.5 | N |  |  | SB | N | 7 | 2018 |  |  | N | Commercial CHP | 5 | X T T T T T: X; WAT BLQ BLQ BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1969 | biomass | TRUE | 55867 | Verso Escanaba LLC | 10208 | Escanaba Mill | MI | Delta | NO.7 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 38.6 | 0.99 | 32 | 32 | 27.2 | N |  |  | OP | X | 1 | 1969 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | TDF | BIT | RFO | NG | [6 empty] | 12H |  | Y |  |  | Y | [18 empty] | Y | Y | Y
Vintage1972 | biomass | TRUE | 55867 | Verso Escanaba LLC | 10208 | Escanaba Mill | MI | Delta | NO.8 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 29.8 | 0.96 | 23 | 23 | 22.1 | N |  |  | OP | X | 1 | 1972 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | TDF | BIT | RFO | NG | [6 empty] | 12H |  | Y |  |  | Y | [18 empty] | Y | Y | Y
Vintage1982 | biomass | TRUE | 55867 | Verso Escanaba LLC | 10208 | Escanaba Mill | MI | Delta | NO9 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 54 | 0.9 | 45 | 45 | 45 | N |  |  | OP | X | 1 | 1982 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | TDF | BIT | RFO | NG | [6 empty] | 12H |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1987 | natural gas combined cycle | FALSE | 3452 | Chevron USA Inc-El Segundo | 10213 | El Segundo Cogen | CA | Los Angeles | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N | ELSEG4G 7 B1 |  | 42.4 | 0.85 | 38.7 | 38.7 | 30 | N |  |  | OP | X | 12 | 1987 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: OG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1987 | natural gas combined cycle | FALSE | 3452 | Chevron USA Inc-El Segundo | 10213 | El Segundo Cogen | CA | Los Angeles | GEN2 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N | ELSEG4G 7 B1 |  | 42.4 | 0.85 | 38.7 | 38.7 | 30 | N |  |  | OP | X | 12 | 1987 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: OG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1996 | natural gas combined cycle | FALSE | 3452 | Chevron USA Inc-El Segundo | 10213 | El Segundo Cogen | CA | Los Angeles | GEN5 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N | ELSEG4G 7 B1 |  | 40.3 | 0.85 | 39.2 | 39.2 | 20 | N |  |  | OP | X | 3 | 1996 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: OG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1996 | natural gas combined cycle | FALSE | 3452 | Chevron USA Inc-El Segundo | 10213 | El Segundo Cogen | CA | Los Angeles | GEN6 | Natural Gas Fired Combined Cycle | CA | CC1 | W | Y | X |  |  | 9.1 | 0.85 | 9.1 | 9.1 | 2 | N |  |  | OP | X | 3 | 1996 |  |  | Y | Industrial CHP | 7 | X T T T: B; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: OG |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage2013 | natural gas combined cycle | FALSE | 3452 | Chevron USA Inc-El Segundo | 10213 | El Segundo Cogen | CA | Los Angeles | GEN7 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | ELSEG4G_7_B1 | ELSEG4G_7_B1 | 40.7 | 0.85 | 40.7 | 40.7 | 25 | N |  |  | OP | X | 6 | 2013 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: OG |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage2013 | natural gas combined cycle | FALSE | 3452 | Chevron USA Inc-El Segundo | 10213 | El Segundo Cogen | CA | Los Angeles | GEN8 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | ELSEG4G_7_B1 | ELSEG4G_7_B1 | 5.2 | 0.85 | 5.2 | 5.2 | 0.5 | N |  |  | OP | X | 6 | 2013 |  |  | N | Industrial CHP | 7 | X T T T: X; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: OG |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1990 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10214 | Lower Saranac Hydroelectric Facility | NY | Clinton | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.2 | 1 | 3 | 2.9 | 0.1 | N |  |  | OP | X | 10 | 1990 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [6 empty] | 10M
Vintage1990 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10214 | Lower Saranac Hydroelectric Facility | NY | Clinton | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.2 | 1 | 3 | 2.9 | 0.1 | N |  |  | OP | X | 10 | 1990 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [6 empty] | 10M
Vintage1990 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10214 | Lower Saranac Hydroelectric Facility | NY | Clinton | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 11 | 1990 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [6 empty] | 10M
Vintage1978 | biomass | TRUE | 57356 | Alabama River Cellulose LLC | 10216 | Alabama River Pulp | AL | Monroe | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 48 | 0.9 | 43.5 | 48.5 | 5 | N |  |  | OP | X | 11 | 1978 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: BLQ; DFO NG NG NG: WDS; DFO NG NG NG: NG | DFO |  |  | N | N |  | OVER |  |  |  |  | N | [18 empty] | N | N | N
Vintage1988 | hydro | TRUE | 55754 | Boralex Hydro Operations Inc | 10218 | Warrensburg Hydroelectric | NY | Warren | HY1 | Conventional Hydroelectric | HY |  | J | X | X | F | F | 2.9 | 0.95 | 2.9 | 2.9 | 0.1 | N |  |  | OP | X | 12 | 1988 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1989 | hydro | TRUE | 55754 | Boralex Hydro Operations Inc | 10219 | Middle Falls Hydro | NY | Washington | HY1 | Conventional Hydroelectric | HY |  | J | X | X | F | F | 1.1 | 0.95 | 1.1 | 1.1 | 0.1 | N |  |  | OP | X | 9 | 1989 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1989 | hydro | TRUE | 55754 | Boralex Hydro Operations Inc | 10219 | Middle Falls Hydro | NY | Washington | HY2 | Conventional Hydroelectric | HY |  | J | X | X | F | F | 1.1 | 0.95 | 1.1 | 1.1 | 0.1 | N |  |  | OP | X | 9 | 1989 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1990 | hydro | TRUE | 55754 | Boralex Hydro Operations Inc | 10220 | Sissonville Hydro | NY | St Lawrence | HY1 | Conventional Hydroelectric | HY |  | J | X | X | E | E | 3 | 0.95 | 3 | 3 | 0.1 | N |  |  | OP | X | 7 | 1990 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1990 | hydro | TRUE | 55754 | Boralex Hydro Operations Inc | 10221 | New York State Dam Hydro | NY | Saratoga | GEN1 | Conventional Hydroelectric | HY |  | J | X | X | F | F | 5.7 | 0.95 | 5.7 | 5.7 | 0.1 | N |  |  | OP | X | 11 | 1990 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1990 | hydro | TRUE | 55754 | Boralex Hydro Operations Inc | 10221 | New York State Dam Hydro | NY | Saratoga | GEN2 | Conventional Hydroelectric | HY |  | J | X | X | F | F | 5.7 | 0.95 | 5.7 | 5.7 | 0.1 | N |  |  | OP | X | 11 | 1990 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1989 | hydro | TRUE | 11278 | Lower Tule River Irrgtn Dist | 10222 | Tulare Success Power Project | CA | Tulare | SPP1 | Conventional Hydroelectric | HY |  | J | X | X |  |  | 1.4 | 1 | 1.4 | 1.4 | 0.8 | N |  |  | SB | Y | 12 | 1989 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1977 | natural gas steam turbine | FALSE | 12311 | Merck & Co Inc | 10224 | Merck Rahway Power Plant | NJ | Union | GEN8 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 5 | 0.8 | 5 | 5 | 2 | N |  |  | OS | X | 1 | 1977 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: DFO; DFO NG NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2004 | natural gas steam turbine | FALSE | 12311 | Merck & Co Inc | 10224 | Merck Rahway Power Plant | NJ | Union | GEN9 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 10.8 | 0.8 | 10.8 | 10.8 | 2 | N |  |  | OP | X | 1 | 2004 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: DFO; DFO NG NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2017 | natural gas steam turbine | FALSE | 12311 | Merck & Co Inc | 10224 | Merck Rahway Power Plant | NJ | Union | GEN9A | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 4.5 | 0.9 | 5.1 | 5.1 | 1 | N |  |  | OP | X | 12 | 2017 |  |  | N | Industrial CHP | 7 | X T T T: X; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: DFO; DFO NG NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2005 | solar pv | FALSE | 12311 | Merck & Co Inc | 10224 | Merck Rahway Power Plant | NJ | Union | SOLAR | Solar Photovoltaic | PV |  | S | X | X |  |  | 0.5 |  | 0.4 | 0.4 |  | N |  |  | OP | X | 12 | 2005 |  |  | N | Industrial CHP | 7 | X T T T: X; DFO BLQ BLQ BLQ: SUN |  |  |  | N | N | [25 empty] | N
Vintage1984 | biomass | TRUE | 50133 | Leaf River Cellulose LLC | 10233 | Leaf River Cellulose LLC | MS | Perry | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X | SME.LEAFRIVER |  | 25.2 | 0.8 | 26.1 | 26.7 | 4 | N |  |  | OP | X | 7 | 1984 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | NG |  |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1984 | biomass | TRUE | 50133 | Leaf River Cellulose LLC | 10233 | Leaf River Cellulose LLC | MS | Perry | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X | SME.LEAFRIVER |  | 25.2 | 0.8 | 26.1 | 26.7 | 4 | N |  |  | OP | X | 7 | 1984 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | NG |  |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1964 | hard coal | FALSE | 61813 | ND Paper, Inc. | 10234 | Biron Mill | WI | Wood | GEN1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 17 | 0.9 | 15.3 | 15.3 | 15.3 | N |  |  | OP | X | 9 | 1964 |  |  | Y | Industrial CHP | 7 | T | BIT | SUB | NG | WDS |  |  | NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1947 | natural gas steam turbine | FALSE | 61813 | ND Paper, Inc. | 10234 | Biron Mill | WI | Wood | GEN3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 7.5 | 0.8 | 7.5 | 7.5 | 7.5 | N |  |  | OP | X | 9 | 1947 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H |  | N |  |  | N | [18 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ; DFO NG NG NG
Vintage1957 | natural gas steam turbine | FALSE | 61813 | ND Paper, Inc. | 10234 | Biron Mill | WI | Wood | GEN4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 15.6 | 0.8 | 12.5 | 12.5 | 12.5 | N |  |  | OP | X | 10 | 1957 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H |  | N |  |  | N | [18 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ; DFO NG NG NG
Vintage1987 | hard coal | FALSE | 61813 | ND Paper, Inc. | 10234 | Biron Mill | WI | Wood | GEN5 | Conventional Steam Coal | ST |  | S | X | X |  |  | 21.5 | 0.8 | 20 | 20 | 20 | N |  |  | OP | X | 2 | 1987 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: SUB; DFO NG NG NG: WDS; DFO NG NG NG: SUB |  |  |  | N | N |  | 12H | N | N | Y |  | Y | [18 empty] | Y | Y | N
Vintage1985 | hydro | TRUE | 60023 | EONY Generation Limited | 10237 | Diana Hydroelectric | NY | Lewis | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 0.9 | 1.7 | 1.7 | 0.4 | N |  |  | OP | X | 7 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [6 empty] | 1H
Vintage1985 | hydro | TRUE | 60023 | EONY Generation Limited | 10238 | Dolgeville Hydro | NY | Herkimer | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5 | 0.9 | 5 | 5 | 0 | N |  |  | OP | X | 7 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [6 empty] | 1H
Vintage1989 | natural gas peaker | FALSE | 3432 | Ticona Polymers Inc | 10243 | Ticona Polymers Inc | TX | Nueces | GEN5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 44.2 | 0.9 | 32.5 | 38 | 18 | N |  |  | OP | X | 4 | 1989 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N | 0 | 12H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1952 | biomass | TRUE | 61723 | Pixelle Specialty Solution, LLC | 10244 | Pixelle Specialty Solutions LLC - Chillicothe Facility | OH | Ross | T-10 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 10.6 | 0.9 | 7.3 | 4.5 | 5 | N |  |  | OS | X | 2 | 1952 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | TDF | DFO |  | DFO |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | Y | Y | N
Vintage1958 | biomass | TRUE | 61723 | Pixelle Specialty Solution, LLC | 10244 | Pixelle Specialty Solutions LLC - Chillicothe Facility | OH | Ross | T-11 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 24 | 0.9 | 12.2 | 6.7 | 8 | N |  |  | OP | X | 2 | 1958 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | TDF | DFO |  | DFO |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | Y | Y | N
Vintage1967 | biomass | TRUE | 61723 | Pixelle Specialty Solution, LLC | 10244 | Pixelle Specialty Solutions LLC - Chillicothe Facility | OH | Ross | T-12 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 31 | 0.9 | 17.9 | 17.9 | 10 | N |  |  | OP | X | 2 | 1967 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | TDF | DFO |  | DFO |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | Y | Y | N
Vintage1978 | natural gas steam turbine | FALSE | 61723 | Pixelle Specialty Solution, LLC | 10244 | Pixelle Specialty Solutions LLC - Chillicothe Facility | OH | Ross | T-13 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 27.2 | 0.9 | 7.4 | 10.3 | 7 | N |  |  | OP | X | 7 | 1978 |  |  | Y | Industrial CHP | 7 | T | NG | BLQ | WDS | TDF | DFO |  | NG | DFO |  |  | N | N |  | 12H | [20 empty] | N |  |  | Y | Y | N
Vintage1970 | other | FALSE | 56147 | Cleveland-Cliffs Burns Harbor LLC | 10245 | ArcelorMittal Burns Harbor | IN | Porter | GEN5 | Other Gases | ST |  | W | X | X |  |  | 62 | 0.95 | 60.5 | 60.5 | 2 | N |  |  | OP | X | 1 | 1970 |  |  | Y | Industrial CHP | 7 | T | OG | NG | BFG |  |  |  | NG |  |  |  | N | N |  | OVER | [20 empty] | N |  |  | N
Vintage1969 | other | FALSE | 56147 | Cleveland-Cliffs Burns Harbor LLC | 10245 | ArcelorMittal Burns Harbor | IN | Porter | GEN6 | Other Gases | ST |  | W | X | X |  |  | 51 | 0.95 | 51 | 51 | 10 | N |  |  | OP | X | 1 | 1969 |  |  | Y | Industrial CHP | 7 | T | OG | NG | BFG |  |  |  | NG |  |  |  | N | N |  | OVER | [20 empty] | N |  |  | N
Vintage1969 | other | FALSE | 56147 | Cleveland-Cliffs Burns Harbor LLC | 10245 | ArcelorMittal Burns Harbor | IN | Porter | GEN7 | Other Gases | ST |  | W | X | X |  |  | 63.2 | 0.95 | 63.2 | 63.2 | 10 | N |  |  | OP | X | 1 | 1969 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: BFG; DFO NG NG NG: OG; DFO NG NG NG: NG |  |  |  | N | N |  | OVER | [20 empty] | N |  |  | N
Vintage2006 | biomass | TRUE | 55849 | Domtar Paper Co LLC Kingsport Mill | 10252 | Domtar Kingsport Mill | TN | Sullivan | NO.1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  | 48934185 | 50 | 0.85 | 46.5 | 47 | 18 | N |  |  | OA | X | 10 | 2006 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | DFO | NG | SLW |  | NG |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | N | N | N
Vintage1989 | hydro | TRUE | 56531 | EIF Haypress LLC | 10253 | Haypress | CA | Sierra | LGEN | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5 | 0.9 | 5 | 5 | 0.7 | N |  |  | OP | X | 1 | 1989 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage1988 | hydro | TRUE | 56531 | EIF Haypress LLC | 10253 | Haypress | CA | Sierra | UGEN | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5 | 0.9 | 5 | 5 | 0.7 | N |  |  | OP | X | 12 | 1988 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage1988 | hydro | TRUE | 59178 | Brookfield Black Bear Hydro, LLC | 10255 | West Enfield Hydro | ME | Penobscot | GEN1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 6.5 | 0.9 | 4.4 | 4.4 | 2 | N |  |  | OP | X | 4 | 1988 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 12H
Vintage1988 | hydro | TRUE | 59178 | Brookfield Black Bear Hydro, LLC | 10255 | West Enfield Hydro | ME | Penobscot | GEN2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 6.5 | 0.9 | 5.1 | 5.1 | 2 | N |  |  | OP | X | 4 | 1988 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 12H
Vintage1981 | hydro | TRUE | 4980 | Haw River Hydro Co | 10258 | Haw River Hydro | NC | Alamance | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.2 | N |  |  | OP | X | 9 | 1981 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 1H | [20 empty] | N |  |  | N
Vintage1982 | hydro | TRUE | 4980 | Haw River Hydro Co | 10258 | Haw River Hydro | NC | Alamance | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 6 | 1982 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 1H | [20 empty] | N |  |  | N
Vintage1991 | natural gas peaker | FALSE | 29925 | Enterprise Products Optg LP | 10261 | Enterprise Products Operating | TX | Chambers | GEN3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.4 | 0.8 | 3 | 2.8 | 2.8 | N |  |  | OP | X | 11 | 1991 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1991 | natural gas peaker | FALSE | 29925 | Enterprise Products Optg LP | 10261 | Enterprise Products Operating | TX | Chambers | GEN4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.4 | 0.8 | 3 | 2.8 | 2.8 | N |  |  | OP | X | 11 | 1991 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1991 | natural gas peaker | FALSE | 29925 | Enterprise Products Optg LP | 10261 | Enterprise Products Operating | TX | Chambers | GEN5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.4 | 0.8 | 3 | 2.8 | 2.8 | N |  |  | OP | X | 11 | 1991 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1996 | natural gas peaker | FALSE | 29925 | Enterprise Products Optg LP | 10261 | Enterprise Products Operating | TX | Chambers | GEN6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.5 | 0.8 | 3 | 2.8 | 2.8 | N |  |  | OP | X | 12 | 1996 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1996 | natural gas peaker | FALSE | 29925 | Enterprise Products Optg LP | 10261 | Enterprise Products Operating | TX | Chambers | GEN7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.5 | 0.8 | 3 | 2.8 | 2.8 | N |  |  | OP | X | 12 | 1996 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1996 | natural gas peaker | FALSE | 29925 | Enterprise Products Optg LP | 10261 | Enterprise Products Operating | TX | Chambers | GEN8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.5 | 0.8 | 3 | 2.8 | 2.8 | N |  |  | OP | X | 12 | 1996 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage2003 | natural gas combined cycle | FALSE | 2848 | California Institute-Technology | 10262 | California Institute of Technology | CA | Los Angeles | GEN6 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 10.5 | 0.9 | 9 | 9.9 | 9 | N |  |  | OP | X | 8 | 2003 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage2003 | natural gas combined cycle | FALSE | 2848 | California Institute-Technology | 10262 | California Institute of Technology | CA | Los Angeles | GEN7 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X |  |  | 2.5 | 0.9 | 2.1 | 2.1 | 2 | N |  |  | OP | X | 10 | 2003 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1989 | natural gas peaker | FALSE | 3662 | Citrus World Inc | 10275 | Florida's Natural Growers | FL | Polk | CE50 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.5 | 0.8 | 3.3 | 2.1 | 0 | N |  |  | OP | X | 12 | 1989 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ; DFO NG NG NG
Vintage2000 | natural gas peaker | FALSE | 3662 | Citrus World Inc | 10275 | Florida's Natural Growers | FL | Polk | TA70 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 7.2 | 0.8 | 6.1 | 5.8 | 0 | N |  |  | OP | X | 11 | 2000 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ; DFO NG NG NG
Vintage1984 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 10276 | Clement Dam Hydro LLC | NH | Belknap | 0049 | Conventional Hydroelectric | HY |  | W | X | X | LD.WEBSTER 34.5 |  | 2.4 | 0.9 | 2.3 | 2.3 | 0.1 | N |  |  | OP | X | 12 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1920 | hydro | TRUE | 2048 | Bowersock Mills & Power Co | 10279 | Kansas River Project | KS | Douglas | 1 | Conventional Hydroelectric | HY |  | S | X | X | KACYBOWERSOCK | KACYBOWERSOCK | 0.3 | 1 | 0.3 | 0.4 | 0.1 | N |  |  | OP | X | 1 | 1920 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage2012 | hydro | TRUE | 2048 | Bowersock Mills & Power Co | 10279 | Kansas River Project | KS | Douglas | 10 | Conventional Hydroelectric | HY |  | S | X | X | KACYBOWERSOCK | KACYBOWERSOCK | 1.3 | 1 | 1.3 | 1.3 | 0.9 | N |  |  | OP | X | 12 | 2012 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2012 | hydro | TRUE | 2048 | Bowersock Mills & Power Co | 10279 | Kansas River Project | KS | Douglas | 11 | Conventional Hydroelectric | HY |  | S | X | X | KACYBOWERSOCK | KACYBOWERSOCK | 1 | 1 | 1 | 1 | 0.8 | N |  |  | OP | X | 12 | 2012 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [6 empty] | 10M | [23 empty] | N
Vintage1922 | hydro | TRUE | 2048 | Bowersock Mills & Power Co | 10279 | Kansas River Project | KS | Douglas | 2 | Conventional Hydroelectric | HY |  | S | X | X | KACYBOWERSOCK | KACYBOWERSOCK | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 7 | 1922 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage1922 | hydro | TRUE | 2048 | Bowersock Mills & Power Co | 10279 | Kansas River Project | KS | Douglas | 3 | Conventional Hydroelectric | HY |  | S | X | X | KACYBOWERSOCK | KACYBOWERSOCK | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 7 | 1922 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage1922 | hydro | TRUE | 2048 | Bowersock Mills & Power Co | 10279 | Kansas River Project | KS | Douglas | 4 | Conventional Hydroelectric | HY |  | S | X | X | KACYBOWERSOCK | KACYBOWERSOCK | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 7 | 1922 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage1922 | hydro | TRUE | 2048 | Bowersock Mills & Power Co | 10279 | Kansas River Project | KS | Douglas | 5 | Conventional Hydroelectric | HY |  | S | X | X | KACYBOWERSOCK | KACYBOWERSOCK | 0.4 | 1 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 7 | 1922 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage1925 | hydro | TRUE | 2048 | Bowersock Mills & Power Co | 10279 | Kansas River Project | KS | Douglas | 6 | Conventional Hydroelectric | HY |  | S | X | X | KACYBOWERSOCK | KACYBOWERSOCK | 0.4 | 1 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 5 | 1925 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage1925 | hydro | TRUE | 2048 | Bowersock Mills & Power Co | 10279 | Kansas River Project | KS | Douglas | 7 | Conventional Hydroelectric | HY |  | S | X | X | KACYBOWERSOCK | `KACYBOWERSOCK | 0.4 | 1 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 5 | 1925 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage2012 | hydro | TRUE | 2048 | Bowersock Mills & Power Co | 10279 | Kansas River Project | KS | Douglas | 8 | Conventional Hydroelectric | HY |  | S | X | X | KACYBOWERSOCK | KACYBOWERSOCK | 1 | 1 | 1 | 1 | 0.8 | N |  |  | OP | X | 12 | 2012 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2012 | hydro | TRUE | 2048 | Bowersock Mills & Power Co | 10279 | Kansas River Project | KS | Douglas | 9 | Conventional Hydroelectric | HY |  | S | X | X | KACYBOWERSOCK | KACYBOWERSOCK | 1.3 | 1 | 1.3 | 1.3 | 0.9 | N |  |  | OP | X | 12 | 2012 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1978 | petroleum | FALSE | 1947 | Bob Jones University | 10280 | Central Plant | SC | GREENVILLE | ENG1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.4 | N |  |  | SB | N | 1 | 1978 |  |  | N | Commercial Non-CHP | 4 | X T T T: X; DFO BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 1H |  |  |  | N | [19 empty] | N | N
Vintage2008 | petroleum | FALSE | 1947 | Bob Jones University | 10280 | Central Plant | SC | GREENVILLE | ENG5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.4 | N |  |  | SB | N | 10 | 2008 |  |  | N | Commercial Non-CHP | 4 | X T T T: X; DFO BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2008 | petroleum | FALSE | 1947 | Bob Jones University | 10280 | Central Plant | SC | GREENVILLE | ENG6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.4 | N |  |  | SB | N | 10 | 2008 |  |  | N | Commercial Non-CHP | 4 | X T T T: X; DFO BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2008 | petroleum | FALSE | 1947 | Bob Jones University | 10280 | Central Plant | SC | GREENVILLE | ENG7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.4 | N |  |  | SB | N | 10 | 2008 |  |  | N | Commercial Non-CHP | 4 | X T T T: X; DFO BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1987 | hydro | FALSE | 1678 | Big Creek Water Works Ltd | 10282 | Big Creek Water Works | CA | Trinity | BCHY | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5 | 0.95 | 4.8 | 4.6 | 0.2 | N |  |  | OP | X | 1 | 1987 |  |  | N | Commercial Non-CHP | 4 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  |  | N |  | 10M
Vintage1987 | hydro | TRUE | 1528 | Beaver Falls Municipal Auth | 10285 | Townsend Hydro | PA | Beaver | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.6 | 0.9 | 2.1 | 2.1 | 0.5 | N |  |  | OP | X | 10 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1987 | hydro | TRUE | 1528 | Beaver Falls Municipal Auth | 10285 | Townsend Hydro | PA | Beaver | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.6 | 0.9 | 2.1 | 2.1 | 0.5 | N |  |  | OP | X | 10 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1981 | hydro | FALSE | 4386 | Cornell Hydro | 10286 | Cornell Hydro | NY | Tompkins | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.9 | 0.5 | 0.7 | 0.2 | N |  |  | OP | X | 12 | 1981 |  |  | N | Commercial Non-CHP | 4 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 1H
Vintage1981 | hydro | FALSE | 4386 | Cornell Hydro | 10286 | Cornell Hydro | NY | Tompkins | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.1 | 0.9 | 1.1 | 1.1 | 0.2 | N |  |  | OP | X | 12 | 1981 |  |  | N | Commercial Non-CHP | 4 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 1H
Vintage1985 | geothermal | TRUE | 34691 | Ormat Nevada Inc | 10287 | Beowawe | NV | Lander | GEN1 | Geothermal | ST |  | S | X | X |  |  | 17 | 0.9 | 12.8 | 13.1 | 5 | N |  |  | OP | X | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: GEO; DFO NG NG NG: GEO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2011 | geothermal | TRUE | 34691 | Ormat Nevada Inc | 10287 | Beowawe | NV | Lander | GEN2 | Geothermal | BT |  | S | X | X |  |  | 3.6 | 0.9 | 1.3 | 2 | 1 | N |  |  | OP | X | 2 | 2011 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: GEO; DFO NG NG NG: GEO |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1983 | biomass | TRUE | 56497 | Big Valley Power (BVP) LLC | 10288 | Big Valley Power LLC | CA | Lassen | IS27 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 9.3 | 0.9 | 8.7 | 8.7 | 8.7 | N |  |  | OS | X | 8 | 1983 |  |  | N | Industrial Non-CHP | 6 | X T T T: X; DFO BLQ BLQ BLQ: WDS; DFO NG NG NG: AB |  |  |  | N |  |  | 12H | [23 empty] | N | N | N
Vintage1987 | biomass | TRUE | 2226 | Bridgewater Power Co LP | 10290 | Bridgewater Power LP | NH | Grafton | GEN1 | Wood/Wood Waste Biomass | ST |  | J | X | X |  |  | 20 | 0.9 | 16 | 16.5 | 2 | N |  |  | OP | X | 8 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WDS; DFO NG NG NG: DFO; DFO NG NG NG: DFO |  |  |  | N | N |  | 12H | N | N | N | [20 empty] | Y | N | N
Vintage1989 | natural gas combined cycle | TRUE | 2938 | Calpine King City Cogen LLC | 10294 | King City Power Plant | CA | Monterey | GTG | Natural Gas Fired Combined Cycle | CT | CC01 | S | X | N |  |  | 90.8 | 0.85 | 73 | 83.5 | 62 | N |  |  | OP | X | 2 | 1989 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ; DFO NG NG NG
Vintage1989 | natural gas combined cycle | TRUE | 2938 | Calpine King City Cogen LLC | 10294 | King City Power Plant | CA | Monterey | STG | Natural Gas Fired Combined Cycle | CA | CC01 | S | N | X |  |  | 42.4 | 0.85 | 38 | 39 | 28 | N |  |  | OP | X | 3 | 1989 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ; DFO NG NG NG
Vintage1984 | hydro | TRUE | 17627 | South Forks Joint Venture | 10296 | South Forks Hydro | ID | Twin Falls | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4 | 0.9 | 4 | 4 | 1 | N |  |  | OP | X | 12 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1984 | hydro | TRUE | 17627 | South Forks Joint Venture | 10296 | South Forks Hydro | ID | Twin Falls | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4 | 0.9 | 4 | 4 | 0.8 | N |  |  | OP | X | 12 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage2014 | natural gas peaker | FALSE | 327 | Air Liquide Large Industries U S LP | 10298 | Bayou Cogen Plant | TX | Harris | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 79.6 | 0.8 | 75 | 93 | 65 | N |  |  | OP | X | 5 | 2014 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: OG |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage2016 | natural gas peaker | FALSE | 327 | Air Liquide Large Industries U S LP | 10298 | Bayou Cogen Plant | TX | Harris | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 79.6 | 0.8 | 75 | 93 | 65 | N |  |  | OP | X | 1 | 2016 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: OG |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage2015 | natural gas peaker | FALSE | 327 | Air Liquide Large Industries U S LP | 10298 | Bayou Cogen Plant | TX | Harris | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 79.6 | 0.8 | 75 | 93 | 65 | N |  |  | OP | X | 1 | 2015 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: OG |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage2015 | natural gas peaker | FALSE | 327 | Air Liquide Large Industries U S LP | 10298 | Bayou Cogen Plant | TX | Harris | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 79.6 | 0.8 | 75 | 93 | 65 | N |  |  | OP | X | 1 | 2015 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: OG |  |  |  |  | N |  | 12H | [23 empty] | N
Vintage1991 | biomass | TRUE | 3998 | Desert View Power Inc | 10300 | Desert View Power | CA | Riverside | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 55.5 | 0.9 | 47 | 47 | 30 | N |  |  | OP | X | 11 | 1991 |  |  | N | IPP Non-CHP | 2 | X | WDS | NG | PC | TDF |  |  | NG |  |  |  | N | N |  | OVER | Y |  |  | N | Y | [18 empty] | Y | Y | N
Vintage1977 | natural gas steam turbine | FALSE | 57145 | Louisiana Sugar Refining LLC | 10301 | Louisiana Sugar Refining | LA | St James | GEN2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 2.5 | 0.8 | 1.7 | 1.7 | 0.2 | N |  |  | OP | X | 3 | 1977 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ; DFO NG NG NG
Vintage1957 | natural gas steam turbine | FALSE | 57145 | Louisiana Sugar Refining LLC | 10301 | Louisiana Sugar Refining | LA | St James | GEN3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 1.7 | 0.8 | 1.5 | 1.5 | 0.1 | N |  |  | SB | Y | 2 | 1957 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ; DFO NG NG NG
Vintage1969 | natural gas steam turbine | FALSE | 57145 | Louisiana Sugar Refining LLC | 10301 | Louisiana Sugar Refining | LA | St James | GEN4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 2.5 | 0.8 | 2.1 | 2 | 0.2 | N |  |  | OP | X | 9 | 1969 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ; DFO NG NG NG
Vintage2015 | natural gas peaker | FALSE | 13657 | Norfork Southern Corp | 10302 | Juniata Locomotive Shop | PA | Blair | GEN3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.7 | N |  |  | OP | X | 4 | 2015 |  |  | N | Commercial Non-CHP | 4 | [11 empty] | N | N |  | 1H |  |  |  |  | N | [18 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1987 | municipal solid waste | FALSE | 12834 | Dutchess County RRA | 10305 | Dutchess Cnty Resource Recovery Facility | NY | Dutchess | GEN1 | Municipal Solid Waste | ST |  | S | X | X | NYISO Zone G 23765 | NYISO | 9.2 | 0.8 | 7.2 | 7.4 | 4 | N |  |  | OP | X | 11 | 1987 |  |  | Y | Commercial CHP | 5 | X T T T: T; DFO BLQ BLQ BLQ: MSW; DFO NG NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1991 | natural gas combined cycle | TRUE | 21970 | Northeast Energy Associates LP | 10307 | Bellingham Cogeneration Facility | MA | Norfolk | CT1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 128.7 | 0.97 | 102 | 126 | 85 | N |  |  | OP | X | 9 | 1991 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: DFO |  |  |  | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage1991 | natural gas combined cycle | TRUE | 21970 | Northeast Energy Associates LP | 10307 | Bellingham Cogeneration Facility | MA | Norfolk | CT2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 128.7 | 0.97 | 102 | 126 | 85 | N |  |  | OP | X | 9 | 1991 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: DFO |  |  |  | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage1991 | natural gas combined cycle | TRUE | 21970 | Northeast Energy Associates LP | 10307 | Bellingham Cogeneration Facility | MA | Norfolk | ST1 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X |  |  | 128.7 | 0.97 | 60 | 84 | 30 | N |  |  | OP | X | 9 | 1991 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1991 | natural gas combined cycle | TRUE | 22290 | Sayreville Power Generation LP | 10308 | Sayreville Cogeneration Facility | NJ | Middlesex | CT1 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N | 50726 |  | 143.4 | 0.9 | 112 | 127.8 | 86 | N |  |  | OP | X | 8 | 1991 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1991 | natural gas combined cycle | TRUE | 22290 | Sayreville Power Generation LP | 10308 | Sayreville Cogeneration Facility | NJ | Middlesex | CT2 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N |  |  | 143.4 | 0.9 | 112 | 127.8 | 86 | N |  |  | OP | X | 8 | 1991 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1991 | natural gas combined cycle | TRUE | 22290 | Sayreville Power Generation LP | 10308 | Sayreville Cogeneration Facility | NJ | Middlesex | ST1 | Natural Gas Fired Combined Cycle | CA | CC1 | W | N | X |  |  | 143.4 | 0.9 | 68 | 77.5 | 26 | N |  |  | OP | X | 8 | 1991 |  |  | N | IPP Non-CHP | 2 | [14 empty] | 12H |  | N | [21 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1985 | natural gas peaker | FALSE | 1182 | BASF Corporation | 10319 | Geismar | LA | Ascension | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 35.7 | 0.98 | 33.7 | 37.7 | 18 | N |  |  | OP | X | 7 | 1985 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [20 empty] | Y | 12 | 2022 | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ; DFO NG NG NG
Vintage1998 | natural gas peaker | FALSE | 1182 | BASF Corporation | 10319 | Geismar | LA | Ascension | GEN2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 41.2 | 0.98 | 39.2 | 43.2 | 20 | N |  |  | OP | X | 11 | 1998 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: OG; DFO NG NG NG: NG |  |  |  | N | N |  | 12H | [20 empty] | Y | 12 | 2022 | Y | Y | N
Vintage2005 | natural gas steam turbine | FALSE | 1182 | BASF Corporation | 10319 | Geismar | LA | Ascension | GEN3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 7.2 | 0.98 | 7.2 | 7.2 | 0.7 | N |  |  | OP | X | 10 | 2005 |  |  | N | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ; DFO NG NG NG
Vintage2015 | hydro | TRUE | 6201 | Farmer's Irrigation District | 10323 | Copper Dam Plant | OR | Hood River | TURGO | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.6 | 1 | 1 | 2.6 | 0.5 | N |  |  | OP | X | 9 | 2015 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1987 | hydro | TRUE | 6201 | Farmer's Irrigation District | 10324 | Peters Drive Plant | OR | Hood River | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 1 | 0.3 | 1.2 | 0.3 | N |  |  | OP | X | 11 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 1H
Vintage1986 | hydro | TRUE | 6288 | Mink Creek Hydro Entity | 10325 | Mink Creek Hydro | ID | Franklin | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.1 | 1 | 2 | 0.6 | 0.2 | N |  |  | OP | X | 12 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 10M
Vintage1965 | natural gas steam turbine | FALSE | 12436 | Michigan State University | 10328 | T B Simon Power Plant | MI | Ingham | GEN1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 12.5 | 0.8 | 12.5 | 12.5 | 2.5 | N |  |  | OP | X | 12 | 1965 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ; DFO NG NG NG
Vintage1966 | natural gas steam turbine | FALSE | 12436 | Michigan State University | 10328 | T B Simon Power Plant | MI | Ingham | GEN2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 12.5 | 0.8 | 12.5 | 12.5 | 2.5 | N |  |  | OP | X | 9 | 1966 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ; DFO NG NG NG
Vintage1974 | natural gas steam turbine | FALSE | 12436 | Michigan State University | 10328 | T B Simon Power Plant | MI | Ingham | GEN3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 15 | 0.85 | 15 | 15 | 2.5 | N |  |  | OP | X | 12 | 1974 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ; DFO NG NG NG
Vintage1993 | natural gas steam turbine | FALSE | 12436 | Michigan State University | 10328 | T B Simon Power Plant | MI | Ingham | GEN4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 21 | 0.85 | 21 | 21 | 5 | N |  |  | OP | X | 8 | 1993 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | OVER | N | N |  |  | N | [18 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ; DFO NG NG NG
Vintage2006 | natural gas steam turbine | FALSE | 12436 | Michigan State University | 10328 | T B Simon Power Plant | MI | Ingham | GEN5 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 24 | 0.85 | 23.8 | 23.8 | 5 | N |  |  | OP | X | 5 | 2006 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | OVER |  |  |  |  | N | [18 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ; DFO NG NG NG
Vintage2006 | natural gas peaker | FALSE | 12436 | Michigan State University | 10328 | T B Simon Power Plant | MI | Ingham | GEN6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 14.3 | 0.85 | 12.6 | 14.3 | 9 | N |  |  | OP | X | 4 | 2006 |  |  | N | Commercial CHP | 5 | [11 empty] | N | N |  | 1H |  |  |  |  | N | [18 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1989 | municipal solid waste | FALSE | 49846 | Covanta Honolulu Resource Recovery | 10334 | H Power | HI | Honolulu | GEN1 | Municipal Solid Waste | ST |  | W | X | X |  |  | 63.7 | 0.85 | 58 | 58 | 5 | N |  |  | OP | X | 11 | 1989 |  |  | N | Commercial Non-CHP | 4 | X T T T: X; DFO BLQ BLQ BLQ: MSW; DFO NG NG NG: DFO |  |  |  |  | N |  | OVER | [23 empty] | N | N | N
Vintage2013 | municipal solid waste | FALSE | 49846 | Covanta Honolulu Resource Recovery | 10334 | H Power | HI | Honolulu | GEN2 | Municipal Solid Waste | ST |  | W | X | X |  |  | 33.6 | 0.85 | 28 | 28 | 5 | N |  |  | OP | X | 2 | 2013 |  |  | N | Commercial Non-CHP | 4 | X T T T: X; DFO BLQ BLQ BLQ: MSW; DFO NG NG NG: DFO |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage2020 | solar pv | FALSE | 49846 | Covanta Honolulu Resource Recovery | 10334 | H Power | HI | Honolulu | PV1 | Solar Photovoltaic | PV |  | W | X | X |  |  | 2.9 |  | 3.6 | 3.3 | 0.2 | N |  |  | OP | X | 6 | 2020 |  |  | N | Commercial Non-CHP | 4 | X T T T: X; DFO BLQ BLQ BLQ: SUN | [30 empty] | N
Vintage2002 | natural gas peaker | TRUE | 194 | Albuquerque City of | 10339 | Southside Water Reclamation Plant | NM | Bernalillo | GEN1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.2 | 0.8 | 2.1 | 2.2 | 0 | N |  |  | OP | X | 11 | 2002 |  |  | Y | IPP CHP | 3 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: OBG |  |  |  | N | N |  | 10M | [23 empty] | Y | N | N
Vintage2002 | natural gas peaker | TRUE | 194 | Albuquerque City of | 10339 | Southside Water Reclamation Plant | NM | Bernalillo | GEN2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.2 | 0.8 | 2.1 | 2.2 | 0 | N |  |  | OP | X | 11 | 2002 |  |  | Y | IPP CHP | 3 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: OBG |  |  |  | N | N |  | 10M | [23 empty] | Y | N | N
Vintage1987 | biomass | TRUE | 194 | Albuquerque City of | 10339 | Southside Water Reclamation Plant | NM | Bernalillo | GEN3 | Other Waste Biomass | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0 | N |  |  | OP | X | 2 | 1987 |  |  | Y | IPP CHP | 3 | X T T T: T; DFO BLQ BLQ BLQ: OBG; DFO NG NG NG: NG |  |  |  | N | N |  | 10M | [23 empty] | Y | N | N
Vintage1987 | biomass | TRUE | 194 | Albuquerque City of | 10339 | Southside Water Reclamation Plant | NM | Bernalillo | GEN4 | Other Waste Biomass | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0 | N |  |  | OP | X | 2 | 1987 |  |  | Y | IPP CHP | 3 | X T T T: T; DFO BLQ BLQ BLQ: OBG; DFO NG NG NG: NG |  |  |  | N | N |  | 10M | [23 empty] | Y | N
Vintage1987 | natural gas combined cycle | TRUE | 65130 | Tesoro Marketing & Refining Co. LLC (Martinez) | 10342 | Marathon Bay Area Cogen | CA | Contra Costa | TG1 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N | FOSTERW_7_N004 | TH_NP15_GEN-APND | 40 | 0.85 | 35 | 37 | 29 | N |  |  | OP | X | 2 | 1987 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1987 | natural gas combined cycle | TRUE | 65130 | Tesoro Marketing & Refining Co. LLC (Martinez) | 10342 | Marathon Bay Area Cogen | CA | Contra Costa | TG2 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N | FOSTERW_7_N004 | TH_NP15_GEN-APND | 40 | 0.85 | 35 | 37 | 29 | N |  |  | OP | X | 2 | 1987 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1987 | natural gas combined cycle | TRUE | 65130 | Tesoro Marketing & Refining Co. LLC (Martinez) | 10342 | Marathon Bay Area Cogen | CA | Contra Costa | TG3 | Natural Gas Fired Combined Cycle | CA | CC1 | W | N | X | FOSTERW_7_N004 | TH_np15_GEN-APND | 33.5 | 0.8 | 33.5 | 33.5 | 5 | N |  |  | OP | X | 2 | 1987 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1990 | hard coal | TRUE | 49889 | Mount Carmel Cogen Inc | 10343 | Foster Wheeler Mt Carmel Cogen | PA | Northumberland | TG1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 47.3 | 1 | 43 | 40 | 28 | N |  |  | OP | X | 1 | 1990 |  |  | Y | IPP CHP | 3 | T | WC | NG | PG |  |  |  | NG |  |  |  | N | N |  | OVER | Y |  |  |  | Y | [18 empty] | Y | Y | N
Vintage1987 | biomass | TRUE | 8641 | Hillman Power Co | 10346 | Hillman Power LLC | MI | Montmorency | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 22 | 0.85 | 17.7 | 18.1 | 8 | N |  |  | OP | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | X | WDS | TDF | NG |  |  |  | NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1989 | natural gas peaker | TRUE | 59879 | Greenleaf Energy LLC | 10349 | Greenleaf 2 Power Plant | CA | Sutter | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 49.5 | 0.89 | 49.5 | 49.5 | 42 | N |  |  | OP | X | 10 | 1989 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1992 | biomass | TRUE | 57432 | ReEnergy Livermore Falls | 10354 | ReEnergy Livermore Falls | ME | Androscoggin | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X | Maine | Maine | 39.6 | 0.9 | 38 | 38 | 18 | N |  |  | OP | X | 8 | 1992 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WDS; DFO NG NG NG: WDS |  |  |  | N | N |  | 12H |  |  | N |  | N | [18 empty] | N | N
Vintage1963 | natural gas steam turbine | FALSE | 55919 | Georgia-Pacific Consumer Oper. Green Bay LLC | 10360 | Consumer Operations LLC | WI | Brown | GEN6 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 18.7 | 0.85 | 18 | 18 | 2 | N |  |  | OP | X | 1 | 1963 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | N | [22 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ; DFO NG NG NG
Vintage1969 | natural gas steam turbine | FALSE | 55919 | Georgia-Pacific Consumer Oper. Green Bay LLC | 10360 | Consumer Operations LLC | WI | Brown | GEN7 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 28.9 | 0.85 | 23 | 23 | 3 | N |  |  | OP | X | 1 | 1969 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | N | [22 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ; DFO NG NG NG
Vintage1986 | natural gas peaker | FALSE | 7127 | Georgia-Pacific Consr Prods LP-Savannah | 10361 | Savannah River Mill | GA | Effingham | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 25.2 | 0.8 | 21.4 | 24.7 | 2 | N |  |  | SB | Y | 12 | 1986 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1986 | natural gas peaker | FALSE | 7127 | Georgia-Pacific Consr Prods LP-Savannah | 10361 | Savannah River Mill | GA | Effingham | GEN2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 25.2 | 0.8 | 21.4 | 24.7 | 2 | N |  |  | OS | X | 12 | 1986 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1988 | petroleum | FALSE | 7127 | Georgia-Pacific Consr Prods LP-Savannah | 10361 | Savannah River Mill | GA | Effingham | GEN3 | Petroleum Coke | ST |  | S | X | X |  |  | 45 | 0.8 | 41.9 | 42.3 | 2 | N |  |  | OP | X | 2 | 1988 |  |  | Y | Industrial CHP | 7 | T | PC | BIT | WDS |  |  |  | DFO |  |  |  | N | N |  | 12H | Y |  |  |  | Y | [18 empty] | Y | Y | N
Vintage1989 | petroleum | FALSE | 7127 | Georgia-Pacific Consr Prods LP-Savannah | 10361 | Savannah River Mill | GA | Effingham | GEN4 | Petroleum Coke | ST |  | S | X | X |  |  | 45 | 0.8 | 41.9 | 42.3 | 2 | N |  |  | OP | X | 9 | 1989 |  |  | Y | Industrial CHP | 7 | T | PC | BIT | WDS |  |  |  | DFO |  |  |  | N | N |  | 12H | Y |  |  |  | Y | [18 empty] | Y | Y | N
Vintage1979 | natural gas steam turbine | FALSE | 6589 | Georgia-Pacific Consumer Operations LLC | 10362 | Georgia-Pacific Muskogee LLC | OK | Muskogee | GEN1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 25 | 0.8 | 11.6 | 15.2 | 3 | N |  |  | OP | X | 6 | 1979 |  |  | Y | Industrial CHP | 7 | T | NG | SUB | BIT |  |  |  | NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1980 | natural gas steam turbine | FALSE | 6589 | Georgia-Pacific Consumer Operations LLC | 10362 | Georgia-Pacific Muskogee LLC | OK | Muskogee | GEN2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 44.5 | 0.8 | 21.6 | 22.4 | 5 | N |  |  | OP | X | 6 | 1980 |  |  | Y | Industrial CHP | 7 | T | NG | SUB | BIT |  |  |  | NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1982 | natural gas steam turbine | FALSE | 6589 | Georgia-Pacific Consumer Operations LLC | 10362 | Georgia-Pacific Muskogee LLC | OK | Muskogee | GEN3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 44.5 | 0.8 | 34.3 | 33.8 | 5 | N |  |  | OP | X | 11 | 1982 |  |  | Y | Industrial CHP | 7 | T | NG | SUB | BIT |  |  |  | NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1985 | biomass | TRUE | 59593 | NC Renewable Power - Lumberton LLC | 10382 | Lumberton | NC | Robeson | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 34.7 | 0.85 | 34.7 | 34.7 | 5 | N |  |  | OP | X | 12 | 1985 |  |  | Y | IPP CHP | 3 | X T T T: B; DFO BLQ BLQ BLQ: WDS; DFO NG NG NG: OBS; DFO NG NG NG: DFO |  |  |  | N | N |  | 12H |  |  |  |  | N | [18 empty] | Y | Y | N
Vintage2011 | biomass | TRUE | 57223 | Sycamore Energy LLC | 10387 | Sycamore Energy LLC | CA | San Diego | 1A | Landfill Gas | GT |  | S | X | X |  |  | 1.2 | 0.98 | 1.2 | 1.2 | 0.9 | N |  |  | OP | X | 5 | 2011 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: LFG |  |  |  |  | N |  | 1H | [23 empty] | N
Vintage2011 | biomass | TRUE | 57223 | Sycamore Energy LLC | 10387 | Sycamore Energy LLC | CA | San Diego | 2A | Landfill Gas | GT |  | S | X | X |  |  | 1.2 | 0.98 | 1.2 | 1.2 | 0.9 | N |  |  | OP | X | 5 | 2011 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: LFG |  |  |  |  | N |  | 1H | [23 empty] | N
Vintage2004 | biomass | TRUE | 57223 | Sycamore Energy LLC | 10387 | Sycamore Energy LLC | CA | San Diego | 3 | Landfill Gas | GT |  | S | X | X |  |  | 3 | 0.98 | 2.8 | 3 | 2.4 | N |  |  | OP | X | 4 | 2004 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: LFG; DFO NG NG NG: PG |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1939 | other | FALSE | 56165 | Cleveland Cliffs | 10397 | Indiana Harbor West | IN | Lake | GEN5 | Other Gases | ST |  | W | X | X |  |  | 12.5 | 0.8 | 3.1 | 4.9 | 2 | N |  |  | SB | Y | 10 | 1939 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: BFG; DFO NG NG NG: NG; DFO NG NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | N | N
Vintage1953 | other | FALSE | 56165 | Cleveland Cliffs | 10397 | Indiana Harbor West | IN | Lake | GEN6 | Other Gases | ST |  | W | X | X |  |  | 12.5 | 0.8 | 3.1 | 4.9 | 2 | N |  |  | SB | Y | 5 | 1953 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: BFG; DFO NG NG NG: NG; DFO NG NG NG: NG |  |  |  | N |  |  | 12H | [23 empty] | N | N
Vintage1959 | other | FALSE | 56165 | Cleveland Cliffs | 10397 | Indiana Harbor West | IN | Lake | GEN7 | Other Gases | ST |  | W | X | X |  |  | 32 | 0.85 | 16 | 16 | 3 | N |  |  | OP | X | 5 | 1959 |  |  | Y | Industrial CHP | 7 | X T T T: B; DFO BLQ BLQ BLQ: BFG; DFO NG NG NG: NG; DFO NG NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | N | N
Vintage1961 | other | FALSE | 56165 | Cleveland Cliffs | 10397 | Indiana Harbor West | IN | Lake | GEN8 | Other Gases | ST |  | W | X | X |  |  | 40 | 0.85 | 24 | 29 | 4 | N |  |  | OP | X | 6 | 1961 |  |  | Y | Industrial CHP | 7 | X T T T: B; DFO BLQ BLQ BLQ: BFG; DFO NG NG NG: NG; DFO NG NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | N | N
Vintage2002 | other | FALSE | 56165 | Cleveland Cliffs | 10397 | Indiana Harbor West | IN | Lake | GEN9 | Other Gases | ST |  | W | X | X |  |  | 55 | 0.95 | 28 | 29 | 2 | N |  |  | OP | X | 11 | 2002 |  |  | Y | Industrial CHP | 7 | X T T T: B; DFO BLQ BLQ BLQ: BFG; DFO NG NG NG: NG; DFO NG NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | N | N
Vintage1965 | other | FALSE | 9454 | ArcelorMittal Cleveland Inc | 10398 | Arcelormittal Cleveland Inc | OH | Cuyahoga | GEN3 | Other Gases | ST |  | S | X | X | ATSI |  | 10 | 1 | 10 | 10 | 3 | N |  |  | OP | X | 1 | 1965 |  |  | Y | Industrial CHP | 7 | X T T T: B; DFO BLQ BLQ BLQ: BFG; DFO NG NG NG: NG; DFO NG NG NG: NG |  |  |  | N | N |  | 12H |  | N | [21 empty] | Y | Y | N
Vintage1965 | other | FALSE | 9454 | ArcelorMittal Cleveland Inc | 10398 | Arcelormittal Cleveland Inc | OH | Cuyahoga | GEN5 | Other Gases | ST |  | S | X | X | ATSI |  | 10 | 1 | 8 | 9 | 3 | N |  |  | OP | X | 1 | 1965 |  |  | Y | Industrial CHP | 7 | B | BFG | NG | RFO |  |  |  | NG |  |  |  | N | N |  | 12H |  | N | [21 empty] | Y | Y | N
Vintage1950 | other | FALSE | 9454 | ArcelorMittal Cleveland Inc | 10398 | Arcelormittal Cleveland Inc | OH | Cuyahoga | GENA | Other Gases | ST |  | S | X | X | ATSI |  | 15 | 1 | 12 | 14 | 3 | N |  |  | OS | X | 1 | 1950 |  |  | Y | Industrial CHP | 7 | T | BFG | NG | RFO |  |  |  | NG |  |  |  | N | N |  | 12H |  | N | [21 empty] | Y | Y | N
Vintage1965 | other | FALSE | 9454 | ArcelorMittal Cleveland Inc | 10398 | Arcelormittal Cleveland Inc | OH | Cuyahoga | GENB | Other Gases | ST |  | S | X | X | ATSI |  | 10 | 1 | 8 | 9 | 3 | N |  |  | OP | X | 1 | 1965 |  |  | Y | Industrial CHP | 7 | T | BFG | NG | RFO |  |  |  | NG |  |  |  | N | N |  | 12H |  | N | [21 empty] | Y | Y | N
Vintage2010 | other | FALSE | 9454 | ArcelorMittal Cleveland Inc | 10398 | Arcelormittal Cleveland Inc | OH | Cuyahoga | GENC | Other Gases | ST |  | S | X | X | ATSI |  | 22 | 1 | 22 | 22 | 4 | N |  |  | OP | X | 2 | 2010 |  |  | Y | Industrial CHP | 7 | T | BFG | NG | RFO |  |  |  | NG |  |  |  | N | N |  | 12H |  | N | [21 empty] | Y | Y | N
Vintage1990 | natural gas combined cycle | TRUE | 10337 | KES Kingsburg LP | 10405 | Kingsburg Cogen | CA | Fresno | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | KINGSBUR_7_B1 | KINGSBUR_7_B1 | 23.1 | 0.9 | 22 | 23 | 18 | N |  |  | OP | X | 12 | 1990 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1990 | natural gas combined cycle | TRUE | 10337 | KES Kingsburg LP | 10405 | Kingsburg Cogen | CA | Fresno | GEN2 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 13.1 | 0.9 | 11.8 | 11.8 | 4 | N |  |  | OP | X | 12 | 1990 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage2013 | natural gas peaker | FALSE | 3692 | Clark University | 10408 | Clark University | MA | Worcester | GEN2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1 | N |  |  | OP | X | 1 | 2013 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage2016 | hydro | FALSE | 11936 | McBryde Sugar Co Ltd | 10412 | Kalaheo Hydro | HI | Kauai | KPH1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.9 | 2 | 2 | 0.2 | N |  |  | OP | X | 9 | 2016 |  |  | N | Industrial Non-CHP | 6 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1906 | hydro | FALSE | 11936 | McBryde Sugar Co Ltd | 10413 | Wainiha Hydro | HI | Kauai | WAIA | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 0.8 | 1.7 | 1.7 | 0.2 | N |  |  | OP | X | 1 | 1906 |  |  | N | Industrial Non-CHP | 6 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M | [23 empty] | N | N | N
Vintage1910 | hydro | FALSE | 11936 | McBryde Sugar Co Ltd | 10413 | Wainiha Hydro | HI | Kauai | WAIB | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 0.8 | 1.7 | 1.7 | 0.2 | N |  |  | OP | X | 1 | 1910 |  |  | N | Industrial Non-CHP | 6 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [5 empty] | 0 | 10M | [20 empty] | N |  |  | N | N | N
Vintage1953 | natural gas steam turbine | FALSE | 56600 | Ascend Performance Materials LLC | 10416 | Pensacola Florida Plant | FL | Escambia | GEN1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 5 | 1 | 5 | 5 | 1 | N |  |  | OP | X | 9 | 1953 |  |  | Y | Industrial CHP | 7 | T | NG | WO | OG | RFO |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1957 | natural gas steam turbine | FALSE | 56600 | Ascend Performance Materials LLC | 10416 | Pensacola Florida Plant | FL | Escambia | GEN2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 5 | 1 | 5 | 5 | 1 | N |  |  | OP | X | 1 | 1957 |  |  | Y | Industrial CHP | 7 | T | NG | WO | OG | RFO |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1958 | natural gas steam turbine | FALSE | 56600 | Ascend Performance Materials LLC | 10416 | Pensacola Florida Plant | FL | Escambia | GEN3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 6 | 1 | 6 | 6 | 1 | N |  |  | OP | X | 3 | 1958 |  |  | Y | Industrial CHP | 7 | T | NG | WO | OG | RFO |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1993 | natural gas peaker | FALSE | 56600 | Ascend Performance Materials LLC | 10416 | Pensacola Florida Plant | FL | Escambia | GEN4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 86 | 1 | 82 | 100 | 30 | N |  |  | OP | X | 8 | 1993 |  |  | Y | Industrial CHP | 7 | T | NG | OG | WO | RFO |  |  | NG |  |  |  | N | N |  | 12H | [20 empty] | Y | 11 | 2022 | N | N | N
Vintage1985 | natural gas steam turbine | FALSE | 39878 | Solutia Inc-Indian | 10417 | Indian Orchard Plant 1 | MA | Hampden | TG | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 5.7 | 0.8 | 3.2 | 4.1 | 1 | N |  |  | OP | X | 5 | 1985 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: PUR; DFO NG NG NG: NG |  |  |  | N | N |  | 12H |  |  |  |  | N | [18 empty] | N
Vintage1993 | natural gas steam turbine | FALSE | 56488 | Ascend Performance Materials | 10418 | Ascend Performance Materials Texas Inc. | TX | Brazoria | GEN1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 6 | 0.8 | 5.2 | 5.2 | 2.3 | N |  |  | OP | X | 6 | 1993 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | OVER |  |  |  | N |  | N | N | [16 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ; DFO NG NG NG
Vintage2000 | natural gas steam turbine | FALSE | 56488 | Ascend Performance Materials | 10418 | Ascend Performance Materials Texas Inc. | TX | Brazoria | GEN4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 46.1 | 0.8 | 42.5 | 42.5 | 8 | N |  |  | OP | X | 10 | 2000 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | OVER |  |  |  | N | [19 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ; DFO NG NG NG
Vintage1987 | hydro | TRUE | 5068 | Denver City & County of | 10421 | Dillon Hydro Plant | CO | Summit | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 0.95 | 1.8 | 1.8 | 0.8 | N |  |  | OP | X | 10 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1959 | hydro | TRUE | 5068 | Denver City & County of | 10422 | Williams Fork Hydro Plant | CO | Grand | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.95 | 3 | 3 | 0.5 | N |  |  | OP | X | 7 | 1959 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage2012 | hydro | TRUE | 5068 | Denver City & County of | 10422 | Williams Fork Hydro Plant | CO | Grand | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.95 | 0.5 | 0.5 | 0.5 | N |  |  | OP | X | 9 | 2012 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | N | [22 empty] | N
Vintage1988 | hydro | TRUE | 5068 | Denver City & County of | 10423 | North Fork Hydro Plant | CO | Park | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.5 | 0.9 | 5.5 | 5.5 | 0.8 | N |  |  | OA | X | 1 | 1988 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage2007 | hydro | TRUE | 5068 | Denver City & County of | 10424 | Gross Hydro Plant | CO | Jefferson | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7.8 | 0.9 | 7.8 | 7.8 | 0.7 | N |  |  | OP | X | 8 | 2007 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1967 | biomass | TRUE | 54745 | International Paper - Orange | 10425 | International Paper - Orange | TX | Orange | TG | Wood/Wood Waste Biomass | ST |  | W | X | X |  |  | 48 | 1 | 33.2 | 33.8 | 5 | N |  |  | OP | X | 11 | 1967 |  |  | Y | Industrial CHP | 7 | B | BLQ | NG | WDS | TDF |  |  | NG |  |  |  | N | N |  | 12H | N | N | N |  | N | N | N | [16 empty] | Y | N | N
Vintage1954 | biomass | TRUE | 23632 | Inland Paperboard - Rome Mill | 10426 | Inland Paperboard Packaging Rome | GA | Floyd | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 5 | 0.8 | 5 | 5 | 5 | N |  |  | OP | X | 10 | 1954 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | BIT | OTH |  |  | DFO | RFO | NG |  | N |  |  | 12H | Y | Y |  |  | Y | [18 empty] | N | N | N
Vintage1954 | biomass | TRUE | 23632 | Inland Paperboard - Rome Mill | 10426 | Inland Paperboard Packaging Rome | GA | Floyd | GEN3 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 5 | 0.8 | 5 | 5 | 5 | N |  |  | OP | X | 10 | 1954 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | BIT | OTH |  |  | DFO | RFO | NG |  | N |  |  | 12H | Y | Y |  |  | Y | [18 empty] | N | N | N
Vintage1961 | biomass | TRUE | 23632 | Inland Paperboard - Rome Mill | 10426 | Inland Paperboard Packaging Rome | GA | Floyd | GEN4 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 22 | 0.85 | 20 | 20 | 20 | N |  |  | OP | X | 4 | 1961 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | BIT | OTH |  |  | DFO | RFO | NG |  | N |  |  | 12H | Y | Y |  |  | Y | [18 empty] | N | N | N
Vintage1989 | biomass | TRUE | 23632 | Inland Paperboard - Rome Mill | 10426 | Inland Paperboard Packaging Rome | GA | Floyd | GEN5 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 38.4 | 0.85 | 31 | 30 | 30 | N |  |  | OP | X | 4 | 1989 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | BIT | OTH |  |  | DFO | RFO | NG |  | N |  |  | 12H | Y | Y |  |  | Y | [18 empty] | N | N | N
Vintage2019 | natural gas peaker | FALSE | 22091 | New-Indy Ontario LLC | 10427 | New-Indy Ontario Mill | CA | San Bernardino | GEN2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 16.5 | 1 | 14.7 | 14.8 | 8 | N |  |  | OP | X | 11 | 2019 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage2019 | natural gas peaker | FALSE | 22091 | New-Indy Ontario LLC | 10427 | New-Indy Ontario Mill | CA | San Bernardino | GEN3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 16.5 | 1 | 14.7 | 14.8 | 8 | N |  |  | OP | X | 11 | 2019 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1947 | natural gas steam turbine | FALSE | 623 | Anheuser-Busch Inc | 10430 | Anheuser-Busch St Louis | MO | St Louis City | GEN1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 11 | 0.98 | 11 | 11 | 2 | N |  |  | OP | X | 1 | 1947 |  |  | Y | Industrial CHP | 7 | X T T T: B; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: OBG; DFO NG NG NG: OBG | NG |  |  | N | N |  | 12H |  | N | [21 empty] | Y | Y | N
Vintage1948 | natural gas steam turbine | FALSE | 623 | Anheuser-Busch Inc | 10430 | Anheuser-Busch St Louis | MO | St Louis City | GEN3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 11 | 0.98 | 11 | 11 | 2 | N |  |  | OP | X | 1 | 1948 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: OBG; DFO NG NG NG: OBG | NG |  |  | N | N |  | 12H |  | N | [21 empty] | Y | Y | N
Vintage1939 | natural gas steam turbine | FALSE | 623 | Anheuser-Busch Inc | 10430 | Anheuser-Busch St Louis | MO | St Louis City | GEN4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 4.1 | 0.98 | 4.1 | 4.1 | 0.5 | N |  |  | OS | X | 1 | 1939 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: OBG; DFO NG NG NG: OBG | NG |  |  | N | N |  | 12H |  | N | [21 empty] | Y | Y | N
Vintage1987 | natural gas peaker | FALSE | 623 | Anheuser-Busch Inc | 10431 | Anheuser-Busch Jacksonville | FL | Duval | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 8.7 | 0.8 | 8.7 | 8.7 | 1 | N |  |  | OP | X | 11 | 1987 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1981 | other | FALSE | 9383 | Mosaic Fertilizer LLC | 10434 | Mosaic New Wales Operations | FL | Polk | TG1 | All Other | ST |  | S | X | X |  |  | 10 | 0.85 | 8 | 8 | 2 | N |  |  | OS | X | 8 | 1981 |  |  | Y | Industrial CHP | 7 | X T T T: B; DFO BLQ BLQ BLQ: WH; DFO NG NG NG: NG |  |  |  | N |  |  | OVER | [23 empty] | N | N
Vintage1984 | other | FALSE | 9383 | Mosaic Fertilizer LLC | 10434 | Mosaic New Wales Operations | FL | Polk | TG2 | All Other | ST |  | S | X | X |  |  | 58.5 | 0.85 | 48 | 48 | 2 | N |  |  | OP | X | 12 | 1984 |  |  | Y | Industrial CHP | 7 | X T T T: B; DFO BLQ BLQ BLQ: WH; DFO NG NG NG: NG |  |  |  | N |  |  | OVER | [23 empty] | N | N
Vintage1982 | other | FALSE | 9383 | Mosaic Fertilizer LLC | 10434 | Mosaic New Wales Operations | FL | Polk | TG3 | All Other | ST |  | S | X | X |  |  | 32 | 0.8 | 32 | 32 | 2 | N |  |  | OP | X | 12 | 1982 |  |  | Y | Industrial CHP | 7 | X T T T: B; DFO BLQ BLQ BLQ: WH; DFO NG NG NG: NG |  |  |  | N |  |  | OVER | [23 empty] | N | N
Vintage2014 | other | FALSE | 9383 | Mosaic Fertilizer LLC | 10434 | Mosaic New Wales Operations | FL | Polk | TG4 | All Other | ST |  | S | X | X |  |  | 35 | 0.85 | 24 | 24 | 3.5 | N |  |  | OP | X | 5 | 2014 |  |  | N | Industrial CHP | 7 | X T T T: X; DFO BLQ BLQ BLQ: WH; DFO NG NG NG: NG | [6 empty] | OVER | [23 empty] | N | N
Vintage1991 | municipal solid waste | TRUE | 49966 | Covanta Camden Energy Recovery Center | 10435 | Camden Resource Recovery Facility | NJ | Camden | TGA | Municipal Solid Waste | ST |  | S | X | X | CCRF | CCRF | 17.5 | 0.9 | 16.5 | 16.5 | 4 | N |  |  | OP | X | 3 | 1991 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: MSW; DFO NG NG NG: NG |  |  |  | N | N |  | OVER |  |  | N |  | N | [18 empty] | N | N | N
Vintage1991 | municipal solid waste | TRUE | 49966 | Covanta Camden Energy Recovery Center | 10435 | Camden Resource Recovery Facility | NJ | Camden | TGB | Municipal Solid Waste | ST |  | S | X | X | CCRF | CCRF | 17.5 | 0.9 | 16.5 | 16.5 | 4 | N |  |  | OP | X | 3 | 1991 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: MSW; DFO NG NG NG: NG |  |  |  | N | N |  | OVER |  |  | N |  | N | [18 empty] | N | N | N
Vintage1989 | natural gas peaker | FALSE | 6091 | Exxon Mobil Refining and Supply Co. | 10436 | ExxonMobil Baytown Refinery | TX | Harris | GT38 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | EXN_G8 | EXN_G8 | 45.7 | 0.85 | 31 | 35 | 18 | N |  |  | OP | X | 8 | 1989 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1977 | natural gas peaker | FALSE | 6091 | Exxon Mobil Refining and Supply Co. | 10436 | ExxonMobil Baytown Refinery | TX | Harris | GT41 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | EXN_G9 | EXN_G9 | 27.6 | 0.8 | 18 | 24 | 16 | N |  |  | OP | X | 1 | 1977 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1977 | natural gas peaker | FALSE | 6091 | Exxon Mobil Refining and Supply Co. | 10436 | ExxonMobil Baytown Refinery | TX | Harris | GT42 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | EXN_G10 | EXN_G10 | 27.6 | 0.8 | 18 | 24 | 16 | N |  |  | OP | X | 1 | 1977 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1977 | natural gas peaker | FALSE | 6091 | Exxon Mobil Refining and Supply Co. | 10436 | ExxonMobil Baytown Refinery | TX | Harris | GT43 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | EXN_G11 | EXN_G11 | 27.6 | 0.8 | 18 | 24 | 16 | N |  |  | OP | X | 1 | 1977 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1977 | natural gas peaker | FALSE | 6091 | Exxon Mobil Refining and Supply Co. | 10436 | ExxonMobil Baytown Refinery | TX | Harris | GT44 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | EXN_G12 | EXN_G12 | 27.6 | 0.8 | 18 | 24 | 16 | N |  |  | OP | X | 1 | 1977 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1988 | natural gas peaker | FALSE | 6091 | Exxon Mobil Refining and Supply Co. | 10436 | ExxonMobil Baytown Refinery | TX | Harris | GT45 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | EXN_G13 | EXN_G13 | 45.7 | 0.85 | 31 | 35 | 18 | N |  |  | OP | X | 6 | 1988 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1952 | other | FALSE | 6091 | Exxon Mobil Refining and Supply Co. | 10436 | ExxonMobil Baytown Refinery | TX | Harris | ST34 | All Other | ST |  | S | X | X | EXN_G15 | EXN_G15 | 7.5 | 0.85 | 7.5 | 7.5 | 0.5 | N |  |  | OP | X | 1 | 1952 |  |  | N | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ; DFO NG NG NG
Vintage2017 | solar pv | TRUE | 60246 | Sunray Energy 2, LLC | 10437 | Sunray 2 | CA | San Bernardino | SUN2 | Solar Photovoltaic | PV |  | W | X | X |  |  | 20 |  | 20 | 18.5 |  | N |  |  | OP | X | 6 | 2017 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: SUN |  |  |  | N | [26 empty] | N
Vintage2017 | solar pv | TRUE | 60247 | Sunray Energy 3 LLC | 10438 | Sunray 3 | CA | San Bernardino | SUN3 | Solar Photovoltaic | PV |  | W | X | X |  |  | 13.8 |  | 13.8 | 13 |  | N |  |  | OP | X | 6 | 2017 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: SUN | [30 empty] | N
Vintage1990 | solar thermal | TRUE | 61950 | Terra-Gen Operating Co-Solar | 10446 | SEGS IX | CA | San Bernardino | GEN1 | Solar Thermal without Energy Storage | ST |  | S | X | X |  |  | 92 | 0.85 | 88 | 64 | 7 | N |  |  | OP | X | 9 | 1990 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: SUN; DFO NG NG NG: NG; DFO NG NG NG: SUN |  |  |  | N | N | 0 | 1H | [20 empty] | N |  |  | N | N | N
Vintage1986 | hydro | TRUE | 58149 | Renewable World Energies LLC | 10453 | LAC Courte Oreilles Hydroelect | WI | Sawyer | U1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0 | N |  |  | OP | X | 12 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [5 empty] | 0 | 10M | [23 empty] | N
Vintage1986 | hydro | TRUE | 58149 | Renewable World Energies LLC | 10453 | LAC Courte Oreilles Hydroelect | WI | Sawyer | U2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.8 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 12 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [5 empty] | 0 | 10M | [23 empty] | N
Vintage1986 | hydro | TRUE | 58149 | Renewable World Energies LLC | 10453 | LAC Courte Oreilles Hydroelect | WI | Sawyer | U3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.8 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 12 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [5 empty] | 0 | 10M | [23 empty] | N
Vintage1988 | hydro | TRUE | 63235 | Brookfield Renewable Trading and Marketing LP | 10458 | Muck Valley Hydroelectric | CA | Lassen | GEN1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 29.9 | 1 | 29.9 | 29.9 | 1 | N |  |  | OP | X | 12 | 1988 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 1H
Vintage1989 | biomass | TRUE | 1746 | Black River Generation LLC | 10464 | ReEnergy Black River | NY | Jefferson | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 55.5 | 0.95 | 55 | 56 | 15 | N |  |  | OP | X | 6 | 1989 |  |  | N | IPP Non-CHP | 2 | X | WDS | TDF | DFO |  |  |  | DFO | JF |  |  | N | N |  | 12H | N |  |  |  | N | [18 empty] | Y | Y | N
Vintage1987 | hydro | TRUE | 55754 | Boralex Hydro Operations Inc | 10467 | Fourth Branch Hydroelectric Facility | NY | Saratoga | 1 | Conventional Hydroelectric | HY |  | W | X | X | F | F | 3.3 | 0.95 | 3.3 | 3.3 | 0.1 | N |  |  | OP | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1986 | biomass | TRUE | 11217 | Los Angeles County Sanitation | 10472 | Puente Hills Energy Recovery | CA | Los Angeles | GEN1 | Landfill Gas | ST |  | S | X | X |  |  | 50 | 0.9 | 45 | 45 | 13 | N |  |  | OP | X | 10 | 1986 |  |  | N | Commercial Non-CHP | 4 | X T T T: X; DFO BLQ BLQ BLQ: LFG; DFO NG NG NG: WO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1981 | other | FALSE | 56150 | ArcelorMittal USA Inc | 10475 | Expander Turbine | IN | Lake | 16TG | Other Gases | OT |  | S | X | X |  |  | 20 | 1 | 18.8 | 18.8 | 5 | N |  |  | OP | X | 5 | 1981 |  |  | N | Industrial Non-CHP | 6 | X T T T: X; DFO BLQ BLQ BLQ: BFG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1968 | biomass | TRUE | 55965 | Verso Corporation | 10477 | Wisconsin Rapids Pulp Mill | WI | Wood | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 32 | 0.85 | 27.2 | 32 | 27.2 | N |  |  | OS | X | 9 | 1968 |  |  | Y | Industrial CHP | 7 | T | BLQ | SUB | NG | WDS | OBL |  | NG |  |  |  | N |  |  | 12H | Y |  |  |  | Y | [18 empty] | Y | Y
Vintage1991 | biomass | TRUE | 55965 | Verso Corporation | 10477 | Wisconsin Rapids Pulp Mill | WI | Wood | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 40.3 | 0.85 | 37.5 | 40.3 | 37.5 | N |  |  | OS | X | 9 | 1991 |  |  | Y | Industrial CHP | 7 | T | BLQ | SUB | NG | WDS | OBL |  | NG |  |  |  | N |  |  | 12H | Y |  |  |  | Y | [18 empty] | Y | Y
Vintage1990 | geothermal | TRUE | 34691 | Ormat Nevada Inc | 10479 | Mammoth G3 | CA | Mono | T101 | Geothermal | BT |  | W | X | X |  |  | 5 | 0.8 | 3.3 | 5 | 3.3 | N |  |  | OP | X | 12 | 1990 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: GEO | [6 empty] | OVER | [23 empty] | N
Vintage1990 | geothermal | TRUE | 34691 | Ormat Nevada Inc | 10479 | Mammoth G3 | CA | Mono | T102 | Geothermal | BT |  | W | X | X |  |  | 5 | 0.8 | 3.3 | 5 | 3.3 | N |  |  | OP | X | 12 | 1990 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: GEO | [6 empty] | OVER | [23 empty] | N
Vintage1990 | geothermal | TRUE | 34691 | Ormat Nevada Inc | 10479 | Mammoth G3 | CA | Mono | T103 | Geothermal | BT |  | W | X | X |  |  | 5 | 0.8 | 3.3 | 5 | 3.3 | N |  |  | OP | X | 12 | 1990 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: GEO | [6 empty] | OVER | [23 empty] | N
Vintage1984 | geothermal | TRUE | 34691 | Ormat Nevada Inc | 10480 | Mammoth G1 | CA | Mono | GEN1 | Geothermal | BT |  | W | X | X |  |  | 5 | 0.8 | 3.3 | 5 | 3.3 | N |  |  | OP | X | 12 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: GEO |  |  |  | N |  |  | OVER | [23 empty] | N
Vintage1984 | geothermal | TRUE | 34691 | Ormat Nevada Inc | 10480 | Mammoth G1 | CA | Mono | GEN2 | Geothermal | BT |  | W | X | X |  |  | 5 | 0.8 | 3.3 | 5 | 3.3 | N |  |  | OP | X | 12 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: GEO |  |  |  | N |  |  | OVER | [23 empty] | N
Vintage1990 | geothermal | TRUE | 34691 | Ormat Nevada Inc | 10481 | Mammoth G2 | CA | Mono | 1 | Geothermal | BT |  | W | X | X |  |  | 5 | 0.8 | 3.3 | 5 | 3.3 | N |  |  | OP | X | 12 | 1990 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: GEO |  |  |  | N |  |  | OVER | [23 empty] | N
Vintage1990 | geothermal | TRUE | 34691 | Ormat Nevada Inc | 10481 | Mammoth G2 | CA | Mono | 2 | Geothermal | BT |  | W | X | X |  |  | 5 | 0.8 | 3.3 | 5 | 3.3 | N |  |  | OP | X | 12 | 1990 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: GEO |  |  |  | N |  |  | OVER | [23 empty] | N
Vintage1990 | geothermal | TRUE | 34691 | Ormat Nevada Inc | 10481 | Mammoth G2 | CA | Mono | 3 | Geothermal | BT |  | W | X | X |  |  | 5 | 0.8 | 3.3 | 5 | 3.3 | N |  |  | OP | X | 12 | 1990 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: GEO |  |  |  | N |  |  | OVER | [23 empty] | N
Vintage2015 | biomass | TRUE | 1991 | Boise White Paper LLC | 10486 | Boise Cascade International Falls | MN | Koochiching | GEN 6 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 52.3 | 0.8 | 40 | 40 | 1 | N |  |  | OP | X | 10 | 2015 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | SLW |  |  | NG |  |  |  | N | N |  | OVER |  |  |  |  | N | [18 empty] | Y | Y | N
Vintage1946 | hydro | FALSE | 1991 | Boise White Paper LLC | 10487 | International Falls Power | MN | Koochiching | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 0.8 | 2.2 | 2.2 | 0 | N |  |  | OP | X | 1 | 1946 |  |  | N | Industrial Non-CHP | 6 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 12H | [23 empty] | N
Vintage1946 | hydro | FALSE | 1991 | Boise White Paper LLC | 10487 | International Falls Power | MN | Koochiching | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 0.8 | 2.2 | 2.2 | 0 | N |  |  | OP | X | 1 | 1946 |  |  | N | Industrial Non-CHP | 6 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 12H | [23 empty] | N
Vintage1946 | hydro | FALSE | 1991 | Boise White Paper LLC | 10487 | International Falls Power | MN | Koochiching | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 0.8 | 2.2 | 2.2 | 0 | N |  |  | OP | X | 1 | 1946 |  |  | N | Industrial Non-CHP | 6 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 12H | [23 empty] | N
Vintage1946 | hydro | FALSE | 1991 | Boise White Paper LLC | 10487 | International Falls Power | MN | Koochiching | GEN4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 0.8 | 2.2 | 2.2 | 0 | N |  |  | OP | X | 1 | 1946 |  |  | N | Industrial Non-CHP | 6 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 12H | [23 empty] | N
Vintage1946 | hydro | FALSE | 1991 | Boise White Paper LLC | 10487 | International Falls Power | MN | Koochiching | GEN5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 0.8 | 2.2 | 2.2 | 0 | N |  |  | OP | X | 1 | 1946 |  |  | N | Industrial Non-CHP | 6 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 12H | [23 empty] | N
Vintage1924 | hydro | FALSE | 1991 | Boise White Paper LLC | 10487 | International Falls Power | MN | Koochiching | GEN6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0 | N |  |  | OP | X | 1 | 1924 |  |  | N | Industrial Non-CHP | 6 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 12H | [23 empty] | N
Vintage1924 | hydro | FALSE | 1991 | Boise White Paper LLC | 10487 | International Falls Power | MN | Koochiching | GEN7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0 | N |  |  | OP | X | 1 | 1924 |  |  | N | Industrial Non-CHP | 6 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 12H | [23 empty] | N
Vintage1969 | biomass | TRUE | 1924 | Packaging Corporation of America | 10488 | DeRidder Mill | LA | Beauregard | TG | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 61.5 | 0.95 | 61.5 | 61.5 | 16 | N |  |  | OP | X | 10 | 1969 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS |  |  |  | NG |  |  |  | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage1985 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 10490 | Upper Beaver Falls Project | NY | Lewis | 1G | Conventional Hydroelectric | HY |  | W | X | X | 23633 |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 1 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [6 empty] | 10M
Vintage1954 | natural gas steam turbine | FALSE | 61813 | ND Paper, Inc. | 10491 | Mead Rumford Cogen | ME | Oxford | 3STG | Natural Gas Steam Turbine | ST |  | S | X | X | NPCC/ISONewEngland/Catalyst345 | NPCC/ISONewEngland/Catalyst345 | 12.5 | 0.85 | 12.5 | 12.5 | 12.5 | N |  |  | OS | X | 10 | 1954 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: RFO; DFO NG NG NG: RFO |  |  |  | N | N |  | 12H |  |  |  |  | N | [18 empty] | Y | Y | Y
Vintage1918 | hydro | TRUE | 50083 | Brookfield Power New England | 10493 | Rumford Falls Hydro Facility | ME | Oxford | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8.1 | 0.9 | 8.1 | 8.1 | 4 | N |  |  | OP | X | 1 | 1918 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 1H | [23 empty] | N
Vintage1918 | hydro | TRUE | 50083 | Brookfield Power New England | 10493 | Rumford Falls Hydro Facility | ME | Oxford | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8.1 | 0.9 | 8.1 | 8.1 | 4 | N |  |  | OP | X | 1 | 1918 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [5 empty] | 0 | 1H | [23 empty] | N
Vintage1926 | hydro | TRUE | 50083 | Brookfield Power New England | 10493 | Rumford Falls Hydro Facility | ME | Oxford | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8.8 | 0.9 | 8.8 | 8.8 | 8 | N |  |  | OP | X | 1 | 1926 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [5 empty] | 0 | 1H | [23 empty] | N
Vintage1950 | hydro | TRUE | 50083 | Brookfield Power New England | 10493 | Rumford Falls Hydro Facility | ME | Oxford | GEN4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.3 | 0.9 | 4.3 | 4.3 | 2 | N |  |  | SB | N | 1 | 1950 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 1H | [23 empty] | N
Vintage1954 | hydro | TRUE | 50083 | Brookfield Power New England | 10493 | Rumford Falls Hydro Facility | ME | Oxford | GEN5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7.6 | 0.9 | 7.6 | 7.6 | 3.5 | N |  |  | OP | X | 10 | 1954 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1954 | hydro | TRUE | 50083 | Brookfield Power New England | 10493 | Rumford Falls Hydro Facility | ME | Oxford | GEN6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7.6 | 0.9 | 7.6 | 7.6 | 3.5 | N |  |  | OP | X | 10 | 1954 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 1H | [23 empty] | N
Vintage1988 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10494 | Sheldon Springs Hydroelectric | VT | Franklin | IG-1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 1 | 1.7 | 1.7 | 0.1 | N |  |  | OP | X | 7 | 1988 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [6 empty] | 10M
Vintage1988 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10494 | Sheldon Springs Hydroelectric | VT | Franklin | IG-2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 1 | 1.7 | 1.7 | 0.1 | N |  |  | OP | X | 7 | 1988 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [6 empty] | 10M
Vintage1988 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10494 | Sheldon Springs Hydroelectric | VT | Franklin | IG-3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 1 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 7 | 1988 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [6 empty] | 10M
Vintage1988 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10494 | Sheldon Springs Hydroelectric | VT | Franklin | SG-1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10.2 | 1 | 9.7 | 9.4 | 0.1 | N |  |  | OP | X | 7 | 1988 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [6 empty] | 10M
Vintage1988 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10494 | Sheldon Springs Hydroelectric | VT | Franklin | SG-2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10.2 | 1 | 9.7 | 9.4 | 1 | N |  |  | OP | X | 7 | 1988 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [6 empty] | 10M
Vintage1988 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10494 | Sheldon Springs Hydroelectric | VT | Franklin | SG-3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 1 | 1 | 0.9 | 1 | N |  |  | OP | X | 7 | 1988 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [6 empty] | 10M
Vintage1990 | biomass | TRUE | 61813 | ND Paper, Inc. | 10495 | Rumford Cogeneration | ME | Oxford | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X | NPCC/ISO New England/345 Catalyst 115 | NPCC/ISO New England/345 Catalyst 11 | 102.6 | 0.89 | 85 | 95 | 5 | N |  |  | OP | X | 1 | 1990 |  |  | Y | IPP CHP | 3 | T | BLQ | WDS | TDF | BIT | SLW |  | RFO |  |  |  | N | N |  | 12H | Y |  |  |  | Y | N | [17 empty] | Y | Y | N
Vintage1985 | natural gas peaker | TRUE | 10203 | Kern River Cogeneration Co | 10496 | Kern River Cogeneration | CA | Kern | GTAG | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 75 | 1 | 72 | 77 | 70 | N |  |  | OP | X | 7 | 1985 |  |  | Y | IPP CHP | 3 | [14 empty] | 1H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1985 | natural gas peaker | TRUE | 10203 | Kern River Cogeneration Co | 10496 | Kern River Cogeneration | CA | Kern | GTBG | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 75 | 1 | 72 | 77 | 70 | N |  |  | OP | X | 7 | 1985 |  |  | Y | IPP CHP | 3 | [14 empty] | 1H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1985 | natural gas peaker | TRUE | 10203 | Kern River Cogeneration Co | 10496 | Kern River Cogeneration | CA | Kern | GTCG | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 75 | 1 | 72 | 77 | 70 | N |  |  | OP | X | 7 | 1985 |  |  | Y | IPP CHP | 3 | [14 empty] | 1H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1985 | natural gas peaker | TRUE | 10203 | Kern River Cogeneration Co | 10496 | Kern River Cogeneration | CA | Kern | GTDG | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 75 | 1 | 72 | 77 | 70 | N |  |  | OP | X | 7 | 1985 |  |  | Y | IPP CHP | 3 | [14 empty] | 1H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1989 | natural gas peaker | TRUE | 12449 | Mid Set Cogeneration Co | 10501 | Mid-Set Cogeneration | CA | Kern | K100 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 39.1 | 1 | 36 | 34 | 36 | N |  |  | OS | X | 4 | 1989 |  |  | Y | IPP CHP | 3 | [14 empty] | 10M | [23 empty] | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1991 | municipal solid waste | TRUE | 20541 | Wheelabrator Environmental Systems | 10503 | Wheelabrator Hudson Falls | NY | Washington | GEN1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 14.4 | 0.9 | 11.5 | 11.5 | 2 | N |  |  | OP | X | 11 | 1991 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: MSW; DFO NG NG NG: NG | WO |  |  | N | N |  | 12H |  |  | N |  | N | [18 empty] | N | N | N
Vintage1948 | natural gas steam turbine | FALSE | 450 | The Amalgamated Sugar Co | 10504 | Amalgamated Sugar Twin Falls | ID | Twin Falls | 1500 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 1.5 | 0.8 | 1.2 | 1.2 | 0.2 | N |  |  | OP | X | 12 | 1948 |  |  | Y | Industrial CHP | 7 | T | NG | BIT | SUB |  |  |  | NG |  |  |  | N | N |  | 12H | N | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1948 | natural gas steam turbine | FALSE | 450 | The Amalgamated Sugar Co | 10504 | Amalgamated Sugar Twin Falls | ID | Twin Falls | 2500 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 2.5 | 0.8 | 2.3 | 2.3 | 0.2 | N |  |  | OP | X | 12 | 1948 |  |  | Y | Industrial CHP | 7 | T | NG | BIT | SUB |  |  |  | NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1994 | hard coal | FALSE | 450 | The Amalgamated Sugar Co | 10504 | Amalgamated Sugar Twin Falls | ID | Twin Falls | 4000 | Conventional Steam Coal | ST |  | S | X | X |  |  | 6.2 | 0.8 | 5 | 5 | 0.4 | N |  |  | OP | X | 9 | 1994 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: BIT; DFO NG NG NG: SUB; DFO NG NG NG: DFO |  |  |  | N | N |  | 12H | Y |  |  |  | Y | [18 empty] | N | N | N
Vintage1987 | biomass | TRUE | 56174 | Finch Paper LLC | 10511 | Finch Paper | NY | Warren | GEN6 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 29 | 0.9 | 23 | 27 | 3 | N |  |  | OP | X | 6 | 1987 |  |  | Y | Industrial CHP | 7 | T | WDL | NG | WDS |  |  |  | NG |  |  |  | N | N |  | OVER | [23 empty] | Y | N | N
Vintage1914 | hydro | TRUE | 16498 | SFR Hydro Cor | 10519 | Milton Hydro | NH | Strafford | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 0.9 | 0.1 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1914 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1914 | hydro | TRUE | 16498 | SFR Hydro Cor | 10519 | Milton Hydro | NH | Strafford | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.9 | 0.2 | 0.4 | 0.2 | N |  |  | OP | X | 1 | 1914 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1984 | hydro | TRUE | 16498 | SFR Hydro Cor | 10519 | Milton Hydro | NH | Strafford | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.9 | 0.1 | 0.3 | 0.1 | N |  |  | OP | X | 6 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1987 | hydro | TRUE | 16498 | SFR Hydro Cor | 10519 | Milton Hydro | NH | Strafford | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.9 | 0.3 | 0.5 | 0.2 | N |  |  | OP | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1925 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 10520 | Dayton Hydro | IL | LaSalle | 1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.6 | 1 | 1.6 | 1.6 | 0.5 | N |  |  | OP | X | 1 | 1925 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1925 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 10520 | Dayton Hydro | IL | LaSalle | 2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1 | 1 | 1 | 1 | 0.3 | N |  |  | OP | X | 1 | 1925 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1925 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 10520 | Dayton Hydro | IL | LaSalle | 3 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1 | 1 | 1 | 1 | 0.3 | N |  |  | OP | X | 1 | 1925 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1998 | natural gas combined cycle | FALSE | 60641 | Veolia NA - Municipal & Commercial Business | 10521 | Lederle Laboratories | NY | Rockland | 3A | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 1.5 | 1 | 1.5 | 1.5 | 0.1 | N |  |  | OP | X | 12 | 1998 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1991 | natural gas combined cycle | FALSE | 60641 | Veolia NA - Municipal & Commercial Business | 10521 | Lederle Laboratories | NY | Rockland | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 8.3 | 1 | 8.3 | 8.3 | 4.5 | N |  |  | OP | X | 1 | 1991 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1991 | natural gas combined cycle | FALSE | 60641 | Veolia NA - Municipal & Commercial Business | 10521 | Lederle Laboratories | NY | Rockland | GEN2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 8.3 | 1 | 8.3 | 8.3 | 4.5 | N |  |  | OP | X | 1 | 1991 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1990 | natural gas combined cycle | FALSE | 60641 | Veolia NA - Municipal & Commercial Business | 10521 | Lederle Laboratories | NY | Rockland | GEN3 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 2.2 | 1 | 2.2 | 2.2 | 0.1 | N |  |  | OP | X | 7 | 1990 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1997 | natural gas combined cycle | FALSE | 60641 | Veolia NA - Municipal & Commercial Business | 10521 | Lederle Laboratories | NY | Rockland | TG4 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 3.1 | 1 | 1.4 | 1.4 | 0.1 | N |  |  | OP | X | 7 | 1997 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1987 | hydro | TRUE | 55753 | Essex Hydro Associates LLC | 10523 | Benton Falls Associates | ME | Kennebec | GEN1 | Conventional Hydroelectric | HY |  | J | X | X |  |  | 3.5 | 0.9 | 3.3 | 3.2 | 0.3 | N |  |  | OP | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1987 | hydro | TRUE | 55753 | Essex Hydro Associates LLC | 10523 | Benton Falls Associates | ME | Kennebec | GEN2 | Conventional Hydroelectric | HY |  | J | X | X |  |  | 0.7 | 0.9 | 0.7 | 0.6 | 0.3 | N |  |  | OP | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1990 | biomass | TRUE | 3837 | CMS Generation Operating Co II | 10525 | Craven County Wood Energy LP | NC | Craven | 1UNI | Wood/Wood Waste Biomass | ST |  | J | X | X |  |  | 50 | 0.85 | 47 | 47 | 25 | N |  |  | OP | X | 11 | 1990 |  |  | N | IPP Non-CHP | 2 | X | WDS | OBS | WO |  |  |  | NG |  |  |  | N | N | 0 | 12H |  |  | N | [17 empty] | N |  |  | Y | Y | N
Vintage1990 | hydro | TRUE | 5226 | Dodge Falls Associates LP | 10526 | Dodge Falls Associates | NH | Grafton | 1UNI | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5 | 0.9 | 5 | 5 | 0.4 | N |  |  | OA | X | 12 | 1990 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1924 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 10530 | Feeder Dam Hydro Plant | NY | Saratoga | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24058 | 24058 | 1 | 0.8 | 0.9 | 1 | 0.5 | N |  |  | OP | X | 1 | 1924 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [6 empty] | 10M
Vintage1924 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 10530 | Feeder Dam Hydro Plant | NY | Saratoga | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24058 | 24058 | 1 | 0.8 | 0.9 | 1 | 0.5 | N |  |  | OP | X | 1 | 1924 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [6 empty] | 10M
Vintage1924 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 10530 | Feeder Dam Hydro Plant | NY | Saratoga | 3 | Conventional Hydroelectric | HY |  | S | X | X | 24058 | 24058 | 1 | 0.8 | 1 | 1 | 0.5 | N |  |  | OP | X | 1 | 1924 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [6 empty] | 10M
Vintage1924 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 10530 | Feeder Dam Hydro Plant | NY | Saratoga | 4 | Conventional Hydroelectric | HY |  | S | X | X | 24058 | 24058 | 1 | 0.8 | 0.9 | 1 | 0.5 | N |  |  | OP | X | 1 | 1924 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [6 empty] | 10M
Vintage1924 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 10530 | Feeder Dam Hydro Plant | NY | Saratoga | 5 | Conventional Hydroelectric | HY |  | S | X | X | 24058 | 24058 | 1 | 0.8 | 1 | 1 | 0.5 | N |  |  | OP | X | 1 | 1924 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [6 empty] | 10M
Vintage1931 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 10531 | Beebee Island Hydro Plant | NY | Jefferson | 1 | Conventional Hydroelectric | HY |  | S | X | X | 24047 | 24047 | 4 | 0.8 | 4.3 | 4.4 | 2.8 | N |  |  | OP | X | 1 | 1931 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 10M
Vintage1931 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 10531 | Beebee Island Hydro Plant | NY | Jefferson | 2 | Conventional Hydroelectric | HY |  | S | X | X | 24047 | 24047 | 5 | 0.8 | 4.3 | 4.4 | 2.4 | N |  |  | OP | X | 1 | 1931 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 10M
Vintage1991 | biomass | TRUE | 55858 | EDL Inc | 10532 | Grand River | MI | Clinton | 2-1 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 1 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 4 | 1991 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1991 | biomass | TRUE | 55858 | EDL Inc | 10532 | Grand River | MI | Clinton | 2-3 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 1 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 4 | 1991 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1996 | biomass | TRUE | 55858 | EDL Inc | 10532 | Grand River | MI | Clinton | 2-4 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 1 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 1 | 1996 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1997 | biomass | TRUE | 55858 | EDL Inc | 10532 | Grand River | MI | Clinton | 2-5 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 1 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 8 | 1997 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1931 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10538 | Dexter Plant | NY | Jefferson | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 1 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 1 | 1931 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [5 empty] | 0 | 1H
Vintage1931 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10538 | Dexter Plant | NY | Jefferson | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 1 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 1 | 1931 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [5 empty] | 0 | 1H
Vintage1958 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10538 | Dexter Plant | NY | Jefferson | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 1 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1958 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [5 empty] | 0 | 1H
Vintage1986 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10538 | Dexter Plant | NY | Jefferson | GEN4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 1 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 7 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [5 empty] | 0 | 1H
Vintage1986 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10538 | Dexter Plant | NY | Jefferson | GEN5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 1 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 7 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [5 empty] | 0 | 1H
Vintage1988 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10538 | Dexter Plant | NY | Jefferson | GEN6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 1 | 1.2 | 1.2 | 0.1 | N |  |  | OP | X | 7 | 1988 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [5 empty] | 0 | 1H
Vintage1988 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10538 | Dexter Plant | NY | Jefferson | GEN7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 1 | 1.2 | 1.2 | 0.1 | N |  |  | OP | X | 5 | 1988 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [5 empty] | 0 | 1H
Vintage1929 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10539 | Theresa Plant | NY | Jefferson | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 1 | 1 | 0.9 | 0.1 | N |  |  | OP | X | 1 | 1929 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [5 empty] | 0 | 1H
Vintage1927 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10539 | Theresa Plant | NY | Jefferson | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 1 | 1927 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [5 empty] | 0 | 1H
Vintage1914 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10540 | Diamond Island Plant | NY | Jefferson | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 1 | 0.4 | 0.4 | 0.1 | N |  |  | OA | X | 1 | 1914 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [6 empty] | 1H
Vintage1914 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10540 | Diamond Island Plant | NY | Jefferson | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 1 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 1 | 1914 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [6 empty] | 1H
Vintage1914 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10540 | Diamond Island Plant | NY | Jefferson | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 1 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 1 | 1914 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [6 empty] | 1H
Vintage1922 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10544 | Hailesboro 4 Plant | NY | St Lawrence | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 1 | 0.8 | 0.7 | 0.1 | N |  |  | OP | X | 1 | 1922 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [5 empty] | 0 | 1H
Vintage1922 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10544 | Hailesboro 4 Plant | NY | St Lawrence | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 1 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 1 | 1922 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [5 empty] | 0 | 1H
Vintage1984 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10545 | Copenhagen Plant | NY | Lewis | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 1 | 1.4 | 1.4 | 0.1 | N |  |  | OP | X | 6 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [5 empty] | 0 | 1H
Vintage1984 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10545 | Copenhagen Plant | NY | Lewis | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 1 | 1.4 | 1.4 | 0.1 | N |  |  | OP | X | 6 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [5 empty] | 0 | 1H
Vintage1984 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10545 | Copenhagen Plant | NY | Lewis | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 8 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [5 empty] | 0 | 1H
Vintage1982 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10546 | Beaver Valley Patterson Dam | PA | Beaver | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 1 | 0.4 | 0.4 | 0.1 | N |  |  | OS | X | 9 | 1982 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [5 empty] | 0 | 1H
Vintage1982 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10546 | Beaver Valley Patterson Dam | PA | Beaver | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 1 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 9 | 1982 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [5 empty] | 0 | 1H
Vintage1982 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10546 | Beaver Valley Patterson Dam | PA | Beaver | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 1 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 9 | 1982 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [5 empty] | 0 | 1H
Vintage1949 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10547 | Pyrites Plant | NY | St Lawrence | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 1 | 1.1 | 1.1 | 0.1 | N |  |  | OP | X | 1 | 1949 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [5 empty] | 0 | 1H
Vintage1985 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10547 | Pyrites Plant | NY | St Lawrence | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.5 | 1 | 3.3 | 3.2 | 0.1 | N |  |  | OP | X | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [5 empty] | 0 | 1H
Vintage1985 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10547 | Pyrites Plant | NY | St Lawrence | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.5 | 1 | 3.3 | 3.2 | 0.1 | N |  |  | OP | X | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [5 empty] | 0 | 1H
Vintage1984 | natural gas peaker | FALSE | 16732 | San Jose State University Fclts Dev &Ops | 10548 | San Jose Cogeneration | CA | Santa Clara | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 6 | 0.9 | 5.6 | 5.6 | 0 | N |  |  | OP | X | 12 | 1984 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [20 empty] | Y | 11 | 2022 | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage2011 | biomass | TRUE | 463 | Ameresco LFG I Inc | 10549 | Al Turi | NY | Orange | 2 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.4 | N |  |  | OS | X | 7 | 2011 | 1 | 2022 | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: LFG |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2011 | biomass | TRUE | 463 | Ameresco LFG I Inc | 10549 | Al Turi | NY | Orange | 3 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.4 | N |  |  | OS | X | 7 | 2011 | 1 | 2022 | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: LFG |  |  |  | N |  |  | 10M | [23 empty] | N | N | N
Vintage1998 | biomass | TRUE | 463 | Ameresco LFG I Inc | 10549 | Al Turi | NY | Orange | 3010 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.4 | N |  |  | OS | X | 11 | 1998 | 1 | 2022 | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: LFG |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1934 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10550 | High Shoals Hydro (NC) | NC | Lincoln | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 1 | 1.8 | 1.8 | 0.1 | N |  |  | OP | X | 7 | 1934 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT | [5 empty] | 0 | 10M
Vintage1987 | natural gas combined cycle | FALSE | 6541 | Formosa Plastics Corp | 10554 | Formosa Utility Venture Ltd | TX | Calhoun | BO3 | Natural Gas Fired Combined Cycle | CT | CHP1 | S | X | N |  |  | 36.2 | 0.85 | 32 | 32 | 20 | N |  |  | OP | X | 3 | 1987 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ; DFO NG NG NG
Vintage1994 | natural gas combined cycle | FALSE | 6541 | Formosa Plastics Corp | 10554 | Formosa Utility Venture Ltd | TX | Calhoun | ST1 | Natural Gas Fired Combined Cycle | CA | CHP1 | S | Y | X |  |  | 33.5 | 0.85 | 28.5 | 28.5 | 14 | N |  |  | OP | X | 3 | 1994 |  |  | Y | Industrial CHP | 7 | X T T T: B; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: OG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1994 | natural gas combined cycle | FALSE | 6541 | Formosa Plastics Corp | 10554 | Formosa Utility Venture Ltd | TX | Calhoun | ST2 | Natural Gas Fired Combined Cycle | CA | CHP1 | S | Y | X |  |  | 66.3 | 0.85 | 57.5 | 57.5 | 10 | N |  |  | OP | X | 3 | 1994 |  |  | Y | Industrial CHP | 7 | X T T T: B; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: OG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage2002 | natural gas combined cycle | FALSE | 6541 | Formosa Plastics Corp | 10554 | Formosa Utility Venture Ltd | TX | Calhoun | ST3 | Natural Gas Fired Combined Cycle | CA | CHP1 | S | Y | X |  |  | 55 | 0.85 | 47.3 | 51.7 | 14 | N |  |  | OP | X | 8 | 2002 |  |  | Y | Industrial CHP | 7 | X T T T: B; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: OG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1993 | natural gas combined cycle | FALSE | 6541 | Formosa Plastics Corp | 10554 | Formosa Utility Venture Ltd | TX | Calhoun | TBG1 | Natural Gas Fired Combined Cycle | CT | CHP1 | S | X | N |  |  | 82.5 | 0.85 | 72 | 90 | 60 | N |  |  | OP | X | 4 | 1993 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: OG; DFO NG NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1993 | natural gas combined cycle | FALSE | 6541 | Formosa Plastics Corp | 10554 | Formosa Utility Venture Ltd | TX | Calhoun | TBG2 | Natural Gas Fired Combined Cycle | CT | CHP1 | S | X | N |  |  | 82.5 | 0.85 | 72 | 90 | 60 | N |  |  | OP | X | 7 | 1993 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: OG; DFO NG NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1993 | natural gas combined cycle | FALSE | 6541 | Formosa Plastics Corp | 10554 | Formosa Utility Venture Ltd | TX | Calhoun | TBG3 | Natural Gas Fired Combined Cycle | CT | CHP1 | S | X | N |  |  | 82.5 | 0.85 | 72 | 90 | 60 | N |  |  | OP | X | 9 | 1993 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: OG; DFO NG NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1994 | natural gas combined cycle | FALSE | 6541 | Formosa Plastics Corp | 10554 | Formosa Utility Venture Ltd | TX | Calhoun | TBG4 | Natural Gas Fired Combined Cycle | CT | CHP1 | S | X | N |  |  | 82.5 | 0.85 | 72 | 90 | 63 | N |  |  | OP | X | 5 | 1994 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: OG; DFO NG NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1994 | natural gas combined cycle | FALSE | 6541 | Formosa Plastics Corp | 10554 | Formosa Utility Venture Ltd | TX | Calhoun | TBG5 | Natural Gas Fired Combined Cycle | CT | CHP1 | S | X | N |  |  | 82.5 | 0.85 | 72 | 90 | 63 | N |  |  | OP | X | 10 | 1994 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: OG; DFO NG NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage2003 | natural gas combined cycle | FALSE | 6541 | Formosa Plastics Corp | 10554 | Formosa Utility Venture Ltd | TX | Calhoun | TBG6 | Natural Gas Fired Combined Cycle | CT | CHP1 | S | X | N |  |  | 85.9 | 0.85 | 72 | 90 | 60 | N |  |  | OP | X | 6 | 2003 |  |  | Y | Industrial CHP | 7 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ; DFO NG NG NG
Vintage1989 | hydro | TRUE | 2179 | Brassua Hydroelectric LP | 10555 | Brassua Hydroelectric Project | ME | Somerset | 1 | Conventional Hydroelectric | HY |  | J | X | X |  |  | 3.6 | 0.9 | 3.6 | 3.6 | 0.2 | N |  |  | OP | X | 9 | 1989 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1985 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10556 | Boott Hydropower | MA | Middlesex | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7.5 | 1 | 7.1 | 6.9 | 0.1 | N |  |  | OP | X | 10 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1985 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10556 | Boott Hydropower | MA | Middlesex | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7.5 | 1 | 7.1 | 6.9 | 0.1 | N |  |  | OP | X | 10 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1985 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10556 | Boott Hydropower | MA | Middlesex | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7.9 | 1 | 7.5 | 7.3 | 0.1 | N |  |  | OP | X | 10 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1954 | biomass | TRUE | 15726 | Rayonier Advanced Materials | 10560 | Jesup Plant | GA | Wayne | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 5 | 0.8 | 4.7 | 4.7 | 2.5 | N |  |  | OP | X | 6 | 1954 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | RFO | DFO |  | RFO | DFO | NG | BLQ | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1957 | biomass | TRUE | 15726 | Rayonier Advanced Materials | 10560 | Jesup Plant | GA | Wayne | GEN4 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 7.5 | 0.8 | 7 | 7.1 | 3 | N |  |  | OP | X | 6 | 1957 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | RFO | DFO |  | RFO | DFO | NG | BLQ | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1971 | biomass | TRUE | 15726 | Rayonier Advanced Materials | 10560 | Jesup Plant | GA | Wayne | GEN5 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 30 | 0.85 | 27.9 | 28.2 | 8 | N |  |  | OP | X | 6 | 1971 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | RFO | DFO |  | RFO | DFO | NG | BLQ | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1982 | biomass | TRUE | 15726 | Rayonier Advanced Materials | 10560 | Jesup Plant | GA | Wayne | GEN6 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 27 | 0.85 | 25.1 | 25.4 | 8 | N |  |  | OP | X | 6 | 1982 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: BLQ; DFO NG NG NG: RFO; DFO NG NG NG: RFO | DFO | BLQ |  | N |  |  | 12H | [23 empty] | Y | Y | N
Vintage1950 | biomass | TRUE | 15726 | Rayonier Advanced Materials | 10562 | Fernandina Plant | FL | Nassau | GEN4 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 20 | 0.85 | 21 | 21 | 6 | N |  |  | OP | X | 9 | 1950 |  |  | Y | Industrial CHP | 7 | T | WDL | WDS | OBS | TDF | OTH |  | DFO | RFO | NG | WDL | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage2012 | biomass | TRUE | 15726 | Rayonier Advanced Materials | 10562 | Fernandina Plant | FL | Nassau | GEN5 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 22 | 0.85 | 21 | 21 | 3.5 | N |  |  | OP | X | 10 | 2012 |  |  | Y | Industrial CHP | 7 | T | WDL | WDS | OBS | TDF | OTH |  | DFO | RFO | NG | WDS | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1994 | hard coal | TRUE | 14932 | US Operating Services Company | 10566 | Chambers Cogeneration LP | NJ | Salem | GEN1 | Conventional Steam Coal | ST |  | W | X | X | CHAMBERS23KV CCLPGEN | Chambers CCLPGEN 23 KV bus | 285 | 0.85 | 244 | 242 | 46 | N |  |  | OP | X | 3 | 1994 | 3 | 2024 | Y | IPP CHP | 3 | X T T T: T; DFO BLQ BLQ BLQ: BIT; DFO NG NG NG: DFO; DFO NG NG NG: DFO |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1990 | natural gas combined cycle | TRUE | 291 | Algonquin Windsor Locks LLC | 10567 | Algonquin Windsor Locks | CT | Hartford | GTG | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | 392 | 392 | 40 | 0.85 | 35 | 45 | 15 | N |  |  | OP | X | 1 | 1990 |  |  | Y | IPP CHP | 3 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage2012 | natural gas combined cycle | TRUE | 291 | Algonquin Windsor Locks LLC | 10567 | Algonquin Windsor Locks | CT | Hartford | GTG2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | 392 | 392 | 15 | 0.85 | 13 | 15 | 9 | N |  |  | OP | X | 7 | 2012 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1990 | natural gas combined cycle | TRUE | 291 | Algonquin Windsor Locks LLC | 10567 | Algonquin Windsor Locks | CT | Hartford | STG | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X | 392 | 392 | 16 | 0.85 | 16 | 16 | 1 | N |  |  | OP | X | 1 | 1990 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to DFO BLQ BLQ BLQ
Vintage1988 | natural gas peaker | FALSE | 914 | Total Petrochemicals USA Inc | 10568 | Port Arthur Texas Refinery | TX | Jefferson | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 38.4 | 0.9 | 27.9 | 41.5 | 20 | N |  |  | OP | X | 8 | 1988 |  |  | Y | Industrial CHP | 7 | X T T T: T; DFO BLQ BLQ BLQ: NG; DFO NG NG NG: OG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1986 | hydro | TRUE | 23037 | Errol Hydroelectric Co LLC | 10570 | Errol Hydroelectric Project | NH | Coos | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.9 | 3 | 3 | 1 | N |  |  | OP | X | 11 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 1H | [23 empty] | N
Vintage1984 | onshore wind | TRUE | 2770 | Terra-Gen Operating Co-Wind | 10586 | Cameron Ridge LLC | CA | Kern | EXIS | Onshore Wind Turbine | WT |  | W | X | X |  |  | 59.6 |  | 59.6 | 59.6 | 0 | N |  |  | OP | X | 12 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WND |  |  |  | N | N | 114
Vintage1984 | biomass | TRUE | 135 | Agrilectric Power Partners Ltd | 10593 | Agrilectric Power Partners Ltd | LA | Calcasieu | GEN1 | Other Waste Biomass | ST |  | S | X | X | Rice1 | Rice1 | 12.1 | 0.85 | 11.1 | 11.1 | 3 | N |  |  | OP | X | 7 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: AB; DFO NG NG NG: NG |  |  |  | N | N |  | 12H |  |  |  | N | [19 empty] | N | N | N
Vintage1984 | onshore wind | TRUE | 2770 | Terra-Gen Operating Co-Wind | 10597 | Ridgetop Energy LLC | CA | Kern | WGN1 | Onshore Wind Turbine | WT |  | W | X | X |  |  | 29 |  | 29 | 29 | 0 | N |  |  | OP | X | 1 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WND |  |  |  | N | N | 239
Vintage1982 | other | FALSE | 2674 | Tesoro Refining & Marketing Company LLC | 10601 | Tesoro Wilmington Calciner | CA | Los Angeles | GEN1 | All Other | ST |  | S | X | X |  |  | 34 | 0.95 | 30.7 | 30.7 | 5 | N |  |  | OP | X | 12 | 1982 |  |  | Y | Industrial CHP | 7 | X T T T: B; DFO BLQ BLQ BLQ: WH; DFO NG NG NG: NG |  |  |  | N | N |  | OVER |  |  |  | N | N | [18 empty] | N | N | N
Vintage1990 | hard coal | TRUE | 5670 | Ebensburg Power Co | 10603 | Ebensburg Power | PA | Cambria | GEN1 | Conventional Steam Coal | ST |  | J | X | X | CSLOPE | CSLOPE | 57.6 | 0.9 | 50 | 50 | 15 | N |  |  | OP | X | 11 | 1990 |  |  | N | IPP Non-CHP | 2 | X T T T: X; DFO BLQ BLQ BLQ: WC; DFO NG NG NG: NG |  |  |  | N | N |  | 12H | Y |  |  |  | Y | [18 empty] | N | N
Vintage1954 | biomass | TRUE | 50003 | Brunswick Cellulose LLC | 10605 | Brunswick Cellulose | GA | Glynn | GEN3 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 9.2 | 1 | 9.2 | 9.2 | 0.1 | N |  |  | OP | X | 6 | 1954 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | RFO | TDF | DFO | NG | RFO | DFO |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1960 | biomass | TRUE | 50003 | Brunswick Cellulose LLC | 10605 | Brunswick Cellulose | GA | Glynn | GEN4 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 50 | 0.98 | 50 | 50 | 0.1 | N |  |  | OP | X | 8 | 1960 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | RFO | TDF | DFO | NG | RFO | DFO |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1996 | biomass | TRUE | 50003 | Brunswick Cellulose LLC | 10605 | Brunswick Cellulose | GA | Glynn | GEN5 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 13 | 0.85 | 13 | 13 | 0.1 | N |  |  | OP | X | 10 | 1996 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | RFO | TDF | DFO | NG | RFO | DFO |  | N | N |  | 12H | N | [5 empty] | N | [16 empty] | Y | Y | Y
Vintage1962 | natural gas steam turbine | FALSE | 4580 | Georgia-Pacific Crossett LLC | 10606 | Georgia-Pacific Crossett LLC | AR | Ashley | GEN4 | Natural Gas Steam Turbine | ST |  | S | X | X | EAI.EAILD | EAI.EAILD | 25 | 0.85 | 28 | 28 | 2 | N |  |  | OP | X | 5 | 1962 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N | 0 | 12H |  | N | [21 empty] | N | N | N | bar: X T T T to WC BLQ BLQ BLQ; NG NG NG NG
Vintage1986 | hydro | TRUE | 56467 | Ampersand Gilman Hydro LP | 10608 | Gilman Mill | VT | Essex | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 0.8 | 2.1 | 2.1 | 0.2 | N |  |  | OP | X | 3 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WC BLQ BLQ BLQ: WAT |  | N | N | 0 | 1H
Vintage1966 | hydro | TRUE | 56467 | Ampersand Gilman Hydro LP | 10608 | Gilman Mill | VT | Essex | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.8 | 0.9 | 0.9 | 0.3 | N |  |  | OP | X | 1 | 1966 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WC BLQ BLQ BLQ: WAT |  | N | N | 0 | 1H
Vintage1941 | hydro | TRUE | 56467 | Ampersand Gilman Hydro LP | 10608 | Gilman Mill | VT | Essex | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 1 | 1941 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WC BLQ BLQ BLQ: WAT |  | N | N | 0 | 1H
Vintage1941 | hydro | TRUE | 56467 | Ampersand Gilman Hydro LP | 10608 | Gilman Mill | VT | Essex | GEN4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 1 | 1941 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WC BLQ BLQ BLQ: WAT |  | N | N | 0 | 1H
Vintage1968 | natural gas steam turbine | FALSE | 7166 | Georgia-Pacific Monticello LLC | 10610 | Georgia-Pacific Monticello Paper | MS | Lawrence | GEN1 | Natural Gas Steam Turbine | ST |  | S | X | X | SME.SME_LOAD |  | 49.3 | 0.85 | 49.3 | 49.3 | 5 | N |  |  | OP | X | 6 | 1968 |  |  | Y | Industrial CHP | 7 | X T T T: T; WC BLQ BLQ BLQ: NG; WC NG NG NG: BLQ; WC WDS WDS WDS: WDS; NG NG NG NG: NG |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1968 | natural gas steam turbine | FALSE | 7166 | Georgia-Pacific Monticello LLC | 10610 | Georgia-Pacific Monticello Paper | MS | Lawrence | GEN2 | Natural Gas Steam Turbine | ST |  | S | X | X | SME.SME_LOAD |  | 32.2 | 0.89 | 32.2 | 32.2 | 5 | N |  |  | OP | X | 6 | 1968 |  |  | Y | Industrial CHP | 7 | X T T T: T; WC BLQ BLQ BLQ: NG; WC NG NG NG: BLQ; WC WDS WDS WDS: WDS; NG NG NG NG: NG |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1965 | biomass | TRUE | 50128 | Georgia-Pacific Consr Ops LLC-Palatka | 10611 | Georgia-Pacific Palatka Operations | FL | Putnam | GEN4 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 47.8 | 0.99 | 44.6 | 45.1 | 5 | N |  |  | OP | X | 6 | 1965 |  |  | Y | Industrial CHP | 7 | X T T T: T; WC BLQ BLQ BLQ: BLQ; WC NG NG NG: NG; NG NG NG NG: NG |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1993 | biomass | TRUE | 50128 | Georgia-Pacific Consr Ops LLC-Palatka | 10611 | Georgia-Pacific Palatka Operations | FL | Putnam | GEN8 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 32 | 0.85 | 25.1 | 25.4 | 3 | N |  |  | OP | X | 5 | 1993 |  |  | Y | Industrial CHP | 7 | X T T T: T; WC BLQ BLQ BLQ: BLQ; WC NG NG NG: NG; NG NG NG NG: NG |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1912 | hydro | FALSE | 5232 | Woodland Pulp LLC | 10613 | Woodland Pulp, LLC | ME | Washington | HG1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.8 | 2.9 | 2.8 | 1.5 | N |  |  | OP | X | 6 | 1912 |  |  | N | Industrial CHP | 7 | X T T T: X; WC BLQ BLQ BLQ: WAT |  | N |  | 0 | 10M | [23 empty] | N
Vintage1970 | hydro | FALSE | 5232 | Woodland Pulp LLC | 10613 | Woodland Pulp, LLC | ME | Washington | HG10 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.8 | 1.1 | 1.1 | 0.7 | N |  |  | SB | Y | 6 | 1970 |  |  | N | Industrial CHP | 7 | X T T T: X; WC BLQ BLQ BLQ: WAT |  | N |  | 0 | 10M | [23 empty] | N
Vintage1912 | hydro | FALSE | 5232 | Woodland Pulp LLC | 10613 | Woodland Pulp, LLC | ME | Washington | HG2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.8 | 2.9 | 2.8 | 0.7 | N |  |  | SB | Y | 6 | 1912 |  |  | N | Industrial CHP | 7 | X T T T: X; WC BLQ BLQ BLQ: WAT |  | N |  | 0 | 10M | [23 empty] | N
Vintage1929 | hydro | FALSE | 5232 | Woodland Pulp LLC | 10613 | Woodland Pulp, LLC | ME | Washington | HG3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.3 | 0.8 | 3.1 | 3 | 1.5 | N |  |  | OP | X | 6 | 1929 |  |  | N | Industrial CHP | 7 | X T T T: X; WC BLQ BLQ BLQ: WAT |  | N |  | 0 | 10M
Vintage1906 | hydro | FALSE | 5232 | Woodland Pulp LLC | 10613 | Woodland Pulp, LLC | ME | Washington | HG4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.7 | 0.7 | N |  |  | SB | Y | 6 | 1906 |  |  | N | Industrial CHP | 7 | X T T T: X; WC BLQ BLQ BLQ: WAT |  | N |  | 0 | 10M
Vintage1906 | hydro | FALSE | 5232 | Woodland Pulp LLC | 10613 | Woodland Pulp, LLC | ME | Washington | HG5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.7 | 0.7 | N |  |  | SB | Y | 6 | 1906 |  |  | N | Industrial CHP | 7 | X T T T: X; WC BLQ BLQ BLQ: WAT |  | N |  | 0 | 10M
Vintage1906 | hydro | FALSE | 5232 | Woodland Pulp LLC | 10613 | Woodland Pulp, LLC | ME | Washington | HG6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.7 | 0.7 | N |  |  | SB | Y | 6 | 1906 |  |  | N | Industrial CHP | 7 | X T T T: X; WC BLQ BLQ BLQ: WAT |  | N |  | 0 | 10M
Vintage1970 | hydro | FALSE | 5232 | Woodland Pulp LLC | 10613 | Woodland Pulp, LLC | ME | Washington | HG7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.8 | 1.5 | 1.5 | 0.7 | N |  |  | OP | X | 6 | 1970 |  |  | N | Industrial CHP | 7 | X T T T: X; WC BLQ BLQ BLQ: WAT |  | N |  | 0 | 10M
Vintage1970 | hydro | FALSE | 5232 | Woodland Pulp LLC | 10613 | Woodland Pulp, LLC | ME | Washington | HG8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.8 | 1.9 | 1.8 | 0.7 | N |  |  | OP | X | 6 | 1970 |  |  | N | Industrial CHP | 7 | X T T T: X; WC BLQ BLQ BLQ: WAT |  | N |  | 0 | 10M
Vintage1970 | hydro | FALSE | 5232 | Woodland Pulp LLC | 10613 | Woodland Pulp, LLC | ME | Washington | HG9 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.8 | 1.9 | 1.8 | 0.7 | N |  |  | OP | X | 6 | 1970 |  |  | N | Industrial CHP | 7 | X T T T: X; WC BLQ BLQ BLQ: WAT |  | N |  | 0 | 10M | [23 empty] | N
Vintage1966 | biomass | TRUE | 5232 | Woodland Pulp LLC | 10613 | Woodland Pulp, LLC | ME | Washington | TG10 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 23 | 0.8 | 26 | 26 | 7 | N |  |  | OP | X | 3 | 1966 |  |  | Y | Industrial CHP | 7 | B | BLQ | NG | WDS | RFO |  |  | RFO |  |  |  | N |  |  | 12H | [23 empty] | Y | Y | N
Vintage1970 | biomass | TRUE | 5232 | Woodland Pulp LLC | 10613 | Woodland Pulp, LLC | ME | Washington | TG11 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 26.8 | 0.8 | 20 | 20 | 7 | N |  |  | OP | X | 3 | 1970 |  |  | Y | Industrial CHP | 7 | B | BLQ | NG | WDS | RFO |  |  | RFO |  |  |  | N |  |  | 12H | [23 empty] | Y | Y | N
Vintage1995 | natural gas combined cycle | TRUE | 58338 | Lakeside Beaver Falls LLC | 10617 | CH Resources Beaver Falls | NY | Lewis | GEN1 | Natural Gas Fired Combined Cycle | CT | CC01 | S | X | N | NYISO ZONE E | NYISO ZONE E | 65.5 | 0.9 | 49.7 | 61 | 30 | N |  |  | OP | X | 4 | 1995 |  |  | Y | IPP CHP | 3 | X T T T: T; WC BLQ BLQ BLQ: NG; WC NG NG NG: DFO; NG NG NG NG: NG |  | N | N |  | OVER | [23 empty] | Y | N | Y
Vintage1995 | natural gas combined cycle | TRUE | 58338 | Lakeside Beaver Falls LLC | 10617 | CH Resources Beaver Falls | NY | Lewis | GEN2 | Natural Gas Fired Combined Cycle | CA | CC01 | S | Y | X | NYISO ZONE E | NYISO ZONE E | 42.3 | 0.9 | 30.6 | 31.8 | 15 | N |  |  | OP | X | 4 | 1995 |  |  | Y | IPP CHP | 3 | X T T T: B; WC BLQ BLQ BLQ: NG; WC NG NG NG: DFO; NG NG NG NG: NG |  | N | N |  | OVER | [23 empty] | Y | N | Y
Vintage1991 | natural gas combined cycle | TRUE | 3085 | Carthage Energy LLC | 10620 | Carthage Energy LLC | NY | Jefferson | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | 23857 | 23857 | 40.9 | 0.95 | 40.1 | 45 | 25 | N |  |  | OP | X | 11 | 1991 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WC BLQ BLQ BLQ: NG; WC NG NG NG: DFO |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1991 | natural gas combined cycle | TRUE | 3085 | Carthage Energy LLC | 10620 | Carthage Energy LLC | NY | Jefferson | GEN2 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | 23857 | 23857 | 22 | 0.95 | 21 | 21.5 | 10 | N |  |  | OP | X | 11 | 1991 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to WC BLQ BLQ BLQ
Vintage1994 | natural gas combined cycle | TRUE | 58337 | Lakeside Syracuse LLC | 10621 | CH Resources Syracuse | NY | Onondaga | GEN1 | Natural Gas Fired Combined Cycle | CT | CC01 | S | X | N | NYISO Zone C | NYISO Zone C | 65.5 | 0.9 | 59.6 | 73.4 | 30 | N |  |  | OP | X | 1 | 1994 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | N | bar: X T T T to WC BLQ BLQ BLQ; NG NG NG NG
Vintage1994 | natural gas combined cycle | TRUE | 58337 | Lakeside Syracuse LLC | 10621 | CH Resources Syracuse | NY | Onondaga | GEN2 | Natural Gas Fired Combined Cycle | CA | CC01 | S | Y | X | NYISO Zone C | NYISO Zone C | 37.2 | 0.9 | 28.8 | 28.8 | 15 | N |  |  | OP | X | 1 | 1994 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | N | bar: X T T T to WC BLQ BLQ BLQ; NG NG NG NG
Vintage1989 | natural gas combined cycle | FALSE | 11216 | Los Angeles County | 10623 | Civic Center | CA | Los Angeles | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 22.1 | 0.92 | 22.1 | 22.1 | 16 | Y | 6 | 2020 | OP | X | 8 | 1989 |  |  | Y | Commercial CHP | 5 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | N | bar: X T T T to WC BLQ BLQ BLQ
Vintage1989 | natural gas combined cycle | FALSE | 11216 | Los Angeles County | 10623 | Civic Center | CA | Los Angeles | GEN2 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X |  |  | 12.4 | 0.92 | 1.5 | 0.5 | 0.5 | Y | 6 | 2020 | OP | X | 8 | 1989 |  |  | Y | Commercial CHP | 5 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | N | bar: X T T T to WC BLQ BLQ BLQ
Vintage1958 | biomass | TRUE | 55863 | Evergreen Packaging Inc | 10627 | Pine Bluff Mill | AR | Jefferson | 1TG1 | Wood/Wood Waste Biomass | ST |  | S | X | X | EAILD | EAILD | 40 | 0.85 | 32 | 31 | 10 | N |  |  | OP | X | 5 | 1958 |  |  | Y | Industrial CHP | 7 | T | BLQ | PUR | WDS | NG | TDF | RFO | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1958 | biomass | TRUE | 55863 | Evergreen Packaging Inc | 10627 | Pine Bluff Mill | AR | Jefferson | 2TG1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 20 | 0.85 | 15.9 | 18.4 | 7 | N |  |  | OP | X | 5 | 1958 |  |  | Y | Industrial CHP | 7 | T | BLQ | PUR | WDS | NG | TDF | RFO | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1962 | biomass | TRUE | 55863 | Evergreen Packaging Inc | 10627 | Pine Bluff Mill | AR | Jefferson | 3TG1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 25 | 0.85 | 13 | 13 | 7 | N |  |  | OP | X | 11 | 1962 |  |  | Y | Industrial CHP | 7 | T | BLQ | PUR | WDS | NG | TDF | RFO | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1984 | municipal solid waste | TRUE | 20541 | Wheelabrator Environmental Systems | 10629 | Wheelabrator Baltimore Refuse | MD | Baltimore City | GEN1 | Municipal Solid Waste | ST |  | S | X | X | WESTPORT 34 KV BRESCO | WESTPORT 34 KV BRESCO | 60.2 | 0.9 | 57 | 57 | 10 | N |  |  | OP | X | 11 | 1984 |  |  | N | IPP CHP | 3 | B T T T: X; NG BLQ BLQ BLQ: MSW; NG NG NG NG: NG |  |  |  | N | N |  | 12H |  |  |  | N | N | [18 empty] | N | N
Vintage2001 | municipal solid waste | TRUE | 20541 | Wheelabrator Environmental Systems | 10629 | Wheelabrator Baltimore Refuse | MD | Baltimore City | GEN2 | Municipal Solid Waste | ST |  | S | X | X |  |  | 4.3 | 0.9 | 4.3 | 4.3 | 2 | N |  |  | OP | X | 1 | 2001 |  |  | Y | IPP CHP | 3 | B T T T: T; NG BLQ BLQ BLQ: MSW; NG NG NG NG: NG |  |  |  | N | N |  | 12H |  |  |  | N | N | [18 empty] | N | N
Vintage1989 | geothermal | TRUE | 49899 | CalEnergy Operating Corporation | 10631 | CE Leathers | CA | Imperial | GEN1 | Geothermal | ST |  | W | X | X |  |  | 45.5 | 0.85 | 42 | 42 | 2 | N |  |  | OP | X | 11 | 1989 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: GEO; NG NG NG NG: GEO |  |  |  | N | N |  | 12H | [23 empty] | N | N
Vintage1988 | geothermal | TRUE | 49899 | CalEnergy Operating Corporation | 10632 | Del Ranch Company | CA | Imperial | GEN1 | Geothermal | ST |  | W | X | X |  |  | 45.5 | 0.85 | 42 | 42 | 2 | N |  |  | OP | X | 10 | 1988 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: GEO; NG NG NG NG: GEO |  |  |  | N | N |  | 12H | [23 empty] | N | N
Vintage1990 | natural gas combined cycle | TRUE | 55983 | Luminant Generation Company LLC | 10633 | Hopewell Cogeneration | VA | Prince George | GT1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | PJM | PJM | 101 | 1 | 94.1 | 101 | 55 | N |  |  | OP | X | 1 | 1990 |  |  | Y | IPP CHP | 3 | B T T T: T; NG BLQ BLQ BLQ: NG; NG PUR PUR PUR: DFO; NG NG NG NG: NG | DFO |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1990 | natural gas combined cycle | TRUE | 55983 | Luminant Generation Company LLC | 10633 | Hopewell Cogeneration | VA | Prince George | GT2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | PJM | PJM | 101 | 1 | 94.1 | 101 | 55 | N |  |  | OP | X | 2 | 1990 |  |  | Y | IPP CHP | 3 | B T T T: T; NG BLQ BLQ BLQ: NG; NG PUR PUR PUR: DFO; NG NG NG NG: NG | DFO |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1990 | natural gas combined cycle | TRUE | 55983 | Luminant Generation Company LLC | 10633 | Hopewell Cogeneration | VA | Prince George | GT3 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | PJM | PJM | 101 | 1 | 94.1 | 101 | 55 | N |  |  | OP | X | 3 | 1990 |  |  | Y | IPP CHP | 3 | B T T T: T; NG BLQ BLQ BLQ: NG; NG PUR PUR PUR: DFO; NG NG NG NG: NG | DFO |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1990 | other | TRUE | 55983 | Luminant Generation Company LLC | 10633 | Hopewell Cogeneration | VA | Prince George | ST1 | All Other | CA | CC1 | S | N | X |  |  | 96 | 1 | 96 | 96 | 55 | N |  |  | OP | X | 3 | 1990 |  |  | Y | IPP CHP | 3 | T | OTH | OTH | OTH |  |  |  | OTH |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1988 | geothermal | TRUE | 49899 | CalEnergy Operating Corporation | 10634 | Elmore Company | CA | Imperial | GEN1 | Geothermal | ST |  | W | X | X |  |  | 45.5 | 0.85 | 49 | 49 | 2 | N |  |  | OP | X | 11 | 1988 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: GEO; NG NG NG NG: GEO |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1989 | municipal solid waste | TRUE | 473 | Covanta Hempstead Company | 10642 | Covanta Hempstead | NY | Nassau | GEN1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 78.6 | 1 | 71.8 | 71.8 | 24 | N |  |  | OP | X | 4 | 1989 |  |  | N | IPP Non-CHP | 2 | X | MSW | DFO | WDS |  |  |  | DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | N
Vintage1990 | municipal solid waste | TRUE | 542 | Covanta Essex Company | 10643 | Covanta Essex Company | NJ | Essex | GEN1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 34.9 | 0.9 | 30 | 30 | 5 | N |  |  | OP | X | 11 | 1990 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: MSW; NG PUR PUR PUR: DFO; NG NG NG NG: DFO |  |  |  | N | N |  | 12H |  |  | N | N | [19 empty] | N | N | N
Vintage1990 | municipal solid waste | TRUE | 542 | Covanta Essex Company | 10643 | Covanta Essex Company | NJ | Essex | GEN2 | Municipal Solid Waste | ST |  | S | X | X |  |  | 34.9 | 0.9 | 30 | 30 | 5 | N |  |  | OP | X | 11 | 1990 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: MSW; NG PUR PUR PUR: DFO; NG NG NG NG: DFO |  |  |  | N | N |  | 12H |  |  | N | [20 empty] | N | N | N
Vintage1991 | municipal solid waste | TRUE | 528 | Covanta Southeastern Connecticut Company | 10646 | Covanta Southeastern Connecticut Company | CT | New London | GEN1 | Municipal Solid Waste | ST |  | S | X | X | 562 | 562 | 18.3 | 0.9 | 16.3 | 18.1 | 3 | N |  |  | OP | X | 12 | 1991 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: MSW; NG PUR PUR PUR: DFO; NG NG NG NG: DFO |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | N | N | N
Vintage1995 | natural gas peaker | TRUE | 60662 | WCAC Operating Company | 10649 | Bear Mountain Limited | CA | Kern | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 46 | 0.85 | 46 | 48 | 32 | N |  |  | OP | X | 4 | 1995 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1991 | natural gas peaker | TRUE | 60662 | WCAC Operating Company | 10650 | Badger Creek Limited | CA | Kern | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 46 | 0.85 | 46 | 48 | 32 | N |  |  | OP | X | 4 | 1991 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1989 | biomass | TRUE | 62970 | Burney Forest Products, A Joint Venture | 10652 | Burney Forest Products | CA | Shasta | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X | BioRAM | BioRAM | 31 | 0.9 | 31 | 31 | 1 | N |  |  | OP | X | 10 | 1989 |  |  | Y | IPP CHP | 3 | B T T T: T; NG BLQ BLQ BLQ: WDS; NG PUR PUR PUR: NG; NG NG NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1922 | hydro | FALSE | 6789 | French Paper Co | 10656 | French Paper Hydro | MI | Berrien | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0 | N |  |  | OP | X | 1 | 1922 |  |  | N | Industrial Non-CHP | 6 | B T T T: X; NG BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1927 | hydro | FALSE | 6789 | French Paper Co | 10656 | French Paper Hydro | MI | Berrien | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0 | N |  |  | OP | X | 1 | 1927 |  |  | N | Industrial Non-CHP | 6 | B T T T: X; NG BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1930 | hydro | FALSE | 6789 | French Paper Co | 10656 | French Paper Hydro | MI | Berrien | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.3 | 0.3 | 0 | N |  |  | OP | X | 1 | 1930 |  |  | N | Industrial Non-CHP | 6 | B T T T: X; NG BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1921 | hydro | FALSE | 6789 | French Paper Co | 10656 | French Paper Hydro | MI | Berrien | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0 | N |  |  | OP | X | 1 | 1921 |  |  | N | Industrial Non-CHP | 6 | B T T T: X; NG BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage2021 | biomass | TRUE | 3953 | Collins Pine Co | 10661 | Collins Pine Project | CA | Plumas | GEN5 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 5 | 0.8 | 5 | 5 | 1 | N |  |  | OP | X | 9 | 2021 |  |  | Y | Industrial CHP | 7 | B T T T: T; NG BLQ BLQ BLQ: WDS; NG NG NG NG: WDS | DFO |  |  | N | N |  | OVER | [23 empty] | N
Vintage1990 | hard coal | TRUE | 14063 | Oklahoma Gas & Electric Co | 10671 | River Valley | OK | Le Flore | GEN1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 175 | 0.9 | 161 | 161 | 80 | N |  |  | OP | X | 9 | 1990 |  |  | N | Electric Utility | 1 | X | SUB | BIT | NG |  |  |  | NG |  |  |  | N | N |  | OVER | Y |  |  |  | Y | [18 empty] | Y | Y | N
Vintage1990 | hard coal | TRUE | 14063 | Oklahoma Gas & Electric Co | 10671 | River Valley | OK | Le Flore | GEN2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 175 | 0.9 | 160 | 160 | 80 | N |  |  | OP | X | 11 | 1990 |  |  | N | Electric Utility | 1 | X | SUB | BIT | NG |  |  |  | NG |  |  |  | N | N |  | OVER | Y |  |  |  | Y | [18 empty] | Y | Y | N
Vintage1992 | hard coal | TRUE | 177 | AES Hawaii LLC | 10673 | AES Hawaii | HI | Honolulu | GEN1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 203 | 0.85 | 180 | 180 | 63 | N |  |  | OP | X | 5 | 1992 | 9 | 2022 | Y | IPP CHP | 3 | T | SUB | WO | BIT | TDF | OBS |  | DFO |  |  |  | N | N |  | OVER | Y |  |  |  | Y | N | [17 empty] | Y | Y | N
Vintage1988 | natural gas combined cycle | TRUE | 178 | CES Placerita Inc | 10677 | CES Placerita Power Plant | CA | Los Angeles | UNT2 | Natural Gas Fired Combined Cycle | CT | CESP | S | X | N |  |  | 60 | 0.85 | 46 | 50 | 23 | N |  |  | OS | X | 6 | 1988 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | N | bar: B T T T to NG BLQ BLQ BLQ; NG NG NG NG
Vintage1988 | natural gas combined cycle | TRUE | 178 | CES Placerita Inc | 10677 | CES Placerita Power Plant | CA | Los Angeles | UNT3 | Natural Gas Fired Combined Cycle | CA | CESP | S | N | X |  |  | 30 | 0.85 | 23 | 25 | 5 | N |  |  | OS | X | 6 | 1988 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1999 | hard coal | TRUE | 35 | AES WR Ltd Partnership | 10678 | AES Warrior Run Cogeneration Facility | MD | Allegany | GEN1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 229 | 0.9 | 180 | 180 | 72 | N |  |  | OP | X | 8 | 1999 |  |  | Y | IPP CHP | 3 | B T T T: T; NG BLQ BLQ BLQ: BIT; NG NG NG NG: DFO |  |  |  | N | Y |  | OVER | Y |  |  |  | Y | [18 empty] | N | N | N
Vintage1990 | natural gas combined cycle | TRUE | 55307 | Colorado Energy Management | 10682 | Brush Generation Facility | CO | Morgan | GT1 | Natural Gas Fired Combined Cycle | CT | CPP | W | X | N |  |  | 23.8 | 0.85 | 25 | 30 | 25 | N |  |  | OP | X | 10 | 1990 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1990 | natural gas peaker | TRUE | 55307 | Colorado Energy Management | 10682 | Brush Generation Facility | CO | Morgan | GT2 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 23.8 | 0.85 | 25 | 30 | 25 | N |  |  | OP | X | 10 | 1990 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1994 | natural gas combined cycle | TRUE | 55307 | Colorado Energy Management | 10682 | Brush Generation Facility | CO | Morgan | GT3 | Natural Gas Fired Combined Cycle | CT | BCP | W | X | N |  |  | 37 | 0.85 | 32 | 38 | 32 | N |  |  | OP | X | 1 | 1994 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1999 | natural gas combined cycle | TRUE | 55307 | Colorado Energy Management | 10682 | Brush Generation Facility | CO | Morgan | GT4 | Natural Gas Fired Combined Cycle | CT | BIV | W | X | Y |  |  | 23.8 | 0.85 | 25 | 30 | 23 | N |  |  | OP | X | 6 | 1999 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1999 | natural gas combined cycle | TRUE | 55307 | Colorado Energy Management | 10682 | Brush Generation Facility | CO | Morgan | GT5 | Natural Gas Fired Combined Cycle | CT | BIV | W | X | Y |  |  | 23.8 | 0.85 | 25 | 30 | 23 | N |  |  | OP | X | 6 | 1999 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1990 | natural gas combined cycle | TRUE | 55307 | Colorado Energy Management | 10682 | Brush Generation Facility | CO | Morgan | ST1 | Natural Gas Fired Combined Cycle | CA | CPP | W | Y | X |  |  | 38 | 0.8 | 30 | 30 | 10 | N |  |  | OP | X | 10 | 1990 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1994 | natural gas combined cycle | TRUE | 55307 | Colorado Energy Management | 10682 | Brush Generation Facility | CO | Morgan | ST2 | Natural Gas Fired Combined Cycle | CA | BCP | W | Y | X |  |  | 37 | 0.85 | 40 | 40 | 15 | N |  |  | OP | X | 1 | 1994 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage2002 | natural gas combined cycle | TRUE | 55307 | Colorado Energy Management | 10682 | Brush Generation Facility | CO | Morgan | ST4 | Natural Gas Fired Combined Cycle | CA | BIV | W | Y | X |  |  | 90 | 0.8 | 90 | 90 | 30 | N |  |  | OP | X | 9 | 2002 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1947 | hard coal | FALSE | 49968 | Searles Valley Minerals Operations Inc. | 10684 | Argus Cogen Plant | CA | San Bernardino | TG5 | Conventional Steam Coal | ST |  | W | X | X | CAISO | CAISO | 7.5 | 0.8 | 7 | 7 | 1 | N |  |  | SB | Y | 12 | 1947 |  |  | Y | Industrial CHP | 7 | B T T T: T; NG BLQ BLQ BLQ: RC; NG PUR PUR PUR: BIT; NG NG NG NG: NG |  |  |  | N | Y |  | 12H |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1978 | hard coal | FALSE | 49968 | Searles Valley Minerals Operations Inc. | 10684 | Argus Cogen Plant | CA | San Bernardino | TG8 | Conventional Steam Coal | ST |  | W | X | X | CAISO | CAISO | 27.5 | 0.8 | 25 | 25 | 10 | N |  |  | OP | X | 7 | 1978 |  |  | Y | Industrial CHP | 7 | B T T T: T; NG BLQ BLQ BLQ: RC; NG PUR PUR PUR: BIT; NG NG NG NG: NG |  |  |  | N | Y |  | 12H |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1978 | hard coal | FALSE | 49968 | Searles Valley Minerals Operations Inc. | 10684 | Argus Cogen Plant | CA | San Bernardino | TG9 | Conventional Steam Coal | ST |  | W | X | X | CAISO | CAISO | 27.5 | 0.8 | 25 | 25 | 10 | N |  |  | OP | X | 7 | 1978 |  |  | Y | Industrial CHP | 7 | B T T T: T; NG BLQ BLQ BLQ: RC; NG PUR PUR PUR: BIT; NG NG NG NG: NG |  |  |  | N | Y |  | 12H |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1969 | natural gas peaker | FALSE | 49968 | Searles Valley Minerals Operations Inc. | 10685 | Westend Facility | CA | San Bernardino | PINA | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 20 | 0.8 | 15 | 15 | 1 | N |  |  | OS | X | 1 | 1969 |  |  | Y | Industrial CHP | 7 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1969 | natural gas steam turbine | TRUE | 12647 | ALLETE, Inc. | 10686 | Rapids Energy Center | MN | Itasca | 6 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 12.5 | 0.8 | 13.1 | 13.1 | 4 | N |  |  | OP | X | 1 | 1969 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: B T T T to NG BLQ BLQ BLQ; NG NG NG NG
Vintage1980 | natural gas steam turbine | TRUE | 12647 | ALLETE, Inc. | 10686 | Rapids Energy Center | MN | Itasca | 7 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 14 | 0.85 | 9.5 | 9.5 | 6 | N |  |  | OP | X | 1 | 1980 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: B T T T to NG BLQ BLQ BLQ; NG NG NG NG
Vintage1943 | hydro | TRUE | 12647 | ALLETE, Inc. | 10686 | Rapids Energy Center | MN | Itasca | HYD | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.9 | 0.8 | 0.8 | 0.8 | 0.2 | N |  |  | OP | X | 1 | 1943 |  |  | N | Electric Utility | 1 | B T T T: X; NG BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage1984 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10687 | Black River Hydro Associates | NY | Lewis | DE1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 1 | 1.5 | 1.5 | 0.1 | N |  |  | OP | X | 1 | 1984 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT | [6 empty] | 1H
Vintage1984 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10687 | Black River Hydro Associates | NY | Lewis | PL1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 1 | 2.1 | 2 | 0.1 | N |  |  | OA | X | 1 | 1984 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT | [6 empty] | 1H
Vintage1984 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10687 | Black River Hydro Associates | NY | Lewis | RI1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.9 | 1 | 1.8 | 1.8 | 0.1 | N |  |  | OP | X | 1 | 1984 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT | [6 empty] | 1H
Vintage1990 | natural gas peaker | FALSE | 6088 | Exxon Mobil Corp | 10690 | ExxonMobil Baton Rouge Turbine Generator | LA | East Baton Rouge | CTG1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | EES.ENCO | EES.ENCO | 85.3 | 0.9 | 75.6 | 84.5 | 60 | N |  |  | OP | X | 5 | 1990 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N | 0 | 12H | [23 empty] | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1989 | natural gas peaker | FALSE | 6091 | Exxon Mobil Refining and Supply Co. | 10692 | ExxonMobil Baytown Turbine | TX | Harris | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | EXN_G1 | EXN_G1 | 39.7 | 0.85 | 29 | 35 | 25 | N |  |  | OP | X | 2 | 1989 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1989 | natural gas peaker | FALSE | 6091 | Exxon Mobil Refining and Supply Co. | 10692 | ExxonMobil Baytown Turbine | TX | Harris | GEN2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | EXN_G2 | EXN_G2 | 39.7 | 0.85 | 29 | 35 | 25 | N |  |  | OP | X | 4 | 1989 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1989 | natural gas peaker | FALSE | 6091 | Exxon Mobil Refining and Supply Co. | 10692 | ExxonMobil Baytown Turbine | TX | Harris | GEN3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | EXN_G3 | EXN_G3 | 39.7 | 0.85 | 29 | 35 | 25 | N |  |  | OP | X | 3 | 1989 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1997 | natural gas peaker | FALSE | 6091 | Exxon Mobil Refining and Supply Co. | 10692 | ExxonMobil Baytown Turbine | TX | Harris | GEN4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | EXN_G4 | EXN_G4 | 98.9 | 0.85 | 78 | 89 | 50 | N |  |  | OP | X | 2 | 1997 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage2004 | natural gas peaker | FALSE | 6091 | Exxon Mobil Refining and Supply Co. | 10692 | ExxonMobil Baytown Turbine | TX | Harris | GEN5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | EXN_G14 | EXN_G14 | 163.8 | 0.85 | 140 | 180.1 | 80 | N |  |  | OP | X | 12 | 2004 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1987 | biomass | TRUE | 11704 | Maryland Environmental Service | 10693 | Eastern Correctional Institute | MD | Somerset | 1147 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 1.9 | 0.8 | 1.3 | 0.8 | 0.5 | N |  |  | OP | X | 8 | 1987 |  |  | Y | Commercial CHP | 5 | B T T T: T; NG BLQ BLQ BLQ: WDS; NG PUR PUR PUR: DFO; NG NG NG NG: PG | DFO |  |  | N | N |  | 12H |  |  | N | [20 empty] | Y | Y | N
Vintage1987 | biomass | TRUE | 11704 | Maryland Environmental Service | 10693 | Eastern Correctional Institute | MD | Somerset | 1148 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 1.9 | 0.8 | 1.3 | 0.8 | 0.5 | N |  |  | OP | X | 8 | 1987 |  |  | Y | Commercial CHP | 5 | B T T T: T; NG BLQ BLQ BLQ: WDS; NG PUR PUR PUR: DFO; NG NG NG NG: PG | DFO |  |  | N | N |  | 12H |  |  | N | [20 empty] | Y | Y | N
Vintage1988 | petroleum | FALSE | 11704 | Maryland Environmental Service | 10693 | Eastern Correctional Institute | MD | Somerset | DG1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.4 | N |  |  | SB | Y | 11 | 1988 |  |  | N | Commercial CHP | 5 | B T T T: X; NG BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1988 | petroleum | FALSE | 11704 | Maryland Environmental Service | 10693 | Eastern Correctional Institute | MD | Somerset | DG2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.4 | N |  |  | SB | Y | 11 | 1988 |  |  | N | Commercial CHP | 5 | B T T T: X; NG BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1920 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 10694 | Pepperell Hydro Power Plant | MA | Middlesex | 2121 | Conventional Hydroelectric | HY |  | W | X | X | 4332 |  | 0.8 | 0.9 | 0.8 | 0.7 | 0.3 | N |  |  | OP | X | 1 | 1920 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT | [6 empty] | 10M
Vintage1920 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 10694 | Pepperell Hydro Power Plant | MA | Middlesex | 8281 | Conventional Hydroelectric | HY |  | W | X | X | 4332 |  | 0.8 | 0.8 | 0.8 | 0.7 | 0.3 | N |  |  | OP | X | 1 | 1920 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT | [6 empty] | 10M
Vintage2006 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 10694 | Pepperell Hydro Power Plant | MA | Middlesex | G3 | Conventional Hydroelectric | HY |  | W | X | X | 4332 |  | 0.6 | 0.9 | 0.6 | 0.5 | 0.3 | N |  |  | OP | X | 12 | 2006 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT | [6 empty] | 10M
Vintage1966 | biomass | TRUE | 59867 | Hood Container of Louisiana, LLC | 10697 | St Francisville Mill | LA | West Feliciana | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 12.5 | 0.9 | 16 | 16.5 | 3 | N |  |  | OP | X | 3 | 1966 |  |  | Y | Industrial CHP | 7 | B T T T: T; NG BLQ BLQ BLQ: BLQ; NG PUR PUR PUR: NG; NG NG NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1992 | natural gas steam turbine | FALSE | 7475 | Graphic Packaging Corp | 10698 | Graphic Packaging | MI | Kalamazoo | GEN2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 1.8 | 0.8 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 1 | 1992 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | N | bar: B T T T to NG BLQ BLQ BLQ; NG NG NG NG
Vintage1993 | biomass | TRUE | 7136 | Georgia-Pacific Consr Prods LP-Naheola | 10699 | Georgia-Pacific Consr Prods LP-Naheola | AL | Choctaw | GT3 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 47.2 | 0.85 | 37.4 | 37.7 | 3 | N |  |  | OP | X | 4 | 1993 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | DFO | WDS |  |  | NG | DFO |  |  | N | N |  | 12H |  |  | N | [20 empty] | Y | Y | N
Vintage2019 | biomass | TRUE | 7136 | Georgia-Pacific Consr Prods LP-Naheola | 10699 | Georgia-Pacific Consr Prods LP-Naheola | AL | Choctaw | TG4 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 40.3 | 0.85 | 29.4 | 29.7 | 2.6 | N |  |  | OP | X | 6 | 2019 |  |  | Y | Industrial CHP | 7 | T | WDS | NG | BLQ | DFO |  |  | NG | DFO |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1965 | biomass | TRUE | 61813 | ND Paper, Inc. | 10700 | Red Shield Envir Old Town Facility | ME | Penobscot | TG4 | Wood/Wood Waste Biomass | ST |  | S | X | X | NPCC/ISO New England/Graham 46 | NPCC/ISO New England/Graham 46 | 12.5 | 0.85 | 7.5 | 12.5 | 2 | N |  |  | OP | X | 7 | 1965 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | RFO | WDS |  |  | BLQ |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1987 | biomass | TRUE | 61813 | ND Paper, Inc. | 10700 | Red Shield Envir Old Town Facility | ME | Penobscot | TG6 | Wood/Wood Waste Biomass | ST |  | S | X | X | NPCC/ISO New England/Graham 46 | NPCC/ISO New England/Graham 46 | 16 | 0.85 | 14 | 14 | 2 | N |  |  | OP | X | 12 | 1987 |  |  | Y | Industrial CHP | 7 | B T T T: T; NG BLQ BLQ BLQ: WDS; NG PUR PUR PUR: NG; NG NG NG NG: WDS |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1990 | hydro | TRUE | 17725 | Snow Mountain Hydro LLC | 10706 | Burney Creek | CA | Shasta | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.9 | 3 | 3 | 0.2 | N |  |  | OP | X | 3 | 1990 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1990 | hydro | TRUE | 17725 | Snow Mountain Hydro LLC | 10707 | Cove Hydroelectric | CA | Shasta | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5 | 0.9 | 5 | 5 | 0.2 | N |  |  | OP | X | 2 | 1990 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1989 | hydro | TRUE | 17725 | Snow Mountain Hydro LLC | 10708 | Lost Creek I | CA | Shasta | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.1 | 0.9 | 1.1 | 1.1 | 0.1 | N |  |  | OP | X | 12 | 1989 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1990 | hydro | TRUE | 17725 | Snow Mountain Hydro LLC | 10709 | Ponderosa Bailey Creek | CA | Tehama | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.1 | 0.9 | 1.1 | 1.1 | 0.1 | N |  |  | OP | X | 3 | 1990 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1985 | onshore wind | TRUE | 16630 | San Gorgonio Farms Inc | 10718 | Karen Avenue Wind Farm | CA | Riverside | WND | Onshore Wind Turbine | WT |  | S | X | X | GARNET_2_WIND2 | GARNET_2_WIND2 | 11.7 |  | 11.7 | 11.7 | 0 | N |  |  | OP | X | 1 | 1985 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WND |  |  |  | N | N | 12 | 10M | [23 empty] | N
Vintage2012 | natural gas peaker | FALSE | 9948 | Kyocera International, Ind | 10720 | Kyocera America Project | CA | San Diego | 0287 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.7 | 0.95 | 1.7 | 1.7 | 0.8 | N |  |  | OP | X | 9 | 2012 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage2012 | natural gas peaker | FALSE | 9948 | Kyocera International, Ind | 10720 | Kyocera America Project | CA | San Diego | 0333 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.1 | 0.95 | 2.1 | 2.1 | 1 | N |  |  | OP | X | 9 | 2012 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N | 0 | 1H | [23 empty] | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1992 | natural gas combined cycle | TRUE | 16909 | Selkirk Cogen Partners LP | 10725 | Selkirk Cogen | NY | Albany | GEN1 | Natural Gas Fired Combined Cycle | CT | F802 | W | X | Y | Selkirk-I | Selkirk-I | 95.2 | 0.9 | 76.9 | 105.5 | 45 | N |  |  | OP | X | 4 | 1992 |  |  | Y | IPP CHP | 3 | B T T T: T; NG BLQ BLQ BLQ: NG; NG PUR PUR PUR: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1992 | natural gas combined cycle | TRUE | 16909 | Selkirk Cogen Partners LP | 10725 | Selkirk Cogen | NY | Albany | GEN2 | Natural Gas Fired Combined Cycle | CA | F801 | W | Y | X | Selkirk-I | Selkirk-I | 12 | 0.85 |  |  | 11 | N |  |  | SB | Y | 4 | 1992 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N |  | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1994 | natural gas combined cycle | TRUE | 16909 | Selkirk Cogen Partners LP | 10725 | Selkirk Cogen | NY | Albany | GEN3 | Natural Gas Fired Combined Cycle | CT | F802 | W | X | N | Selkirk-II | Selkirk-II | 95.2 | 0.9 | 272.3 | 333.1 | 45 | N |  |  | OP | X | 4 | 1994 |  |  | Y | IPP CHP | 3 | B T T T: T; NG BLQ BLQ BLQ: NG; NG PUR PUR PUR: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1994 | natural gas combined cycle | TRUE | 16909 | Selkirk Cogen Partners LP | 10725 | Selkirk Cogen | NY | Albany | GEN4 | Natural Gas Fired Combined Cycle | CT | F802 | W | X | N | Selkirk-II | Selkirk-II | 95.2 | 0.9 |  |  | 45 | N |  |  | OP | X | 4 | 1994 |  |  | Y | IPP CHP | 3 | B T T T: T; NG BLQ BLQ BLQ: NG; NG PUR PUR PUR: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1994 | natural gas combined cycle | TRUE | 16909 | Selkirk Cogen Partners LP | 10725 | Selkirk Cogen | NY | Albany | GEN5 | Natural Gas Fired Combined Cycle | CA | F802 | W | Y | X | Selkirk-II | Selkirk-II | 148.4 | 0.95 |  |  | 11 | N |  |  | OP | X | 4 | 1994 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N |  | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1993 | natural gas combined cycle | TRUE | 11741 | Masspower | 10726 | Masspower | MA | Hampden | GEN1 | Natural Gas Fired Combined Cycle | CT | G321 | S | X | N | WCMASS | WCMASS | 90 | 0.85 | 83 | 95 | 64 | N |  |  | OP | X | 7 | 1993 |  |  | Y | IPP CHP | 3 | B T T T: T; NG BLQ BLQ BLQ: NG; NG PUR PUR PUR: DFO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1993 | natural gas combined cycle | TRUE | 11741 | Masspower | 10726 | Masspower | MA | Hampden | GEN2 | Natural Gas Fired Combined Cycle | CT | G321 | S | X | N | WCMASS | WCMASS | 90 | 0.85 | 83 | 95 | 64 | N |  |  | OP | X | 7 | 1993 |  |  | Y | IPP CHP | 3 | B T T T: T; NG BLQ BLQ BLQ: NG; NG PUR PUR PUR: DFO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1993 | natural gas combined cycle | TRUE | 11741 | Masspower | 10726 | Masspower | MA | Hampden | GEN3 | Natural Gas Fired Combined Cycle | CA | G321 | S | N | X | WCMASS | WCMASS | 80.9 | 0.85 | 79 | 90 | 60 | N |  |  | OP | X | 7 | 1993 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1986 | hydro | TRUE | 56838 | KEI (Maine) Power Management (III) LLC | 10728 | Barker Lower | ME | Androscoggin | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 0.99 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 4 | 1986 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 1H | [20 empty] | N |  |  | N |  | N
Vintage1990 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10735 | Barber Dam | ID | Ada | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.1 | 1 | 4 | 4 | 0.1 | N |  |  | OP | X | 8 | 1990 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT | [5 empty] | 0 | 10M
Vintage1989 | hydro | TRUE | 8353 | Sprague Hydro LLC | 10737 | Sprague Hydro | OR | Klamath | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 1 | 1 | 1 | 0.1 | N |  |  | OP | X | 10 | 1989 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT | [5 empty] | 0 | 10M
Vintage1989 | hydro | TRUE | 62045 | Wood Hydro, LLC | 10740 | Magic Dam Hydroelectric Project | ID | Blaine | GEN1 | Conventional Hydroelectric | HY |  | S | X | X | Mid C | WECC | 3 | 0.9 | 2.9 | 2.8 | 1 | N |  |  | OP | X | 5 | 1989 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1989 | hydro | TRUE | 62045 | Wood Hydro, LLC | 10740 | Magic Dam Hydroelectric Project | ID | Blaine | GEN2 | Conventional Hydroelectric | HY |  | S | X | X | Mid C | WECC | 3 | 0.9 | 2.9 | 2.8 | 1 | N |  |  | OP | X | 5 | 1989 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1989 | hydro | TRUE | 62045 | Wood Hydro, LLC | 10740 | Magic Dam Hydroelectric Project | ID | Blaine | GEN3 | Conventional Hydroelectric | HY |  | S | X | X | Mid C | WECC | 3 | 0.9 | 2.9 | 2.8 | 1 | N |  |  | OP | X | 5 | 1989 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1991 | hard coal | TRUE | 12949 | Morgantown Energy Associates | 10743 | Morgantown Energy Facility | WV | Monongalia | GEN1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 68.9 | 0.85 | 50 | 50 | 20 | N |  |  | OS | X | 11 | 1991 |  |  | Y | IPP CHP | 3 | B T T T: T; NG BLQ BLQ BLQ: WC; NG NG NG NG: NG |  |  |  | N | N |  | OVER | Y |  |  |  | Y | [18 empty] | N | N | N
Vintage1990 | petroleum | TRUE | 12492 | Midland Cogeneration Venture | 10745 | Midland Cogeneration Venture | MI | Midland | 1G12 | Petroleum Liquids | IC |  | S | X | X |  |  | 5.2 | 0.8 | 5.2 | 5.2 | 1 | N |  |  | SB | Y | 2 | 1990 |  |  | Y | IPP CHP | 3 | B T T T: T; NG BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1998 | natural gas combined cycle | TRUE | 12492 | Midland Cogeneration Venture | 10745 | Midland Cogeneration Venture | MI | Midland | BP15 | Natural Gas Fired Combined Cycle | CA | 1 | S | Y | X |  |  | 13.4 | 0.8 | 13.4 | 13.4 | 1 | N |  |  | OP | X | 7 | 1998 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | OVER | [23 empty] | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1990 | natural gas combined cycle | TRUE | 12492 | Midland Cogeneration Venture | 10745 | Midland Cogeneration Venture | MI | Midland | GT10 | Natural Gas Fired Combined Cycle | CT | 1 | S | X | N |  |  | 87.1 | 0.85 | 88 | 103 | 70 | N |  |  | OP | X | 1 | 1990 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1990 | natural gas combined cycle | TRUE | 12492 | Midland Cogeneration Venture | 10745 | Midland Cogeneration Venture | MI | Midland | GT11 | Natural Gas Fired Combined Cycle | CT | 1 | S | X | N |  |  | 87.1 | 0.85 | 88 | 103 | 70 | N |  |  | OP | X | 2 | 1990 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1990 | natural gas combined cycle | TRUE | 12492 | Midland Cogeneration Venture | 10745 | Midland Cogeneration Venture | MI | Midland | GT12 | Natural Gas Fired Combined Cycle | CT | 1 | S | X | N |  |  | 87.1 | 0.85 | 88 | 103 | 70 | N |  |  | OP | X | 3 | 1990 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1990 | natural gas combined cycle | TRUE | 12492 | Midland Cogeneration Venture | 10745 | Midland Cogeneration Venture | MI | Midland | GT13 | Natural Gas Fired Combined Cycle | CT | 1 | S | X | N |  |  | 87.1 | 0.85 | 88 | 103 | 70 | N |  |  | OP | X | 4 | 1990 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1990 | natural gas combined cycle | TRUE | 12492 | Midland Cogeneration Venture | 10745 | Midland Cogeneration Venture | MI | Midland | GT14 | Natural Gas Fired Combined Cycle | CT | 1 | S | X | N |  |  | 87.1 | 0.85 | 88 | 103 | 70 | N |  |  | OP | X | 5 | 1990 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1989 | natural gas combined cycle | TRUE | 12492 | Midland Cogeneration Venture | 10745 | Midland Cogeneration Venture | MI | Midland | GT3 | Natural Gas Fired Combined Cycle | CT | 1 | S | X | N |  |  | 87.1 | 0.85 | 88 | 103 | 70 | N |  |  | OP | X | 6 | 1989 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1989 | natural gas combined cycle | TRUE | 12492 | Midland Cogeneration Venture | 10745 | Midland Cogeneration Venture | MI | Midland | GT4 | Natural Gas Fired Combined Cycle | CT | 1 | S | X | N |  |  | 87.1 | 0.85 | 88 | 103 | 70 | N |  |  | OP | X | 8 | 1989 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1989 | natural gas combined cycle | TRUE | 12492 | Midland Cogeneration Venture | 10745 | Midland Cogeneration Venture | MI | Midland | GT5 | Natural Gas Fired Combined Cycle | CT | 1 | S | X | N |  |  | 87.1 | 0.85 | 88 | 103 | 70 | N |  |  | OP | X | 9 | 1989 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1989 | natural gas combined cycle | TRUE | 12492 | Midland Cogeneration Venture | 10745 | Midland Cogeneration Venture | MI | Midland | GT6 | Natural Gas Fired Combined Cycle | CT | 1 | S | X | N |  |  | 87.1 | 0.85 | 88 | 103 | 70 | N |  |  | OP | X | 10 | 1989 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1989 | natural gas combined cycle | TRUE | 12492 | Midland Cogeneration Venture | 10745 | Midland Cogeneration Venture | MI | Midland | GT7 | Natural Gas Fired Combined Cycle | CT | 1 | S | X | N |  |  | 87.1 | 0.85 | 88 | 103 | 70 | N |  |  | OP | X | 9 | 1989 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1989 | natural gas combined cycle | TRUE | 12492 | Midland Cogeneration Venture | 10745 | Midland Cogeneration Venture | MI | Midland | GT8 | Natural Gas Fired Combined Cycle | CT | 1 | S | X | N |  |  | 87.1 | 0.85 | 88 | 103 | 70 | N |  |  | OP | X | 12 | 1989 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1990 | natural gas combined cycle | TRUE | 12492 | Midland Cogeneration Venture | 10745 | Midland Cogeneration Venture | MI | Midland | GT9 | Natural Gas Fired Combined Cycle | CT | 1 | S | X | N |  |  | 87.1 | 0.85 | 88 | 103 | 70 | N |  |  | OP | X | 1 | 1990 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1990 | natural gas combined cycle | TRUE | 12492 | Midland Cogeneration Venture | 10745 | Midland Cogeneration Venture | MI | Midland | ST1 | Natural Gas Fired Combined Cycle | CA | 1 | S | Y | X |  |  | 410 | 0.9 | 410 | 410 | 25 | N |  |  | OP | X | 2 | 1990 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | OVER | [23 empty] | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1990 | natural gas combined cycle | TRUE | 12492 | Midland Cogeneration Venture | 10745 | Midland Cogeneration Venture | MI | Midland | ST2 | Natural Gas Fired Combined Cycle | CA | 1 | S | Y | X |  |  | 380 | 0.85 | 380 | 380 | 40 | N |  |  | SB | Y | 9 | 1990 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | OVER | [23 empty] | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1991 | municipal solid waste | TRUE | 570 | Covanta Delaware Valley LP | 10746 | Covanta Delaware Valley | PA | Delaware | GEN1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 90 | 1 | 80 | 80 | 20 | N |  |  | OP | X | 4 | 1991 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: MSW; NG PUR PUR PUR: NG; NG NG NG NG: MSW |  |  |  | N | N |  | OVER |  |  |  | N | [19 empty] | N | N | N
Vintage2006 | biomass | TRUE | 12869 | Monterey Regional Waste Mgmt | 10748 | Marina Landfill Gas | CA | Monterey | U1C06 | Landfill Gas | IC |  | S | X | X | CSTRVLLE_1_N |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.8 | N |  |  | OP | X | 5 | 2006 |  |  | N | Commercial Non-CHP | 4 | B T T T: X; NG BLQ BLQ BLQ: LFG |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2018 | biomass | TRUE | 12869 | Monterey Regional Waste Mgmt | 10748 | Marina Landfill Gas | CA | Monterey | U2J18 | Landfill Gas | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.7 | N |  |  | OP | X | 7 | 2018 |  |  | N | Commercial Non-CHP | 4 | B T T T: X; NG BLQ BLQ BLQ: LFG |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage2017 | biomass | TRUE | 12869 | Monterey Regional Waste Mgmt | 10748 | Marina Landfill Gas | CA | Monterey | U3J17 | Landfill Gas | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.5 | N |  |  | OP | X | 8 | 2017 |  |  | N | Commercial Non-CHP | 4 | B T T T: X; NG BLQ BLQ BLQ: LFG | [6 empty] | 10M | [23 empty] | N
Vintage2016 | biomass | TRUE | 12869 | Monterey Regional Waste Mgmt | 10748 | Marina Landfill Gas | CA | Monterey | U4J16 | Landfill Gas | IC |  | S | X | X | CSTRVLLE_N003 |  | 1.4 | 0.8 | 1.2 | 1.2 | 0.7 | N |  |  | OP | X | 7 | 2016 |  |  | N | Commercial Non-CHP | 4 | B T T T: X; NG BLQ BLQ BLQ: LFG |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1993 | natural gas combined cycle | TRUE | 63360 | Camden Plant Holdings LLC | 10751 | Camden Plant Holdings LLC | NJ | Camden | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N | 50476 | 50476 | 95.2 | 0.9 | 145 | 144.7 | 72 | N |  |  | OP | X | 3 | 1993 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1993 | natural gas combined cycle | TRUE | 63360 | Camden Plant Holdings LLC | 10751 | Camden Plant Holdings LLC | NJ | Camden | GEN2 | Natural Gas Fired Combined Cycle | CA | CC1 | W | Y | X | 50476 | 50476 | 77.7 | 0.9 |  |  | 32 | N |  |  | OP | X | 3 | 1993 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1987 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10752 | Lachute Hydro Lower | NY | Essex | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.8 | 1 | 3.6 | 3.5 | 0.1 | N |  |  | OP | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1987 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10753 | Lachute Hydro Upper | NY | Essex | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.2 | 1 | 4.9 | 4.8 | 0.1 | N |  |  | OP | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1987 | natural gas combined cycle | TRUE | 30151 | Tri-State G & T Assn, Inc | 10755 | Rifle Generating Station | CO | Garfield | GT2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 15 | 0.85 | 13 | 15 | 12.4 | N |  |  | OP | X | 8 | 1987 | 10 | 2022 | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1987 | natural gas combined cycle | TRUE | 30151 | Tri-State G & T Assn, Inc | 10755 | Rifle Generating Station | CO | Garfield | GT3 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 15 | 0.85 | 13 | 15 | 12.4 | N |  |  | OP | X | 8 | 1987 | 10 | 2022 | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1987 | natural gas combined cycle | TRUE | 30151 | Tri-State G & T Assn, Inc | 10755 | Rifle Generating Station | CO | Garfield | GT4 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 15 | 0.85 | 13 | 15 | 12.4 | N |  |  | OP | X | 8 | 1987 | 10 | 2022 | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1987 | natural gas combined cycle | TRUE | 30151 | Tri-State G & T Assn, Inc | 10755 | Rifle Generating Station | CO | Garfield | ST1 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X |  |  | 39 | 0.85 | 34 | 34.8 | 24 | N |  |  | OP | X | 8 | 1987 | 10 | 2022 | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1989 | geothermal | TRUE | 49899 | CalEnergy Operating Corporation | 10759 | Salton Sea Power Gen Co - Unit 3 | CA | Imperial | GEN1 | Geothermal | ST |  | W | X | X |  |  | 53.9 | 0.9 | 50 | 50 | 2 | N |  |  | OP | X | 2 | 1989 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: GEO; NG NG NG NG: GEO |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1994 | natural gas combined cycle | TRUE | 13407 | Nevada Power Co | 10761 | Las Vegas Generating Station | NV | Clark | GEN1 | Natural Gas Fired Combined Cycle | CT | CCB1 | S | X | N |  |  | 49.8 | 0.9 | 41 | 43 | 21 | N |  |  | OP | X | 3 | 1994 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1994 | natural gas combined cycle | TRUE | 13407 | Nevada Power Co | 10761 | Las Vegas Generating Station | NV | Clark | GEN2 | Natural Gas Fired Combined Cycle | CA | CCB1 | S | N | X |  |  | 11.5 | 0.9 | 9 | 10 | 5 | N |  |  | OP | X | 4 | 1994 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage2003 | natural gas combined cycle | TRUE | 13407 | Nevada Power Co | 10761 | Las Vegas Generating Station | NV | Clark | GEN3 | Natural Gas Fired Combined Cycle | CT | CCB2 | S | X | Y |  |  | 60.5 | 0.9 | 45 | 47 | 18 | N |  |  | OP | X | 1 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage2003 | natural gas combined cycle | TRUE | 13407 | Nevada Power Co | 10761 | Las Vegas Generating Station | NV | Clark | GEN4 | Natural Gas Fired Combined Cycle | CT | CCB2 | S | X | Y |  |  | 60.5 | 0.9 | 45 | 47 | 18 | N |  |  | OP | X | 1 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage2003 | natural gas combined cycle | TRUE | 13407 | Nevada Power Co | 10761 | Las Vegas Generating Station | NV | Clark | GEN5 | Natural Gas Fired Combined Cycle | CT | CCB3 | S | X | Y |  |  | 60.5 | 0.9 | 45 | 47 | 18 | N |  |  | OP | X | 1 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage2003 | natural gas combined cycle | TRUE | 13407 | Nevada Power Co | 10761 | Las Vegas Generating Station | NV | Clark | GEN6 | Natural Gas Fired Combined Cycle | CT | CCB3 | S | X | Y |  |  | 60.5 | 0.9 | 45 | 47 | 18 | N |  |  | OP | X | 1 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 1H | [23 empty] | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage2003 | natural gas combined cycle | TRUE | 13407 | Nevada Power Co | 10761 | Las Vegas Generating Station | NV | Clark | GEN7 | Natural Gas Fired Combined Cycle | CA | CCB2 | S | N | X |  |  | 27.8 | 0.9 | 26 | 26 | 13 | N |  |  | OP | X | 1 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [23 empty] | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage2003 | natural gas combined cycle | TRUE | 13407 | Nevada Power Co | 10761 | Las Vegas Generating Station | NV | Clark | GEN8 | Natural Gas Fired Combined Cycle | CA | CCB3 | S | N | X |  |  | 27.8 | 0.9 | 26 | 26 | 13 | N |  |  | OP | X | 1 | 2003 |  |  | N | Electric Utility | 1 | [11 empty] | N |  |  | 12H | [23 empty] | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage2007 | geothermal | TRUE | 34691 | Ormat Nevada Inc | 10763 | Ormesa III | CA | Imperial | GBU | Geothermal | BT |  | S | X | X |  |  | 8 | 0.8 | 5.3 | 8 | 5.3 | N |  |  | OP | X | 4 | 2007 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: GEO |  |  |  | N |  |  | OVER | [23 empty] | N
Vintage1989 | geothermal | TRUE | 34691 | Ormat Nevada Inc | 10763 | Ormesa III | CA | Imperial | GEN1 | Geothermal | ST |  | S | X | X |  |  | 21.6 | 0.9 | 14.4 | 21.6 | 14.4 | N |  |  | OS | X | 5 | 1989 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: GEO |  |  |  | N |  |  | OVER | [23 empty] | N
Vintage2020 | geothermal | TRUE | 34691 | Ormat Nevada Inc | 10763 | Ormesa III | CA | Imperial | OE301 | Geothermal | BT |  | S | X | X |  |  | 16 | 0.8 | 10.7 | 16 | 10.7 | N |  |  | OP | X | 4 | 2020 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: GEO |  |  |  | N |  |  | OVER | [23 empty] | N
Vintage1985 | biomass | TRUE | 56120 | Blue Lake Power LLC | 10764 | Blue Lake Power LLC | CA | Humboldt | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 13.8 | 0.85 | 11.5 | 10 | 10 | N |  |  | OS | X | 7 | 1985 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WDS; NG PUR PUR PUR: PG; NG NG NG NG: PG |  |  |  | N | N |  | OVER | [23 empty] | Y | N | N
Vintage1987 | biomass | TRUE | 62815 | Stored Solar J&WE | 10765 | Indeck Jonesboro Energy Center | ME | Washington | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 27.5 | 0.85 | 20.2 | 20.2 | 6 | N |  |  | SB | Y | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WDS; NG NG NG NG: PG |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1987 | biomass | TRUE | 62815 | Stored Solar J&WE | 10766 | Indeck West Enfield Energy Center | ME | Penobscot | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X | UN.ENFLD_ME115 IND5 |  | 27.5 | 0.85 | 20.4 | 21.4 | 6 | N |  |  | OP | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WDS; NG NG NG NG: PG |  |  |  | N | N |  | OVER | [23 empty] | N
Vintage1988 | biomass | TRUE | 15986 | Rio Bravo Fresno | 10767 | Rio Bravo Fresno | CA | Fresno | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X | POD_ULTPFR_1_UNIT 1 APND | POD_ULTPFR_1_UNIT 1 APND | 28 | 0.85 | 24.3 | 24.3 | 12.2 | N |  |  | OP | X | 7 | 1988 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WDS; NG NG NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1992 | biomass | TRUE | 19876 | Virginia Electric & Power Co | 10771 | Hopewell Power Station | VA | Hopewell City | 1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 71.1 | 0.85 | 51 | 51 | 20 | N |  |  | OP | X | 7 | 1992 | 1 | 2028 | N | Electric Utility | 1 | B T T T: X; NG BLQ BLQ BLQ: WDS; NG NG NG NG: NG |  |  |  | N |  |  | 12H |  |  |  |  | N | [18 empty] | N
Vintage1989 | biomass | TRUE | 16077 | Rio Bravo Rocklin | 10772 | Rio Bravo Rocklin | CA | Placer | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 27.9 | 0.85 | 24.4 | 24.4 | 12.2 | N |  |  | OP | X | 6 | 1989 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WDS; NG PUR PUR PUR: NG; NG NG NG NG: NG |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1992 | biomass | TRUE | 19876 | Virginia Electric & Power Co | 10773 | Altavista Power Station | VA | Campbell | 1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 71.1 | 0.85 | 51 | 51 | 20 | N |  |  | OP | X | 2 | 1992 | 1 | 2028 | N | Electric Utility | 1 | B T T T: X; NG BLQ BLQ BLQ: WDS; NG PUR PUR PUR: NG; NG NG NG NG: NG | [6 empty] | 12H |  |  |  |  | N | [18 empty] | N
Vintage1992 | biomass | TRUE | 19876 | Virginia Electric & Power Co | 10774 | Southampton Power Station | VA | Southampton | 1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 71.1 | 0.85 | 51 | 51 | 20 | N |  |  | OP | X | 3 | 1992 | 1 | 2028 | N | Electric Utility | 1 | B T T T: X; NG BLQ BLQ BLQ: WDS; NG NG NG NG: DFO | [6 empty] | 12H |  |  |  |  | N | [18 empty] | N | N
Vintage1990 | natural gas peaker | TRUE | 5533 | EF Oxnard, LLC | 10776 | E F Oxnard Energy Facility | CA | Ventura | GTG | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SNCLRA_6_OXGEN | SNCLRA_6_OXGEN | 48.5 | 0.85 | 48.5 | 48.5 | 29.8 | N |  |  | OP | X | 6 | 1990 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1989 | biomass | TRUE | 56866 | HL Power Company | 10777 | HL Power | CA | Lassen | GEN1 | Wood/Wood Waste Biomass | ST |  | W | X | X |  |  | 36.2 | 0.9 | 30 | 30 | 16 | N |  |  | OP | X | 7 | 1989 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WDS; NG PUR PUR PUR: NG; NG NG NG NG: NG |  |  |  | N | N | 0 | 12H | [23 empty] | Y | N | N
Vintage1983 | hydro | TRUE | 10363 | Koyle Hydro Inc | 10781 | Koyle Ranch Hydroelectric Project | ID | Gooding | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 0.87 | 0.2 | 0.2 | 0.2 | N |  |  | OP | X | 12 | 1983 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1983 | hydro | TRUE | 10363 | Koyle Hydro Inc | 10781 | Koyle Ranch Hydroelectric Project | ID | Gooding | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.9 | 0.3 | 0.3 | 0.3 | N |  |  | OP | X | 12 | 1983 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1983 | hydro | TRUE | 10363 | Koyle Hydro Inc | 10781 | Koyle Ranch Hydroelectric Project | ID | Gooding | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.9 | 0.8 | 0.7 | 0.8 | N |  |  | OP | X | 12 | 1983 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1990 | hard coal | TRUE | 4217 | Colstrip Energy LP | 10784 | Colstrip Energy LP | MT | Rosebud | GEN1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 46.1 | 0.9 | 38 | 40.5 | 23 | N |  |  | OP | X | 2 | 1990 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WC; NG NG NG NG: DFO |  |  |  | N | N |  | OVER | Y |  |  |  | Y | [18 empty] | N | N | N
Vintage1989 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10787 | Piedmont Hydro Power Project | SC | Greenville | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 1 | 1 | 1 | 0.1 | N |  |  | OP | X | 5 | 1989 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT | [5 empty] | 0 | 10M
Vintage1987 | natural gas combined cycle | FALSE | 57160 | Performance Materials NA, Inc. | 10789 | Sabine River Works | TX | Orange | GEN1 | Natural Gas Fired Combined Cycle | CT | CCL1 | S | X | N | EES.CONC | EES.CONC | 89.9 | 0.92 | 82 | 98 | 60 | N |  |  | OP | X | 3 | 1987 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1948 | natural gas combined cycle | FALSE | 57160 | Performance Materials NA, Inc. | 10789 | Sabine River Works | TX | Orange | GEN3 | Natural Gas Fired Combined Cycle | CA | CCL1 | S | Y | X | EES.CONC | EES.CONC | 6.2 | 0.85 | 5 | 5 | 2.5 | N |  |  | OS | X | 1 | 1948 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage2001 | natural gas combined cycle | FALSE | 57160 | Performance Materials NA, Inc. | 10789 | Sabine River Works | TX | Orange | GT1A | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | EES.CONC | EES.CONC | 180 | 0.85 | 160 | 175 | 100 | N |  |  | OP | X | 12 | 2001 |  |  | Y | Industrial CHP | 7 | B T T T: T; NG BLQ BLQ BLQ: NG; NG PUR PUR PUR: OG; NG NG NG NG: NG |  |  |  | N | N |  | OVER | [20 empty] | N |  |  | N | N | N
Vintage2001 | natural gas combined cycle | FALSE | 57160 | Performance Materials NA, Inc. | 10789 | Sabine River Works | TX | Orange | GT1B | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | EES.CONC | EES.CONC | 180 | 0.85 | 160 | 175 | 100 | N |  |  | OP | X | 12 | 2001 |  |  | Y | Industrial CHP | 7 | B T T T: T; NG BLQ BLQ BLQ: NG; NG PUR PUR PUR: OG; NG NG NG NG: NG |  |  |  | N | N |  | OVER | [20 empty] | N |  |  | N | N | N
Vintage2001 | natural gas combined cycle | FALSE | 57160 | Performance Materials NA, Inc. | 10789 | Sabine River Works | TX | Orange | ST1A | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | EES.CONC | EES.CONC | 145 | 0.85 | 100 | 100 | 50 | N |  |  | OP | X | 12 | 2001 |  |  | Y | Industrial CHP | 7 | B T T T: T; NG BLQ BLQ BLQ: NG; NG PUR PUR PUR: OG; NG NG NG NG: NG |  |  |  | N | N | 0 | OVER | [20 empty] | N |  |  | N | N | N
Vintage1987 | natural gas peaker | FALSE | 50006 | Invista | 10790 | Victoria Texas Plant | TX | Victoria | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 102.4 | 0.85 | 75 | 88 | 20 | N |  |  | OP | X | 4 | 1987 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: B T T T to NG BLQ BLQ BLQ; NG NG NG NG
Vintage1993 | natural gas steam turbine | FALSE | 50006 | Invista | 10795 | Camden South Carolina | SC | Kershaw | GEN3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 19 | 0.8 | 17.5 | 18 | 1 | N |  |  | OP | X | 7 | 1993 |  |  | Y | Industrial CHP | 7 | B T T T: B; NG BLQ BLQ BLQ: NG; NG PUR PUR PUR: DFO; NG NG NG NG: NG |  |  |  | N | N |  | 12H |  |  |  |  | N | [18 empty] | Y | Y | Y
Vintage1933 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10798 | Fries Hydroelectric Project | VA | Grayson | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 1 | 2 | 2 | 0.1 | N |  |  | OP | X | 1 | 1933 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT | [5 empty] | 0 | 10M
Vintage1933 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10798 | Fries Hydroelectric Project | VA | Grayson | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 1 | 0.8 | 0.7 | 0.1 | N |  |  | OP | X | 1 | 1933 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT | [5 empty] | 0 | 10M
Vintage1933 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10798 | Fries Hydroelectric Project | VA | Grayson | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 1 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1933 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT | [5 empty] | 0 | 10M
Vintage1981 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10798 | Fries Hydroelectric Project | VA | Grayson | GEN4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 1 | 2 | 2 | 0.1 | N |  |  | OP | X | 1 | 1981 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT | [5 empty] | 0 | 10M
Vintage1989 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10799 | Pelzer Upper | SC | Anderson | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 1 | 1.9 | 1.8 | 0.1 | N |  |  | OP | X | 12 | 1989 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT | [6 empty] | 10M
Vintage1989 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10800 | Pelzer Lower | SC | Anderson | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.3 | 1 | 3.1 | 3 | 0.1 | N |  |  | OP | X | 12 | 1989 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT | [6 empty] | 10M
Vintage1939 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10801 | Ware Shoals Hydro Project | SC | Laurens | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 1 | 3 | 3 | 0.1 | N |  |  | OP | X | 1 | 1939 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT | [5 empty] | 0 | 10M
Vintage1986 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10801 | Ware Shoals Hydro Project | SC | Laurens | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.2 | 1 | 3 | 3 | 0.1 | N |  |  | OP | X | 1 | 1986 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT | [5 empty] | 0 | 10M
Vintage1993 | natural gas steam turbine | TRUE | 40052 | AG Energy LP | 10803 | Ogdensburg Power | NY | St Lawrence | GEN3 | Natural Gas Steam Turbine | ST |  | J | X | X | nyiso | nyiso | 26.9 | 0.9 | 23 | 25 | 5 | N |  |  | OS | X | 10 | 1993 |  |  | Y | IPP CHP | 3 | B T T T: T; NG BLQ BLQ BLQ: NG; NG PUR PUR PUR: DFO; NG NG NG NG: NG |  |  |  | N | N | 0 | 12H | [23 empty] | N |  | N
Vintage1989 | natural gas combined cycle | TRUE | 5530 | E F Kenilworth LLC | 10805 | Kenilworth Energy Facility | NJ | Union | GEN1 | Natural Gas Fired Combined Cycle | CT | G741 | S | X | Y | 50389 Aldene | 50389 Aldene | 22 | 0.8 | 20 | 22 | 12 | N |  |  | OP | X | 3 | 1989 |  |  | Y | IPP CHP | 3 | B T T T: T; NG BLQ BLQ BLQ: NG; NG PUR PUR PUR: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1989 | natural gas combined cycle | TRUE | 5530 | E F Kenilworth LLC | 10805 | Kenilworth Energy Facility | NJ | Union | GEN2 | Natural Gas Fired Combined Cycle | CA | G741 | S | N | X | 50389 Aldene | 50389 Aldene | 6.8 | 0.8 | 4.5 | 5.5 | 1.2 | N |  |  | OP | X | 4 | 1989 |  |  | Y | IPP CHP | 3 | B T T T: B; NG BLQ BLQ BLQ: NG; NG PUR PUR PUR: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1988 | hydro | TRUE | 3490 | Crystal Springs Hydro Elec LP | 10806 | Crystal Springs | ID | Twin Falls | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.3 | 0.95 | 2 | 2 | 0.1 | N |  |  | OP | X | 1 | 1988 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT | [6 empty] | 10M
Vintage1990 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10807 | Dietrich Drop | ID | Lincoln | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.8 | 1 | 4.8 | 4.8 | 0.1 | N |  |  | OP | X | 8 | 1990 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT | [5 empty] | 0 | 10M
Vintage1990 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10808 | Low Line Rapids | ID | Twin Falls | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.8 | 1 | 2.7 | 2.6 | 0.1 | N |  |  | OP | X | 8 | 1990 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT | [5 empty] | 0 | 10M
Vintage1990 | hydro | TRUE | 63985 | Hydroland Omega LLC | 10809 | Rock Creek II | ID | Twin Falls | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.9 | 1 | 1.8 | 1.8 | 0.1 | N |  |  | OP | X | 8 | 1990 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT | [5 empty] | 0 | 10M
Vintage1985 | hydro | TRUE | 5811 | Empire Hydro Partners | 10817 | Port Leyden Hydroelectric Project | NY | Lewis | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.2 | N |  |  | OP | X | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT | [5 empty] | 0 | 12H
Vintage1985 | hydro | TRUE | 5811 | Empire Hydro Partners | 10817 | Port Leyden Hydroelectric Project | NY | Lewis | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.5 | N |  |  | OP | X | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT | [5 empty] | 0 | 12H
Vintage1990 | natural gas combined cycle | TRUE | 64125 | Ada Cogeneration LLC | 10819 | Ada Cogeneration LP | MI | Kent | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 23 | 0.9 | 22 | 23 | 14 | N |  |  | OP | X | 10 | 1990 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1990 | natural gas combined cycle | TRUE | 64125 | Ada Cogeneration LLC | 10819 | Ada Cogeneration LP | MI | Kent | GEN2 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 10.1 | 0.9 | 8 | 9 | 3 | N |  |  | OP | X | 10 | 1990 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: B T T T to NG BLQ BLQ BLQ
Vintage1992 | biomass | TRUE | 3836 | CMS Generation Operating LLC | 10822 | Grayling Generating Station | MI | Crawford | GEN1 | Wood/Wood Waste Biomass | ST |  | J | X | X | cons.grayling & cons.graylgy2 | MISO | 38 | 0.85 | 38 | 38 | 10 | N |  |  | OP | X | 5 | 1992 |  |  | N | IPP Non-CHP | 2 | X | WDS | TDF | NG |  |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1995 | petroleum | FALSE | 11427 | Massachusetts Wtr Rauth-Deer I | 10823 | Deer Island Treatment Plant | MA | Suffolk | G101 | Petroleum Liquids | GT |  | S | X | X |  |  | 26 | 0.9 | 22 | 27 | 8 | N |  |  | SB | Y | 8 | 1995 |  |  | N | Commercial CHP | 5 | B T T T: X; NG BLQ BLQ BLQ: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1995 | petroleum | FALSE | 11427 | Massachusetts Wtr Rauth-Deer I | 10823 | Deer Island Treatment Plant | MA | Suffolk | G201 | Petroleum Liquids | GT |  | S | X | X |  |  | 26 | 0.9 | 22 | 27 | 8 | N |  |  | SB | Y | 8 | 1995 |  |  | N | Commercial CHP | 5 | B T T T: X; NG BLQ BLQ BLQ: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2001 | hydro | FALSE | 11427 | Massachusetts Wtr Rauth-Deer I | 10823 | Deer Island Treatment Plant | MA | Suffolk | H101 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.9 | 1 | 1 | 0.2 | N |  |  | OP | X | 7 | 2001 |  |  | N | Commercial CHP | 5 | B T T T: X; NG BLQ BLQ BLQ: WAT |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage2001 | hydro | FALSE | 11427 | Massachusetts Wtr Rauth-Deer I | 10823 | Deer Island Treatment Plant | MA | Suffolk | H201 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.9 | 1 | 1 | 0.2 | N |  |  | OP | X | 7 | 2001 |  |  | N | Commercial CHP | 5 | B T T T: X; NG BLQ BLQ BLQ: WAT | [6 empty] | 10M | [23 empty] | N
Vintage2008 | solar pv | FALSE | 11427 | Massachusetts Wtr Rauth-Deer I | 10823 | Deer Island Treatment Plant | MA | Suffolk | PV101 | Solar Photovoltaic | PV |  | S | X | X |  |  | 0.1 |  | 0.1 | 0.1 |  | N |  |  | OP | X | 5 | 2008 |  |  | N | Commercial CHP | 5 | B T T T: X; NG BLQ BLQ BLQ: SUN
Vintage1998 | biomass | TRUE | 11427 | Massachusetts Wtr Rauth-Deer I | 10823 | Deer Island Treatment Plant | MA | Suffolk | S101 | Other Waste Biomass | ST |  | S | X | X |  |  | 17.5 | 0.9 | 9 | 17.5 | 1 | N |  |  | OP | X | 7 | 1998 |  |  | Y | Commercial CHP | 5 | B T T T: T; NG BLQ BLQ BLQ: OBG; NG PUR PUR PUR: DFO; NG NG NG NG: DFO | [6 empty] | 12H | [23 empty] | Y | Y | N
Vintage2009 | onshore wind | FALSE | 11427 | Massachusetts Wtr Rauth-Deer I | 10823 | Deer Island Treatment Plant | MA | Suffolk | WT101 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 0.6 |  | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 11 | 2009 |  |  | N | Commercial CHP | 5 | B T T T: X; NG BLQ BLQ BLQ: WND | [5 empty] | 1
Vintage2009 | onshore wind | FALSE | 11427 | Massachusetts Wtr Rauth-Deer I | 10823 | Deer Island Treatment Plant | MA | Suffolk | WT102 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 0.6 |  | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 11 | 2009 |  |  | N | Commercial CHP | 5 | B T T T: X; NG BLQ BLQ BLQ: WND | [5 empty] | 1
Vintage1951 | hydro | TRUE | 11426 | Massachusetts Water Res Auth | 10824 | Oakdale Power Station | MA | Worcester | OAKD | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.5 | 1 | 3 | 3 | 1 | N |  |  | OP | X | 5 | 1951 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage1969 | hydro | TRUE | 11426 | Massachusetts Water Res Auth | 10825 | Cosgrove Intake and Power Station | MA | Worcester | UNI1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 1 | 1 | 1 | 0.8 | N |  |  | OP | X | 1 | 1969 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1969 | hydro | TRUE | 11426 | Massachusetts Water Res Auth | 10825 | Cosgrove Intake and Power Station | MA | Worcester | UNI2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 1 | 1 | 1 | 0.8 | N |  |  | OP | X | 1 | 1969 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1989 | biomass | TRUE | 54806 | DTE Energy Services-Woodland | 10836 | Woodland Biomass Power Ltd | CA | Yolo | GEN1 | Wood/Wood Waste Biomass | ST |  | W | X | X |  |  | 28 | 0.85 | 25 | 25 | 4 | N |  |  | OP | X | 9 | 1989 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WDS; NG PUR PUR PUR: NG; NG NG NG NG: NG |  |  |  | N | N |  | OVER | [23 empty] | N
Vintage1989 | biomass | TRUE | 64893 | Clean Energy Systems Mendota | 10837 | Covanta Mendota | CA | Fresno | GEN1 | Wood/Wood Waste Biomass | ST |  | W | X | X |  |  | 28 | 0.85 | 25 | 25 | 12 | N |  |  | OS | X | 7 | 1989 |  |  | N | Commercial Non-CHP | 4 | B T T T: X; NG BLQ BLQ BLQ: WDS; NG NG NG NG: NG |  |  |  | N |  |  | 12H | [23 empty] | N | N | N
Vintage1987 | biomass | TRUE | 64003 | Stored Solar Services, LLC | 10838 | Stored Solar Springfield, LLC | NH | Sullivan | GEN1 | Wood/Wood Waste Biomass | ST |  | W | X | X | 436 | 436 | 20 | 0.8 | 16.1 | 16.3 | 14 | N |  |  | OP | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WDS; NG NG NG NG: WDS |  |  |  | N | N |  | 12H |  |  | N |  | N | [18 empty] | N
Vintage1988 | biomass | TRUE | 64003 | Stored Solar Services, LLC | 10839 | Stored Solar Whitefield, LLC | NH | Coos | GEN1 | Wood/Wood Waste Biomass | ST |  | W | X | X |  |  | 19.9 | 1 | 17 | 17.5 | 10 | N |  |  | OP | X | 3 | 1988 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WDS; NG NG NG NG: WDS |  |  |  | N | N |  | OVER | [23 empty] | N
Vintage1990 | biomass | TRUE | 64894 | Clean Energy Systems Delano | 10840 | Covanta Delano Energy | CA | Kern | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 31.8 | 0.85 | 27 | 27 | 22 | N |  |  | OS | X | 6 | 1990 |  |  | N | Commercial Non-CHP | 4 | B T T T: X; NG BLQ BLQ BLQ: WDS; NG NG NG NG: NG | [6 empty] | OVER | [23 empty] | N
Vintage1993 | biomass | TRUE | 64894 | Clean Energy Systems Delano | 10840 | Covanta Delano Energy | CA | Kern | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 25.2 | 0.85 | 22 | 22 | 18 | N |  |  | OS | X | 7 | 1993 |  |  | N | Commercial Non-CHP | 4 | B T T T: X; NG BLQ BLQ BLQ: WDS; NG NG NG NG: NG | [6 empty] | OVER | [23 empty] | N
Vintage1986 | hydro | TRUE | 63985 | Hydroland Omega LLC | 10848 | Walden | NY | Orange | GEN1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.2 | 1 | 1.1 | 1.1 | 0.1 | N |  |  | OP | X | 4 | 1986 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1986 | hydro | TRUE | 63985 | Hydroland Omega LLC | 10848 | Walden | NY | Orange | GEN2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.8 | 1 | 0.8 | 0.7 | 0.1 | N |  |  | OP | X | 4 | 1986 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1986 | hydro | TRUE | 63985 | Hydroland Omega LLC | 10848 | Walden | NY | Orange | GEN3 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.4 | 1 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 4 | 1986 |  |  | N | IPP Non-CHP | 2 | B T T T: X; NG BLQ BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1955 | hard coal | FALSE | 3807 | Cleveland Cliffs Inc | 10849 | Silver Bay Power | MN | Lake | GEN1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 50 | 0.8 | 36 | 36 | 10 | N |  |  | OS | X | 10 | 1955 |  |  | Y | Industrial CHP | 7 | B T T T: T; NG BLQ BLQ BLQ: SUB; NG PUR PUR PUR: NG; NG NG NG NG: DFO |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1962 | hard coal | FALSE | 3807 | Cleveland Cliffs Inc | 10849 | Silver Bay Power | MN | Lake | GEN2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 81.6 | 0.85 | 69 | 69 | 10 | N |  |  | OS | X | 1 | 1962 |  |  | Y | Industrial CHP | 7 | B T T T: T; NG BLQ BLQ BLQ: SUB; NG PUR PUR PUR: NG; NG NG NG NG: NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | N | N
Vintage1984 | hydro | FALSE | 8736 | Hollingworth & Vose Co Center Falls | 10853 | Center Falls | NY | Washington | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.3 | 0.4 | 0.1 | N |  |  | OP | X | 1 | 1984 |  |  | N | Industrial Non-CHP | 6 | B T T T: X; NG BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 1H | [20 empty] | N |  |  | N
Vintage1984 | hydro | FALSE | 8736 | Hollingworth & Vose Co Center Falls | 10853 | Center Falls | NY | Washington | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.3 | 0.4 | 0.1 | N |  |  | OP | X | 1 | 1984 |  |  | N | Industrial Non-CHP | 6 | B T T T: X; NG BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 1H | [20 empty] | N |  |  | N
Vintage1984 | hydro | FALSE | 8736 | Hollingworth & Vose Co Center Falls | 10853 | Center Falls | NY | Washington | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.8 | 0.2 | 0.3 | 0.1 | N |  |  | OS | X | 1 | 1984 |  |  | N | Industrial Non-CHP | 6 | B T T T: X; NG BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 1H | [20 empty] | N |  |  | N
Vintage1952 | natural gas steam turbine | FALSE | 3106 | Cargill Inc North America Sweetners | 10855 | Cargill Corn Milling Division | IA | Monroe | GEN1 | Natural Gas Steam Turbine | ST |  | S | X | X | Miso | Miso | 20 | 0.85 | 18.7 | 18.8 | 5 | N |  |  | SB | Y | 12 | 1952 |  |  | Y | Industrial CHP | 7 | B T T T: T; NG BLQ BLQ BLQ: NG; NG NG NG NG: SUB |  |  |  | N | N |  | 12H |  |  |  | N | [19 empty] | N | N | N
Vintage1952 | natural gas steam turbine | FALSE | 3106 | Cargill Inc North America Sweetners | 10855 | Cargill Corn Milling Division | IA | Monroe | GEN2 | Natural Gas Steam Turbine | ST |  | S | X | X | Miso | Miso | 20 | 0.85 | 18 | 18 | 5 | N |  |  | OP | X | 12 | 1952 |  |  | Y | Industrial CHP | 7 | B T T T: T; NG BLQ BLQ BLQ: NG; NG NG NG NG: SUB |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2009 | hard coal | FALSE | 772 | Archer Daniels Midland Co | 10860 | Archer Daniels Midland Clinton | IA | Clinton | 1A | Conventional Steam Coal | ST |  | S | X | X | Sales to Utility only | Sales to Utility only | 75 | 0.85 | 75 | 75 | 0 | N |  |  | OP | X | 2 | 2009 |  |  | Y | Industrial CHP | 7 | T | SUB | OBS | WDS | TDF | BIT | PC | NG |  |  |  | N |  |  | 12H | Y |  |  |  | Y | [18 empty] | Y | Y | N
Vintage2009 | hard coal | FALSE | 772 | Archer Daniels Midland Co | 10860 | Archer Daniels Midland Clinton | IA | Clinton | 2A | Conventional Steam Coal | ST |  | S | X | X | Sales to Utility only | Sales to Utility only | 105 | 0.85 | 105 | 105 | 20 | N |  |  | OP | X | 4 | 2009 |  |  | Y | Industrial CHP | 7 | T | SUB | OBS | WDS | TDF | BIT | PC | NG |  |  |  | N |  |  | 12H | Y |  |  |  | Y | [18 empty] | Y | Y | N
Vintage1988 | hard coal | FALSE | 772 | Archer Daniels Midland Co | 10861 | Archer Daniels Midland Des Moines | IA | Polk | GEN1 | Conventional Steam Coal | ST |  | S | X | X | No sales | No sales | 7.9 | 0.85 | 7.9 | 7.9 | 0.8 | N |  |  | OP | X | 5 | 1988 |  |  | Y | Industrial CHP | 7 | T T T: T; NG SUB SUB: SUB; SUB NG NG: NG |  |  |  | N |  |  | 12H | Y |  |  |  | Y | [18 empty] | N
Vintage1988 | hard coal | FALSE | 772 | Archer Daniels Midland Co | 10862 | Archer Daniels Midland Lincoln | NE | Lancaster | GEN1 | Conventional Steam Coal | ST |  | S | X | X | No sales | No sales | 7.9 | 0.85 | 7.9 | 7.9 | 0.8 | N |  |  | OP | X | 7 | 1988 |  |  | Y | Industrial CHP | 7 | T T T: T; NG SUB SUB: SUB; SUB NG NG: NG |  |  |  | N |  |  | 12H | Y |  |  |  | Y | [18 empty] | N
Vintage1987 | hard coal | FALSE | 772 | Archer Daniels Midland Co | 10863 | Archer Daniels Midland Mankato | MN | Blue Earth | GEN1 | Conventional Steam Coal | ST |  | S | X | X | No sales | No sales | 6.1 | 0.85 | 6.2 | 6.2 | 0.8 | N |  |  | OP | X | 10 | 1987 |  |  | Y | Industrial CHP | 7 | T T T: T; NG SUB SUB: SUB; SUB NG NG: NG |  |  |  | N |  |  | OVER | Y |  |  |  | Y | [18 empty] | N
Vintage1988 | hard coal | FALSE | 772 | Archer Daniels Midland Co | 10864 | Archer Daniels Midland Cedar Rapids | IA | Linn | GEN1 | Conventional Steam Coal | ST |  | S | X | X | Sales to Utility only | Sales to Utility only | 31 | 0.8 | 31 | 31 | 0 | N |  |  | OP | X | 11 | 1988 |  |  | Y | Industrial CHP | 7 | T | SUB | BIT | SLW |  |  |  | NG |  |  |  | N |  |  | 12H | Y |  |  |  | Y | [18 empty] | Y | Y
Vintage1988 | hard coal | FALSE | 772 | Archer Daniels Midland Co | 10864 | Archer Daniels Midland Cedar Rapids | IA | Linn | GEN2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 31 | 0.8 | 31 | 31 | 0 | N |  |  | OP | X | 11 | 1988 |  |  | Y | Industrial CHP | 7 | T | SUB | BIT | SLW |  |  |  | NG |  |  |  | N |  |  | 12H | Y |  |  |  | Y | [18 empty] | Y | Y
Vintage1988 | hard coal | FALSE | 772 | Archer Daniels Midland Co | 10864 | Archer Daniels Midland Cedar Rapids | IA | Linn | GEN3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 31 | 0.8 | 31 | 31 | 0 | N |  |  | OP | X | 11 | 1988 |  |  | Y | Industrial CHP | 7 | T | SUB | BIT | SLW |  |  |  | NG |  |  |  | N |  |  | 12H | Y |  |  |  | Y | [18 empty] | Y | Y
Vintage1988 | hard coal | FALSE | 772 | Archer Daniels Midland Co | 10864 | Archer Daniels Midland Cedar Rapids | IA | Linn | GEN4 | Conventional Steam Coal | ST |  | S | X | X |  |  | 31 | 0.8 | 31 | 31 | 0 | N |  |  | OP | X | 11 | 1988 |  |  | Y | Industrial CHP | 7 | T | SUB | BIT | SLW |  |  |  | NG |  |  |  | N |  |  | 12H | Y |  |  |  | Y | [18 empty] | Y | Y
Vintage1995 | hard coal | FALSE | 772 | Archer Daniels Midland Co | 10864 | Archer Daniels Midland Cedar Rapids | IA | Linn | GEN5 | Conventional Steam Coal | ST |  | S | X | X |  |  | 31 | 0.8 | 31 | 31 | 0 | N |  |  | OP | X | 2 | 1995 |  |  | Y | Industrial CHP | 7 | T | SUB | BIT | SLW |  |  |  | NG |  |  |  | N |  |  | 12H | Y |  |  |  | Y | [18 empty] | Y | Y
Vintage2000 | hard coal | FALSE | 772 | Archer Daniels Midland Co | 10864 | Archer Daniels Midland Cedar Rapids | IA | Linn | GEN6 | Conventional Steam Coal | ST |  | S | X | X |  |  | 101.1 | 0.85 | 105 | 105 | 20 | N |  |  | OP | X | 11 | 2000 |  |  | Y | Industrial CHP | 7 | T | SUB | BIT | SLW |  |  |  | NG |  |  |  | N |  |  | 12H | Y |  |  |  | Y | [18 empty] | Y | Y
Vintage2016 | natural gas peaker | FALSE | 772 | Archer Daniels Midland Co | 10864 | Archer Daniels Midland Cedar Rapids | IA | Linn | GEN7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 38.5 | 0.85 | 35 | 41 | 4 | N |  |  | OP | X | 9 | 2016 |  |  | N | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: T T T to NG SUB SUB
Vintage1987 | hard coal | FALSE | 772 | Archer Daniels Midland Co | 10865 | Archer Daniels Midland Decatur | IL | Macon | GEN2 | Conventional Steam Coal | ST |  | S | X | X | Sales to Utility only | Sales to Utility only | 31 | 0.8 | 31 | 31 | 0 | N |  |  | OP | X | 4 | 1987 |  |  | Y | Industrial CHP | 7 | T | BIT | SUB | TDF | WDS |  |  | NG |  |  |  | N |  |  | 12H | Y | N |  |  | Y | [18 empty] | Y | Y | N
Vintage1987 | hard coal | FALSE | 772 | Archer Daniels Midland Co | 10865 | Archer Daniels Midland Decatur | IL | Macon | GEN3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 31 | 0.8 | 31 | 31 | 0 | N |  |  | OP | X | 4 | 1987 |  |  | Y | Industrial CHP | 7 | T | BIT | SUB | TDF | WDS |  |  | NG |  |  |  | N |  |  | 12H | Y |  |  |  | Y | [18 empty] | Y | Y | N
Vintage1987 | hard coal | FALSE | 772 | Archer Daniels Midland Co | 10865 | Archer Daniels Midland Decatur | IL | Macon | GEN4 | Conventional Steam Coal | ST |  | S | X | X |  |  | 31 | 0.8 | 31 | 31 | 0 | N |  |  | OP | X | 5 | 1987 |  |  | Y | Industrial CHP | 7 | T | BIT | SUB | TDF | WDS |  |  | NG |  |  |  | N |  |  | 12H | Y |  |  |  | Y | [18 empty] | Y | Y | N
Vintage1987 | hard coal | FALSE | 772 | Archer Daniels Midland Co | 10865 | Archer Daniels Midland Decatur | IL | Macon | GEN5 | Conventional Steam Coal | ST |  | S | X | X |  |  | 31 | 0.8 | 31 | 31 | 0 | N |  |  | OP | X | 12 | 1987 |  |  | Y | Industrial CHP | 7 | T | BIT | SUB | TDF | WDS |  |  | NG |  |  |  | N |  |  | 12H | Y |  |  |  | Y | [18 empty] | Y | Y | N
Vintage1994 | hard coal | FALSE | 772 | Archer Daniels Midland Co | 10865 | Archer Daniels Midland Decatur | IL | Macon | GEN6 | Conventional Steam Coal | ST |  | S | X | X |  |  | 31 | 0.8 | 31 | 31 | 0 | N |  |  | OP | X | 9 | 1994 |  |  | Y | Industrial CHP | 7 | T | BIT | SUB | TDF | WDS |  |  | NG |  |  |  | N |  |  | 12H | Y |  |  |  | Y | [18 empty] | Y | Y | N
Vintage1997 | hard coal | FALSE | 772 | Archer Daniels Midland Co | 10865 | Archer Daniels Midland Decatur | IL | Macon | GEN7 | Conventional Steam Coal | ST |  | S | X | X |  |  | 75 | 0.85 | 75 | 75 | 0 | N |  |  | OP | X | 4 | 1997 |  |  | Y | Industrial CHP | 7 | T | BIT | SUB | TDF | WDS |  |  | NG |  |  |  | N |  |  | 12H | Y |  |  |  | Y | [18 empty] | Y | Y | N
Vintage2005 | hard coal | FALSE | 772 | Archer Daniels Midland Co | 10865 | Archer Daniels Midland Decatur | IL | Macon | GEN8 | Conventional Steam Coal | ST |  | S | X | X |  |  | 105 | 0.85 | 105 | 105 | 32 | N |  |  | OP | X | 4 | 2005 |  |  | Y | Industrial CHP | 7 | T | BIT | SUB | TDF | WDS |  |  | NG |  |  |  | N |  |  | 12H | Y |  |  |  | Y | [18 empty] | Y | Y | N
Vintage1988 | natural gas peaker | FALSE | 64580 | BioUrja Renewables LLC | 10866 | Archer Daniels Midland Peoria | IL | Peoria | GEN6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 18 | 0.85 | 15 | 18 | 5 | N |  |  | OP | X | 1 | 1988 |  |  | Y | Industrial CHP | 7 | [11 empty] | N |  |  | 12H |  |  |  |  | N | [18 empty] | N | bar: T T T to NG SUB SUB
Vintage1988 | natural gas peaker | FALSE | 64580 | BioUrja Renewables LLC | 10866 | Archer Daniels Midland Peoria | IL | Peoria | GEN7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 18 | 0.85 | 15 | 18 | 5 | N |  |  | OP | X | 1 | 1988 |  |  | Y | Industrial CHP | 7 | [11 empty] | N |  |  | 12H | [23 empty] | N | bar: T T T to NG SUB SUB
Vintage1989 | natural gas steam turbine | FALSE | 7 | Primary Products Ingredients Americas, LLC | 10867 | Primient Decatur Plant Cogen | IL | Macon | GEN1 | Natural Gas Steam Turbine | ST |  | S | X | X | AMIL WPSE | AMIL WPSE | 64.8 | 0.8 | 62 | 62 | 3 | N |  |  | OP | X | 1 | 1989 |  |  | Y | Industrial CHP | 7 | T T T: T; NG SUB SUB: NG; NG OBS OBS: BIT; SUB NG NG: NG |  |  |  | N | N | 0 | 12H | Y |  |  | N | Y | [18 empty] | N | N | N
Vintage1985 | biomass | TRUE | 1745 | Biomass One LP | 10869 | Biomass One LP | OR | Jackson | BBC | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 10 | 0.8 | 8.5 | 8.5 | 6 | N |  |  | SB | Y | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WDS; SUB NG NG: NG |  |  |  | N | N | 0 | OVER | [20 empty] | N |  |  | N | N | N
Vintage1985 | biomass | TRUE | 1745 | Biomass One LP | 10869 | Biomass One LP | OR | Jackson | GE | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 15 | 0.8 | 14 | 14 | 5 | N |  |  | OP | X | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WDS; SUB NG NG: NG |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | N | N | N
Vintage2009 | biomass | TRUE | 1745 | Biomass One LP | 10869 | Biomass One LP | OR | Jackson | GE-2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 15 | 0.8 | 14 | 14 | 5 | N |  |  | OP | X | 1 | 2009 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WDS; SUB NG NG: NG |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | N | N | N
Vintage1989 | natural gas peaker | TRUE | 56214 | Hazleton Generation LLC | 10870 | Hazelton | PA | Luzerne | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 72.5 | 0.8 | 58.9 | 58.9 | 12 | N |  |  | SB | Y | 1 | 1989 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: NG; NG OBS OBS: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 56214 | Hazleton Generation LLC | 10870 | Hazelton | PA | Luzerne | GEN2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 33 | 0.8 | 28.3 | 29.8 | 12 | N |  |  | SB | Y | 6 | 2002 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: NG; NG OBS OBS: DFO |  |  |  | N | N | 0 | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 56214 | Hazleton Generation LLC | 10870 | Hazelton | PA | Luzerne | GEN3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 33 | 0.8 | 29.3 | 31 | 12 | N |  |  | SB | Y | 6 | 2002 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: NG; NG OBS OBS: DFO |  |  |  | N | N | 0 | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage2002 | natural gas peaker | TRUE | 56214 | Hazleton Generation LLC | 10870 | Hazelton | PA | Luzerne | GEN4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 33 | 0.8 | 29.1 | 31.2 | 12 | N |  |  | SB | Y | 6 | 2002 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: NG; NG OBS OBS: DFO |  |  |  | N | N | 0 | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1988 | hydro | TRUE | 56590 | Silverstreet Hydro | 10872 | Kings Falls Hydroelectric | NY | Lewis | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.95 | 0.2 | 0.1 | 0.1 | N |  |  | OP | X | 10 | 1988 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N |  |  | 10M
Vintage1987 | geothermal | TRUE | 4397 | Coso Operating Co LLC | 10873 | Coso Finance Partners | CA | Inyo | GEN1 | Geothermal | ST |  | S | X | X |  |  | 32.2 | 0.9 | 27.5 | 27.5 | 3 | N |  |  | OP | X | 7 | 1987 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: GEO; SUB NG NG: GEO |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | N | N | N
Vintage1988 | geothermal | TRUE | 4397 | Coso Operating Co LLC | 10873 | Coso Finance Partners | CA | Inyo | GEN2 | Geothermal | ST |  | S | X | X |  |  | 30 | 0.9 | 27 | 27 | 3 | N |  |  | OP | X | 11 | 1988 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: GEO; SUB NG NG: GEO |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | N | N | N
Vintage1988 | geothermal | TRUE | 4397 | Coso Operating Co LLC | 10873 | Coso Finance Partners | CA | Inyo | GEN3 | Geothermal | ST |  | S | X | X |  |  | 30 | 0.9 | 26.7 | 27.2 | 3 | N |  |  | OP | X | 11 | 1988 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: GEO; SUB NG NG: GEO |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | N | N | N
Vintage1989 | geothermal | TRUE | 4397 | Coso Operating Co LLC | 10874 | Coso Power Developers | CA | Inyo | GEN4 | Geothermal | ST |  | S | X | X |  |  | 30 | 0.9 | 30 | 30 | 3 | N |  |  | OP | X | 11 | 1989 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: GEO; SUB NG NG: GEO |  |  |  | N |  |  | 12H | [23 empty] | N | N | N
Vintage1989 | geothermal | TRUE | 4397 | Coso Operating Co LLC | 10874 | Coso Power Developers | CA | Inyo | GEN5 | Geothermal | ST |  | S | X | X |  |  | 30 | 0.9 | 23.4 | 27 | 3 | N |  |  | OP | X | 12 | 1989 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: GEO; SUB NG NG: GEO |  |  |  | N |  |  | 12H | [23 empty] | N | N | N
Vintage1989 | geothermal | TRUE | 4397 | Coso Operating Co LLC | 10874 | Coso Power Developers | CA | Inyo | GEN6 | Geothermal | ST |  | S | X | X |  |  | 30 | 0.9 | 26.9 | 29 | 3 | N |  |  | OP | X | 12 | 1989 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: GEO; SUB NG NG: GEO |  |  |  | N |  |  | 12H | [23 empty] | N | N | N
Vintage1988 | geothermal | TRUE | 4397 | Coso Operating Co LLC | 10875 | Coso Energy Developers | CA | Inyo | GEN7 | Geothermal | ST |  | S | X | X |  |  | 30 | 0.9 | 21.8 | 26.1 | 3 | N |  |  | OP | X | 12 | 1988 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: GEO; SUB NG NG: GEO |  |  |  | N |  |  | 12H | [23 empty] | N | N | N
Vintage1988 | geothermal | TRUE | 4397 | Coso Operating Co LLC | 10875 | Coso Energy Developers | CA | Inyo | GEN8 | Geothermal | ST |  | S | X | X |  |  | 30 | 0.9 | 22.5 | 28.5 | 3 | N |  |  | OP | X | 12 | 1988 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: GEO; SUB NG NG: GEO |  |  |  | N |  |  | 12H | [23 empty] | N | N | N
Vintage1989 | geothermal | TRUE | 4397 | Coso Operating Co LLC | 10875 | Coso Energy Developers | CA | Inyo | GEN9 | Geothermal | ST |  | S | X | X |  |  | 30 | 0.9 | 23.5 | 28.7 | 3 | N |  |  | OP | X | 8 | 1989 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: GEO; SUB NG NG: GEO |  |  |  | N |  |  | 12H | [23 empty] | N | N | N
Vintage1982 | geothermal | TRUE | 49899 | CalEnergy Operating Corporation | 10878 | Salton Sea Power Gen Co Unit 1 | CA | Imperial | EE11 | Geothermal | ST |  | W | X | X |  |  | 10 | 0.9 | 10 | 10 | 2 | N |  |  | OP | X | 7 | 1982 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: GEO; SUB NG NG: GEO |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1990 | geothermal | TRUE | 49899 | CalEnergy Operating Corporation | 10879 | Salton Sea Power Gen Co - Unit 2 | CA | Imperial | GEN1 | Geothermal | ST |  | W | X | X |  |  | 11.5 | 0.9 | 17 | 17 | 2 | N |  |  | OP | X | 3 | 1990 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: GEO; SUB NG NG: GEO |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1990 | geothermal | TRUE | 49899 | CalEnergy Operating Corporation | 10879 | Salton Sea Power Gen Co - Unit 2 | CA | Imperial | GEN2 | Geothermal | ST |  | W | X | X |  |  | 5 | 1 | 4 | 4 | 2 | N |  |  | OP | X | 3 | 1990 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: GEO; SUB NG NG: GEO |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1990 | geothermal | TRUE | 49899 | CalEnergy Operating Corporation | 10879 | Salton Sea Power Gen Co - Unit 2 | CA | Imperial | GEN3 | Geothermal | ST |  | W | X | X |  |  | 3.5 | 0.85 | 2.1 | 2.1 | 1 | N |  |  | OP | X | 3 | 1990 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: GEO; SUB NG NG: GEO |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1987 | hydro | TRUE | 12239 | Mega Renewables | 10880 | Bidwell Ditch Project | CA | Shasta | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 0.95 | 1.8 | 1.8 | 0.2 | N |  |  | OP | X | 3 | 1987 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N |  | 0 | 1H
Vintage1986 | hydro | TRUE | 16997 | Shasta Hydroelectric Inc | 10881 | Roaring Creek Water Power | CA | Shasta | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.95 | 2 | 2 | 0.2 | N |  |  | OP | X | 12 | 1986 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT | [5 empty] | 0 | 1H
Vintage1986 | hydro | TRUE | 12239 | Mega Renewables | 10882 | Hatchet Creek Project | CA | Shasta | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.8 | 0.95 | 6.8 | 6.8 | 0.3 | N |  |  | OP | X | 12 | 1986 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT | [5 empty] | 0 | 10M
Vintage2003 | natural gas peaker | FALSE | 12258 | MATEP LLC | 10883 | Medical Area Total Energy Plant | MA | Suffolk | CT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 12.5 | 0.85 | 12.5 | 12.5 | 6 | N |  |  | OP | X | 12 | 2003 |  |  | Y | Commercial CHP | 5 | T T T: T; NG SUB SUB: NG; NG OBS OBS: DFO |  |  |  | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage2003 | natural gas peaker | FALSE | 12258 | MATEP LLC | 10883 | Medical Area Total Energy Plant | MA | Suffolk | CT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 12.5 | 0.85 | 12.5 | 12.5 | 6 | N |  |  | OP | X | 12 | 2003 |  |  | Y | Commercial CHP | 5 | T T T: T; NG SUB SUB: NG; NG OBS OBS: DFO |  |  |  | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage2017 | natural gas peaker | FALSE | 12258 | MATEP LLC | 10883 | Medical Area Total Energy Plant | MA | Suffolk | CT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 13.8 | 1 | 13.5 | 14.9 | 8 | N |  |  | OP | X | 7 | 2017 |  |  | Y | Commercial CHP | 5 | T T T: T; NG SUB SUB: NG; NG OBS OBS: DFO | [6 empty] | 12H | [23 empty] | Y | N | Y
Vintage1985 | petroleum | FALSE | 12258 | MATEP LLC | 10883 | Medical Area Total Energy Plant | MA | Suffolk | DEG1 | Petroleum Liquids | IC |  | S | X | X |  |  | 6.8 | 0.85 | 6 | 6.7 | 2 | N |  |  | SB | Y | 6 | 1985 |  |  | Y | Commercial CHP | 5 | T T T: T; NG SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1985 | petroleum | FALSE | 12258 | MATEP LLC | 10883 | Medical Area Total Energy Plant | MA | Suffolk | DEG2 | Petroleum Liquids | IC |  | S | X | X |  |  | 6.8 | 0.85 | 6 | 6.7 | 2 | N |  |  | SB | Y | 7 | 1985 |  |  | Y | Commercial CHP | 5 | T T T: T; NG SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1985 | petroleum | FALSE | 12258 | MATEP LLC | 10883 | Medical Area Total Energy Plant | MA | Suffolk | DEG3 | Petroleum Liquids | IC |  | S | X | X |  |  | 6.8 | 0.85 | 6 | 6.7 | 2 | N |  |  | SB | Y | 10 | 1985 |  |  | Y | Commercial CHP | 5 | T T T: T; NG SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1985 | petroleum | FALSE | 12258 | MATEP LLC | 10883 | Medical Area Total Energy Plant | MA | Suffolk | DEG4 | Petroleum Liquids | IC |  | S | X | X |  |  | 6.8 | 0.85 | 6 | 6.7 | 2 | N |  |  | SB | Y | 10 | 1985 |  |  | Y | Commercial CHP | 5 | T T T: T; NG SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1985 | petroleum | FALSE | 12258 | MATEP LLC | 10883 | Medical Area Total Energy Plant | MA | Suffolk | DEG5 | Petroleum Liquids | IC |  | S | X | X |  |  | 6.8 | 0.85 | 6 | 6.7 | 2 | N |  |  | SB | Y | 11 | 1985 |  |  | Y | Commercial CHP | 5 | T T T: T; NG SUB SUB: DFO |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1980 | natural gas steam turbine | FALSE | 12258 | MATEP LLC | 10883 | Medical Area Total Energy Plant | MA | Suffolk | STG2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 11 | 0.85 | 11 | 10.3 | 1 | N |  |  | OP | X | 1 | 1980 |  |  | Y | Commercial CHP | 5 | T T T: T; NG SUB SUB: NG; NG OBS OBS: DFO; SUB NG NG: NG |  |  |  | N |  |  | 12H |  |  |  |  | N | [18 empty] | Y | N | Y
Vintage1980 | natural gas steam turbine | FALSE | 12258 | MATEP LLC | 10883 | Medical Area Total Energy Plant | MA | Suffolk | STG3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 11 | 0.85 | 11 | 10.3 | 1 | N |  |  | OP | X | 1 | 1980 |  |  | Y | Commercial CHP | 5 | T T T: T; NG SUB SUB: NG; NG OBS OBS: DFO; SUB NG NG: NG |  |  |  | N |  |  | 12H |  |  |  |  | N | [18 empty] | Y | N | Y
Vintage1987 | natural gas peaker | FALSE | 11216 | Los Angeles County | 10884 | Olive View Medical Center | CA | Los Angeles | CTC1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 2.8 | 0.9 | 2.7 | 2.7 | 0.5 | N |  |  | OP | X | 2 | 1987 |  |  | Y | Commercial CHP | 5 | T T T: T; NG SUB SUB: NG; NG OBS OBS: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1987 | natural gas peaker | FALSE | 11216 | Los Angeles County | 10884 | Olive View Medical Center | CA | Los Angeles | CTC2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 2.8 | 0.9 | 2.7 | 2.7 | 0.5 | N |  |  | OP | X | 2 | 1987 |  |  | Y | Commercial CHP | 5 | T T T: T; NG SUB SUB: NG; NG OBS OBS: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1986 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 10902 | Victory Mills | NY | Cayuga | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.7 | 1 | 1.6 | 1.6 | 0.1 | N |  |  | OP | X | 12 | 1986 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N |  | 0 | 10M
Vintage1999 | hydro | TRUE | 3473 | Metro Wtr Recl Dist Grtr Chi | 10903 | Lockport Powerhouse | IL | Will | 1GEN | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8 | 1 | 6 | 6 | 2.5 | N |  |  | OA | X | 2 | 1999 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2001 | hydro | TRUE | 3473 | Metro Wtr Recl Dist Grtr Chi | 10903 | Lockport Powerhouse | IL | Will | 2GEN | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8 | 1 | 6 | 6 | 2.5 | N |  |  | OP | X | 12 | 2001 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1990 | natural gas combined cycle | TRUE | 15114 | Pittsfield Generating Company, LP | 50002 | Pittsfield Generating LP | MA | Berkshire | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N | 326 UN.ALTRESCO13.8ALTR | UN.ALTRESCO13.8ALTR | 40.7 | 0.95 | 36.7 | 45 | 25 | N |  |  | OP | X | 7 | 1990 |  |  | Y | IPP CHP | 3 | T T T: T; NG SUB SUB: NG; NG OBS OBS: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1990 | natural gas combined cycle | TRUE | 15114 | Pittsfield Generating Company, LP | 50002 | Pittsfield Generating LP | MA | Berkshire | GEN2 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N | 326 UN.ALTRESCO13.8ALTR | 326 UN.ALTRESCO13.8ALTR | 40.7 | 0.95 | 35.2 | 44.1 | 25 | N |  |  | OP | X | 7 | 1990 |  |  | Y | IPP CHP | 3 | T T T: T; NG SUB SUB: NG; NG OBS OBS: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1990 | natural gas combined cycle | TRUE | 15114 | Pittsfield Generating Company, LP | 50002 | Pittsfield Generating LP | MA | Berkshire | GEN3 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N | 326 UN.ALTRESCO13.8ALTR | 326 UN.ALTRESCO13.8ALTR | 40.7 | 0.95 | 38.2 | 45.2 | 25 | N |  |  | OP | X | 7 | 1990 |  |  | Y | IPP CHP | 3 | T T T: T; NG SUB SUB: NG; NG OBS OBS: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1990 | natural gas combined cycle | TRUE | 15114 | Pittsfield Generating Company, LP | 50002 | Pittsfield Generating LP | MA | Berkshire | GEN4 | Natural Gas Fired Combined Cycle | CA | CC1 | W | N | X | 326 UN.ALTRESCO13.8ALTR | 326 UN.ALTRESCO13.8ALTR | 53.4 | 0.95 | 47.6 | 51.5 | 6 | N |  |  | OP | X | 7 | 1990 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | bar: T T T to NG SUB SUB
Vintage1990 | natural gas peaker | TRUE | 60662 | WCAC Operating Company | 50003 | Chalk Cliff Limited | CA | Kern | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 46 | 0.85 | 46 | 48 | 32 | N |  |  | OP | X | 3 | 1990 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T T T to NG SUB SUB
Vintage1992 | natural gas combined cycle | TRUE | 3890 | EFS Cogen Holdings I LLC | 50006 | Linden Cogen Plant | NJ | Union | GTG1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 95.2 | 0.9 | 98.9 | 102 | 47.6 | N |  |  | OP | X | 3 | 1992 |  |  | Y | IPP CHP | 3 | T T T: T; NG SUB SUB: NG; NG OBS OBS: WO |  |  |  | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage1992 | natural gas combined cycle | TRUE | 3890 | EFS Cogen Holdings I LLC | 50006 | Linden Cogen Plant | NJ | Union | GTG2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 95.2 | 0.9 | 98.9 | 102 | 47.6 | N |  |  | OP | X | 3 | 1992 |  |  | Y | IPP CHP | 3 | T T T: T; NG SUB SUB: NG; NG OBS OBS: WO |  |  |  | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage1992 | natural gas combined cycle | TRUE | 3890 | EFS Cogen Holdings I LLC | 50006 | Linden Cogen Plant | NJ | Union | GTG3 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 95.2 | 0.9 | 98.9 | 102 | 47.6 | N |  |  | OP | X | 4 | 1992 |  |  | Y | IPP CHP | 3 | T T T: T; NG SUB SUB: NG; NG OBS OBS: WO |  |  |  | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage1992 | natural gas combined cycle | TRUE | 3890 | EFS Cogen Holdings I LLC | 50006 | Linden Cogen Plant | NJ | Union | GTG4 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 95.2 | 0.9 | 98.9 | 102 | 47.6 | N |  |  | OP | X | 3 | 1992 |  |  | Y | IPP CHP | 3 | T T T: T; NG SUB SUB: NG; NG OBS OBS: WO |  |  |  | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage1992 | natural gas combined cycle | TRUE | 3890 | EFS Cogen Holdings I LLC | 50006 | Linden Cogen Plant | NJ | Union | GTG5 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 95.2 | 0.9 | 98.9 | 102 | 47.6 | N |  |  | OP | X | 4 | 1992 |  |  | Y | IPP CHP | 3 | T T T: T; NG SUB SUB: NG; NG OBS OBS: WO |  |  |  | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage2002 | natural gas combined cycle | TRUE | 3890 | EFS Cogen Holdings I LLC | 50006 | Linden Cogen Plant | NJ | Union | GTG6 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 212.5 | 0.85 | 160.3 | 174.8 | 90 | N |  |  | OP | X | 1 | 2002 |  |  | Y | IPP CHP | 3 | T T T: T; NG SUB SUB: NG; NG OBS OBS: DFO |  |  |  | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage1992 | natural gas combined cycle | TRUE | 3890 | EFS Cogen Holdings I LLC | 50006 | Linden Cogen Plant | NJ | Union | STG1 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 95.2 | 0.9 | 98.9 | 102.2 | 25 | N |  |  | OP | X | 3 | 1992 |  |  | Y | IPP CHP | 3 | T T T: T; NG SUB SUB: NG; NG OBS OBS: WO |  |  |  | N |  |  | 12H | [23 empty] | N |  | N
Vintage1992 | natural gas combined cycle | TRUE | 3890 | EFS Cogen Holdings I LLC | 50006 | Linden Cogen Plant | NJ | Union | STG2 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 95.2 | 0.9 | 98.9 | 102.2 | 25 | N |  |  | OP | X | 3 | 1992 |  |  | Y | IPP CHP | 3 | T T T: T; NG SUB SUB: NG; NG OBS OBS: WO |  |  |  | N |  |  | 12H | [23 empty] | N |  | N
Vintage1992 | natural gas combined cycle | TRUE | 3890 | EFS Cogen Holdings I LLC | 50006 | Linden Cogen Plant | NJ | Union | STG3 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 95.2 | 0.9 | 98.5 | 102.2 | 25 | N |  |  | OP | X | 4 | 1992 |  |  | Y | IPP CHP | 3 | T T T: T; NG SUB SUB: NG; NG OBS OBS: WO |  |  |  | N |  |  | 12H | [23 empty] | N |  | N
Vintage1912 | hydro | FALSE | 55698 | Hawks Nest Hydro LLC | 50010 | Glen Ferris Hydro | WV | Fayette | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.9 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 1 | 1912 |  |  | N | Industrial Non-CHP | 6 | T T T: X; NG SUB SUB: WAT |  |  |  | N |  | 0 | 10M
Vintage1912 | hydro | FALSE | 55698 | Hawks Nest Hydro LLC | 50010 | Glen Ferris Hydro | WV | Fayette | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.9 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 1 | 1912 |  |  | N | Industrial Non-CHP | 6 | T T T: X; NG SUB SUB: WAT |  |  |  | N |  | 0 | 10M
Vintage1912 | hydro | FALSE | 55698 | Hawks Nest Hydro LLC | 50010 | Glen Ferris Hydro | WV | Fayette | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.9 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 1 | 1912 |  |  | N | Industrial Non-CHP | 6 | T T T: X; NG SUB SUB: WAT |  |  |  | N |  | 0 | 10M
Vintage1912 | hydro | FALSE | 55698 | Hawks Nest Hydro LLC | 50010 | Glen Ferris Hydro | WV | Fayette | GEN4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.9 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 1 | 1912 |  |  | N | Industrial Non-CHP | 6 | T T T: X; NG SUB SUB: WAT |  |  |  | N |  | 0 | 10M
Vintage1912 | hydro | FALSE | 55698 | Hawks Nest Hydro LLC | 50010 | Glen Ferris Hydro | WV | Fayette | GEN5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.9 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 1 | 1912 |  |  | N | Industrial Non-CHP | 6 | T T T: X; NG SUB SUB: WAT |  |  |  | N |  | 0 | 10M
Vintage1912 | hydro | FALSE | 55698 | Hawks Nest Hydro LLC | 50010 | Glen Ferris Hydro | WV | Fayette | GEN6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.9 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 1 | 1912 |  |  | N | Industrial Non-CHP | 6 | T T T: X; NG SUB SUB: WAT |  |  |  | N |  | 0 | 10M
Vintage1917 | hydro | FALSE | 55698 | Hawks Nest Hydro LLC | 50010 | Glen Ferris Hydro | WV | Fayette | GEN7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.9 | 0.9 | 1.9 | 1.9 | 0.7 | N |  |  | OP | X | 1 | 1917 |  |  | N | Industrial Non-CHP | 6 | T T T: X; NG SUB SUB: WAT |  |  |  | N |  | 0 | 10M
Vintage1917 | hydro | FALSE | 55698 | Hawks Nest Hydro LLC | 50010 | Glen Ferris Hydro | WV | Fayette | GEN8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.9 | 0.9 | 1.9 | 1.9 | 0.7 | N |  |  | OP | X | 1 | 1917 |  |  | N | Industrial Non-CHP | 6 | T T T: X; NG SUB SUB: WAT |  |  |  | N |  | 0 | 10M
Vintage1936 | hydro | FALSE | 55698 | Hawks Nest Hydro LLC | 50011 | Hawks Nest Hydro | WV | Fayette | GEN1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 25.5 | 0.9 | 24.2 | 23.5 | 2 | N |  |  | OP | X | 6 | 1936 |  |  | N | Industrial Non-CHP | 6 | T T T: X; NG SUB SUB: WAT |  |  |  | N |  | 0 | 10M
Vintage1936 | hydro | FALSE | 55698 | Hawks Nest Hydro LLC | 50011 | Hawks Nest Hydro | WV | Fayette | GEN2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 25.5 | 0.9 | 24.2 | 23.5 | 2 | N |  |  | OP | X | 6 | 1936 |  |  | N | Industrial Non-CHP | 6 | T T T: X; NG SUB SUB: WAT |  |  |  | N |  | 0 | 10M
Vintage1936 | hydro | FALSE | 55698 | Hawks Nest Hydro LLC | 50011 | Hawks Nest Hydro | WV | Fayette | GEN3 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 25.5 | 0.9 | 24.2 | 23.5 | 2 | N |  |  | OP | X | 6 | 1936 |  |  | N | Industrial Non-CHP | 6 | T T T: X; NG SUB SUB: WAT |  |  |  | N |  | 0 | 10M
Vintage1936 | hydro | FALSE | 55698 | Hawks Nest Hydro LLC | 50011 | Hawks Nest Hydro | WV | Fayette | GEN4 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 25.5 | 0.9 | 24.2 | 23.5 | 2 | N |  |  | OP | X | 6 | 1936 |  |  | N | Industrial Non-CHP | 6 | T T T: X; NG SUB SUB: WAT |  |  |  | N |  | 0 | 10M
Vintage1988 | natural gas peaker | FALSE | 6426 | Flint Hills Resources Corpus Christi LLC | 50026 | Corpus Refinery | TX | Nueces | FR6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 47 | 0.85 | 32 | 41 | 5 | N |  |  | OP | X | 5 | 1988 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: T T T to NG SUB SUB
Vintage1964 | biomass | TRUE | 16064 | Graphic Packaging International | 50028 | Plant 31 Paper Mill | LA | Ouachita | GEN5 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 25 | 0.85 | 25 | 25 | 3 | N |  |  | OP | X | 1 | 1964 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | NG |  |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1977 | biomass | TRUE | 16064 | Graphic Packaging International | 50028 | Plant 31 Paper Mill | LA | Ouachita | GEN6 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 20 | 0.85 | 20 | 20 | 3 | N |  |  | OP | X | 1 | 1977 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | NG |  |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage2016 | natural gas peaker | FALSE | 16064 | Graphic Packaging International | 50028 | Plant 31 Paper Mill | LA | Ouachita | GEN7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 39.2 | 0.92 | 32 | 39 | 26 | N |  |  | OP | X | 2 | 2016 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T T T to NG SUB SUB
Vintage1992 | hydro | TRUE | 63840 | Clear Energy Capital, LLC | 50031 | Mt Ida Hydroelectric | NY | Rensselaer | 3983 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 1 | 1.5 | 1.5 | 0.2 | N |  |  | OP | X | 1 | 1992 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N |  | 0 | 10M
Vintage1992 | hydro | TRUE | 63840 | Clear Energy Capital, LLC | 50031 | Mt Ida Hydroelectric | NY | Rensselaer | 3986 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 1 | 1.5 | 1.5 | 0.2 | N |  |  | OP | X | 1 | 1992 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N |  | 0 | 10M
Vintage1985 | hydro | TRUE | 19774 | Valley Falls Associates | 50034 | Valley Falls Hydroelectric Facility | NY | Rensselaer | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 0.4 | N |  |  | OP | X | 8 | 1985 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT | [5 empty] | 0 | 10M | [23 empty] | N |  | N
Vintage1992 | municipal solid waste | FALSE | 22219 | Maine Waste to Energy | 50035 | MMWAC Resource Recovery Facility | ME | Androscoggin | ST1 | Municipal Solid Waste | ST |  | S | X | X | 4171 | 4171 | 5 | 0.8 | 2.7 | 2.7 | 1.9 | N |  |  | OP | X | 6 | 1992 |  |  | N | Commercial Non-CHP | 4 | T T T: X; NG SUB SUB: MSW; SUB NG NG: NG |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1988 | hydro | TRUE | 4434 | New Martinsville Hannibal Hydro | 50036 | New Martinsville Hannibal Hydro | WV | Wetzel | UNT1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18.7 | 0.95 | 9.5 | 9.5 | 1 | N |  |  | OP | X | 8 | 1988 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1988 | hydro | TRUE | 4434 | New Martinsville Hannibal Hydro | 50036 | New Martinsville Hannibal Hydro | WV | Wetzel | UNT2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18.7 | 0.95 | 9.5 | 9.5 | 1 | N |  |  | OP | X | 7 | 1988 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1989 | hydro | TRUE | 30347 | Olcese Water District | 50037 | Rio Bravo Hydro Project | CA | Kern | UNT1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7 | 0.9 | 6.7 | 6.4 | 1.5 | N |  |  | SB | Y | 5 | 1989 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT | [5 empty] | 0 | 12H
Vintage1989 | hydro | TRUE | 30347 | Olcese Water District | 50037 | Rio Bravo Hydro Project | CA | Kern | UNT2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7 | 0.9 | 6.7 | 6.4 | 1.5 | N |  |  | SB | Y | 6 | 1989 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT | [5 empty] | 0 | 12H
Vintage1939 | natural gas steam turbine | FALSE | 16544 | Saint - Gobain Abrasives Inc | 50041 | Norton Powerhouse | MA | Worcester | GEN1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 0.4 | N |  |  | OP | X | 1 | 1939 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H |  | N | [21 empty] | N | N | N | bar: T T T to NG SUB SUB; SUB NG NG
Vintage1954 | natural gas steam turbine | FALSE | 16544 | Saint - Gobain Abrasives Inc | 50041 | Norton Powerhouse | MA | Worcester | GEN2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 3.1 | 0.8 | 3.1 | 3.1 | 0.4 | N |  |  | OP | X | 1 | 1954 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H |  | N | [21 empty] | N | N | N | bar: T T T to NG SUB SUB; SUB NG NG
Vintage1982 | natural gas combined cycle | FALSE | 14254 | Oxy Vinyls LP | 50043 | Houston Chemical Complex Battleground | TX | Harris | GT1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | DIB | DIB | 104.2 | 0.9 | 66 | 74 | 52 | N |  |  | OP | X | 5 | 1982 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T T T to NG SUB SUB
Vintage1982 | natural gas combined cycle | FALSE | 14254 | Oxy Vinyls LP | 50043 | Houston Chemical Complex Battleground | TX | Harris | GT2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | DIB | DIB | 104.2 | 0.9 | 66 | 74 | 52 | N |  |  | OP | X | 6 | 1982 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T T T to NG SUB SUB
Vintage2005 | natural gas combined cycle | FALSE | 14254 | Oxy Vinyls LP | 50043 | Houston Chemical Complex Battleground | TX | Harris | GT3 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | DIB | DIB | 84.9 | 0.9 | 69 | 78 | 55 | N |  |  | OP | X | 6 | 2005 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T T T to NG SUB SUB
Vintage1982 | natural gas combined cycle | FALSE | 14254 | Oxy Vinyls LP | 50043 | Houston Chemical Complex Battleground | TX | Harris | ST | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | DIB | DIB | 87.4 | 0.85 | 62 | 74 | 25 | N |  |  | OP | X | 8 | 1982 |  |  | Y | Industrial CHP | 7 | T T T: T; NG SUB SUB: NG; NG OBS OBS: OG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1912 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50047 | International Paper Jay Hydro | ME | Franklin | GEN1 | Conventional Hydroelectric | HY |  | W | X | X | 4168 | 4168 | 0.5 | 0.9 | 0.5 | 0.5 | 0.2 | N |  |  | OP | X | 1 | 1912 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 1H
Vintage1912 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50047 | International Paper Jay Hydro | ME | Franklin | GEN2 | Conventional Hydroelectric | HY |  | W | X | X | 4168 | 4168 | 0.5 | 0.9 | 0.5 | 0.5 | 0.2 | N |  |  | OP | X | 1 | 1912 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 1H
Vintage1912 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50047 | International Paper Jay Hydro | ME | Franklin | GEN3 | Conventional Hydroelectric | HY |  | W | X | X | 4168 | 4168 | 0.5 | 0.9 | 0.5 | 0.5 | 0.2 | N |  |  | OP | X | 1 | 1912 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 1H
Vintage1912 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50047 | International Paper Jay Hydro | ME | Franklin | GEN4 | Conventional Hydroelectric | HY |  | W | X | X | 4168 | 4168 | 0.5 | 0.9 | 0.5 | 0.5 | 0.2 | N |  |  | OP | X | 1 | 1912 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 1H
Vintage1912 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50047 | International Paper Jay Hydro | ME | Franklin | GEN5 | Conventional Hydroelectric | HY |  | W | X | X | 4168 | 4168 | 0.5 | 0.9 | 0.5 | 0.5 | 0.2 | N |  |  | OP | X | 1 | 1912 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 1H
Vintage1912 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50047 | International Paper Jay Hydro | ME | Franklin | GEN6 | Conventional Hydroelectric | HY |  | W | X | X | 4168 | 4168 | 0.6 | 0.9 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 1 | 1912 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 1H
Vintage1988 | biomass | TRUE | 60153 | Mendocino Forest Products | 50049 | Humboldt Sawmill Company | CA | Humboldt | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 12.5 | 0.99 | 13 | 13 | 1 | N |  |  | OP | X | 3 | 1988 |  |  | Y | Industrial CHP | 7 | T T T: T; NG SUB SUB: WDS; NG OBS OBS: DFO; SUB NG NG: DFO |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | Y | Y | N
Vintage1988 | biomass | TRUE | 60153 | Mendocino Forest Products | 50049 | Humboldt Sawmill Company | CA | Humboldt | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 12.5 | 0.99 | 13 | 13 | 1 | N |  |  | OP | X | 3 | 1988 |  |  | Y | Industrial CHP | 7 | T T T: T; NG SUB SUB: WDS; NG OBS OBS: DFO; SUB NG NG: DFO |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | Y | Y | N
Vintage1938 | biomass | TRUE | 60153 | Mendocino Forest Products | 50049 | Humboldt Sawmill Company | CA | Humboldt | GEN3 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 7.5 | 0.99 | 7.5 | 7.5 | 1 | N |  |  | OS | X | 1 | 1938 |  |  | N | Industrial CHP | 7 | T T T: X; NG SUB SUB: WDS; NG OBS OBS: DFO; SUB NG NG: DFO |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | Y | Y | N
Vintage1987 | municipal solid waste | FALSE | 6036 | ESOCO Orrington LLC | 50051 | Penobscot Energy Recovery | ME | Penobscot | GEN1 | Municipal Solid Waste | ST |  | J | X | X | MAINE | MAINE | 25.3 | 0.85 | 21.2 | 21.2 | 5 | N |  |  | OP | X | 11 | 1987 |  |  | N | Commercial Non-CHP | 4 | X | MSW | DFO | WDS |  |  |  | DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1986 | natural gas peaker | FALSE | 15941 | Rice University | 50054 | Rice University | TX | Harris | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.1 | 0.98 | 3.1 | 2.8 | 2.8 | N |  |  | SB | N | 1 | 1986 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H |  |  |  | N | [19 empty] | N | N | N | bar: T T T to NG SUB SUB
Vintage1989 | natural gas peaker | FALSE | 15941 | Rice University | 50054 | Rice University | TX | Harris | GEN2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.8 | 0.98 | 3.8 | 3.8 | 3.8 | N |  |  | OP | X | 2 | 1989 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T T T to NG SUB SUB
Vintage1987 | biomass | TRUE | 15380 | Prince George's County | 50060 | Brown Station Road Plant I | MD | Prince Georges | 3972 | Landfill Gas | IC |  | S | X | X | RITCHIE 69 KV PG COGEN |  | 0.9 | 0.8 | 0.8 | 0.8 | 0.4 | N |  |  | OA | X | 10 | 1987 |  |  | N | Commercial Non-CHP | 4 | T T T: X; NG SUB SUB: LFG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1987 | biomass | TRUE | 15380 | Prince George's County | 50060 | Brown Station Road Plant I | MD | Prince Georges | 9314 | Landfill Gas | IC |  | S | X | X | RITCHIE 69 KV PG COGEN |  | 0.9 | 0.8 | 0.8 | 0.8 | 0.4 | N |  |  | OA | X | 10 | 1987 |  |  | N | Commercial Non-CHP | 4 | T T T: X; NG SUB SUB: LFG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1987 | biomass | TRUE | 15380 | Prince George's County | 50060 | Brown Station Road Plant I | MD | Prince Georges | 9340 | Landfill Gas | IC |  | S | X | X | RITCHIE 69 KV PG COGEN |  | 0.9 | 0.8 | 0.8 | 0.8 | 0.4 | N |  |  | OA | X | 10 | 1987 |  |  | N | Commercial Non-CHP | 4 | T T T: X; NG SUB SUB: LFG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2002 | natural gas combined cycle | FALSE | 16625 | San Diego State University | 50061 | San Diego State University | CA | San Diego | GEN2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 5.1 | 1 | 4.6 | 4.8 | 3.4 | N |  |  | OP | X | 9 | 2002 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T T T to NG SUB SUB
Vintage2002 | natural gas combined cycle | FALSE | 16625 | San Diego State University | 50061 | San Diego State University | CA | San Diego | GEN3 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 5.1 | 1 | 4.6 | 4.8 | 3.4 | N |  |  | OP | X | 9 | 2002 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T T T to NG SUB SUB
Vintage2002 | natural gas combined cycle | FALSE | 16625 | San Diego State University | 50061 | San Diego State University | CA | San Diego | GEN4 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 4.1 | 1 | 4.1 | 4.1 | 1 | N |  |  | OP | X | 12 | 2002 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: T T T to NG SUB SUB
Vintage2009 | solar pv | FALSE | 16625 | San Diego State University | 50061 | San Diego State University | CA | San Diego | GEN5 | Solar Photovoltaic | PV |  | S | X | X |  |  | 0.1 |  | 0.1 | 0.1 |  | N |  |  | OP | X | 9 | 2009 |  |  | N | Commercial CHP | 5 | T T T: X; NG SUB SUB: SUN
Vintage2011 | solar pv | FALSE | 16625 | San Diego State University | 50061 | San Diego State University | CA | San Diego | GEN6 | Solar Photovoltaic | PV |  | S | X | X |  |  | 0.3 |  | 0.3 | 0.2 |  | N |  |  | OP | X | 10 | 2011 |  |  | N | Commercial CHP | 5 | T T T: X; NG SUB SUB: SUN
Vintage2012 | solar pv | FALSE | 16625 | San Diego State University | 50061 | San Diego State University | CA | San Diego | GEN7 | Solar Photovoltaic | PV |  | S | X | X |  |  | 0.3 |  | 0.3 | 0.2 |  | N |  |  | OP | X | 4 | 2012 |  |  | N | Commercial CHP | 5 | T T T: X; NG SUB SUB: SUN
Vintage2014 | solar pv | FALSE | 16625 | San Diego State University | 50061 | San Diego State University | CA | San Diego | GEN8 | Solar Photovoltaic | PV |  | S | X | X |  |  | 0.1 |  | 0.1 | 0.1 |  | N |  |  | OP | X | 3 | 2014 |  |  | N | Commercial CHP | 5 | T T T: X; NG SUB SUB: SUN
Vintage2015 | natural gas peaker | FALSE | 22142 | Santa Cruz Cogeneration Assoc | 50064 | Univ of Calif Santa Cruz Cogeneration | CA | Santa Cruz | 003 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 4.4 | 0.9 | 4.4 | 4.4 | 0.5 | N |  |  | OP | X | 7 | 2015 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T T T to NG SUB SUB
Vintage1984 | geothermal | TRUE | 7160 | Geysers Power Co LLC | 50066 | Calistoga Power Plant | CA | Lake | UNT1 | Geothermal | ST |  | S | X | X |  |  | 88.2 | 1 | 50 | 55 | 15 | N |  |  | OP | X | 3 | 1984 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: GEO; SUB NG NG: GEO |  |  |  | N |  |  | 12H | [23 empty] | N | N
Vintage1984 | geothermal | TRUE | 7160 | Geysers Power Co LLC | 50066 | Calistoga Power Plant | CA | Lake | UNT2 | Geothermal | ST |  | S | X | X |  |  | 88.2 | 1 | 50 | 55 | 15 | N |  |  | OP | X | 3 | 1984 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: GEO; SUB NG NG: GEO |  |  |  | N |  |  | 12H | [23 empty] | N | N
Vintage1985 | natural gas steam turbine | FALSE | 17145 | Sid Richardson Carbon Ltd | 50067 | Borger Plant | TX | Hutchinson | GEN1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 37.5 | 0.8 | 27.5 | 27.5 | 2.5 | N |  |  | OP | X | 2 | 1985 |  |  | Y | Industrial CHP | 7 | T T T: T; NG SUB SUB: NG; NG OBS OBS: BFG; SUB NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1989 | municipal solid waste | FALSE | 17445 | Solid Waste Authority of Palm Beach Co | 50071 | Palm Beach Renewable Energy Facility 1 | FL | Palm Beach | GEN1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 62.3 | 0.85 | 50 | 50 | 0 | N |  |  | OP | X | 5 | 1989 |  |  | N | Commercial Non-CHP | 4 | T T T: X; NG SUB SUB: MSW; SUB NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1987 | hydro | TRUE | 19532 | United Water Conservation District | 50076 | Santa Felicia Dam | CA | Ventura | UNT1 | Conventional Hydroelectric | HY |  | S | X | X | GEN | GEN | 0.2 | 0.9 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 6 | 1987 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1987 | hydro | TRUE | 19532 | United Water Conservation District | 50076 | Santa Felicia Dam | CA | Ventura | UNT2 | Conventional Hydroelectric | HY |  | S | X | X | GEN | GEN | 1.1 | 0.9 | 1.1 | 1 | 0.8 | N |  |  | OP | X | 6 | 1987 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1980 | hydro | TRUE | 63985 | Hydroland Omega LLC | 50079 | Goodyear Lake Plant | NY | Otsego | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 1 | 0.8 | 0.7 | 0.1 | N |  |  | OP | X | 8 | 1980 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT | [5 empty] | 0 | 1H
Vintage1980 | hydro | TRUE | 63985 | Hydroland Omega LLC | 50079 | Goodyear Lake Plant | NY | Otsego | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 1 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 8 | 1980 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT | [5 empty] | 0 | 1H
Vintage1985 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50080 | Otis Hydro | ME | Franklin | GEN1 | Conventional Hydroelectric | HY |  | W | X | X | 4168 |  | 5.1 | 0.9 | 5.1 | 5.1 | 2 | N |  |  | OP | X | 1 | 1985 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N |  | 1H
Vintage1985 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50080 | Otis Hydro | ME | Franklin | GEN2 | Conventional Hydroelectric | HY |  | W | X | X | 4168 |  | 5.1 | 0.9 | 5.1 | 5.1 | 2 | N |  |  | OP | X | 1 | 1985 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N |  | 1H
Vintage1981 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50081 | International Paper Riley Hydro | ME | Franklin | GEN1 | Conventional Hydroelectric | HY |  | W | X | X | 4168 |  | 1.1 | 0.85 | 1.1 | 1.1 | 0.8 | N |  |  | OP | X | 12 | 1981 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 1H
Vintage1981 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50081 | International Paper Riley Hydro | ME | Franklin | GEN2 | Conventional Hydroelectric | HY |  | W | X | X | 4168 |  | 1.1 | 0.85 | 1.1 | 1.1 | 0.8 | N |  |  | OP | X | 12 | 1981 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 1H
Vintage1981 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50081 | International Paper Riley Hydro | ME | Franklin | GEN3 | Conventional Hydroelectric | HY |  | W | X | X | 4168 |  | 1.1 | 0.85 | 1.1 | 1.1 | 0.8 | N |  |  | OP | X | 12 | 1981 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 1H
Vintage1981 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50081 | International Paper Riley Hydro | ME | Franklin | GEN4 | Conventional Hydroelectric | HY |  | W | X | X | 4168 |  | 1.1 | 0.85 | 1.1 | 1.1 | 0.8 | N |  |  | OP | X | 12 | 1981 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 1H
Vintage1981 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50081 | International Paper Riley Hydro | ME | Franklin | GEN5 | Conventional Hydroelectric | HY |  | W | X | X | 4168 |  | 1.1 | 0.85 | 1.1 | 1.1 | 0.8 | N |  |  | OP | X | 12 | 1981 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 1H
Vintage1981 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50081 | International Paper Riley Hydro | ME | Franklin | GEN6 | Conventional Hydroelectric | HY |  | W | X | X | 4168 |  | 1.1 | 0.85 | 1.1 | 1.1 | 0.8 | N |  |  | OP | X | 12 | 1981 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 1H
Vintage1910 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50082 | International Paper Livermore Hydro | ME | Androscoggin | GEN1 | Conventional Hydroelectric | HY |  | W | X | X | 4168 | 4168 | 1.1 | 0.9 | 1.1 | 1.1 | 0.4 | N |  |  | OP | X | 1 | 1910 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N |  | 1H
Vintage1910 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50082 | International Paper Livermore Hydro | ME | Androscoggin | GEN2 | Conventional Hydroelectric | HY |  | W | X | X | 4168 | 4168 | 1.1 | 0.9 | 1.1 | 1.1 | 0.4 | N |  |  | OP | X | 1 | 1910 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N |  | 1H
Vintage1910 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50082 | International Paper Livermore Hydro | ME | Androscoggin | GEN3 | Conventional Hydroelectric | HY |  | W | X | X | 4168 | 4168 | 1.1 | 0.9 | 1.1 | 1.1 | 0.4 | N |  |  | OP | X | 1 | 1910 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N |  | 1H
Vintage1910 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50082 | International Paper Livermore Hydro | ME | Androscoggin | GEN4 | Conventional Hydroelectric | HY |  | W | X | X | 4168 | 4168 | 1.2 | 0.9 | 1.2 | 1.2 | 0.4 | N |  |  | OP | X | 1 | 1910 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N |  | 1H
Vintage1910 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50082 | International Paper Livermore Hydro | ME | Androscoggin | GEN5 | Conventional Hydroelectric | HY |  | W | X | X | 4168 | 4168 | 1.1 | 0.9 | 1.1 | 1.1 | 0.4 | N |  |  | OP | X | 1 | 1910 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N |  | 1H
Vintage1910 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50082 | International Paper Livermore Hydro | ME | Androscoggin | GEN6 | Conventional Hydroelectric | HY |  | W | X | X | 4168 | 4168 | 0.7 | 0.9 | 0.7 | 0.7 | 0.4 | N |  |  | OP | X | 1 | 1910 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N |  | 1H
Vintage1910 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50082 | International Paper Livermore Hydro | ME | Androscoggin | GEN7 | Conventional Hydroelectric | HY |  | W | X | X | 4168 | 4168 | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | N |  |  | OP | X | 1 | 1910 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N |  | 1H
Vintage1910 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50082 | International Paper Livermore Hydro | ME | Androscoggin | GEN8 | Conventional Hydroelectric | HY |  | W | X | X | 4168 | 4168 | 1 | 0.9 | 1 | 1 | 0.4 | N |  |  | OP | X | 1 | 1910 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  |  | N |  | 1H
Vintage2004 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50082 | International Paper Livermore Hydro | ME | Androscoggin | GEN9 | Conventional Hydroelectric | HY |  | W | X | X | 4168 | 4168 | 1 | 0.9 | 1 | 0.9 | 0.7 | N |  |  | OP | X | 9 | 2004 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  |  | N |  | 1H
Vintage1974 | natural gas steam turbine | FALSE | 23955 | University of Massachusetts Medical | 50087 | Univ of Massachusetts Medical Center | MA | Worcester | GEN1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 2.5 | 0.8 | 1.5 | 1.5 | 0.5 | N |  |  | OP | X | 4 | 1974 |  |  | Y | Commercial CHP | 5 | T T T: B; NG SUB SUB: NG; NG OBS OBS: RFO; SUB NG NG: NG | RFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1974 | natural gas steam turbine | FALSE | 23955 | University of Massachusetts Medical | 50087 | Univ of Massachusetts Medical Center | MA | Worcester | GEN2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 2.5 | 0.8 | 1.5 | 1.5 | 0.5 | N |  |  | OP | X | 4 | 1974 |  |  | Y | Commercial CHP | 5 | T T T: B; NG SUB SUB: NG; NG OBS OBS: RFO; SUB NG NG: NG | RFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas steam turbine | FALSE | 23955 | University of Massachusetts Medical | 50087 | Univ of Massachusetts Medical Center | MA | Worcester | GEN3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 5 | 0.9 | 3 | 3 | 1.5 | N |  |  | OP | X | 6 | 2002 |  |  | Y | Commercial CHP | 5 | T T T: B; NG SUB SUB: NG; NG OBS OBS: RFO; SUB NG NG: NG | RFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2013 | natural gas peaker | FALSE | 23955 | University of Massachusetts Medical | 50087 | Univ of Massachusetts Medical Center | MA | Worcester | GEN4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 7.5 | 0.9 | 6 | 7.5 | 4.5 | N |  |  | OP | X | 2 | 2013 |  |  | N | Commercial CHP | 5 | T T T: X; NG SUB SUB: NG; NG OBS OBS: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1982 | natural gas steam turbine | FALSE | 21223 | University of Northern Iowa | 50088 | University of Northern Iowa | IA | Black Hawk | GEN1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 7.5 | 0.85 | 7.5 | 7.5 | 2.6 | N |  |  | OP | X | 11 | 1982 |  |  | Y | Commercial CHP | 5 | B | NG | PC | BIT | DFO |  |  | DFO |  |  |  | N | N | 0 | 12H | Y | Y |  |  | Y | [15 empty] | N |  |  | Y | Y | Y
Vintage1987 | natural gas peaker | FALSE | 24010 | University of San Francisco | 50089 | Univ of San Francisco Cogen | CA | San Francisco | S-17 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.4 | 1.4 | 1 | N |  |  | OP | X | 9 | 1987 |  |  | Y | Commercial CHP | 5 | [11 empty] | N |  |  | 1H | [23 empty] | N | N | N | bar: T T T to NG SUB SUB
Vintage1986 | hydro | TRUE | 16990 | Sheep Creek Hydro Inc | 50091 | Sheep Creek Hydro | WA | Stevens | TB1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 0.8 | 0.4 | N |  |  | OP | X | 6 | 1986 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1986 | hydro | TRUE | 16990 | Sheep Creek Hydro Inc | 50091 | Sheep Creek Hydro | WA | Stevens | TB2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.2 | 0.1 | N |  |  | SB | Y | 6 | 1986 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1988 | hydro | TRUE | 63985 | Hydroland Omega LLC | 50093 | Chateaugay High Falls Hydro | NY | Franklin | WT | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.7 | 1 | 1.6 | 1.6 | 0.1 | N |  |  | OP | X | 12 | 1988 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT | [5 empty] | 0 | 10M
Vintage1983 | natural gas peaker | FALSE | 19148 | Vicinity Energy Trenton, L.P. | 50094 | Vicinity Energy Trenton, L.P. | NJ | Mercer | 7214 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 6 | 0.8 | 5.8 | 5.8 | 2.8 | N |  |  | OP | X | 12 | 1983 |  |  | Y | Commercial CHP | 5 | T T T: T; NG SUB SUB: NG; NG OBS OBS: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1983 | biomass | TRUE | 18461 | Tamarack Energy | 50099 | Tamarack Energy Partnership | ID | Adams | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 6.2 | 0.8 | 5.8 | 6.2 | 3 | N |  |  | OP | X | 6 | 1983 |  |  | Y | IPP CHP | 3 | T T T: T; NG SUB SUB: WDS; SUB NG NG: WDS |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1954 | biomass | TRUE | 12307 | WestRock (TX) | 50101 | WestRock (TX) | TX | Jasper | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 7.5 | 0.95 | 9.5 | 9.5 | 4.8 | N |  |  | OP | X | 6 | 1954 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | NG |  |  |  | WDS | NG |  |  | N | N |  | 12H |  |  | N | [20 empty] | Y | Y | N
Vintage1965 | biomass | TRUE | 12307 | WestRock (TX) | 50101 | WestRock (TX) | TX | Jasper | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 32.6 | 0.95 | 32 | 33 | 16.3 | N |  |  | OP | X | 5 | 1965 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | NG |  |  |  | WDS | NG |  |  | N | N |  | 12H |  |  | N | [20 empty] | Y | Y | N
Vintage1986 | biomass | TRUE | 12307 | WestRock (TX) | 50101 | WestRock (TX) | TX | Jasper | GEN3 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 17.6 | 0.95 | 18 | 18 | 10 | N |  |  | OP | X | 1 | 1986 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | NG |  |  |  | WDS | NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1981 | hydro | TRUE | 13442 | New Hampshire Hydro Associates | 50103 | China Mill Hydro | NH | Merrimack | GEN 1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.7 | 0.8 | 1.7 | 1.7 | 0 | N |  |  | OP | X | 7 | 1981 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1989 | natural gas combined cycle | TRUE | 54700 | Paris Generation LP | 50109 | Paris Energy Center | TX | Lamar | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | TNSKA_CC1 | TNSKA_CC1 | 87.8 | 0.85 | 78 | 91 | 40 | N |  |  | OP | X | 7 | 1989 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: NG; NG OBS OBS: DFO; SUB NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1989 | natural gas combined cycle | TRUE | 54700 | Paris Generation LP | 50109 | Paris Energy Center | TX | Lamar | GEN2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | TNSKA_CC1 | TNSKA_CC1 | 87.8 | 0.85 | 80 | 94 | 40 | N |  |  | OP | X | 7 | 1989 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: NG; NG OBS OBS: DFO; SUB NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1989 | natural gas combined cycle | TRUE | 54700 | Paris Generation LP | 50109 | Paris Energy Center | TX | Lamar | GEN3 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | TNSKA_CC1 | TNSKA_CC1 | 90 | 0.85 | 78 | 90 | 20 | N |  |  | OP | X | 12 | 1989 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T T T to NG SUB SUB
Vintage1986 | biomass | TRUE | 17164 | Sierra Pacific Industries | 50110 | Sierra Pacific Burney Facility | CA | Shasta | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X | SPI-BURN_7_N003 | SPI-BURN_7_N003 | 20 | 0.85 | 18.9 | 17.9 | 1 | N |  |  | OP | X | 10 | 1986 |  |  | Y | Industrial CHP | 7 | T T T: T; NG SUB SUB: WDS; SUB NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage2018 | biomass | TRUE | 17164 | Sierra Pacific Industries | 50112 | Sierra Pacific Quincy Facility | CA | Plumas | GEN3 | Wood/Wood Waste Biomass | ST |  | S | X | X | SPI-QUCY_7_N002 | SPI-QUCY_7_N002 | 35.2 | 0.9 | 24 | 24 | 3.2 | N |  |  | OP | X | 5 | 2018 |  |  | N | Industrial Non-CHP | 6 | T T T: X; NG SUB SUB: WDS; NG OBS OBS: DFO; SUB NG NG: DFO |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1984 | natural gas peaker | FALSE | 22669 | U S Borax Inc | 50115 | US Borax | CA | Kern | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 48.2 | 0.85 | 39 | 42 | 39 | N |  |  | OP | X | 7 | 1984 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T T T to NG SUB SUB; SUB NG NG
Vintage2010 | natural gas combined cycle | FALSE | 19537 | University of Texas at Austin | 50118 | Hal C Weaver Power Plant | TX | Travis | GEN10 | Natural Gas Fired Combined Cycle | CT | HCWP | S | X | N |  |  | 34.4 | 0.8 | 33 | 32.5 | 21 | N |  |  | OP | X | 3 | 2010 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H |  |  |  |  | N | [18 empty] | N |  | N | bar: T T T to NG SUB SUB
Vintage1951 | natural gas combined cycle | FALSE | 19537 | University of Texas at Austin | 50118 | Hal C Weaver Power Plant | TX | Travis | GEN4 | Natural Gas Fired Combined Cycle | CA | HCWP | S | Y | X |  |  | 7.6 | 0.8 | 7.6 | 7.6 | 2 | N |  |  | SB | Y | 10 | 1951 |  |  | Y | Commercial CHP | 5 | T T T: T; NG SUB SUB: NG; NG OBS OBS: DFO |  |  |  | N | N |  | 12H |  |  |  |  | N | [18 empty] | Y | N | Y
Vintage1959 | natural gas combined cycle | FALSE | 19537 | University of Texas at Austin | 50118 | Hal C Weaver Power Plant | TX | Travis | GEN5 | Natural Gas Fired Combined Cycle | CA | HCWP | S | Y | X |  |  | 6 | 0.8 | 6 | 6 | 2 | N |  |  | SB | Y | 9 | 1959 |  |  | Y | Commercial CHP | 5 | T T T: T; NG SUB SUB: NG; NG OBS OBS: DFO |  |  |  | N | N |  | 12H |  |  |  |  | N | [18 empty] | Y | N | Y
Vintage1979 | natural gas combined cycle | FALSE | 19537 | University of Texas at Austin | 50118 | Hal C Weaver Power Plant | TX | Travis | GEN7 | Natural Gas Fired Combined Cycle | CA | HCWP | S | Y | X |  |  | 28.8 | 0.8 | 27.6 | 27.2 | 12.5 | N |  |  | SB | Y | 1 | 1979 |  |  | Y | Commercial CHP | 5 | T T T: T; NG SUB SUB: NG; NG OBS OBS: DFO |  |  |  |  | N |  | 12H |  |  |  |  | N | [18 empty] | Y | N | Y
Vintage1987 | natural gas combined cycle | FALSE | 19537 | University of Texas at Austin | 50118 | Hal C Weaver Power Plant | TX | Travis | GEN8 | Natural Gas Fired Combined Cycle | CT | HCWP | S | X | N |  |  | 48.5 | 0.8 | 46.5 | 45.8 | 23 | N |  |  | OP | X | 11 | 1987 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 12H |  |  |  |  | N | [18 empty] | N |  | N | bar: T T T to NG SUB SUB
Vintage2004 | natural gas combined cycle | FALSE | 19537 | University of Texas at Austin | 50118 | Hal C Weaver Power Plant | TX | Travis | GEN9 | Natural Gas Fired Combined Cycle | CA | HCWP | S | Y | X |  |  | 27.2 | 0.8 | 26.1 | 25.7 | 11 | N |  |  | OP | X | 11 | 2004 |  |  | Y | Commercial CHP | 5 | T T T: T; NG SUB SUB: NG; NG OBS OBS: DFO |  |  |  | N | N |  | 12H |  |  |  |  | N | [18 empty] | Y | N | Y
Vintage1987 | other | FALSE | 4208 | Phillips 66 Company | 50119 | Phillips 66 Rodeo Refinery | CA | Contra Costa | GENA | Other Gases | GT |  | S | X | X |  |  | 18.3 | 0.85 | 15.3 | 16.5 | 12 | N |  |  | OP | X | 5 | 1987 |  |  | Y | Industrial CHP | 7 | T T T: T; NG SUB SUB: OG; NG OBS OBS: NG |  |  |  | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage1987 | other | FALSE | 4208 | Phillips 66 Company | 50119 | Phillips 66 Rodeo Refinery | CA | Contra Costa | GENB | Other Gases | GT |  | S | X | X |  |  | 18.3 | 0.85 | 15.4 | 16.6 | 12 | N |  |  | OP | X | 5 | 1987 |  |  | Y | Industrial CHP | 7 | T T T: T; NG SUB SUB: OG; NG OBS OBS: NG |  |  |  | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage1987 | other | FALSE | 4208 | Phillips 66 Company | 50119 | Phillips 66 Rodeo Refinery | CA | Contra Costa | GENC | Other Gases | GT |  | S | X | X |  |  | 18.3 | 0.85 | 14.9 | 16.4 | 12 | N |  |  | OP | X | 5 | 1987 |  |  | Y | Industrial CHP | 7 | T T T: T; NG SUB SUB: OG; NG OBS OBS: NG |  |  |  | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage1983 | other | FALSE | 19685 | Valero Refining Co | 50121 | Valero Refinery Corpus Christi West | TX | Nueces | PRU | All Other | ST | TG | S | X | X |  |  | 12 | 1 | 12 | 12 | 0 | N |  |  | OP | X | 9 | 1983 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: T T T to NG SUB SUB; SUB NG NG
Vintage1983 | petroleum | FALSE | 19685 | Valero Refining Co | 50121 | Valero Refinery Corpus Christi West | TX | Nueces | TG1 | Petroleum Coke | ST | TG | S | X | X |  |  | 28.6 | 0.8 | 26.6 | 26.9 | 5 | N |  |  | OP | X | 11 | 1983 |  |  | N | Industrial Non-CHP | 6 | X | PC | OG | NG |  |  |  | WH |  |  |  | N | N |  | 12H | Y |  |  |  |  | Y | [17 empty] | N
Vintage1983 | petroleum | FALSE | 19685 | Valero Refining Co | 50121 | Valero Refinery Corpus Christi West | TX | Nueces | TG2 | Petroleum Coke | ST | TG | S | X | X |  |  | 28.6 | 0.8 | 26.6 | 26.9 | 5 | N |  |  | OP | X | 11 | 1983 |  |  | N | Industrial Non-CHP | 6 | X | PC | OG | NG |  |  |  | WH |  |  |  | N | N |  | 12H | Y |  |  |  |  | Y | [17 empty] | N
Vintage1983 | hydro | TRUE | 20148 | Watervliet City of | 50123 | Normanskill Hydro Project | NY | Albany | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 1 | 1.2 | 1.2 | 0.5 | N |  |  | OP | X | 4 | 1983 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 10M
Vintage1987 | hydro | TRUE | 7601 | Green Mountain Power Corp | 50126 | Ottauquechee Hydro | VT | Windsor | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 1 | 1.1 | 1.1 | 0.1 | N |  |  | OP | X | 7 | 1987 |  |  | N | Electric Utility | 1 | T T T: X; NG SUB SUB: WAT |  |  |  | N |  |  | 10M
Vintage1983 | hydro | TRUE | 7601 | Green Mountain Power Corp | 50126 | Ottauquechee Hydro | VT | Windsor | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 1 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 4 | 1983 |  |  | N | Electric Utility | 1 | T T T: X; NG SUB SUB: WAT |  |  |  | N |  | 0 | 10M
Vintage1987 | natural gas combined cycle | TRUE | 54777 | Signal Hill Generating LLC | 50127 | Signal Hill Generating LLC | TX | Wichita | GTA | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y | WFCOGEN_CC1 | WFCOGEN_CC1 | 20 | 0.8 | 19.7 | 19.7 | 2 | N |  |  | OP | X | 6 | 1987 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T T T to NG SUB SUB
Vintage1987 | natural gas combined cycle | TRUE | 54777 | Signal Hill Generating LLC | 50127 | Signal Hill Generating LLC | TX | Wichita | GTB | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y | WFCOGEN_CC1 | WFCOGEN_CC1 | 20 | 0.8 | 19.7 | 19.7 | 2 | N |  |  | OP | X | 6 | 1987 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T T T to NG SUB SUB
Vintage1987 | natural gas combined cycle | TRUE | 54777 | Signal Hill Generating LLC | 50127 | Signal Hill Generating LLC | TX | Wichita | GTC | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y | WFCOGEN_CC1 | WFCOGEN_CC1 | 20 | 0.8 | 19.7 | 19.7 | 2 | N |  |  | OP | X | 6 | 1987 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T T T to NG SUB SUB
Vintage1987 | natural gas combined cycle | TRUE | 54777 | Signal Hill Generating LLC | 50127 | Signal Hill Generating LLC | TX | Wichita | STD | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X | WFCOGEN_CC1 | WFCOGEN_CC1 | 20 | 0.8 | 17 | 16 | 2 | N |  |  | OP | X | 6 | 1987 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N | 0 | 12H | [23 empty] | N | N | N | bar: T T T to NG SUB SUB
Vintage1985 | hydro | TRUE | 22079 | Yolo County Flood Control WCD | 50128 | Clear Lake Hydro Project | CA | Lake | 3381 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 1 | 2.4 | 2.3 |  | N |  |  | OS | X | 9 | 1985 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1983 | hydro | TRUE | 22079 | Yolo County Flood Control WCD | 50129 | Indian Valley Dam Hydro Project | CA | Lake | 1641 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.4 | 0.8 | 1.3 | 1.3 | 1 | N |  |  | SB | Y | 10 | 1983 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1983 | hydro | TRUE | 22079 | Yolo County Flood Control WCD | 50129 | Indian Valley Dam Hydro Project | CA | Lake | 1642 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.4 | 0.8 | 1.3 | 1.3 | 1 | N |  |  | SB | Y | 10 | 1983 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1983 | hydro | TRUE | 22079 | Yolo County Flood Control WCD | 50129 | Indian Valley Dam Hydro Project | CA | Lake | 8332 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.1 | 0.88 | 0.1 | 0.1 | 0.1 | N |  |  | SB | Y | 10 | 1983 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1991 | natural gas peaker | TRUE | 3852 | Coalinga Cogeneration Co | 50131 | Coalinga Cogeneration | CA | Fresno | K100 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 38.4 | 1 | 36 | 38 | 36 | N |  |  | OS | X | 10 | 1991 |  |  | Y | IPP CHP | 3 | [14 empty] | 10M | [23 empty] | N | N | bar: T T T to NG SUB SUB
Vintage1987 | natural gas peaker | TRUE | 18390 | Sycamore Cogeneration Co | 50134 | Sycamore Cogeneration | CA | Kern | GTAG | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 75 | 1 | 75 | 78 | 70 | N |  |  | OP | X | 12 | 1987 |  |  | Y | IPP CHP | 3 | [11 empty] | N |  |  | 10M | [23 empty] | N | N | bar: T T T to NG SUB SUB
Vintage1987 | natural gas peaker | TRUE | 18390 | Sycamore Cogeneration Co | 50134 | Sycamore Cogeneration | CA | Kern | GTBG | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 75 | 1 | 75 | 78 | 70 | N |  |  | OP | X | 12 | 1987 |  |  | Y | IPP CHP | 3 | [11 empty] | N |  |  | 10M | [23 empty] | N | N | bar: T T T to NG SUB SUB
Vintage1987 | natural gas peaker | TRUE | 18390 | Sycamore Cogeneration Co | 50134 | Sycamore Cogeneration | CA | Kern | GTCG | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 75 | 1 | 75 | 78 | 70 | N |  |  | OP | X | 12 | 1987 |  |  | Y | IPP CHP | 3 | [11 empty] | N |  |  | 10M | [23 empty] | N | N | bar: T T T to NG SUB SUB
Vintage1987 | natural gas peaker | TRUE | 18390 | Sycamore Cogeneration Co | 50134 | Sycamore Cogeneration | CA | Kern | GTDG | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 75 | 1 | 75 | 78 | 70 | N |  |  | OP | X | 12 | 1987 |  |  | Y | IPP CHP | 3 | [11 empty] | N |  |  | 10M | [23 empty] | N | bar: T T T to NG SUB SUB
Vintage2008 | natural gas peaker | FALSE | 17460 | South Oak Hospital | 50136 | South Oaks Hospital | NY | Suffolk | CG1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.2 | 1 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 4 | 2008 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: T T T to NG SUB SUB
Vintage2008 | natural gas peaker | FALSE | 17460 | South Oak Hospital | 50136 | South Oaks Hospital | NY | Suffolk | CG2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.2 | 1 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 4 | 2008 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: T T T to NG SUB SUB
Vintage2008 | natural gas peaker | FALSE | 17460 | South Oak Hospital | 50136 | South Oaks Hospital | NY | Suffolk | CG3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.2 | 1 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 4 | 2008 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: T T T to NG SUB SUB
Vintage2008 | natural gas peaker | FALSE | 17460 | South Oak Hospital | 50136 | South Oaks Hospital | NY | Suffolk | CG4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.2 | 1 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 4 | 2008 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: T T T to NG SUB SUB
Vintage2008 | natural gas peaker | FALSE | 17460 | South Oak Hospital | 50136 | South Oaks Hospital | NY | Suffolk | CG5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.2 | 1 | 0.1 | 0.1 | 0.1 | N |  |  | OP | X | 4 | 2008 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: T T T to NG SUB SUB
Vintage1983 | biomass | TRUE | 27211 | Snider Industries Inc | 50141 | Snider Industries | TX | Harrison | WGN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 5 | 0.8 | 5 | 5 | 1 | N |  |  | OP | X | 8 | 1983 |  |  | Y | Industrial CHP | 7 | T T T: B; NG SUB SUB: WDS; SUB NG NG: WDS |  |  |  | Y | N | 0 | 12H | [23 empty] | N
Vintage1948 | natural gas steam turbine | FALSE | 27131 | Imperial Savannah LP | 50146 | Imperial Savannah LP | GA | Chatham | GENA | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 2.7 | 0.8 | 2.7 | 2.7 | 0.5 | N |  |  | OP | X | 3 | 1948 |  |  | Y | Industrial CHP | 7 | T T T: T; NG SUB SUB: NG; NG OBS OBS: BIT; SUB NG NG: NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1959 | natural gas steam turbine | FALSE | 27131 | Imperial Savannah LP | 50146 | Imperial Savannah LP | GA | Chatham | GENB | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 0.5 | N |  |  | OP | X | 2 | 1959 |  |  | Y | Industrial CHP | 7 | T T T: T; NG SUB SUB: NG; NG OBS OBS: BIT; SUB NG NG: NG |  |  |  | N | N |  | 12H | N | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1946 | natural gas steam turbine | FALSE | 27131 | Imperial Savannah LP | 50146 | Imperial Savannah LP | GA | Chatham | GENC | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.3 | N |  |  | OP | X | 8 | 1946 |  |  | Y | Industrial CHP | 7 | T T T: T; NG SUB SUB: NG; NG OBS OBS: BIT; SUB NG NG: NG |  |  |  | N | N |  | 12H | N | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1985 | natural gas steam turbine | FALSE | 27131 | Imperial Savannah LP | 50146 | Imperial Savannah LP | GA | Chatham | GEND | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 5 | 1 | 4.5 | 4.5 | 1 | N |  |  | OP | X | 3 | 1985 |  |  | Y | Industrial CHP | 7 | T T T: T; NG SUB SUB: NG; NG OBS OBS: BIT; SUB NG NG: NG |  |  |  | N | N |  | 12H | N | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1987 | hydro | TRUE | 16713 | Santa Fe Irrigation District | 50147 | R E Badger Filtration Plant | CA | San Diego | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.4 | 0.8 | 1 | 0.5 | 0.5 | N |  |  | OP | X | 7 | 1987 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N |  | 0 | 1H
Vintage1988 | natural gas combined cycle | FALSE | 15320 | Linde Inc | 50148 | Linde Wilmington | CA | Los Angeles | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y | LADWP | LADWP | 25 | 0.9 | 21 | 21 | 18 | N |  |  | SB | Y | 12 | 1988 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | bar: T T T to NG SUB SUB
Vintage1988 | natural gas combined cycle | FALSE | 15320 | Linde Inc | 50148 | Linde Wilmington | CA | Los Angeles | GEN2 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 6 | 0.9 | 6 | 6 | 4 | N |  |  | SB | Y | 12 | 1988 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | bar: T T T to NG SUB SUB
Vintage1964 | natural gas steam turbine | FALSE | 19450 | Union Carbide Corp-Seadrift | 50150 | Union Carbide Seadrift Cogen | TX | Calhoun | GE10 | Natural Gas Steam Turbine | ST | G621 | S | X | X | UCC_COG_PUN1 | ERCOT SOUTH ZONE | 15 | 0.85 | 15 | 15 | 2 | N |  |  | OP | X | 1 | 1964 |  |  | Y | Industrial CHP | 7 | T T T: B; NG SUB SUB: NG; NG OBS OBS: OG; SUB NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2000 | natural gas peaker | FALSE | 19450 | Union Carbide Corp-Seadrift | 50150 | Union Carbide Seadrift Cogen | TX | Calhoun | GE11 | Natural Gas Fired Combustion Turbine | GT | G621 | S | X | X | UCC_COG_PUN1 | ERCOT SOUTH ZONE | 35 | 0.85 | 30 | 38 | 20 | N |  |  | OP | X | 11 | 2000 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T T T to NG SUB SUB
Vintage1987 | natural gas steam turbine | FALSE | 19450 | Union Carbide Corp-Seadrift | 50150 | Union Carbide Seadrift Cogen | TX | Calhoun | GEN5 | Natural Gas Steam Turbine | ST | G621 | S | X | X | UCC_COG_PUN1 | ERCOT SOUTH ZONE | 15 | 0.9 | 15 | 15 | 2 | N |  |  | OP | X | 11 | 1987 |  |  | Y | Industrial CHP | 7 | T T T: B; NG SUB SUB: NG; NG OBS OBS: OG; SUB NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1987 | natural gas peaker | FALSE | 19450 | Union Carbide Corp-Seadrift | 50150 | Union Carbide Seadrift Cogen | TX | Calhoun | GEN6 | Natural Gas Fired Combustion Turbine | GT | G621 | S | X | X | UCC_COG_PUN1 | ERCOT SOUTH ZONE | 35 | 0.9 | 30 | 38 | 17 | N |  |  | OP | X | 11 | 1987 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T T T to NG SUB SUB
Vintage1987 | other | FALSE | 19450 | Union Carbide Corp-Seadrift | 50150 | Union Carbide Seadrift Cogen | TX | Calhoun | GEN7 | Other Gases | ST | G621 | S | X | X | UCC_COG_PUN1 | ERCOT SOUTH ZONE | 6 | 0.9 | 6 | 6 | 1.5 | N |  |  | OA | X | 11 | 1987 |  |  | Y | Industrial CHP | 7 | T T T: B; NG SUB SUB: OG; NG OBS OBS: NG; SUB NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1987 | natural gas peaker | FALSE | 19450 | Union Carbide Corp-Seadrift | 50150 | Union Carbide Seadrift Cogen | TX | Calhoun | GEN8 | Natural Gas Fired Combustion Turbine | GT | G621 | S | X | X | UCC_COG_PUN1 | ERCOT SOUTH ZONE | 35 | 0.9 | 30 | 38 | 17 | N |  |  | OP | X | 11 | 1987 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T T T to NG SUB SUB
Vintage1987 | natural gas steam turbine | FALSE | 19450 | Union Carbide Corp-Seadrift | 50150 | Union Carbide Seadrift Cogen | TX | Calhoun | GEN9 | Natural Gas Steam Turbine | ST | G621 | S | X | X | UCC_COG_PUN1 | ERCOT SOUTH ZONE | 15 | 0.9 | 15 | 15 | 2 | N |  |  | OP | X | 11 | 1987 |  |  | Y | Industrial CHP | 7 | T T T: B; NG SUB SUB: NG; NG OBS OBS: OG; SUB NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1969 | natural gas peaker | FALSE | 19450 | Union Carbide Corp-Seadrift | 50150 | Union Carbide Seadrift Cogen | TX | Calhoun | IGT | Natural Gas Fired Combustion Turbine | GT | G621 | S | X | X | UCC_COG_PUN1 | ERCOT SOUTH ZONE | 12 | 0.9 | 12 | 12 |  | N |  |  | OP | X | 1 | 1969 |  |  | N | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T T T to NG SUB SUB
Vintage1996 | natural gas combined cycle | FALSE | 5352 | Dow Chemical Co - St Charles | 50152 | Dow St Charles Operations | LA | St Charles | CGN1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 125.8 | 0.95 | 100 | 116 | 60 | N |  |  | OP | X | 12 | 1996 |  |  | Y | Industrial CHP | 7 | T T T: T; NG SUB SUB: NG; NG OBS OBS: OG |  |  |  | N | N | 0 | 12H | [23 empty] | N
Vintage1997 | natural gas combined cycle | FALSE | 5352 | Dow Chemical Co - St Charles | 50152 | Dow St Charles Operations | LA | St Charles | CGN2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 125.8 | 0.95 | 100 | 116 | 60 | N |  |  | OP | X | 1 | 1997 |  |  | Y | Industrial CHP | 7 | T T T: T; NG SUB SUB: NG; NG OBS OBS: OG |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage2002 | natural gas combined cycle | FALSE | 5352 | Dow Chemical Co - St Charles | 50152 | Dow St Charles Operations | LA | St Charles | CSTG | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 50 | 0.95 | 50 | 50 | 15 | N |  |  | OP | X | 12 | 2002 |  |  | Y | Industrial CHP | 7 | T T T: T; NG SUB SUB: NG; NG OBS OBS: OG |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1997 | natural gas combined cycle | FALSE | 5352 | Dow Chemical Co - St Charles | 50152 | Dow St Charles Operations | LA | St Charles | STG | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 22 | 0.95 | 20 | 20 | 5 | N |  |  | OP | X | 2 | 1997 |  |  | Y | Industrial CHP | 7 | T T T: T; NG SUB SUB: NG; NG OBS OBS: OG |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1996 | other | FALSE | 39066 | Union Carbide Corp-Texas City | 50153 | Texas City Plant Union Carbide | TX | Galveston | STG | All Other | ST |  | S | X | X |  |  | 45 | 0.9 | 38 | 38 | 10 | N |  |  | OP | X | 3 | 1996 |  |  | Y | Industrial CHP | 7 | T T T: B; NG SUB SUB: PUR; SUB NG NG: PUR |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1990 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 50156 | Bear Creek | CA | Shasta | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.2 | 1 | 3 | 2.9 | 0.1 | N |  |  | OP | X | 1 | 1990 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT | [6 empty] | 10M
Vintage1916 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50166 | International Paper Woronoco Mill | MA | Hampden | GEN1 | Conventional Hydroelectric | HY |  | W | X | X | 4506 |  | 0.5 | 0.9 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 1 | 1916 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N |  | 10M
Vintage1913 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50166 | International Paper Woronoco Mill | MA | Hampden | GEN2 | Conventional Hydroelectric | HY |  | W | X | X | 4506 |  | 1.8 | 0.95 | 1.7 | 1.7 | 0.3 | N |  |  | OP | X | 1 | 1913 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 10M
Vintage1916 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50166 | International Paper Woronoco Mill | MA | Hampden | GEN2A | Conventional Hydroelectric | HY |  | W | X | X | 4506 |  | 0.5 | 0.9 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 1 | 1916 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N |  | 10M
Vintage1982 | natural gas peaker | FALSE | 13914 | Occidental Chemical Corporation | 50169 | Wichita Plant | KS | Sedgwick | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 43.7 | 0.8 | 27 | 33 | 13 | N |  |  | SB | Y | 8 | 1982 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N | 0 | 12H | [23 empty] | N | N | N | bar: T T T to NG SUB SUB
Vintage1986 | natural gas peaker | FALSE | 1569 | Berry Petroleum Co | 50170 | Berry Cogen | CA | Kern | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | ZP26 | ZP26 | 38.7 | 0.85 | 35 | 37.5 | 33.5 | N |  |  | OP | X | 12 | 1986 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T T T to NG SUB SUB
Vintage1986 | hydro | TRUE | 56840 | Emporia Hydro Power LP | 50175 | Emporia | VA | Greensville | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.99 | 2 | 2 | 0.3 | N |  |  | OP | X | 1 | 1986 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 12H | [20 empty] | N |  |  | N |  | N
Vintage1986 | hydro | TRUE | 56840 | Emporia Hydro Power LP | 50175 | Emporia | VA | Greensville | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.99 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 1 | 1986 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 12H | [23 empty] | N
Vintage1987 | hydro | TRUE | 56842 | Union Falls Hydro Power LP | 50176 | Union Falls | NY | Clinton | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 0.99 | 1.3 | 1.3 | 0.1 | N |  |  | OP | X | 1 | 1987 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 1H | [20 empty] | N |  |  | N |  | N
Vintage1987 | hydro | TRUE | 56842 | Union Falls Hydro Power LP | 50176 | Union Falls | NY | Clinton | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 0.99 | 1.3 | 1.3 | 0.1 | N |  |  | OP | X | 1 | 1987 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 1H | [20 empty] | N |  |  | N |  | N
Vintage1981 | hydro | TRUE | 56844 | Blackstone Hydro Inc. | 50177 | Blackstone/Tupperware | RI | Providence | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.99 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 1 | 1981 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 1H | [20 empty] | N |  |  | N |  | N
Vintage1981 | hydro | TRUE | 56844 | Blackstone Hydro Inc. | 50177 | Blackstone/Tupperware | RI | Providence | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.99 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 1 | 1981 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 1H | [20 empty] | N |  |  | N |  | N
Vintage1981 | hydro | TRUE | 56844 | Blackstone Hydro Inc. | 50177 | Blackstone/Tupperware | RI | Providence | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.99 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 1 | 1981 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 1H | [20 empty] | N |  |  | N |  | N
Vintage1981 | hydro | TRUE | 56844 | Blackstone Hydro Inc. | 50177 | Blackstone/Tupperware | RI | Providence | GEN4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.99 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 1 | 1981 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 1H | [20 empty] | N |  |  | N |  | N
Vintage1915 | hydro | TRUE | 56843 | Banister Hydro LP | 50178 | Halifax | VA | Halifax | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.99 | 0.8 | 0.8 | 0.2 | N |  |  | OP | X | 1 | 1915 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 12H | [20 empty] | N |  |  | N |  | N
Vintage1915 | hydro | TRUE | 56843 | Banister Hydro LP | 50178 | Halifax | VA | Halifax | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.99 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 1 | 1915 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 12H | [20 empty] | N |  |  | N |  | N
Vintage1915 | hydro | TRUE | 56843 | Banister Hydro LP | 50178 | Halifax | VA | Halifax | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.99 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 1 | 1915 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N |  | 0 | 12H | [20 empty] | N |  |  | N |  | N
Vintage1986 | hydro | TRUE | 58896 | Siskiyou Power Authority | 50179 | Box Canyon Dam | CA | Siskiyou | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 0.2 | N |  |  | OP | X | 6 | 1986 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N |  | 0 | 1H | [23 empty] | N
Vintage1986 | hydro | TRUE | 58896 | Siskiyou Power Authority | 50179 | Box Canyon Dam | CA | Siskiyou | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 0.2 | N |  |  | OP | X | 6 | 1986 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT |  |  |  | N |  | 0 | 1H | [23 empty] | N
Vintage1990 | hydro | TRUE | 60821 | Olsen Power Partners | 50180 | Olsen | CA | Shasta | GEN1 | Conventional Hydroelectric | HY |  | J | X | X |  |  | 5 | 0.9 | 4.8 | 4.6 | 0.2 | N |  |  | OP | X | 1 | 1990 |  |  | N | IPP Non-CHP | 2 | T T T: X; NG SUB SUB: WAT | [6 empty] | 1H
Vintage1990 | biomass | TRUE | 20492 | International Paper Columbus Mill | 50184 | Columbus MS | MS | Lowndes | TG1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 64 | 0.9 | 64 | 64 | 2 | N |  |  | OP | X | 4 | 1990 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | NG | DFO | BIT |  | NG | DFO |  |  | N | N |  | 12H |  |  | Y |  |  |  | Y | [16 empty] | Y | Y | N
Vintage1982 | biomass | TRUE | 20492 | International Paper Columbus Mill | 50184 | Columbus MS | MS | Lowndes | TG2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 46 | 0.8 | 46 | 46 | 5 | N |  |  | OP | X | 6 | 1982 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | NG | DFO | BIT |  | NG | DFO |  |  | N | N |  | 12H |  |  | Y |  |  |  | Y | [16 empty] | Y | Y | N
Vintage1982 | biomass | TRUE | 20492 | International Paper Columbus Mill | 50184 | Columbus MS | MS | Lowndes | TG3 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 14.6 | 0.8 | 14.6 | 14.6 | 3 | N |  |  | OP | X | 6 | 1982 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | NG | DFO | BIT |  | NG | DFO |  |  | N | N |  | 12H |  |  | Y |  |  |  | Y | [16 empty] | Y | Y | N
Vintage1987 | biomass | TRUE | 20492 | International Paper Columbus Mill | 50184 | Columbus MS | MS | Lowndes | TG4 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 4 | 1 | 4 | 4 | 1 | N |  |  | SB | Y | 8 | 1987 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | NG | DFO | BIT |  | NG | DFO |  |  | N | N |  | 12H |  |  | Y |  |  |  | Y | [16 empty] | Y | Y | N
Vintage1957 | biomass | TRUE | 20547 | Cosmo Specialty Fibers | 50185 | Cosmo Specialty Fibers Plant | WA | Grays Harbor | TG1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 7.5 | 0.8 | 8.5 | 9 | 1 | N |  |  | OP | X | 1 | 1957 |  |  | Y | Industrial CHP | 7 | B | WDL | WDS | RFO |  |  |  | RFO |  |  |  | N | N |  | 12H |  |  |  |  | N | [18 empty] | Y | Y | N
Vintage1957 | biomass | TRUE | 20547 | Cosmo Specialty Fibers | 50185 | Cosmo Specialty Fibers Plant | WA | Grays Harbor | TG2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 7.5 | 0.8 | 8.5 | 9 | 1 | N |  |  | OP | X | 1 | 1957 |  |  | Y | Industrial CHP | 7 | B | WDL | WDS | RFO |  |  |  | RFO |  |  |  | N | N |  | 12H |  |  |  |  | N | [18 empty] | Y | Y | N
Vintage1948 | biomass | TRUE | 60561 | Nippon Dynawave Packaging Co. | 50187 | Nippon Dynawave Packaging Longview WA | WA | Cowlitz | TG1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 8 | 0.98 | 7.4 | 7.5 | 2.3 | N |  |  | OP | X | 1 | 1948 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | RFO |  |  |  | RFO |  |  |  | N | N |  | 12H |  |  |  |  | N | [18 empty] | Y | Y | Y
Vintage1948 | biomass | TRUE | 60561 | Nippon Dynawave Packaging Co. | 50187 | Nippon Dynawave Packaging Longview WA | WA | Cowlitz | TG2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 5 | 0.8 | 4.7 | 4.7 | 2.3 | N |  |  | OP | X | 1 | 1948 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | RFO |  |  |  | RFO |  |  |  | N | N |  | 12H |  |  |  |  | N | [18 empty] | Y | Y | Y
Vintage1954 | biomass | TRUE | 60561 | Nippon Dynawave Packaging Co. | 50187 | Nippon Dynawave Packaging Longview WA | WA | Cowlitz | TG4 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 18 | 0.96 | 16.7 | 16.9 | 2 | N |  |  | OP | X | 1 | 1954 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | RFO |  |  |  | RFO |  |  |  | N | N |  | 12H |  |  | N |  | N | [18 empty] | Y | Y | Y
Vintage1976 | biomass | TRUE | 60561 | Nippon Dynawave Packaging Co. | 50187 | Nippon Dynawave Packaging Longview WA | WA | Cowlitz | TG5 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 31.4 | 0.8 | 29.2 | 29.5 | 6 | N |  |  | OP | X | 1 | 1976 |  |  | Y | Industrial CHP | 7 | T | WDS | SUB | SLW | DFO |  |  | DFO |  |  |  | N | N |  | 12H |  |  | Y |  | Y | [18 empty] | Y | Y | N
Vintage2014 | biomass | TRUE | 20511 | International Paper Co. - New Bern Mill | 50188 | International Paper Co. - New Bern Mill | NC | Craven | TG2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 38.1 | 0.85 | 29 | 33 | 10 | N |  |  | OP | X | 4 | 2014 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | DFO | OBG |  |  | NG | DFO |  |  | N | N |  | OVER |  |  |  |  | N | [18 empty] | Y | Y | Y
Vintage1978 | biomass | TRUE | 55903 | Domtar Paper Company LLC | 50189 | Domtar Paper Co LLC Plymouth NC | NC | Martin | TG10 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 72 | 0.97 | 74 | 74 | 14 | N |  |  | OP | X | 6 | 1978 |  |  | Y | Industrial CHP | 7 | T | WDS | NG | SLW | DFO |  |  | NG | RFO | BLQ |  | N | N |  | 12H |  | N | [21 empty] | Y | Y | Y
Vintage1976 | biomass | TRUE | 55903 | Domtar Paper Company LLC | 50189 | Domtar Paper Co LLC Plymouth NC | NC | Martin | TG9 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 42 | 0.8 | 40.8 | 40.8 | 14 | N |  |  | OP | X | 9 | 1976 |  |  | Y | Industrial CHP | 7 | T | BLQ | DFO | WDS | RFO | NG |  | DFO |  |  |  | N | N |  | 12H |  | N | [21 empty] | Y | Y | N
Vintage1910 | hydro | FALSE | 55997 | Domtar Paper Company Rothschild | 50190 | Domtar Paper Company Rothschild | WI | Marathon | HG1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 1 | 1910 |  |  | N | Industrial Non-CHP | 6 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1910 | hydro | FALSE | 55997 | Domtar Paper Company Rothschild | 50190 | Domtar Paper Company Rothschild | WI | Marathon | HG2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 1 | 1910 |  |  | N | Industrial Non-CHP | 6 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1910 | hydro | FALSE | 55997 | Domtar Paper Company Rothschild | 50190 | Domtar Paper Company Rothschild | WI | Marathon | HG3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 1 | 1910 |  |  | N | Industrial Non-CHP | 6 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1910 | hydro | FALSE | 55997 | Domtar Paper Company Rothschild | 50190 | Domtar Paper Company Rothschild | WI | Marathon | HG4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.2 | N |  |  | OP | X | 1 | 1910 |  |  | N | Industrial Non-CHP | 6 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1910 | hydro | FALSE | 55997 | Domtar Paper Company Rothschild | 50190 | Domtar Paper Company Rothschild | WI | Marathon | HG5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.8 | 1 | 0.9 | 0.1 | N |  |  | OP | X | 1 | 1910 |  |  | N | Industrial Non-CHP | 6 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1910 | hydro | FALSE | 55997 | Domtar Paper Company Rothschild | 50190 | Domtar Paper Company Rothschild | WI | Marathon | HG6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.8 | 0.7 | 0.6 | 0.1 | N |  |  | OP | X | 1 | 1910 |  |  | N | Industrial Non-CHP | 6 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1910 | hydro | FALSE | 55997 | Domtar Paper Company Rothschild | 50190 | Domtar Paper Company Rothschild | WI | Marathon | HG7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.2 | N |  |  | OP | X | 1 | 1910 |  |  | N | Industrial Non-CHP | 6 | T T T: X; NG SUB SUB: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1949 | biomass | TRUE | 56289 | International Paper Corporation - Springfield | 50191 | IP Springfield Oregon | OR | Lane | TG1 | Wood/Wood Waste Biomass | ST |  | S | X | X | midc | midc | 7.5 | 0.8 | 7.5 | 7.5 | 2 | N |  |  | OS | X | 1 | 1949 |  |  | N | Industrial CHP | 7 | X | BLQ | NG | DFO |  |  |  | NG |  |  |  | N |  |  | OVER | [23 empty] | Y | Y | Y
Vintage1949 | biomass | TRUE | 56289 | International Paper Corporation - Springfield | 50191 | IP Springfield Oregon | OR | Lane | TG2 | Wood/Wood Waste Biomass | ST |  | S | X | X | midc | midc | 5 | 0.8 | 5 | 5 | 1 | N |  |  | OS | X | 1 | 1949 |  |  | N | Industrial CHP | 7 | X | BLQ | NG | DFO |  |  |  | NG |  |  |  | N |  |  | OVER | [23 empty] | Y | Y | Y
Vintage1953 | biomass | TRUE | 56289 | International Paper Corporation - Springfield | 50191 | IP Springfield Oregon | OR | Lane | TG3 | Wood/Wood Waste Biomass | ST |  | S | X | X | midc | midc | 12.5 | 0.8 | 12.5 | 12.5 | 2.5 | N |  |  | OS | X | 1 | 1953 |  |  | Y | Industrial CHP | 7 | B | BLQ | NG | DFO |  |  |  | NG |  |  |  | N |  |  | OVER | [23 empty] | Y | Y | Y
Vintage1976 | biomass | TRUE | 56289 | International Paper Corporation - Springfield | 50191 | IP Springfield Oregon | OR | Lane | TG4 | Wood/Wood Waste Biomass | ST |  | W | X | X | midc | midc | 40 | 0.8 | 33 | 33 | 8 | N |  |  | OP | X | 10 | 1976 |  |  | Y | Industrial CHP | 7 | T T T: B; NG SUB SUB: BLQ; NG OBS OBS: NG; SUB NG NG: NG |  |  |  | N |  |  | 12H | [23 empty] | Y | Y | N
Vintage1971 | biomass | TRUE | 56164 | International Paper - Valliant | 50192 | International Paper Valliant OK | OK | McCurtain | TG1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 68 | 0.9 | 57.8 | 57.8 | 25 | Y | 9 | 2021 | OP | X | 10 | 1971 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | RFO | DFO | WDS | OBS | NG |  |  |  | N |  |  | OVER |  | N | [21 empty] | Y | Y | Y
Vintage1982 | natural gas peaker | FALSE | 1058 | B Braun Medical Inc | 50200 | B Braun Medical | CA | Orange | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 2.8 | 0.8 | 2.7 | 2.6 | 1 | N |  |  | OP | X | 11 | 1982 | 12 | 2023 | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: T to BLQ
Vintage1995 | natural gas peaker | FALSE | 1058 | B Braun Medical Inc | 50200 | B Braun Medical | CA | Orange | GEN2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.3 | 0.8 | 3 | 2.9 | 1 | N |  |  | OP | X | 1 | 1995 | 12 | 2023 | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: T to BLQ
Vintage2010 | biomass | TRUE | 56216 | Multitrade Rabun Gap LLC | 50201 | Multitrade Rabun Gap, LLC | GA | RABUN | ST2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 17.9 | 0.9 | 18 | 18 | 1.5 | N |  |  | OP | X | 1 | 2010 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WDS; NG: WDS |  |  |  | N | N |  | OVER | [23 empty] | N | N
Vintage1986 | natural gas peaker | FALSE | 19351 | U S Gypsum Co | 50203 | US Gypsum Oakfield | NY | Genesee | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 241 | 241 | 5.8 | 0.8 | 4.9 | 5.7 | 0.5 | N |  |  | OP | X | 4 | 1986 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: T to BLQ
Vintage1984 | other | FALSE | 28473 | Harvest Midstream Co | 50205 | Williams Ignacio Natural Gas Plant | CO | La Plata | 7101 | All Other | ST |  | S | X | X |  |  | 6.1 | 0.8 | 6.1 | 6.1 | 4.5 | N |  |  | OP | X | 12 | 1984 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: WH; NG: NG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1989 | hydro | TRUE | 27762 | Ptarmigan Res & Engy Inc | 50206 | Vallecito Hydroelectric | CO | La Plata | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 1 | 0.8 | 0.8 | 0.1 | N |  |  | OP | X | 5 | 1989 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 10M | [20 empty] | N
Vintage1989 | hydro | TRUE | 27762 | Ptarmigan Res & Engy Inc | 50206 | Vallecito Hydroelectric | CO | La Plata | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 0.3 | N |  |  | OP | X | 5 | 1989 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1989 | hydro | TRUE | 27762 | Ptarmigan Res & Engy Inc | 50206 | Vallecito Hydroelectric | CO | La Plata | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 0.3 | N |  |  | OP | X | 5 | 1989 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1986 | biomass | TRUE | 64003 | Stored Solar Services, LLC | 50208 | Stored Solar Bethlehem LLC | NH | GRAFTON | GEN1 | Wood/Wood Waste Biomass | ST |  | W | X | X |  |  | 17.5 | 1 | 15 | 15 | 11.4 | N |  |  | OP | X | 12 | 1986 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WDS; NG: WDS |  |  |  | N | N |  | OVER |  |  | N |  | N | [18 empty] | N | N | N
Vintage1985 | geothermal | TRUE | 49899 | CalEnergy Operating Corporation | 50210 | Vulcan-BN Geothermal Power Company | CA | Imperial | GEN1 | Geothermal | ST |  | W | X | X |  |  | 30.1 | 0.85 | 29 | 29 | 2 | N |  |  | OP | X | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: GEO; NG: GEO |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1985 | geothermal | TRUE | 49899 | CalEnergy Operating Corporation | 50210 | Vulcan-BN Geothermal Power Company | CA | Imperial | GEN2 | Geothermal | ST |  | W | X | X |  |  | 9.5 | 0.85 | 9 | 9 | 2 | N |  |  | OP | X | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: GEO; NG: GEO |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1989 | municipal solid waste | TRUE | 21128 | York County Solid W & R Auth | 50215 | York County Resource Recovery | PA | York | GEN1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 36.5 | 0.85 | 30 | 30 | 11.7 | N |  |  | OP | X | 11 | 1989 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: MSW; NG: NG | DFO |  |  | N | N |  | 12H | [23 empty] | N | N
Vintage1988 | natural gas combined cycle | FALSE | 867 | ARCO Products Co-Watson | 50216 | Watson Cogeneration | CA | Los Angeles | GN91 | Natural Gas Fired Combined Cycle | CT | CC1 | J | X | N | POD_ARCOGN_2_UNITS | POD_ARCOGN_2_UNITS | 82 | 0.9 | 82 | 82 | 68 | N |  |  | OP | X | 3 | 1988 |  |  | Y | Industrial CHP | 7 | T | NG | OG | WO |  |  |  | WO | NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1988 | natural gas combined cycle | FALSE | 867 | ARCO Products Co-Watson | 50216 | Watson Cogeneration | CA | Los Angeles | GN92 | Natural Gas Fired Combined Cycle | CT | CC1 | J | X | N | POD_ARCOGN_2_UNITS | POD_ARCOGN_2_UNITS | 82 | 0.9 | 82 | 82 | 68 | N |  |  | OP | X | 2 | 1988 |  |  | Y | Industrial CHP | 7 | T | NG | OG | WO |  |  |  | WO | NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1988 | natural gas combined cycle | FALSE | 867 | ARCO Products Co-Watson | 50216 | Watson Cogeneration | CA | Los Angeles | GN93 | Natural Gas Fired Combined Cycle | CT | CC1 | J | X | N | POD_ARCOGN_2_UNITS | POD_ARCOGN_2_UNITS | 82 | 0.9 | 82 | 82 | 68 | N |  |  | OP | X | 1 | 1988 |  |  | Y | Industrial CHP | 7 | T | NG | OG | WO |  |  |  | WO | NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1987 | natural gas combined cycle | FALSE | 867 | ARCO Products Co-Watson | 50216 | Watson Cogeneration | CA | Los Angeles | GN94 | Natural Gas Fired Combined Cycle | CT | CC1 | J | X | N | POD_ARCOGN_2_UNITS | POD_ARCOGN_2_UNITS | 82 | 0.9 | 82 | 82 | 68 | N |  |  | OP | X | 12 | 1987 |  |  | Y | Industrial CHP | 7 | T | NG | OG | WO |  |  |  | WO | NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1988 | natural gas combined cycle | FALSE | 867 | ARCO Products Co-Watson | 50216 | Watson Cogeneration | CA | Los Angeles | GN95 | Natural Gas Fired Combined Cycle | CA | CC1 | J | Y | X | POD_ARCOGN_2_UNITS | POD_ARCOGN_2_UNITS | 38.5 | 0.9 | 35 | 35 | 10 | N |  |  | OP | X | 2 | 1988 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: NG; NG: OG |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1987 | natural gas combined cycle | FALSE | 867 | ARCO Products Co-Watson | 50216 | Watson Cogeneration | CA | Los Angeles | GN96 | Natural Gas Fired Combined Cycle | CA | CC1 | J | Y | X | POD_ARCOGN_2_UNITS | POD_ARCOGN_2_UNITS | 38.5 | 0.9 | 35 | 35 | 10 | N |  |  | OP | X | 12 | 1987 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: NG; NG: OG |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1982 | hydro | TRUE | 19281 | Turlock Irrigation District | 50218 | Woodward Power Plant | CA | Stanislaus | U1 | Conventional Hydroelectric | HY |  | W | X | X | MRTU_VALLYHM_1_N004 |  | 2.8 | 0.95 | 2.7 | 2.6 | 0.3 | N |  |  | OP | X | 4 | 1982 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1983 | hydro | TRUE | 19281 | Turlock Irrigation District | 50219 | Frankenheimer Power Plant | CA | Stanislaus | U1 | Conventional Hydroelectric | HY |  | W | X | X | MRTU_COTTLE_7_N002 |  | 5.3 | 0.95 | 4 | 4.3 | 0.5 | N |  |  | OP | X | 3 | 1983 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1989 | hydro | TRUE | 13353 | Nelson Creek Power Inc | 50223 | Nelson Creek | CA | Shasta | 1296 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.9 | 0.5 | 0.9 | 0.1 | N |  |  | OP | X | 10 | 1989 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 1H | [23 empty] | N
Vintage1981 | biomass | TRUE | 22045 | Oxnard City of | 50224 | Oxnard Wastewater Treatment Plant | CA | Ventura | 7610 | Other Waste Biomass | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.4 | 0.4 | 0.4 | N |  |  | OP | X | 8 | 1981 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: OBG; NG: NG; RFO: PG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1981 | biomass | TRUE | 22045 | Oxnard City of | 50224 | Oxnard Wastewater Treatment Plant | CA | Ventura | 7710 | Other Waste Biomass | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.4 | 0.4 | 0.4 | N |  |  | OP | X | 8 | 1981 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: OBG; NG: NG; RFO: PG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1981 | biomass | TRUE | 22045 | Oxnard City of | 50224 | Oxnard Wastewater Treatment Plant | CA | Ventura | 7810 | Other Waste Biomass | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.4 | 0.4 | 0.4 | N |  |  | OP | X | 8 | 1981 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: OBG; NG: NG; RFO: PG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1988 | municipal solid waste | TRUE | 15824 | Ecomaine | 50225 | Regional Waste Systems | ME | Cumberland | TG1 | Municipal Solid Waste | ST |  | S | X | X | 4001:Z.Maine | 4001:Z.Maine | 13.3 | 0.99 | 11.5 | 11.5 | 3 | N |  |  | OP | X | 6 | 1988 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: MSW; NG: NG; NG: NG |  |  |  | N |  |  | 12H | [23 empty] | N
Vintage1985 | hydro | TRUE | 22614 | Rocky Brook Electric Inc | 50228 | Rocky Brook Hydroelectric | WA | Jefferson | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 1 | 0.1 | 1.2 | 0.1 | N |  |  | SB | Y | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1972 | natural gas steam turbine | FALSE | 18760 | TPC Group, LLC | 50229 | Texas Petrochemicals | TX | Harris | TG2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 35 | 0.8 | 35 | 35 | 8 | N |  |  | OP | X | 6 | 1972 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: NG; NG: OG; NG: NG |  |  |  | N | N |  | OVER |  |  |  |  | N | [15 empty] | N |  |  | N | N | N
Vintage1987 | petroleum | FALSE | 16191 | Robbins Lumber Inc | 50230 | Robbins Lumber | ME | WALDO | CAT | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 1 | 1987 |  |  | N | Industrial CHP | 7 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1981 | biomass | TRUE | 16191 | Robbins Lumber Inc | 50230 | Robbins Lumber | ME | WALDO | WEST | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 1.2 | 0.8 | 1.1 | 1.1 | 0.4 | N |  |  | OS | X | 1 | 1981 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: WDS; NG: WDS |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1986 | hydro | TRUE | 22635 | San Gabriel Valley Mun Wtr Dt | 50233 | San Dimas Wash Generating Station | CA | Los Angeles | 4011 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 1 | 1 | 1 | 0.3 | N |  |  | SB | Y | 3 | 1986 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 1H |  |  |  | N | [19 empty] | N
Vintage1985 | natural gas peaker | FALSE | 16583 | San Antonio Regional Hospital | 50234 | San Antonio Regional Hospital | CA | San Bernardino | 2074 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.9 | 0.8 | 0.5 | N |  |  | OP | X | 1 | 1985 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1985 | natural gas peaker | FALSE | 16583 | San Antonio Regional Hospital | 50234 | San Antonio Regional Hospital | CA | San Bernardino | 2075 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.9 | 0.8 | 0.5 | N |  |  | OP | X | 1 | 1985 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage2001 | natural gas peaker | FALSE | 16583 | San Antonio Regional Hospital | 50234 | San Antonio Regional Hospital | CA | San Bernardino | 2076 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.9 | 0.8 | 0.5 | N |  |  | OP | X | 3 | 2001 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1995 | natural gas steam turbine | FALSE | 15526 | Purdue University | 50240 | Purdue University | IN | Tippecanoe | GEN1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 30.8 | 0.8 | 30.8 | 30.8 | 5 | N |  |  | OP | X | 7 | 1995 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: NG; NG: BIT; NG: NG |  |  |  | N | N |  | 12H | Y |  |  |  | Y | [18 empty] | Y | Y | N
Vintage1969 | natural gas steam turbine | FALSE | 15526 | Purdue University | 50240 | Purdue University | IN | Tippecanoe | GEN2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 10.6 | 0.8 | 7 | 10.6 | 3 | N |  |  | OP | X | 1 | 1969 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: NG; NG: BIT; NG: NG |  |  |  | N | N |  | 12H | Y |  |  |  | Y | [18 empty] | Y | Y | N
Vintage2000 | petroleum | FALSE | 15526 | Purdue University | 50240 | Purdue University | IN | Tippecanoe | GEN3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | SB | Y | 1 | 2000 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1987 | natural gas peaker | FALSE | 27378 | Tenet Hospital Ltd | 50241 | Tenet Hospital | TX | El Paso | 9541 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.1 | 0.8 | 2.1 | 2.1 | 0.3 | N |  |  | OP | X | 3 | 1987 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: NG; NG: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1987 | natural gas peaker | FALSE | 27378 | Tenet Hospital Ltd | 50241 | Tenet Hospital | TX | El Paso | 9542 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.1 | 0.8 | 2.1 | 2.1 | 0.3 | N |  |  | OP | X | 3 | 1987 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: NG; NG: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | TRUE | 9303 | Bucksport Generation LLC | 50243 | Bucksport Generation LLC | ME | Hancock | GEN4 | Natural Gas Fired Combustion Turbine | GT | CC1 | S | X | X | 47390 | 47390 | 186.8 | 0.85 | 178 | 183.1 | 110 | N |  |  | OP | X | 1 | 2001 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: NG; NG: DFO; NG: NG |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1937 | biomass | TRUE | 23815 | Blue Ridge Paper Products Inc | 50244 | Canton North Carolina | NC | Haywood | GEN8 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 7.5 | 0.8 | 7.5 | 7.5 | 2 | N |  |  | OP | X | 1 | 1937 |  |  | Y | Industrial CHP | 7 | T | BLQ | BIT | NG | WDS | RFO |  | NG | PG | DFO |  | N | N |  | 12H |  | Y | Y |  | Y | [18 empty] | Y | Y | N
Vintage1941 | biomass | TRUE | 23815 | Blue Ridge Paper Products Inc | 50244 | Canton North Carolina | NC | Haywood | GEN9 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 7.5 | 0.8 | 7.5 | 7.5 | 2 | N |  |  | OP | X | 1 | 1941 |  |  | Y | Industrial CHP | 7 | T | BLQ | BIT | NG | WDS | RFO |  | NG | PG | DFO |  | N | N |  | 12H |  | Y | Y |  | Y | [18 empty] | Y | Y | N
Vintage1946 | biomass | TRUE | 23815 | Blue Ridge Paper Products Inc | 50244 | Canton North Carolina | NC | Haywood | GN10 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 7.5 | 0.8 | 7.5 | 7.5 | 2 | N |  |  | OP | X | 1 | 1946 |  |  | Y | Industrial CHP | 7 | T | BLQ | BIT | NG | WDS | RFO |  | NG | PG | DFO |  | N | N |  | 12H |  | Y | Y |  | Y | [18 empty] | Y | Y | N
Vintage1949 | biomass | TRUE | 23815 | Blue Ridge Paper Products Inc | 50244 | Canton North Carolina | NC | Haywood | GN11 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 7.5 | 0.8 | 7.5 | 7.5 | 2 | N |  |  | OP | X | 1 | 1949 |  |  | Y | Industrial CHP | 7 | T | BLQ | BIT | NG | WDS | RFO |  | NG | PG | DFO |  | N | N |  | 12H |  | Y | Y |  | Y | [18 empty] | Y | Y | N
Vintage1952 | biomass | TRUE | 23815 | Blue Ridge Paper Products Inc | 50244 | Canton North Carolina | NC | Haywood | GN12 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 10 | 0.8 | 10 | 10 | 2 | N |  |  | OP | X | 1 | 1952 |  |  | Y | Industrial CHP | 7 | T | BLQ | BIT | NG | WDS | RFO |  | NG | PG | DFO |  | N | N |  | 12H |  | Y | Y |  | Y | [18 empty] | Y | Y | N
Vintage1979 | biomass | TRUE | 23815 | Blue Ridge Paper Products Inc | 50244 | Canton North Carolina | NC | Haywood | GN13 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 12.5 | 0.8 | 12.5 | 12.5 | 6.8 | N |  |  | OP | X | 6 | 1979 |  |  | Y | Industrial CHP | 7 | T | BLQ | BIT | NG | WDS | RFO |  | NG | PG | DFO |  | N | N |  | 12H |  | Y | Y |  | Y | [18 empty] | Y | Y | N
Vintage1981 | biomass | TRUE | 9401 | International Paper Co-Pensacola | 50250 | International Paper Pensacola | FL | Escambia | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 39.6 | 0.9 | 36 | 36 | 22 | N |  |  | OP | X | 1 | 1981 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | NG |  |  |  | NG |  |  |  | N | N |  | OVER |  | N |  |  | N | [18 empty] | N | N | N
Vintage1981 | biomass | TRUE | 9401 | International Paper Co-Pensacola | 50250 | International Paper Pensacola | FL | Escambia | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 43.2 | 0.9 | 40 | 40 | 30 | N |  |  | OP | X | 1 | 1981 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | NG |  |  |  | NG |  |  |  | N | N |  | OVER |  | N |  |  | N | [18 empty] | N | N | N
Vintage1985 | biomass | TRUE | 56187 | Verso Paper - Quinnesec | 50251 | Verso Paper Quinnesec Mich Mill | MI | Dickinson | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 28 | 0.8 | 28 | 28 | 5 | N |  |  | OP | X | 10 | 1985 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | NG | BIT |  |  | NG |  |  |  | N | N |  | 12H |  |  | Y |  | Y | [15 empty] | N |  |  | Y | Y | N
Vintage2011 | biomass | TRUE | 56187 | Verso Paper - Quinnesec | 50251 | Verso Paper Quinnesec Mich Mill | MI | Dickinson | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 28 | 0.8 | 31 | 31 | 1.6 | N |  |  | OP | X | 11 | 2011 |  |  | N | Industrial CHP | 7 | X | WDS | NG | BIT |  |  |  | NG |  |  |  | N | N |  | 12H |  |  | Y |  | Y | [15 empty] | N |  |  | Y | Y | N
Vintage1985 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50252 | Sartell Dam | MN | Benton | HG10 | Conventional Hydroelectric | HY |  | W | X | X | NSP.SARTELL | NSP>SARTELL | 0.9 | 0.8 | 0.9 | 0.9 | 0.3 | N |  |  | OP | X | 3 | 1985 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT | [5 empty] | 0 | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50252 | Sartell Dam | MN | Benton | HG11 | Conventional Hydroelectric | HY |  | W | X | X | NSP.SARTELL | NSP.SARTELL | 0.9 | 0.8 | 0.9 | 0.9 | 0.3 | N |  |  | OP | X | 3 | 1985 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT | [5 empty] | 0 | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50252 | Sartell Dam | MN | Benton | HG12 | Conventional Hydroelectric | HY |  | W | X | X | NSP.SARTELL | NSP.SARTELL | 0.9 | 0.8 | 0.9 | 0.9 | 0.3 | N |  |  | OP | X | 3 | 1985 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT | [5 empty] | 0 | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50252 | Sartell Dam | MN | Benton | HG2 | Conventional Hydroelectric | HY |  | W | X | X | NSP.SARTELL | NSP.SARTELL | 0.9 | 0.8 | 0.9 | 0.9 | 0.3 | N |  |  | OP | X | 3 | 1985 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT | [5 empty] | 0 | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50252 | Sartell Dam | MN | Benton | HG3 | Conventional Hydroelectric | HY |  | W | X | X | NSP.SARTELL | NSP.SARTELL | 0.9 | 0.8 | 0.9 | 0.9 | 0.3 | N |  |  | OP | X | 3 | 1985 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT | [5 empty] | 0 | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50252 | Sartell Dam | MN | Benton | HG4 | Conventional Hydroelectric | HY |  | W | X | X | NSP.SARTELL | NSP.SARTELL | 0.9 | 0.8 | 0.9 | 0.9 | 0.3 | N |  |  | OP | X | 3 | 1985 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT | [5 empty] | 0 | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50252 | Sartell Dam | MN | Benton | HG5 | Conventional Hydroelectric | HY |  | W | X | X | NSP.SARTELL | NSP.SARTELL | 0.9 | 0.8 | 0.9 | 0.9 | 0.3 | N |  |  | OP | X | 3 | 1985 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT | [5 empty] | 0 | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50252 | Sartell Dam | MN | Benton | HG6 | Conventional Hydroelectric | HY |  | W | X | X | NSP.SARTELL | NSP.SARTELL | 0.8 | 1 | 0.8 | 0.8 | 0.2 | N |  |  | OP | X | 3 | 1985 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT | [5 empty] | 0 | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50252 | Sartell Dam | MN | Benton | HG7 | Conventional Hydroelectric | HY |  | W | X | X | NSP.SARTELL | NSP.SARTELL | 0.8 | 1 | 0.8 | 0.8 | 0.2 | N |  |  | OP | X | 3 | 1985 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT | [5 empty] | 0 | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50252 | Sartell Dam | MN | Benton | HG8 | Conventional Hydroelectric | HY |  | W | X | X | NSP.SARTELL | NSP.SARTELL | 0.7 | 1 | 0.7 | 0.7 | 0.2 | N |  |  | OP | X | 3 | 1985 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT | [5 empty] | 0 | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50252 | Sartell Dam | MN | Benton | HG9 | Conventional Hydroelectric | HY |  | W | X | X | NSP.SARTELL | NSP.SARTELL | 0.7 | 1 | 0.7 | 0.7 | 0.2 | N |  |  | OP | X | 3 | 1985 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT | [5 empty] | 0 | 10M | [23 empty] | N
Vintage1966 | biomass | TRUE | 64508 | Westrock Kraft Paper, LLC | 50254 | KapStone Kraft Paper Corp | NC | Halifax | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 28.3 | 0.9 | 30 | 30 | 2 | N |  |  | OP | X | 1 | 1966 |  |  | Y | Industrial CHP | 7 | B | BLQ | BIT | RFO | NG | AB | WDS | DFO |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | Y | Y | Y
Vintage2006 | petroleum | FALSE | 13945 | Beaumont Hospital Dearborn Campus | 50260 | Beaumont Hospital Dearborn Campus | MI | Wayne | 1 2M | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0 | N |  |  | SB | N | 1 | 2006 |  |  | N | Commercial Non-CHP | 4 | X B: X; WAT BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2006 | petroleum | FALSE | 13945 | Beaumont Hospital Dearborn Campus | 50260 | Beaumont Hospital Dearborn Campus | MI | Wayne | 2 2M | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0 | N |  |  | SB | N | 1 | 2006 |  |  | N | Commercial Non-CHP | 4 | X B: X; WAT BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2006 | petroleum | FALSE | 13945 | Beaumont Hospital Dearborn Campus | 50260 | Beaumont Hospital Dearborn Campus | MI | Wayne | 500A | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0 | N |  |  | SB | N | 2 | 2006 |  |  | N | Commercial Non-CHP | 4 | X B: X; WAT BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1989 | hydro | TRUE | 40444 | Truckee-Carson Irrigation District | 50261 | New Lahontan | NV | Churchill | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4 | 0.8 | 3.8 | 3.7 | 0.5 | N |  |  | OP | X | 4 | 1989 |  |  | N | IPP Non-CHP | 2 | X B: X; WAT BLQ: WAT | [6 empty] | 10M
Vintage1931 | hydro | TRUE | 15787 | Redlands Water & Power Company | 50267 | Redlands Water & Power | CO | Mesa | RED1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.4 | 0.83 | 1.4 | 1.4 | 1.2 | N |  |  | OP | X | 8 | 1931 |  |  | N | IPP Non-CHP | 2 | X B: X; WAT BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1984 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 50268 | Hewittville Hydroelectric | NY | St Lawrence | HY1 | Conventional Hydroelectric | HY |  | S | X | X | 24057 | 24057 | 3 | 0.9 | 2.2 | 2.2 | 0.2 | N |  |  | OP | X | 9 | 1984 |  |  | N | IPP Non-CHP | 2 | X B: X; WAT BLQ: WAT |  |  |  | N | N | 0 | 10M
Vintage1984 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 50269 | Unionville Hydro Project 2499 NY | NY | St Lawrence | HY1 | Conventional Hydroelectric | HY |  | S | X | X | 24057 | 24057 | 3 | 0.9 | 2.2 | 2.2 | 0.3 | N |  |  | OP | X | 7 | 1984 |  |  | N | IPP Non-CHP | 2 | X B: X; WAT BLQ: WAT |  |  |  | N | N | 0 | 10M
Vintage1993 | natural gas combined cycle | FALSE | 6529 | Exxon Mobil Production Co | 50270 | ExxonMobil Santa Ynez Facility | CA | Santa Barbara | GTG1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 39.5 | 0.85 | 40.2 | 39.2 | 21 | N |  |  | OS | X | 9 | 1993 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | OVER | [23 empty] | N | bar: X B to WAT BLQ
Vintage1993 | natural gas combined cycle | FALSE | 6529 | Exxon Mobil Production Co | 50270 | ExxonMobil Santa Ynez Facility | CA | Santa Barbara | STG1 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 9.8 | 0.85 | 8.9 | 8.8 | 5 | N |  |  | OS | X | 10 | 1993 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | OVER | [23 empty] | N | bar: X B to WAT BLQ
Vintage1988 | municipal solid waste | TRUE | 56125 | Community Eco Springfield LLC | 50273 | Pioneer Valley Resource Recovery | MA | Hampden | DLV1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 9.4 | 0.9 | 7.5 | 7.5 | 2 | N |  |  | OP | X | 5 | 1988 |  |  | N | IPP Non-CHP | 2 | X | MSW | NG | TDF |  |  |  | MSW | NG | WDS |  | N | N |  | OVER | [23 empty] | Y | N | N
Vintage1986 | other | FALSE | 17191 | Simplot Leasing Corp | 50274 | Simplot Leasing Don Plant | ID | Bannock | GEN1 | All Other | ST |  | S | X | X |  |  | 15.9 | 0.85 | 14.8 | 15 | 5 | N |  |  | OP | X | 2 | 1986 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N | 0 | 1H | [20 empty] | N |  |  | N | N | N | bar: X B to WAT BLQ; WAT DFO
Vintage1983 | natural gas steam turbine | FALSE | 14465 | Philip Morris USA - Park 500 | 50275 | Park 500 Philip Morris USA | VA | Chesterfield | TG3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 13 | 0.8 | 10.5 | 11.5 | 4.5 | N |  |  | OP | X | 9 | 1983 |  |  | Y | Industrial CHP | 7 | X B: T; WAT BLQ: NG; WAT BIT: DFO; WAT DFO: NG |  |  |  | N | N |  | 12H |  | N |  |  | N | [18 empty] | Y | N | Y
Vintage1986 | onshore wind | TRUE | 20707 | Wintec Energy Ltd | 50276 | Wintec Energy Ltd | CA | Riverside | EXIS | Onshore Wind Turbine | WT |  | S | X | X |  |  | 5.9 |  | 5.9 | 5.9 | 1 | N |  |  | OP | X | 12 | 1986 | 9 | 2022 | N | IPP Non-CHP | 2 | X B: X; WAT BLQ: WND |  |  |  | N | N | 60 | [21 empty] | N |  |  | N
Vintage1989 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50278 | Worumbo Hydro Station | ME | Androscoggin | GEN1 | Conventional Hydroelectric | HY |  | W | X | X | 487 | 487 | 9.7 | 0.9 | 4.6 | 9.3 | 2 | N |  |  | OP | X | 2 | 1989 |  |  | N | IPP Non-CHP | 2 | X B: X; WAT BLQ: WAT |  |  |  | N | N | 0 | 1H
Vintage1989 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50278 | Worumbo Hydro Station | ME | Androscoggin | GEN2 | Conventional Hydroelectric | HY |  | W | X | X | 487 | 487 | 9.7 | 0.9 | 4.6 | 9.3 | 2 | N |  |  | OP | X | 3 | 1989 |  |  | N | IPP Non-CHP | 2 | X B: X; WAT BLQ: WAT |  |  |  | N | N | 0 | 1H
Vintage1988 | biomass | TRUE | 22174 | PEI Power Corp | 50279 | Archbald Power Station | PA | Lackawanna | GEN1 | Landfill Gas | ST |  | S | X | X | 1048035 | ARCHTAP13 KV PEI 1 | 23.2 | 1 | 20 | 20 | 10 | N |  |  | OP | X | 9 | 1988 |  |  | N | IPP Non-CHP | 2 | X B: X; WAT BLQ: LFG; WAT BIT: NG; WAT DFO: NG |  |  |  | N | N |  | OVER |  |  |  | N | N | [18 empty] | Y | Y | N
Vintage2010 | biomass | TRUE | 22174 | PEI Power Corp | 50279 | Archbald Power Station | PA | Lackawanna | GEN5 | Landfill Gas | GT |  | S | X | X | 87901559 | ARCHTAP 13 KV PEI 5 | 4.6 | 1 | 4 | 4.6 | 2 | N |  |  | OP | X | 2 | 2010 |  |  | N | IPP Non-CHP | 2 | X B: X; WAT BLQ: LFG; WAT DFO: OG |  |  |  | N | N |  | 1H |  |  |  | N | [19 empty] | N | N | N
Vintage2010 | biomass | TRUE | 22174 | PEI Power Corp | 50279 | Archbald Power Station | PA | Lackawanna | GEN6 | Landfill Gas | GT |  | S | X | X | 87901561 | ARCHTAP 13 KV PEI 6 | 4.6 | 1 | 4 | 4.6 | 2 | N |  |  | OP | X | 2 | 2010 |  |  | N | IPP Non-CHP | 2 | X B: X; WAT BLQ: LFG; WAT DFO: OG |  |  |  | N | N |  | 1H |  |  |  | N | [19 empty] | N | N | N
Vintage2001 | natural gas peaker | TRUE | 22174 | PEI Power Corp | 50279 | Archbald Power Station | PA | Lackawanna | Gen2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 1048036 | ARCHBTAP13 KV PEI 2 | 60.5 | 1 | 43.7 | 50 | 25 | N |  |  | OP | X | 5 | 2001 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X B to WAT BLQ; WAT DFO
Vintage1987 | hydro | TRUE | 63070 | GR Catalyst Two LLC | 50280 | Dahowa Hydro | NY | Washington | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 10.5 | 1 | 1.5 | 4.4 | 1.2 | N |  |  | OP | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | X B: X; WAT BLQ: WAT |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N
Vintage1983 | onshore wind | TRUE | 16630 | San Gorgonio Farms Inc | 50281 | San Gorgonio Farms Wind Farm | CA | Riverside | WGEN | Onshore Wind Turbine | WT |  | S | X | X | SANWD_1_QF | SANWD_1_QF | 31 |  | 31 | 31 | 0 | N |  |  | OP | X | 3 | 1983 |  |  | N | IPP Non-CHP | 2 | X B: X; WAT BLQ: WND |  |  |  | N |  | 111 | 10M
Vintage1995 | hydro | TRUE | 60832 | Sugar River Power LLC | 50285 | Lower Village Water Power Project | NH | Sullivan | 0001 | Conventional Hydroelectric | HY |  | S | X | X | 49693 | 49693 | 0.6 | 0.8 | 0.6 | 0.6 | 0.5 | N |  |  | OP | X | 5 | 1995 |  |  | N | IPP Non-CHP | 2 | X B: X; WAT BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1995 | hydro | TRUE | 60832 | Sugar River Power LLC | 50285 | Lower Village Water Power Project | NH | Sullivan | 0002 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.5 | N |  |  | OP | X | 5 | 1995 |  |  | N | IPP Non-CHP | 2 | X B: X; WAT BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1988 | municipal solid waste | TRUE | 16929 | SEMASS Partnership | 50290 | SEMASS Resource Recovery | MA | Plymouth | GEN1 | Municipal Solid Waste | ST |  | S | X | X | SEMASS |  | 64.5 | 0.9 | 53.3 | 53.3 | 6 | N |  |  | OP | X | 7 | 1988 |  |  | N | IPP Non-CHP | 2 | X | MSW | NG | DFO |  |  |  | DFO |  |  |  | N | N | 0 | 12H | [23 empty] | Y | N | N
Vintage1993 | municipal solid waste | TRUE | 16929 | SEMASS Partnership | 50290 | SEMASS Resource Recovery | MA | Plymouth | GEN2 | Municipal Solid Waste | ST |  | S | X | X | SEMASS |  | 34 | 0.9 | 26.7 | 26.7 | 9 | N |  |  | OP | X | 4 | 1993 |  |  | N | IPP Non-CHP | 2 | X | MSW | NG | DFO |  |  |  | DFO |  |  |  | N | N | 0 | 12H | [23 empty] | Y | N | N
Vintage1989 | natural gas combined cycle | TRUE | 24457 | Calpine Eastern Corp | 50292 | Bethpage Power Plant | NY | Nassau | GEN1 | Natural Gas Fired Combined Cycle | CT | G602 | S | X | N | NYISO_CALPINE_BP_GT1_DA | NYISO_CALPINE_BP_GT1_DA | 33.7 | 0.85 | 22.2 | 23.8 | 15 | N |  |  | OA | X | 8 | 1989 |  |  | N | IPP Non-CHP | 2 | X B: X; WAT BLQ: NG; WAT BIT: DFO |  |  |  |  | N |  | 12H | [23 empty] | Y | N | N
Vintage1989 | natural gas combined cycle | TRUE | 24457 | Calpine Eastern Corp | 50292 | Bethpage Power Plant | NY | Nassau | GEN2 | Natural Gas Fired Combined Cycle | CT | G602 | S | X | N | NYISO_CALPINE_BP_GT1_DA | NYISO_CALPINE_BP_GT1_DA | 33.7 | 0.85 | 22.2 | 23.8 | 15 | N |  |  | OP | X | 8 | 1989 |  |  | N | IPP Non-CHP | 2 | X B: X; WAT BLQ: NG; WAT BIT: DFO |  |  |  |  | N |  | 12H | [23 empty] | Y | N | N
Vintage1989 | natural gas combined cycle | TRUE | 24457 | Calpine Eastern Corp | 50292 | Bethpage Power Plant | NY | Nassau | GEN3 | Natural Gas Fired Combined Cycle | CA | G602 | S | N | X | NYISO_CALPINE_BP_GT1_DA | NYISO_CALPINE_BP_GT1_DA | 16.2 | 0.8 | 10.6 | 11.4 | 5 | N |  |  | OP | X | 8 | 1989 |  |  | N | IPP Non-CHP | 2 | [12 empty] | N |  | 12H | [23 empty] | N | N | N | bar: X B to WAT BLQ
Vintage1989 | petroleum | TRUE | 24457 | Calpine Eastern Corp | 50292 | Bethpage Power Plant | NY | Nassau | GEN4 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.4 | N |  |  | SB | Y | 8 | 1989 |  |  | N | IPP Non-CHP | 2 | X B: X; WAT BLQ: DFO |  |  |  |  | N |  | 10M | [23 empty] | N | N | N
Vintage2002 | natural gas peaker | TRUE | 24457 | Calpine Eastern Corp | 50292 | Bethpage Power Plant | NY | Nassau | GEN5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | NYISO_CALPINE_BP_GT1_DA | NYISO_CALPINE_BP_GT1_DA | 60 | 0.85 | 47 | 49.6 | 35 | N |  |  | OP | X | 7 | 2002 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X B to WAT BLQ
Vintage2005 | natural gas combined cycle | TRUE | 24457 | Calpine Eastern Corp | 50292 | Bethpage Power Plant | NY | Nassau | GEN6 | Natural Gas Fired Combined Cycle | CT | G603 | S | X | N | NYISO_CALPINEBETH_PAGE_GT4_DA | NYISO_CALPINEBETH_PAGE_GT4_DA | 60 | 0.85 | 49 | 50 | 35 | N |  |  | OP | X | 7 | 2005 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X B to WAT BLQ
Vintage2005 | natural gas combined cycle | TRUE | 24457 | Calpine Eastern Corp | 50292 | Bethpage Power Plant | NY | Nassau | GEN7 | Natural Gas Fired Combined Cycle | CA | G603 | S | Y | X | NYISO_CALPINEBETH_PAGE_GT4_DA | NYISO_CALPINEBETH_PAGE_GT4_DA | 36 | 0.85 | 33 | 34 | 5 | N |  |  | OP | X | 7 | 2005 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X B to WAT BLQ
Vintage1989 | biomass | TRUE | 19946 | Wadham Energy Ltd Partners | 50293 | Wadham Energy LP | CA | Colusa | GEN1 | Other Waste Biomass | ST |  | S | X | X | WADHAM _7_B1 | WADHAM _7_B1 | 29.1 | 0.9 | 26.5 | 26.5 | 15 | N |  |  | OP | X | 3 | 1989 |  |  | N | IPP Non-CHP | 2 | X B: X; WAT BLQ: AB; WAT DFO: NG |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1985 | biomass | TRUE | 14362 | Packaging Corp of America | 50296 | Packaging Corp of America | TN | Hardin | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 50 | 0.95 | 50 | 50 | 2 | N |  |  | OP | X | 2 | 1985 |  |  | Y | Industrial CHP | 7 | T | WDS | BLQ | NG | TDF | BIT |  | NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | N | [14 empty] | N |  |  | N | N | N
Vintage2010 | biomass | TRUE | 14362 | Packaging Corp of America | 50296 | Packaging Corp of America | TN | Hardin | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 22.5 | 0.9 | 22.5 | 22.5 | 2 | N |  |  | OP | X | 10 | 2010 |  |  | Y | Industrial CHP | 7 | X B: T; WAT BLQ: BLQ; WAT BIT: NG; WAT DFO: NG | DFO |  |  | N | N |  | OVER | [20 empty] | N |  |  | N | N | N
Vintage1988 | natural gas peaker | TRUE | 60134 | AltaGas Ripon Energy Inc. | 50299 | AltaGas Ripon Energy Inc. | CA | San Joaquin | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | POD_SMPRIP_1_SMPSOM-APND | POD_SMPRIP_1_SMPSOM-APND | 49.5 | 0.85 | 46.1 | 46.1 | 30 | N |  |  | OP | X | 4 | 1988 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X B to WAT BLQ; WAT DFO
Vintage2016 | other | TRUE | 54736 | VESI Pomona Energy Storage, Inc. | 50300 | VESI Pomona | CA | Los Angeles | BESS1 | Batteries | BA |  | S | X | X |  |  | 20 |  | 20 | 20 | 20 | N |  |  | OP | X | 12 | 2016 |  |  | N | IPP Non-CHP | 2 | X B: X; WAT BLQ: MWH |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1979 | other | FALSE | 64497 | Deer Park Refinery Limited Partnership (DPRLP) | 50304 | Shell Deer Park | TX | Harris | GEN1 | All Other | ST |  | S | X | X |  |  | 45.9 | 0.9 | 45 | 50 | 10 | N |  |  | OP | X | 10 | 1979 |  |  | N | Industrial CHP | 7 | X B: X; WAT BLQ: PUR; WAT DFO: PUR | [6 empty] | 12H | [20 empty] | N |  |  | N |  | N
Vintage1979 | other | FALSE | 64497 | Deer Park Refinery Limited Partnership (DPRLP) | 50304 | Shell Deer Park | TX | Harris | GEN2 | All Other | ST |  | S | X | X |  |  | 45.9 | 0.9 | 45 | 50 | 10 | N |  |  | OP | X | 10 | 1979 |  |  | N | Industrial CHP | 7 | X B: X; WAT BLQ: PUR; WAT DFO: PUR | [6 empty] | 12H | [20 empty] | N |  |  | N |  | N
Vintage1995 | natural gas peaker | FALSE | 64497 | Deer Park Refinery Limited Partnership (DPRLP) | 50304 | Shell Deer Park | TX | Harris | GEN4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 88.2 | 0.85 | 75 | 85 | 40 | N |  |  | OP | X | 4 | 1995 |  |  | Y | Industrial CHP | 7 | X B: T; WAT BLQ: NG; WAT BIT: OG |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | Y | N | N
Vintage1995 | natural gas peaker | FALSE | 64497 | Deer Park Refinery Limited Partnership (DPRLP) | 50304 | Shell Deer Park | TX | Harris | GEN5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 94 | 0.85 | 78 | 92 | 40 | N |  |  | OP | X | 4 | 1995 |  |  | Y | Industrial CHP | 7 | X B: T; WAT BLQ: NG; WAT BIT: OG |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | Y | N | N
Vintage1999 | petroleum | FALSE | 40430 | Lafarge Corp | 50305 | Alpena Cement Plant | MI | Alpena | GE10 | Petroleum Coke | ST |  | S | X | X |  |  | 3.2 | 0.8 | 3.2 | 3.2 | 0.5 | N |  |  | OP | X | 2 | 1999 |  |  | Y | Industrial CHP | 7 | B | PC | NG | OTH | OBL | WDS | OTH | NG |  |  |  | N | N |  | 12H | N | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1952 | petroleum | FALSE | 40430 | Lafarge Corp | 50305 | Alpena Cement Plant | MI | Alpena | GEN6 | Petroleum Coke | ST |  | S | X | X |  |  | 12 | 0.8 | 12 | 12 | 3 | N |  |  | OP | X | 1 | 1952 |  |  | Y | Industrial CHP | 7 | B | PC | NG | OTH | OBL | WDS | OTH | NG |  |  |  | N | N |  | 12H | N | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1955 | petroleum | FALSE | 40430 | Lafarge Corp | 50305 | Alpena Cement Plant | MI | Alpena | GEN7 | Petroleum Coke | ST |  | S | X | X |  |  | 10 | 0.8 | 10 | 10 | 4 | N |  |  | OP | X | 1 | 1955 |  |  | Y | Industrial CHP | 7 | B | PC | NG | OTH | OBL | WDS | OTH | NG |  |  |  | N | N |  | 12H | N | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1991 | petroleum | FALSE | 40430 | Lafarge Corp | 50305 | Alpena Cement Plant | MI | Alpena | GEN8 | Petroleum Coke | ST |  | S | X | X |  |  | 11 | 0.85 | 11 | 11 | 3 | N |  |  | OP | X | 4 | 1991 |  |  | Y | Industrial CHP | 7 | B | PC | NG | OTH | OBL | WDS | OTH | NG |  |  |  | N | N |  | 12H | N | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1994 | petroleum | FALSE | 40430 | Lafarge Corp | 50305 | Alpena Cement Plant | MI | Alpena | GEN9 | Petroleum Coke | ST |  | S | X | X |  |  | 11 | 0.85 | 11 | 11 | 3 | N |  |  | OP | X | 4 | 1994 |  |  | Y | Industrial CHP | 7 | B | PC | NG | OTH | OBL | WDS | OTH | NG |  |  |  | N | N |  | 12H | N | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1964 | natural gas steam turbine | FALSE | 19533 | University of Oklahoma | 50307 | University of Oklahoma | OK | Cleveland | GEN1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 7.5 | 0.8 | 7.5 | 7.5 | 0.5 | N |  |  | OP | X | 9 | 1964 |  |  | Y | Commercial CHP | 5 | [11 empty] | N |  |  | 12H | [20 empty] | N |  |  | N | bar: T B B B B B to NG PC PC PC PC PC; OG NG NG NG NG NG
Vintage1949 | natural gas steam turbine | FALSE | 19533 | University of Oklahoma | 50307 | University of Oklahoma | OK | Cleveland | GEN2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 0.6 | N |  |  | OP | X | 9 | 1949 |  |  | Y | Commercial CHP | 5 | [11 empty] | N |  |  | 12H | [20 empty] | N |  |  | N | bar: T B B B B B to NG PC PC PC PC PC; OG NG NG NG NG NG
Vintage1949 | natural gas steam turbine | FALSE | 19533 | University of Oklahoma | 50307 | University of Oklahoma | OK | Cleveland | GEN3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 0.6 | N |  |  | OP | X | 8 | 1949 |  |  | Y | Commercial CHP | 5 | [11 empty] | N |  |  | 12H | [20 empty] | N |  |  | N | N | N | bar: T B B B B B to NG PC PC PC PC PC; OG NG NG NG NG NG
Vintage1985 | natural gas steam turbine | FALSE | 19533 | University of Oklahoma | 50307 | University of Oklahoma | OK | Cleveland | GEN4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 4.3 | 0.8 | 4.3 | 4.3 | 0.3 | N |  |  | OP | X | 1 | 1985 |  |  | Y | Commercial CHP | 5 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | N | bar: T B B B B B to NG PC PC PC PC PC; OG NG NG NG NG NG
Vintage2001 | petroleum | FALSE | 19533 | University of Oklahoma | 50307 | University of Oklahoma | OK | Cleveland | GEN5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.4 | N |  |  | OP | X | 1 | 2001 |  |  | Y | Commercial CHP | 5 | T B B B B B: T; NG PC PC PC PC PC: DFO |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1955 | hard coal | TRUE | 56389 | Doyon Utilities - Ft. Wainwright | 50308 | Utility Plants Section | AK | Fairbanks North Star | GEN1 | Conventional Steam Coal | ST | F401 | S | X | X |  |  | 5 | 0.8 | 3.5 | 4.3 | 1.5 | N |  |  | OP | X | 1 | 1955 |  |  | Y | Electric Utility | 1 | T B B B B B: T; NG PC PC PC PC PC: SUB; OG NG NG NG NG NG: SUB |  |  |  | N | N |  | 12H |  |  | Y |  | Y | [18 empty] | N | N | N
Vintage1955 | hard coal | TRUE | 56389 | Doyon Utilities - Ft. Wainwright | 50308 | Utility Plants Section | AK | Fairbanks North Star | GEN3 | Conventional Steam Coal | ST | F401 | S | X | X |  |  | 5 | 0.8 | 6.2 | 6.2 | 1.5 | N |  |  | OP | X | 1 | 1955 |  |  | Y | Electric Utility | 1 | T B B B B B: T; NG PC PC PC PC PC: SUB; OG NG NG NG NG NG: SUB |  |  |  | N | N |  | 12H |  | N | Y |  | Y | [18 empty] | N | N | N
Vintage1955 | hard coal | TRUE | 56389 | Doyon Utilities - Ft. Wainwright | 50308 | Utility Plants Section | AK | Fairbanks North Star | GEN4 | Conventional Steam Coal | ST | F401 | S | X | X |  |  | 5 | 0.8 | 6.2 | 6.2 | 1.5 | N |  |  | OP | X | 1 | 1955 |  |  | Y | Electric Utility | 1 | T B B B B B: T; NG PC PC PC PC PC: SUB; OG NG NG NG NG NG: SUB |  |  |  | N | N |  | 12H |  | N | Y |  | Y | [18 empty] | N | N | N
Vintage1989 | hard coal | TRUE | 56389 | Doyon Utilities - Ft. Wainwright | 50308 | Utility Plants Section | AK | Fairbanks North Star | GEN5 | Conventional Steam Coal | ST | F401 | S | X | X |  |  | 5 | 0.8 | 6.2 | 6.2 | 1.5 | N |  |  | OP | X | 1 | 1989 |  |  | Y | Electric Utility | 1 | T B B B B B: T; NG PC PC PC PC PC: SUB; OG NG NG NG NG NG: SUB |  |  |  | N | N |  | 12H |  |  | Y |  | Y | [18 empty] | N | N | N
Vintage1988 | natural gas peaker | FALSE | 14762 | Pensacola Christian College | 50310 | Standby Generation Plant | FL | Escambia | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0 | N |  |  | SB | Y | 4 | 1988 |  |  | N | Commercial Non-CHP | 4 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: T B B B B B to NG PC PC PC PC PC
Vintage2006 | natural gas peaker | FALSE | 14762 | Pensacola Christian College | 50310 | Standby Generation Plant | FL | Escambia | 1SB | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.9 | 1.3 | 1.3 | 0 | N |  |  | SB | Y | 1 | 2006 |  |  | N | Commercial Non-CHP | 4 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: T B B B B B to NG PC PC PC PC PC
Vintage1988 | natural gas peaker | FALSE | 14762 | Pensacola Christian College | 50310 | Standby Generation Plant | FL | Escambia | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0 | N |  |  | SB | Y | 4 | 1988 |  |  | N | Commercial Non-CHP | 4 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: T B B B B B to NG PC PC PC PC PC
Vintage2006 | natural gas peaker | FALSE | 14762 | Pensacola Christian College | 50310 | Standby Generation Plant | FL | Escambia | 2SB | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.9 | 1.3 | 1.3 | 0 | N |  |  | SB | Y | 1 | 2006 |  |  | N | Commercial Non-CHP | 4 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: T B B B B B to NG PC PC PC PC PC
Vintage1988 | natural gas peaker | FALSE | 14762 | Pensacola Christian College | 50310 | Standby Generation Plant | FL | Escambia | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0 | N |  |  | SB | Y | 10 | 1988 |  |  | N | Commercial Non-CHP | 4 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: T B B B B B to NG PC PC PC PC PC
Vintage2006 | natural gas peaker | FALSE | 14762 | Pensacola Christian College | 50310 | Standby Generation Plant | FL | Escambia | 3SB | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.9 | 1.3 | 1.3 | 0 | N |  |  | SB | Y | 1 | 2006 |  |  | N | Commercial Non-CHP | 4 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: T B B B B B to NG PC PC PC PC PC
Vintage2006 | natural gas peaker | FALSE | 14762 | Pensacola Christian College | 50310 | Standby Generation Plant | FL | Escambia | 4SB | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.9 | 1.3 | 1.3 | 0 | N |  |  | SB | Y | 1 | 2006 |  |  | N | Commercial Non-CHP | 4 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: T B B B B B to NG PC PC PC PC PC
Vintage2006 | natural gas peaker | FALSE | 14762 | Pensacola Christian College | 50310 | Standby Generation Plant | FL | Escambia | 5SB | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.9 | 1.3 | 1.3 | 0 | N |  |  | SB | Y | 1 | 2006 |  |  | N | Commercial Non-CHP | 4 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: T B B B B B to NG PC PC PC PC PC
Vintage2006 | natural gas peaker | FALSE | 14762 | Pensacola Christian College | 50310 | Standby Generation Plant | FL | Escambia | 6SB | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.9 | 1.3 | 1.3 | 0 | N |  |  | SB | Y | 1 | 2006 |  |  | N | Commercial Non-CHP | 4 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: T B B B B B to NG PC PC PC PC PC
Vintage2006 | natural gas peaker | FALSE | 14762 | Pensacola Christian College | 50310 | Standby Generation Plant | FL | Escambia | 7SB | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.9 | 1.3 | 1.3 | 0 | N |  |  | SB | Y | 1 | 2006 |  |  | N | Commercial Non-CHP | 4 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: T B B B B B to NG PC PC PC PC PC
Vintage2006 | natural gas peaker | FALSE | 14762 | Pensacola Christian College | 50310 | Standby Generation Plant | FL | Escambia | 8SB | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.9 | 1.3 | 1.3 | 0 | N |  |  | SB | Y | 1 | 2006 |  |  | N | Commercial Non-CHP | 4 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: T B B B B B to NG PC PC PC PC PC
Vintage1935 | hydro | TRUE | 14539 | Passaic Valley Water Comm | 50311 | Passaic Valley Water Commission | NJ | Passaic | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.89 | 0.6 | 0.6 | 0.3 | N |  |  | OS | X | 1 | 1935 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N |  |  | OVER | [20 empty] | Y | 9 | 2022
Vintage1935 | hydro | TRUE | 14539 | Passaic Valley Water Comm | 50311 | Passaic Valley Water Commission | NJ | Passaic | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.89 | 0.6 | 0.6 | 0.3 | N |  |  | OS | X | 1 | 1935 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N |  |  | OVER | [20 empty] | Y | 9 | 2022
Vintage1935 | hydro | TRUE | 14539 | Passaic Valley Water Comm | 50311 | Passaic Valley Water Commission | NJ | Passaic | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.89 | 0.6 | 0.6 | 0.3 | N |  |  | OS | X | 1 | 1935 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N |  |  | OVER | [20 empty] | Y | 9 | 2022
Vintage1935 | hydro | TRUE | 14539 | Passaic Valley Water Comm | 50311 | Passaic Valley Water Commission | NJ | Passaic | GEN4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.89 | 0.6 | 0.6 | 0.3 | N |  |  | OS | X | 1 | 1935 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT | [6 empty] | OVER | [20 empty] | Y | 9 | 2022
Vintage1985 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50312 | Pembroke Hydro | NH | Merrimack | 1 | Conventional Hydroelectric | HY |  | W | X | X | 4395 | 4395 | 2.7 | 0.9 | 0.6 | 1.2 | 0.2 | N |  |  | OP | X | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N |  |  | 10M
Vintage1982 | hydro | TRUE | 24979 | Ampersand Chasm Hydro LLC | 50315 | Chasm Hydro Partnership | NY | Franklin | 1100 | Conventional Hydroelectric | HY |  | S | X | X | Zone D | Zone D | 1 | 1 | 0.5 | 0.8 | 0.2 | N |  |  | OA | X | 3 | 1982 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1984 | hydro | TRUE | 24979 | Ampersand Chasm Hydro LLC | 50315 | Chasm Hydro Partnership | NY | Franklin | 2600 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.5 | 0.6 | 0.5 | N |  |  | OA | X | 10 | 1984 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N | N | 0 | 10M | [20 empty] | Y | 7 | 2022 | N
Vintage1950 | natural gas steam turbine | FALSE | 3283 | Bunge North America East LLC | 50316 | Bunge North America East LLC | IN | Adams | 3516 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 2 | 0.9 | 2.2 | 2.2 | 1 | N |  |  | OP | X | 12 | 1950 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T B B B B B to NG PC PC PC PC PC; OG NG NG NG NG NG
Vintage1985 | hydro | TRUE | 26287 | Madera-Chowchilla Power Auth | 50322 | Site 980 65 | CA | Madera | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.1 | 0.9 | 2.1 | 2.1 | 0.5 | N |  |  | OP | X | 2 | 1985 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1985 | hydro | TRUE | 15286 | Marco Power Inc | 50323 | Marco Ranch | ID | Jerome | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 8 | 1985 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT | [5 empty] | 0 | 10M
Vintage1985 | hydro | TRUE | 15286 | Marco Power Inc | 50323 | Marco Ranch | ID | Jerome | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 8 | 1985 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT | [5 empty] | 0 | 10M
Vintage1985 | hydro | TRUE | 15286 | Marco Power Inc | 50323 | Marco Ranch | ID | Jerome | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 8 | 1985 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT | [5 empty] | 0 | 10M
Vintage1985 | hydro | TRUE | 15286 | Marco Power Inc | 50323 | Marco Ranch | ID | Jerome | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 8 | 1985 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT | [5 empty] | 0 | 10M
Vintage1983 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50324 | Newfound Hydroelectric | NH | Grafton | 1 | Conventional Hydroelectric | HY |  | W | X | X | 4379 |  | 0.7 | 0.91 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 12 | 1983 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N | N |  | 1H
Vintage1983 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50324 | Newfound Hydroelectric | NH | Grafton | 2 | Conventional Hydroelectric | HY |  | W | X | X | 4379 |  | 0.7 | 0.91 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 12 | 1983 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N | N |  | 1H
Vintage1985 | natural gas combined cycle | FALSE | 14293 | Nalco Co | 50326 | Nalco | IL | DuPage | AT1 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | Y |  |  | 4 | 0.8 | 3 | 3.5 | 0 | N |  |  | OP | X | 11 | 1985 |  |  | Y | Commercial CHP | 5 | [11 empty] | N |  |  | 10M | [23 empty] | N | N | N | bar: T B B B B B to NG PC PC PC PC PC
Vintage1985 | natural gas combined cycle | FALSE | 14293 | Nalco Co | 50326 | Nalco | IL | DuPage | DPOX | Natural Gas Fired Combined Cycle | CA | CC1 | W | Y | X |  |  | 0.7 | 0.8 | 0.7 | 0.7 | 0 | N |  |  | OS | X | 11 | 1985 |  |  | Y | Commercial CHP | 5 | [11 empty] | N |  |  | 10M | [23 empty] | N | N | N | bar: T B B B B B to NG PC PC PC PC PC
Vintage1988 | hydro | TRUE | 64843 | Dakota County, MN | 50328 | Byllesby | MN | Dakota | 1 | Conventional Hydroelectric | HY |  | S | X | X | NSP |  | 0.8 | 1 | 0.8 | 0.8 | 0.2 | N |  |  | OP | X | 3 | 1988 |  |  | N | Electric Utility | 1 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N |  | 0 | 10M
Vintage1988 | hydro | TRUE | 64843 | Dakota County, MN | 50328 | Byllesby | MN | Dakota | 2 | Conventional Hydroelectric | HY |  | S | X | X | NSP |  | 0.8 | 1 | 0.8 | 0.8 | 0.2 | N |  |  | OP | X | 3 | 1988 |  |  | N | Electric Utility | 1 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N |  | 0 | 10M
Vintage1988 | hydro | TRUE | 64843 | Dakota County, MN | 50328 | Byllesby | MN | Dakota | 3 | Conventional Hydroelectric | HY |  | S | X | X | NSP |  | 0.9 | 1 | 0.9 | 0.9 | 0.2 | N |  |  | OP | X | 3 | 1988 |  |  | N | Electric Utility | 1 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N |  | 0 | 10M
Vintage2012 | biomass | TRUE | 10004 | King County Dept-Natural Res | 50329 | West Point Treatment Plant | WA | King | 4 | Other Waste Biomass | IC |  | S | X | X |  |  | 2.3 | 0.7 | 2.3 | 2.3 | 1.7 | N |  |  | OP | X | 6 | 2012 |  |  | Y | Commercial CHP | 5 | T B B B B B: T; NG PC PC PC PC PC: OBG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2012 | biomass | TRUE | 10004 | King County Dept-Natural Res | 50329 | West Point Treatment Plant | WA | King | 5 | Other Waste Biomass | IC |  | S | X | X |  |  | 2.3 | 0.7 | 2.3 | 2.3 | 1.7 | N |  |  | OP | X | 6 | 2012 |  |  | Y | Commercial CHP | 5 | T B B B B B: T; NG PC PC PC PC PC: OBG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2010 | petroleum | FALSE | 7019 | Gay & Robinson Inc | 50333 | Gay Robinson | HI | Kauai | DSL5 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.2 | N |  |  | SB | N | 4 | 2010 |  |  | N | Industrial Non-CHP | 6 | T B B B B B: X; NG PC PC PC PC PC: DFO |  |  |  |  | N |  | 1H | [23 empty] | N
Vintage2010 | petroleum | FALSE | 7019 | Gay & Robinson Inc | 50333 | Gay Robinson | HI | Kauai | DSL6 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.2 | N |  |  | SB | N | 4 | 2010 |  |  | N | Industrial Non-CHP | 6 | T B B B B B: X; NG PC PC PC PC PC: DFO |  |  |  |  | N |  | 1H | [23 empty] | N
Vintage1982 | hydro | FALSE | 7019 | Gay & Robinson Inc | 50333 | Gay Robinson | HI | Kauai | HYD2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.8 | 0.8 | 0.8 | 0.2 | N |  |  | OP | X | 3 | 1982 |  |  | N | Industrial Non-CHP | 6 | T B B B B B: X; NG PC PC PC PC PC: WAT | [5 empty] | 0 | 12H | [23 empty] | N
Vintage2019 | hydro | FALSE | 7019 | Gay & Robinson Inc | 50333 | Gay Robinson | HI | Kauai | HYD3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.5 | 0.9 | 6.5 | 6.5 | 0.5 | N |  |  | OP | X | 1 | 2019 |  |  | N | Industrial Non-CHP | 6 | T B B B B B: X; NG PC PC PC PC PC: WAT | [6 empty] | 1H
Vintage1986 | natural gas peaker | FALSE | 21690 | Moose International | 50337 | Mooseheart Power House | IL | Kane | GEN1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.5 | N |  |  | SB | Y | 8 | 1986 |  |  | Y | Commercial CHP | 5 | [12 empty] | N |  | 1H | [23 empty] | N | bar: T B B B B B to NG PC PC PC PC PC
Vintage1986 | natural gas peaker | FALSE | 21690 | Moose International | 50337 | Mooseheart Power House | IL | Kane | GEN2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.5 | N |  |  | SB | Y | 8 | 1986 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H |  |  |  | N | [19 empty] | N | bar: T B B B B B to NG PC PC PC PC PC
Vintage1986 | natural gas peaker | FALSE | 21690 | Moose International | 50337 | Mooseheart Power House | IL | Kane | GEN3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.3 | N |  |  | SB | Y | 8 | 1986 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H |  |  |  | N | [19 empty] | N | bar: T B B B B B to NG PC PC PC PC PC
Vintage1986 | natural gas peaker | FALSE | 21690 | Moose International | 50337 | Mooseheart Power House | IL | Kane | GEN4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.5 | N |  |  | SB | Y | 8 | 1986 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H |  |  |  | N | [19 empty] | N | bar: T B B B B B to NG PC PC PC PC PC
Vintage2006 | other | FALSE | 15237 | PCS Nitrogen LP | 50341 | PCS Nitrogen Fertilizer LP | LA | Iberville | GEN2 | All Other | ST |  | S | X | X |  |  | 10 | 0.8 | 8 | 8 | 1 | N |  |  | OS | X | 3 | 2006 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: T B B B B B to NG PC PC PC PC PC; OG NG NG NG NG NG
Vintage2010 | petroleum | FALSE | 15237 | PCS Nitrogen LP | 50341 | PCS Nitrogen Fertilizer LP | LA | Iberville | GEN3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 0.1 | N |  |  | SB | Y | 10 | 2010 |  |  | N | Industrial Non-CHP | 6 | T B B B B B: X; NG PC PC PC PC PC: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage2014 | petroleum | FALSE | 15237 | PCS Nitrogen LP | 50341 | PCS Nitrogen Fertilizer LP | LA | Iberville | GEN4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 1.8 | 0.1 | N |  |  | SB | Y | 10 | 2014 |  |  | N | Industrial Non-CHP | 6 | T B B B B B: X; NG PC PC PC PC PC: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1992 | hydro | TRUE | 8530 | HYPOWER INC | 50350 | Forks of Butte Hydro Project | CA | Butte | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 14.5 | 0.9 | 14.5 | 14.5 | 0.7 | N |  |  | OP | X | 3 | 1992 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1987 | hydro | TRUE | 24793 | Briar-Hydro Associates | 50351 | Rolfe Canal Hydro | NH | Merrimack | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.3 | 0.9 | 4.3 | 4.3 | 0.2 | N |  |  | OP | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1987 | hydro | TRUE | 12850 | Monterey Cnty Water Res Agency | 50352 | Nacimiento Hydro Project | CA | San Luis Obispo | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4 | 0.9 | 3.7 | 3.6 | 0.7 | N |  |  | OP | X | 7 | 1987 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1987 | hydro | TRUE | 12850 | Monterey Cnty Water Res Agency | 50352 | Nacimiento Hydro Project | CA | San Luis Obispo | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 7 | 1987 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1983 | hydro | TRUE | 24793 | Briar-Hydro Associates | 50353 | Penacook Lower Falls | NH | Merrimack | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.6 | 0.9 | 4.6 | 4.6 | 0.1 | N |  |  | OP | X | 8 | 1983 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N |  | 0 | 1H | [23 empty] | N
Vintage1987 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50354 | Newport Hydro | NY | Herkimer | 1 | Conventional Hydroelectric | HY |  | W | X | X | 23633 | 23633 | 0.8 | 0.8 | 0.8 | 0.8 | 0.2 | N |  |  | OP | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N |  | 0 | 1H
Vintage1987 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50354 | Newport Hydro | NY | Herkimer | 2 | Conventional Hydroelectric | HY |  | W | X | X | 23633 | 23633 | 0.8 | 0.8 | 0.8 | 0.8 | 0.2 | N |  |  | OP | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N |  | 0 | 1H
Vintage1987 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50354 | Newport Hydro | NY | Herkimer | 3 | Conventional Hydroelectric | HY |  | W | X | X | 23633 | 23633 | 0.1 | 0.8 | 0.1 | 0.1 | 0 | N |  |  | OP | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N |  | 0 | 1H
Vintage1958 | natural gas steam turbine | FALSE | 62972 | Bluestone Coke LLC | 50359 | Sloss Industries Corp | AL | Jefferson | 10 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 12.5 | 0.8 | 8.5 | 7.5 | 3 | N |  |  | OS | X | 5 | 1958 |  |  | Y | Industrial CHP | 7 | T B B B B B: B; NG PC PC PC PC PC: NG; OG NG NG NG NG NG: OG; OG NG NG NG NG NG: OG |  |  |  | N | N |  | 12H | [23 empty] | N | N
Vintage1958 | natural gas steam turbine | FALSE | 62972 | Bluestone Coke LLC | 50359 | Sloss Industries Corp | AL | Jefferson | 9 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 12.5 | 0.8 | 7.5 | 6.5 | 3 | N |  |  | OS | X | 5 | 1958 |  |  | Y | Industrial CHP | 7 | T B B B B B: B; NG PC PC PC PC PC: NG; OG NG NG NG NG NG: OG; OG NG NG NG NG NG: OG |  |  |  | N | N |  | 12H | [23 empty] | N | N
Vintage1989 | hydro | TRUE | 14243 | Owyhee Irrigation District | 50360 | Michell Butte Power Project | OR | Malheur | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.4 | N |  |  | OP | X | 5 | 1989 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT | [6 empty] | 10M
Vintage1985 | hydro | TRUE | 14243 | Owyhee Irrigation District | 50361 | Owyhee Dam Power Project | OR | Malheur | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.3 | 1 | 2.9 | 2.9 | 0.8 | N |  |  | OP | X | 8 | 1985 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT | [6 empty] | 10M
Vintage1993 | hydro | TRUE | 14243 | Owyhee Irrigation District | 50362 | Tunnel 1 Power Project | OR | Malheur | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7 | 1 | 6.7 | 6.4 | 1 | N |  |  | SB | Y | 6 | 1993 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N |  |  | 10M
Vintage1987 | biomass | TRUE | 55960 | Mesquite Lake Energy Park | 50363 | Mesquite Lake Energy Park Plant 2 | CA | Imperial | L313 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 21 | 1 | 15.5 | 15.5 | 0 | N |  |  | OS | X | 11 | 1987 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WDS; OG NG NG NG NG NG: NG |  |  |  | N |  |  | OVER | [23 empty] | N | N | N
Vintage2005 | biomass | TRUE | 56889 | Rhode Island LFG Genco | 50365 | Ridgewood Providence Power | RI | Providence | PH21 | Landfill Gas | IC |  | S | X | X | 10959 | 10959 | 1.6 | 0.8 | 1.5 | 1.5 | 1.5 | N |  |  | OA | X | 8 | 2005 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: LFG |  |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage2005 | biomass | TRUE | 56889 | Rhode Island LFG Genco | 50365 | Ridgewood Providence Power | RI | Providence | PH22 | Landfill Gas | IC |  | S | X | X | 10959 | 10959 | 1.6 | 0.8 | 1.5 | 1.5 | 1.5 | N |  |  | OA | X | 8 | 2005 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: LFG |  |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage2005 | biomass | TRUE | 56889 | Rhode Island LFG Genco | 50365 | Ridgewood Providence Power | RI | Providence | PH23 | Landfill Gas | IC |  | S | X | X | 10959 | 10959 | 1.6 | 0.8 | 1.5 | 1.5 | 1.5 | N |  |  | OA | X | 8 | 2005 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: LFG |  |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage2005 | biomass | TRUE | 56889 | Rhode Island LFG Genco | 50365 | Ridgewood Providence Power | RI | Providence | PH24 | Landfill Gas | IC |  | S | X | X | 10959 | 10959 | 1.6 | 0.8 | 1.5 | 1.5 | 1.5 | N |  |  | OA | X | 8 | 2005 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: LFG |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1962 | natural gas steam turbine | FALSE | 19564 | University of Notre Dame | 50366 | University of Notre Dame | IN | St Joseph | GEN1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 0.5 | N |  |  | OP | X | 6 | 1962 |  |  | Y | Commercial CHP | 5 | T B B B B B: T; NG PC PC PC PC PC: NG; OG NG NG NG NG NG: DFO; OG NG NG NG NG NG: NG | DFO |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1952 | natural gas steam turbine | FALSE | 19564 | University of Notre Dame | 50366 | University of Notre Dame | IN | St Joseph | GEN2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 1.7 | 0.8 | 1.7 | 1.7 | 0.5 | N |  |  | OP | X | 7 | 1952 |  |  | Y | Commercial CHP | 5 | T B B B B B: T; NG PC PC PC PC PC: NG; OG NG NG NG NG NG: DFO; OG NG NG NG NG NG: NG | DFO |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1952 | petroleum | FALSE | 19564 | University of Notre Dame | 50366 | University of Notre Dame | IN | St Joseph | GEN3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.3 | N |  |  | SB | Y | 7 | 1952 |  |  | N | Commercial CHP | 5 | T B B B B B: X; NG PC PC PC PC PC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1952 | petroleum | FALSE | 19564 | University of Notre Dame | 50366 | University of Notre Dame | IN | St Joseph | GEN4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.3 | N |  |  | SB | Y | 7 | 1952 |  |  | N | Commercial CHP | 5 | T B B B B B: X; NG PC PC PC PC PC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N |  | N
Vintage1956 | natural gas steam turbine | FALSE | 19564 | University of Notre Dame | 50366 | University of Notre Dame | IN | St Joseph | GEN5 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.5 | N |  |  | OP | X | 9 | 1956 |  |  | Y | Commercial CHP | 5 | T B B B B B: T; NG PC PC PC PC PC: NG; OG NG NG NG NG NG: DFO; OG NG NG NG NG NG: NG | DFO |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1967 | natural gas steam turbine | FALSE | 19564 | University of Notre Dame | 50366 | University of Notre Dame | IN | St Joseph | GEN6 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 5 | 0.8 | 5 | 5 | 0.5 | N |  |  | OP | X | 2 | 1967 |  |  | Y | Commercial CHP | 5 | T B B B B B: T; NG PC PC PC PC PC: NG; OG NG NG NG NG NG: DFO; OG NG NG NG NG NG: NG | DFO |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage2000 | natural gas steam turbine | FALSE | 19564 | University of Notre Dame | 50366 | University of Notre Dame | IN | St Joseph | GEN7 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 9.4 | 0.8 | 9.4 | 9.4 | 0.5 | N |  |  | OP | X | 3 | 2000 |  |  | Y | Commercial CHP | 5 | T B B B B B: T; NG PC PC PC PC PC: NG; OG NG NG NG NG NG: DFO; OG NG NG NG NG NG: NG | DFO |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage2006 | petroleum | FALSE | 19564 | University of Notre Dame | 50366 | University of Notre Dame | IN | St Joseph | GEN8 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.9 | 0.8 | 1.7 | 1.8 | 0.1 | N |  |  | OP | X | 10 | 2006 |  |  | N | Commercial CHP | 5 | T B B B B B: X; NG PC PC PC PC PC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N | N
Vintage2006 | petroleum | FALSE | 19564 | University of Notre Dame | 50366 | University of Notre Dame | IN | St Joseph | GEN9 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.9 | 0.8 | 1.7 | 1.8 | 0.1 | N |  |  | OP | X | 10 | 2006 |  |  | N | Commercial CHP | 5 | T B B B B B: X; NG PC PC PC PC PC: DFO |  |  |  | N |  |  | 10M | [23 empty] | N | N
Vintage2006 | petroleum | FALSE | 19564 | University of Notre Dame | 50366 | University of Notre Dame | IN | St Joseph | GN10 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.9 | 0.8 | 1.7 | 1.8 | 0.1 | N |  |  | OP | X | 10 | 2006 |  |  | N | Commercial CHP | 5 | T B B B B B: X; NG PC PC PC PC PC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage2019 | natural gas peaker | FALSE | 19564 | University of Notre Dame | 50366 | University of Notre Dame | IN | St Joseph | GT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 5.4 | 0.8 | 5.6 | 4.7 | 2.7 | N |  |  | OP | X | 6 | 2019 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T B B B B B to NG PC PC PC PC PC
Vintage2019 | natural gas peaker | FALSE | 19564 | University of Notre Dame | 50366 | University of Notre Dame | IN | St Joseph | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 5.4 | 0.8 | 5.6 | 4.7 | 2.7 | N |  |  | OP | X | 6 | 2019 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: T B B B B B to NG PC PC PC PC PC
Vintage2009 | natural gas combined cycle | FALSE | 21508 | Cornell University | 50368 | Cornell University Central Heat | NY | Tompkins | CT1 | Natural Gas Fired Combined Cycle | CT | CT1 | S | X | N |  |  | 15 | 0.8 | 12.3 | 14.5 | 8 | N |  |  | OP | X | 12 | 2009 |  |  | Y | Commercial CHP | 5 | T B B B B B: T; NG PC PC PC PC PC: NG; OG NG NG NG NG NG: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage2009 | natural gas combined cycle | FALSE | 21508 | Cornell University | 50368 | Cornell University Central Heat | NY | Tompkins | CT2 | Natural Gas Fired Combined Cycle | CT | CT2 | S | X | N |  |  | 15 | 0.8 | 12.3 | 14.5 | 8 | N |  |  | OP | X | 12 | 2009 |  |  | Y | Commercial CHP | 5 | T B B B B B: T; NG PC PC PC PC PC: NG; OG NG NG NG NG NG: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage2009 | petroleum | FALSE | 21508 | Cornell University | 50368 | Cornell University Central Heat | NY | Tompkins | EDG1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 0.9 | 1 | 0.3 | N |  |  | SB | Y | 12 | 2009 |  |  | N | Commercial CHP | 5 | T B B B B B: X; NG PC PC PC PC PC: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage2009 | petroleum | FALSE | 21508 | Cornell University | 50368 | Cornell University Central Heat | NY | Tompkins | EDG2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 0.9 | 1 | 0.3 | N |  |  | SB | Y | 12 | 2009 |  |  | N | Commercial CHP | 5 | T B B B B B: X; NG PC PC PC PC PC: DFO |  |  |  |  | N |  | 10M | [23 empty] | N | N | N
Vintage1988 | natural gas combined cycle | FALSE | 21508 | Cornell University | 50368 | Cornell University Central Heat | NY | Tompkins | TG1 | Natural Gas Fired Combined Cycle | CA | CT1 | S | Y | X |  |  | 1.8 | 0.8 | 1 | 1.8 | 0.2 | N |  |  | SB | Y | 7 | 1988 |  |  | Y | Commercial CHP | 5 | T B B B B B: B; NG PC PC PC PC PC: NG; OG NG NG NG NG NG: DFO |  |  |  | N |  |  | 12H |  |  |  |  | N | [18 empty] | N | N | N
Vintage1988 | natural gas combined cycle | FALSE | 21508 | Cornell University | 50368 | Cornell University Central Heat | NY | Tompkins | TG2 | Natural Gas Fired Combined Cycle | CA | CT2 | S | Y | X |  |  | 5.7 | 0.8 | 5.3 | 5.7 | 0.4 | N |  |  | OP | X | 10 | 1988 |  |  | Y | Commercial CHP | 5 | T B B B B B: B; NG PC PC PC PC PC: NG; OG NG NG NG NG NG: DFO |  |  |  | N |  |  | 12H |  |  |  |  | N | [18 empty] | N | N | N
Vintage1986 | natural gas peaker | TRUE | 13875 | Energy Center Paxton LLC | 50373 | Paxton Creek Cogeneration | PA | Dauphin | GEN1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PJM West | PJM West | 6.3 | 0.96 | 6 | 6 | 2 | N |  |  | SB | Y | 8 | 1986 |  |  | Y | IPP CHP | 3 | T B B B B B: T; NG PC PC PC PC PC: NG; OG NG NG NG NG NG: DFO; OG NG NG NG NG NG: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | Y | Y
Vintage1986 | natural gas peaker | TRUE | 13875 | Energy Center Paxton LLC | 50373 | Paxton Creek Cogeneration | PA | Dauphin | GEN2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | PJM West | PJM West | 6.3 | 0.96 | 6 | 6 | 2 | N |  |  | SB | Y | 8 | 1986 |  |  | Y | IPP CHP | 3 | T B B B B B: T; NG PC PC PC PC PC: NG; OG NG NG NG NG NG: DFO; OG NG NG NG NG NG: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | Y | Y
Vintage1987 | hydro | TRUE | 30076 | Calleguas Mun Water District | 50375 | East Portal Generator | CA | Los Angeles | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 1 | 1.2 | 1.2 | 0.3 | N |  |  | OP | X | 1 | 1987 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1936 | hydro | TRUE | 42892 | City of Spokane | 50380 | Upriver Dam Hydro Plant | WA | Spokane | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.9 | 0.5 | 1.5 | 0.2 | N |  |  | OP | X | 1 | 1936 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1936 | hydro | TRUE | 42892 | City of Spokane | 50380 | Upriver Dam Hydro Plant | WA | Spokane | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.9 | 0.5 | 1.5 | 0.2 | N |  |  | OP | X | 1 | 1936 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N | N | 0 | 1H
Vintage1936 | hydro | TRUE | 42892 | City of Spokane | 50380 | Upriver Dam Hydro Plant | WA | Spokane | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.9 | 0.5 | 1.5 | 0.2 | N |  |  | OP | X | 1 | 1936 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N | N | 0 | 1H
Vintage1984 | hydro | TRUE | 42892 | City of Spokane | 50380 | Upriver Dam Hydro Plant | WA | Spokane | GEN4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.8 | 0.9 | 1.5 | 5 | 0.5 | N |  |  | OP | X | 6 | 1984 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT | [5 empty] | 0 | 12H
Vintage1984 | hydro | TRUE | 42892 | City of Spokane | 50380 | Upriver Dam Hydro Plant | WA | Spokane | GEN5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.8 | 0.9 | 1.5 | 5 | 0.5 | N |  |  | OP | X | 6 | 1984 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT | [5 empty] | 0 | 12H
Vintage1988 | hydro | TRUE | 20032 | Walla Walla City of | 50382 | Twin Reservoirs | WA | Walla Walla | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 0.9 | 1.8 | 1.5 | 0.4 | N |  |  | OP | X | 4 | 1988 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1985 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50384 | Gregg Falls | NH | Hillsborough | 1 | Conventional Hydroelectric | HY |  | W | X | X | 4397 | 4397 | 2.2 | 0.9 | 2.1 | 2.1 | 0.3 | N |  |  | OP | X | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N |  |  | 10M
Vintage1985 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50384 | Gregg Falls | NH | Hillsborough | 2 | Conventional Hydroelectric | HY |  | W | X | X | 4397 | 4397 | 1.3 | 0.9 | 1.3 | 1.3 | 0.2 | N |  |  | OP | X | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N |  |  | 10M
Vintage1993 | natural gas combined cycle | TRUE | 55846 | Newark Bay Cogeneration Partnership LP | 50385 | Newark Bay Cogeneration Partnership LP | NJ | Essex | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | 93173 | 93173 | 55 | 0.85 | 120.2 | 136.2 | 27 | N |  |  | OP | X | 9 | 1993 | 5 | 2022 | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: T B B B B B to NG PC PC PC PC PC
Vintage1993 | natural gas combined cycle | TRUE | 55846 | Newark Bay Cogeneration Partnership LP | 50385 | Newark Bay Cogeneration Partnership LP | NJ | Essex | GEN2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | 93173 | 93173 | 55 | 0.85 |  |  | 27 | N |  |  | OP | X | 9 | 1993 | 5 | 2022 | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: T B B B B B to NG PC PC PC PC PC
Vintage1993 | natural gas combined cycle | TRUE | 55846 | Newark Bay Cogeneration Partnership LP | 50385 | Newark Bay Cogeneration Partnership LP | NJ | Essex | GEN3 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X | 93173 | 93173 | 42 | 0.85 |  |  | 10 | N |  |  | OP | X | 9 | 1993 | 5 | 2022 | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: T B B B B B to NG PC PC PC PC PC
Vintage1983 | petroleum | FALSE | 4208 | Phillips 66 Company | 50388 | Phillips 66 Carbon Plant | CA | Contra Costa | GEN1 | Petroleum Coke | ST |  | S | X | X |  |  | 27.3 | 0.85 | 20 | 20 | 2 | N |  |  | OP | X | 12 | 1983 | 12 | 2023 | Y | Industrial CHP | 7 | T B B B B B: B; NG PC PC PC PC PC: PC; OG NG NG NG NG NG: NG |  |  |  | N | N |  | OVER |  |  |  | Y | Y | N | [17 empty] | N | N | N
Vintage1990 | natural gas peaker | FALSE | 15173 | Placid Refining Co LLC | 50389 | Port Allen (LA) | LA | West Baton Rouge | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.8 | 0.9 | 3.5 | 3.5 | 2 | N |  |  | OP | X | 5 | 1990 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N | 0 | 10M | [23 empty] | N | N | N | bar: T B B B B B to NG PC PC PC PC PC; OG NG NG NG NG NG
Vintage1990 | natural gas peaker | FALSE | 15173 | Placid Refining Co LLC | 50389 | Port Allen (LA) | LA | West Baton Rouge | GEN2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.8 | 0.9 | 3.5 | 3.5 | 2 | N |  |  | OP | X | 5 | 1990 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N | 0 | 10M | [23 empty] | N | N | N | bar: T B B B B B to NG PC PC PC PC PC; OG NG NG NG NG NG
Vintage1998 | petroleum | FALSE | 22199 | U S Air Force-Eielson AFB | 50392 | Eielson AFB Central Heat & Power Plant | AK | Fairbanks North Star | DG01 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.4 | 1.4 | 0.3 | N |  |  | SB | Y | 11 | 1998 |  |  | N | Commercial CHP | 5 | T B B B B B: X; NG PC PC PC PC PC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1998 | petroleum | FALSE | 22199 | U S Air Force-Eielson AFB | 50392 | Eielson AFB Central Heat & Power Plant | AK | Fairbanks North Star | DG02 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.4 | 1.4 | 0.3 | N |  |  | SB | Y | 11 | 1998 |  |  | N | Commercial CHP | 5 | T B B B B B: X; NG PC PC PC PC PC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1998 | petroleum | FALSE | 22199 | U S Air Force-Eielson AFB | 50392 | Eielson AFB Central Heat & Power Plant | AK | Fairbanks North Star | DG03 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.4 | 1.4 | 0.3 | N |  |  | SB | Y | 11 | 1998 |  |  | N | Commercial CHP | 5 | T B B B B B: X; NG PC PC PC PC PC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1998 | petroleum | FALSE | 22199 | U S Air Force-Eielson AFB | 50392 | Eielson AFB Central Heat & Power Plant | AK | Fairbanks North Star | DG04 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.4 | 1.4 | 0.3 | N |  |  | SB | Y | 11 | 1998 |  |  | N | Commercial CHP | 5 | T B B B B B: X; NG PC PC PC PC PC: DFO |  |  |  | N | N |  | 10M | [23 empty] | N |  | N
Vintage1952 | hard coal | FALSE | 22199 | U S Air Force-Eielson AFB | 50392 | Eielson AFB Central Heat & Power Plant | AK | Fairbanks North Star | TG1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 2.5 | 0.8 | 0.5 | 2.2 | 0.5 | N |  |  | OP | X | 10 | 1952 |  |  | Y | Commercial CHP | 5 | T B B B B B: T; NG PC PC PC PC PC: SUB; OG NG NG NG NG NG: SUB |  |  |  | N | N |  | 12H |  |  | Y |  | Y | [18 empty] | N |  | N
Vintage1952 | hard coal | FALSE | 22199 | U S Air Force-Eielson AFB | 50392 | Eielson AFB Central Heat & Power Plant | AK | Fairbanks North Star | TG2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 2.5 | 0.8 | 0.5 | 2.2 | 0.5 | N |  |  | OP | X | 10 | 1952 |  |  | Y | Commercial CHP | 5 | T B B B B B: T; NG PC PC PC PC PC: SUB; OG NG NG NG NG NG: SUB |  |  |  | N | N |  | 12H |  |  | Y |  | Y | [18 empty] | N |  | N
Vintage1955 | hard coal | FALSE | 22199 | U S Air Force-Eielson AFB | 50392 | Eielson AFB Central Heat & Power Plant | AK | Fairbanks North Star | TG3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 5 | 0.8 | 5 | 5 | 1 | N |  |  | OP | X | 8 | 1955 |  |  | Y | Commercial CHP | 5 | T B B B B B: T; NG PC PC PC PC PC: SUB; OG NG NG NG NG NG: SUB |  |  |  | N | N |  | 12H |  | N | Y |  | Y | [18 empty] | N | N | N
Vintage1969 | hard coal | FALSE | 22199 | U S Air Force-Eielson AFB | 50392 | Eielson AFB Central Heat & Power Plant | AK | Fairbanks North Star | TG4 | Conventional Steam Coal | ST |  | S | X | X |  |  | 5 | 0.8 | 5 | 5 | 1 | N |  |  | OP | X | 6 | 1969 |  |  | Y | Commercial CHP | 5 | T B B B B B: T; NG PC PC PC PC PC: SUB; OG NG NG NG NG NG: SUB |  |  |  | N | N |  | 12H |  | N | Y |  | Y | [18 empty] | N | N | N
Vintage1987 | hard coal | FALSE | 22199 | U S Air Force-Eielson AFB | 50392 | Eielson AFB Central Heat & Power Plant | AK | Fairbanks North Star | TG5 | Conventional Steam Coal | ST |  | S | X | X |  |  | 10 | 0.8 | 9 | 9.5 | 3 | N |  |  | OP | X | 10 | 1987 |  |  | Y | Commercial CHP | 5 | T B B B B B: T; NG PC PC PC PC PC: SUB; OG NG NG NG NG NG: SUB |  |  |  | N | N |  | 12H |  | N | Y |  | Y | [18 empty] | N | N | N
Vintage1986 | hydro | TRUE | 25438 | Friant Power Authority | 50393 | Friant Hydro Facility | CA | Fresno | FR1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18.4 | 0.9 | 20 | 20 | 1 | N |  |  | OP | X | 1 | 1986 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 25438 | Friant Power Authority | 50393 | Friant Hydro Facility | CA | Fresno | M1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9.8 | 0.9 | 9.8 | 9.8 | 1 | N |  |  | OP | X | 7 | 1985 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 25438 | Friant Power Authority | 50393 | Friant Hydro Facility | CA | Fresno | RO1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.84 | 2.3 | 2.3 | 0.5 | N |  |  | OP | X | 4 | 1985 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage2017 | hydro | TRUE | 25438 | Friant Power Authority | 50393 | Friant Hydro Facility | CA | Fresno | RO2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.9 | 0.9 | 7.3 | 7.3 | 0.5 | N |  |  | OP | X | 6 | 2017 |  |  | N | IPP Non-CHP | 2 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1917 | hydro | FALSE | 5033 | Domtar Industries Inc | 50395 | Georgia-Pacific Corp - Nekoosa Mill | WI | Wood | HY1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | N |  |  | OP | X | 1 | 1917 |  |  | N | Industrial CHP | 7 | T B B B B B: X; NG PC PC PC PC PC: WAT |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1917 | hydro | FALSE | 5033 | Domtar Industries Inc | 50395 | Georgia-Pacific Corp - Nekoosa Mill | WI | Wood | HY2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | N |  |  | OP | X | 1 | 1917 |  |  | N | Industrial CHP | 7 | T B B B B B: X; NG PC PC PC PC PC: WAT | [6 empty] | 1H | [23 empty] | N
Vintage1923 | hydro | FALSE | 5033 | Domtar Industries Inc | 50395 | Georgia-Pacific Corp - Nekoosa Mill | WI | Wood | HY3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | N |  |  | OP | X | 1 | 1923 |  |  | N | Industrial CHP | 7 | T B B B B B: X; NG PC PC PC PC PC: WAT | [6 empty] | 1H | [23 empty] | N
Vintage1912 | hydro | FALSE | 5033 | Domtar Industries Inc | 50395 | Georgia-Pacific Corp - Nekoosa Mill | WI | Wood | HY4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.3 | N |  |  | OA | X | 1 | 1912 |  |  | N | Industrial CHP | 7 | T B B B B B: X; NG PC PC PC PC PC: WAT | [6 empty] | 1H | [23 empty] | N
Vintage1950 | hydro | FALSE | 5033 | Domtar Industries Inc | 50395 | Georgia-Pacific Corp - Nekoosa Mill | WI | Wood | HY5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.8 | 0.7 | 0.6 | 0.3 | N |  |  | OA | X | 1 | 1950 |  |  | N | Industrial CHP | 7 | T B B B B B: X; NG PC PC PC PC PC: WAT | [6 empty] | 1H | [23 empty] | N
Vintage1926 | hydro | FALSE | 5033 | Domtar Industries Inc | 50395 | Georgia-Pacific Corp - Nekoosa Mill | WI | Wood | NHG1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1926 |  |  | N | Industrial CHP | 7 | T B B B B B: X; NG PC PC PC PC PC: WAT | [6 empty] | 1H | [23 empty] | N
Vintage1991 | biomass | TRUE | 5033 | Domtar Industries Inc | 50395 | Georgia-Pacific Corp - Nekoosa Mill | WI | Wood | TG14 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 13.1 | 1 | 12.5 | 12.1 | 1 | N |  |  | OP | X | 2 | 1991 |  |  | Y | Industrial CHP | 7 | T B B B B B: T; NG PC PC PC PC PC: BLQ; OG NG NG NG NG NG: NG; OG NG NG NG NG NG: NG |  |  |  | N | N |  | 12H | N | [22 empty] | Y | Y | N
Vintage1951 | natural gas steam turbine | FALSE | 5033 | Domtar Industries Inc | 50395 | Georgia-Pacific Corp - Nekoosa Mill | WI | Wood | TG6 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 6 | 1 | 5.7 | 5.5 | 1 | N |  |  | OP | X | 1 | 1951 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [5 empty] | N | [17 empty] | N | N | N | bar: T B B B B B to NG PC PC PC PC PC; OG NG NG NG NG NG
Vintage1966 | natural gas steam turbine | FALSE | 5033 | Domtar Industries Inc | 50395 | Georgia-Pacific Corp - Nekoosa Mill | WI | Wood | TG8 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 16 | 1 | 13 | 15 | 1 | N |  |  | OP | X | 1 | 1966 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [5 empty] | N | [17 empty] | N | N | N | bar: T B B B B B to NG PC PC PC PC PC; OG NG NG NG NG NG
Vintage1955 | biomass | TRUE | 16294 | Roseburg Forest Products Co | 50396 | Dillard Complex | OR | Douglas | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 5 | 0.8 | 5 | 5 | 1 | N |  |  | OP | X | 1 | 1955 |  |  | Y | Industrial CHP | 7 | T B B B B B: T; NG PC PC PC PC PC: WDS; OG NG NG NG NG NG: NG; OG NG NG NG NG NG: NG |  |  |  | N |  |  | 12H |  |  | N |  | N | [15 empty] | N |  |  | Y | Y | N
Vintage1955 | biomass | TRUE | 16294 | Roseburg Forest Products Co | 50396 | Dillard Complex | OR | Douglas | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 5 | 0.8 | 5 | 5 | 1 | N |  |  | OP | X | 1 | 1955 |  |  | Y | Industrial CHP | 7 | T B B B B B: T; NG PC PC PC PC PC: WDS; OG NG NG NG NG NG: NG; OG NG NG NG NG NG: NG |  |  |  | N |  |  | 12H |  |  | N |  | N | [15 empty] | N |  |  | Y | Y | N
Vintage1955 | biomass | TRUE | 16294 | Roseburg Forest Products Co | 50396 | Dillard Complex | OR | Douglas | GEN3 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 7 | 0.8 | 7 | 7 | 1 | N |  |  | OP | X | 1 | 1955 |  |  | Y | Industrial CHP | 7 | T B B B B B: B; NG PC PC PC PC PC: WDS; OG NG NG NG NG NG: NG; OG NG NG NG NG NG: NG |  |  |  | N |  |  | 12H |  |  | N |  | N | [15 empty] | N |  |  | Y | Y | N
Vintage1955 | biomass | TRUE | 16294 | Roseburg Forest Products Co | 50396 | Dillard Complex | OR | Douglas | GEN4 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 11.5 | 0.85 | 11.5 | 11.5 | 2 | N |  |  | OP | X | 1 | 1955 |  |  | Y | Industrial CHP | 7 | T B B B B B: T; NG PC PC PC PC PC: WDS; OG NG NG NG NG NG: NG; OG NG NG NG NG NG: NG |  |  |  | N |  |  | 12H |  |  | N |  | N | [15 empty] | N |  |  | Y | Y | N
Vintage1955 | biomass | TRUE | 16294 | Roseburg Forest Products Co | 50396 | Dillard Complex | OR | Douglas | GEN5 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 11.5 | 0.85 | 11.5 | 11.5 | 2 | N |  |  | OP | X | 1 | 1955 |  |  | Y | Industrial CHP | 7 | T B B B B B: B; NG PC PC PC PC PC: WDS; OG NG NG NG NG NG: NG; OG NG NG NG NG NG: NG |  |  |  | N |  |  | 12H |  |  | N |  | N | [15 empty] | N |  |  | Y | Y | N
Vintage1955 | biomass | TRUE | 16294 | Roseburg Forest Products Co | 50396 | Dillard Complex | OR | Douglas | GEN6 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 11.5 | 0.85 | 11.5 | 11.5 | 2 | N |  |  | OS | X | 1 | 1955 |  |  | Y | Industrial CHP | 7 | T B B B B B: B; NG PC PC PC PC PC: WDS; OG NG NG NG NG NG: NG; OG NG NG NG NG NG: NG |  |  |  | N |  |  | 12H |  |  | N |  | N | [15 empty] | N |  |  | Y | Y | N
Vintage1948 | natural gas steam turbine | FALSE | 61988 | Pixelle Specialty Solutions LLC - (PA) | 50397 | Pixelle Specialty Solutions LLC - Spring Grove Facility | PA | York | GEN1 | Natural Gas Steam Turbine | ST |  | S | X | X | PHGLATFE115 KV NUG |  | 6 | 0.8 | 5 | 5 | 2 | N |  |  | OP | X | 7 | 1948 |  |  | Y | Industrial CHP | 7 | T | NG | BLQ | BIT | RFO | WDS | SLW | NG |  |  |  | N | N |  | 12H | Y |  |  |  | Y | [18 empty] | Y | Y | N
Vintage1948 | natural gas steam turbine | FALSE | 61988 | Pixelle Specialty Solutions LLC - (PA) | 50397 | Pixelle Specialty Solutions LLC - Spring Grove Facility | PA | York | GEN3 | Natural Gas Steam Turbine | ST |  | S | X | X | PHGLATFE115KV NUG |  | 5.1 | 0.8 | 4 | 4 | 1.2 | N |  |  | OP | X | 5 | 1948 |  |  | Y | Industrial CHP | 7 | T | NG | BLQ | RFO | BIT | SLW | WDS | NG |  |  |  | N | N |  | 12H | Y | N |  |  | Y | [18 empty] | Y | Y | N
Vintage1962 | natural gas steam turbine | FALSE | 61988 | Pixelle Specialty Solutions LLC - (PA) | 50397 | Pixelle Specialty Solutions LLC - Spring Grove Facility | PA | York | GEN4 | Natural Gas Steam Turbine | ST |  | S | X | X | PHGLATFE115 KV NUG |  | 7.5 | 0.8 | 8.7 | 8.7 | 3.5 | N |  |  | OP | X | 8 | 1962 |  |  | Y | Industrial CHP | 7 | T | NG | BLQ | BIT | RFO | SLW | WDS | NG |  |  |  | N | N |  | 12H | Y | N |  |  | Y | [18 empty] | Y | Y | N
Vintage1989 | hard coal | FALSE | 61988 | Pixelle Specialty Solutions LLC - (PA) | 50397 | Pixelle Specialty Solutions LLC - Spring Grove Facility | PA | York | GEN5 | Conventional Steam Coal | ST |  | S | X | X | PHGLATFE115 KV NUG |  | 45.9 | 0.8 | 36.1 | 36.1 | 9 | N |  |  | OP | X | 5 | 1989 |  |  | Y | Industrial CHP | 7 | T | BIT | WDS | SLW | RFO |  |  | RFO |  |  |  | N | N |  | 12H | Y |  |  |  | Y | [18 empty] | Y | Y | N
Vintage1994 | biomass | TRUE | 61988 | Pixelle Specialty Solutions LLC - (PA) | 50397 | Pixelle Specialty Solutions LLC - Spring Grove Facility | PA | York | GEN6 | Wood/Wood Waste Biomass | ST |  | S | X | X | PHGLATFE115 KV NUG |  | 39.1 | 0.8 | 31.2 | 31.2 | 8.2 | N |  |  | OP | X | 1 | 1994 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | RFO | BIT | SLW | WDS | RFO |  |  |  | N | N |  | 12H | Y | N |  | N | Y | [18 empty] | Y | Y | N
Vintage1998 | biomass | TRUE | 30002 | International Paper Co | 50398 | International Paper Savanna Mill | GA | Chatham | GE10 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 82.8 | 0.85 | 82.7 | 82.8 | 10 | N |  |  | OP | X | 4 | 1998 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | DFO | RFO |  |  | NG |  |  |  | N |  |  | 12H | [23 empty] | Y | Y | N
Vintage1981 | natural gas steam turbine | FALSE | 30002 | International Paper Co | 50398 | International Paper Savanna Mill | GA | Chatham | GEN9 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 71.2 | 0.85 | 71.2 | 71.2 | 20 | N |  |  | OP | X | 6 | 1981 |  |  | Y | Industrial CHP | 7 | T | NG | WDS | BIT | DFO | RFO |  | NG |  |  |  | N |  |  | 12H |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1986 | hydro | TRUE | 19560 | Tri-Dam Power Authority | 50400 | Sand Bar Power Plant | CA | Tuolumne | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 16.2 | 0.9 | 15.6 | 14 | 1 | N |  |  | OP | X | 5 | 1986 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1989 | other | FALSE | 54837 | INEOS Nitriles Greenlake | 50404 | BP Chemicals Green Lake Plant | TX | Calhoun | TG2 | All Other | ST |  | S | X | X |  |  | 15 | 0.85 | 15 | 15 | 2 | N |  |  | OP | X | 3 | 1989 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | bar: T to BLQ; RFO
Vintage1997 | other | FALSE | 54837 | INEOS Nitriles Greenlake | 50404 | BP Chemicals Green Lake Plant | TX | Calhoun | TG3 | All Other | ST |  | S | X | X |  |  | 23.8 | 0.85 | 23.8 | 23.8 | 2 | N |  |  | OP | X | 1 | 1997 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | bar: T to BLQ; RFO
Vintage1976 | biomass | TRUE | 16190 | Sappi Fine Paper North America-Somerset | 50406 | Somerset Plant | ME | Somerset | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X | 4156 | 4156 | 45.9 | 0.9 | 48.8 | 48.8 | 5 | N |  |  | OP | X | 1 | 1976 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | NG | TDF | SLW | RFO | RFO | DFO | NG |  | N | N | 0 | OVER | [23 empty] | Y | Y | Y
Vintage1990 | biomass | TRUE | 16190 | Sappi Fine Paper North America-Somerset | 50406 | Somerset Plant | ME | Somerset | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X | 4156 | 4156 | 61.2 | 0.85 | 51 | 51 | 5 | N |  |  | OP | X | 10 | 1990 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | TDF | SLW | RFO | DFO | RFO | NG |  | N | N | 0 | OVER | [23 empty] | Y | Y | Y
Vintage1920 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50408 | Park Mill | WI | Marinette | 1 | Conventional Hydroelectric | HY |  | W | X | X | WPS.MENOMPK |  | 0.4 | 1 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 1 | 1920 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  | N |  | 0 | 10M
Vintage1988 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50408 | Park Mill | WI | Marinette | 10 | Conventional Hydroelectric | HY |  | W | X | X | WPS.MENOMPK |  | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 4 | 1988 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  | N |  | 0 | 10M
Vintage1922 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50408 | Park Mill | WI | Marinette | 2 | Conventional Hydroelectric | HY |  | W | X | X | WPS.MENOMPK |  | 0.2 | 1 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1922 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  | N |  | 0 | 10M
Vintage1946 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50408 | Park Mill | WI | Marinette | 3 | Conventional Hydroelectric | HY |  | W | X | X | WPS.MENOMPK |  | 0.4 | 1 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 1 | 1946 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  | N |  | 0 | 10M
Vintage1966 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50408 | Park Mill | WI | Marinette | 6 | Conventional Hydroelectric | HY |  | W | X | X | WPS.MENOMPK |  | 0.4 | 1 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 10 | 1966 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  | N |  | 0 | 10M
Vintage1968 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50408 | Park Mill | WI | Marinette | 7 | Conventional Hydroelectric | HY |  | W | X | X | WPS.MENOMPK |  | 0.4 | 1 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 7 | 1968 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  | N |  | 0 | 10M
Vintage1924 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50409 | Menominee Mill Marinette | MI | Menominee | 4 | Conventional Hydroelectric | HY |  | W | X | X | WPS.MENOMPK |  | 0.4 | 1 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 1 | 1924 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  | N |  | 0 | 10M
Vintage1924 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50409 | Menominee Mill Marinette | MI | Menominee | 5 | Conventional Hydroelectric | HY |  | W | X | X | WPS.MENOMPK |  | 0.4 | 1 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 1 | 1924 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  | N |  | 0 | 10M
Vintage1978 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50409 | Menominee Mill Marinette | MI | Menominee | 8 | Conventional Hydroelectric | HY |  | W | X | X | WPS.MENOMPK |  | 0.5 | 1 | 0.5 | 0.5 | 0.2 | N |  |  | OP | X | 10 | 1978 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  | N |  | 0 | 10M
Vintage1978 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50409 | Menominee Mill Marinette | MI | Menominee | 9 | Conventional Hydroelectric | HY |  | W | X | X | WPS.MENOMPK |  | 0.5 | 1 | 0.5 | 0.5 | 0.2 | N |  |  | OP | X | 10 | 1978 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  | N |  | 0 | 10M
Vintage2020 | natural gas combined cycle | FALSE | 10273 | Kimberly-Clark Corp | 50410 | Chester Operations | PA | Delaware | 6 | Natural Gas Fired Combined Cycle | CT | 6000 | S | X | N |  |  | 17.3 | 0.92 | 14.1 | 16.3 | 6.5 | N |  |  | OP | X | 7 | 2020 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N | 0 | 1H | [23 empty] | N | N | N | bar: X T T to WH BLQ BLQ
Vintage2020 | natural gas combined cycle | FALSE | 10273 | Kimberly-Clark Corp | 50410 | Chester Operations | PA | Delaware | 6A | Natural Gas Fired Combined Cycle | CA | 6000 | S | Y | X |  |  | 17.3 | 0.92 | 14.1 | 16.3 | 6.5 | N |  |  | OP | X | 8 | 2020 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N | 0 | 1H | [23 empty] | N | N | N | bar: X T T to WH BLQ BLQ
Vintage2020 | natural gas combined cycle | FALSE | 10273 | Kimberly-Clark Corp | 50410 | Chester Operations | PA | Delaware | 7 | Natural Gas Fired Combined Cycle | CT | 7000 | S | X | Y |  |  | 17.3 | 0.92 | 14.1 | 16.3 | 6.5 | N |  |  | OP | X | 8 | 2020 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | bar: X T T to WH BLQ BLQ
Vintage2020 | natural gas combined cycle | FALSE | 10273 | Kimberly-Clark Corp | 50410 | Chester Operations | PA | Delaware | 7A | Natural Gas Fired Combined Cycle | CA | 7000 | S | Y | X |  |  | 17.3 | 0.92 | 14.1 | 16.3 | 6.5 | N |  |  | OP | X | 8 | 2020 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N | 0 | 1H | [23 empty] | N | N | bar: X T T to WH BLQ BLQ
Vintage1989 | natural gas peaker | FALSE | 58485 | Rutgers, The State University of NJ | 50411 | Rutgers Biomedical and Health Cogen | NJ | Essex | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.5 | 0.96 | 3.4 | 3.7 | 2.3 | N |  |  | OA | X | 7 | 1989 |  |  | Y | Commercial CHP | 5 | X T T: T; WH BLQ BLQ: NG; WH WDS NG: DFO |  | N | N |  | 1H | [7 empty] | 2.3 | 2.3 | 1 | 2022 | [9 empty] | N |  |  | N | N | N
Vintage1989 | natural gas peaker | FALSE | 58485 | Rutgers, The State University of NJ | 50411 | Rutgers Biomedical and Health Cogen | NJ | Essex | GEN2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.5 | 0.96 | 3.4 | 3.7 | 2.3 | N |  |  | OA | X | 7 | 1989 |  |  | Y | Commercial CHP | 5 | X T T: T; WH BLQ BLQ: NG; WH WDS NG: DFO |  | N | N |  | 1H | [7 empty] | 2.3 | 2.3 | 1 | 2022 | [9 empty] | N |  |  | N | N | N
Vintage1989 | natural gas peaker | FALSE | 58485 | Rutgers, The State University of NJ | 50411 | Rutgers Biomedical and Health Cogen | NJ | Essex | GEN3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.5 | 0.96 | 3.4 | 3.7 | 2.3 | N |  |  | OA | X | 7 | 1989 |  |  | Y | Commercial CHP | 5 | X T T: T; WH BLQ BLQ: NG; WH WDS NG: DFO |  | N | N |  | 1H | [7 empty] | 2.3 | 2.3 | 1 | 2022 | [9 empty] | N |  |  | N | N | N
Vintage2009 | petroleum | FALSE | 21995 | Olmsted County Public Works | 50413 | Olmsted Waste Energy | MN | Olmsted | DGCAT | Petroleum Liquids | IC |  | S | X | X |  |  | 1.7 | 1 | 1.3 | 1.3 | 0.2 | N |  |  | SB | N | 10 | 2009 |  |  | N | Commercial CHP | 5 | X T T: X; WH BLQ BLQ: DFO |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1987 | municipal solid waste | FALSE | 21995 | Olmsted County Public Works | 50413 | Olmsted Waste Energy | MN | Olmsted | TG2 | Municipal Solid Waste | ST |  | S | X | X |  |  | 2.2 | 1 | 1.3 | 0.8 | 0.4 | N |  |  | OP | X | 4 | 1987 |  |  | Y | Commercial CHP | 5 | X T T: T; WH BLQ BLQ: MSW; WH RFO DFO: NG |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage2010 | municipal solid waste | FALSE | 21995 | Olmsted County Public Works | 50413 | Olmsted Waste Energy | MN | Olmsted | TG3 | Municipal Solid Waste | ST |  | S | X | X |  |  | 5.5 | 1 | 5 | 4.5 | 0.4 | N |  |  | OP | X | 5 | 2010 |  |  | Y | Commercial CHP | 5 | X T T: T; WH BLQ BLQ: MSW; WH RFO DFO: NG |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1987 | municipal solid waste | FALSE | 21995 | Olmsted County Public Works | 50413 | Olmsted Waste Energy | MN | Olmsted | TGI | Municipal Solid Waste | ST |  | S | X | X |  |  | 1.9 | 1 | 1.4 | 1.4 | 0.4 | N |  |  | OP | X | 4 | 1987 |  |  | Y | Commercial CHP | 5 | X T T: T; WH BLQ BLQ: MSW; WH RFO DFO: NG |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1986 | hydro | TRUE | 24793 | Briar-Hydro Associates | 50414 | Penacook Upper Falls Hydro | NH | Merrimack | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.4 | 0.9 | 3.4 | 3.4 | 0.1 | N |  |  | OP | X | 12 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  | N |  |  | 1H | [23 empty] | N
Vintage1986 | hydro | TRUE | 18436 | Ampersand Tannery Island Hydro, LLC | 50416 | Tannery Island Power | NY | Jefferson | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.87 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 6 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  | N |  | 0 | 10M | [23 empty] | N
Vintage1986 | hydro | TRUE | 18436 | Ampersand Tannery Island Hydro, LLC | 50416 | Tannery Island Power | NY | Jefferson | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.87 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 6 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  | N |  | 0 | 10M | [23 empty] | N
Vintage1986 | hydro | TRUE | 18436 | Ampersand Tannery Island Hydro, LLC | 50416 | Tannery Island Power | NY | Jefferson | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.87 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 6 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  | N |  | 0 | 10M | [23 empty] | N
Vintage1986 | hydro | TRUE | 18436 | Ampersand Tannery Island Hydro, LLC | 50416 | Tannery Island Power | NY | Jefferson | GEN4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.87 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 6 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  | N |  | 0 | 10M | [23 empty] | N
Vintage1986 | hydro | TRUE | 18436 | Ampersand Tannery Island Hydro, LLC | 50416 | Tannery Island Power | NY | Jefferson | GEN5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.87 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 6 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  | N |  | 0 | 10M | [23 empty] | N
Vintage1987 | hydro | TRUE | 21086 | Yakima-Tieton Irrigation Dist | 50421 | Orchard Avenue 1 | WA | Yakima | 201 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.7 | 0.2 | N |  |  | OP | X | 3 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  |  |  | 0 | 10M
Vintage1987 | hydro | TRUE | 21086 | Yakima-Tieton Irrigation Dist | 50421 | Orchard Avenue 1 | WA | Yakima | 301 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.7 | 0.2 | N |  |  | OP | X | 3 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  |  |  | 0 | 10M
Vintage1987 | hydro | TRUE | 21086 | Yakima-Tieton Irrigation Dist | 50423 | Cowiche | WA | Yakima | 983 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.7 | 0.8 | 1.6 | 1.6 | 1 | N |  |  | OP | X | 3 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  |  |  | 0 | 10M
Vintage1991 | natural gas peaker | FALSE | 13487 | New York Zoological Society | 50427 | Bronx Zoo | NY | Bronx | GEN1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.4 | N |  |  | SB | Y | 1 | 1991 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X T T to WH BLQ BLQ
Vintage1991 | natural gas peaker | FALSE | 13487 | New York Zoological Society | 50427 | Bronx Zoo | NY | Bronx | GEN2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.4 | N |  |  | SB | Y | 1 | 1991 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X T T to WH BLQ BLQ
Vintage1991 | natural gas peaker | FALSE | 13487 | New York Zoological Society | 50427 | Bronx Zoo | NY | Bronx | GEN3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.8 | N |  |  | OP | X | 1 | 1991 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X T T to WH BLQ BLQ
Vintage1995 | natural gas peaker | FALSE | 13487 | New York Zoological Society | 50427 | Bronx Zoo | NY | Bronx | GEN4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 1 | N |  |  | OP | X | 4 | 1995 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X T T to WH BLQ BLQ
Vintage1986 | natural gas combined cycle | FALSE | 19588 | University of Michigan | 50431 | University of Michigan | MI | Washtenaw | TG1 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X |  |  | 12.5 | 0.8 | 11.5 | 11.5 | 2.5 | N |  |  | OP | X | 1 | 1986 |  |  | Y | Commercial CHP | 5 | X T T: T; WH BLQ BLQ: NG; WH WDS NG: DFO |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1992 | natural gas combined cycle | FALSE | 19588 | University of Michigan | 50431 | University of Michigan | MI | Washtenaw | TG10 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 3.5 | 0.8 | 3.5 | 5 | 0.5 | N |  |  | OP | X | 6 | 1992 |  |  | Y | Commercial CHP | 5 | X T T: T; WH BLQ BLQ: NG; WH WDS NG: DFO |  | N | N |  | 12H | [20 empty] | N |  |  | Y | N | Y
Vintage1975 | natural gas combined cycle | FALSE | 19588 | University of Michigan | 50431 | University of Michigan | MI | Washtenaw | TG7 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X |  |  | 12.5 | 0.8 | 11.5 | 11.5 | 2.5 | N |  |  | OS | X | 1 | 1975 |  |  | Y | Commercial CHP | 5 | X T T: T; WH BLQ BLQ: NG; WH WDS NG: DFO |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1975 | natural gas combined cycle | FALSE | 19588 | University of Michigan | 50431 | University of Michigan | MI | Washtenaw | TG8 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X |  |  | 12.5 | 0.8 | 11.5 | 11.5 | 2.5 | N |  |  | OP | X | 1 | 1975 |  |  | Y | Commercial CHP | 5 | X T T: T; WH BLQ BLQ: NG; WH WDS NG: DFO |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1990 | natural gas combined cycle | FALSE | 19588 | University of Michigan | 50431 | University of Michigan | MI | Washtenaw | TG9 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 3.5 | 0.8 | 3.5 | 5 | 0.5 | N |  |  | OP | X | 8 | 1990 |  |  | Y | Commercial CHP | 5 | X T T: T; WH BLQ BLQ: NG; WH WDS NG: DFO |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1984 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50433 | Ada Dam | MI | Kent | ADA1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.4 | 0.9 | 1.4 | 1.4 | 0.2 | N |  |  | OP | X | 3 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  | N | N | 0 | 10M
Vintage1985 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50435 | Sugarloaf Hydro Plant | CO | Lake | SUG1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 0.4 | N |  |  | OP | X | 11 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  |  |  | 0 | 10M
Vintage1986 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50436 | Cascade Dam | MI | Kent | CAS1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.6 | 0.9 | 1.6 | 1.6 | 0.2 | N |  |  | OP | X | 12 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  |  |  | 0 | 10M
Vintage1988 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50437 | French Landing Dam | MI | Wayne | FRL1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.6 | 0.9 | 1.6 | 1.6 | 0.2 | N |  |  | OP | X | 12 | 1988 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  |  |  |  | 10M
Vintage1971 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50439 | Oconto Falls Lower | WI | Oconto | GEN1 | Conventional Hydroelectric | HY |  | W | X | X | WEC.OCONTOFL |  | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OS | X | 1 | 1971 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  | N |  | 0 | 10M
Vintage1971 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50439 | Oconto Falls Lower | WI | Oconto | GEN2 | Conventional Hydroelectric | HY |  | W | X | X | WEC.OCONTOFL |  | 1.7 | 1 | 1.7 | 1.7 | 0.5 | N |  |  | OP | X | 1 | 1971 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  | N |  | 0 | 10M
Vintage1903 | hydro | FALSE | 16721 | Sappi North America Westbrook Mill | 50447 | S D Warren Westbrook | ME | Cumberland | GEN1 | Conventional Hydroelectric | HY |  | S | X | X | 591_:_UN_PRID_CRN115_SWBK | 591_:_UN_PRID_CRN115_SWBK | 0.6 | 0.8 | 0.6 | 0.6 | 0.2 | N |  |  | OS | X | 1 | 1903 |  |  | N | Industrial CHP | 7 | X T T: X; WH BLQ BLQ: WAT |  | N | N |  | 12H | [23 empty] | N
Vintage1903 | hydro | FALSE | 16721 | Sappi North America Westbrook Mill | 50447 | S D Warren Westbrook | ME | Cumberland | GEN2 | Conventional Hydroelectric | HY |  | S | X | X | 591_:_UN_PRID_CRN115_SWBK | 591_:_UN_PRID_CRN115_SWBK | 0.6 | 0.8 | 0.6 | 0.6 | 0.2 | N |  |  | OS | X | 1 | 1903 |  |  | N | Industrial CHP | 7 | X T T: X; WH BLQ BLQ: WAT |  | N | N | 0 | 12H | [23 empty] | N
Vintage1903 | hydro | FALSE | 16721 | Sappi North America Westbrook Mill | 50447 | S D Warren Westbrook | ME | Cumberland | GEN3 | Conventional Hydroelectric | HY |  | S | X | X | 591_:_UN_PRID_CRN115_SWBK | 591_:_UN_PRID_CRN115_SWBK | 0.6 | 0.8 | 0.6 | 0.6 | 0.2 | N |  |  | OA | X | 1 | 1903 |  |  | N | Industrial CHP | 7 | X T T: X; WH BLQ BLQ: WAT |  | N | N | 0 | 12H | [23 empty] | N
Vintage1913 | hydro | FALSE | 16721 | Sappi North America Westbrook Mill | 50447 | S D Warren Westbrook | ME | Cumberland | GEN4 | Conventional Hydroelectric | HY |  | S | X | X | 591_:_UN_PRID_CRN115_SWBK | 591_:_UN_PRID_CRN115_SWBK | 0.8 | 0.8 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 1 | 1913 |  |  | N | Industrial CHP | 7 | X T T: X; WH BLQ BLQ: WAT |  | N | N |  | 12H | [23 empty] | N
Vintage1913 | hydro | FALSE | 16721 | Sappi North America Westbrook Mill | 50447 | S D Warren Westbrook | ME | Cumberland | GEN5 | Conventional Hydroelectric | HY |  | S | X | X | 591_:_UN_PRID_CRN115_SWBK | 591_:_UN_PRID_CRN115_SWBK | 0.8 | 0.8 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 1 | 1913 |  |  | N | Industrial CHP | 7 | X T T: X; WH BLQ BLQ: WAT |  | N | N |  | 12H | [23 empty] | N
Vintage1913 | hydro | FALSE | 16721 | Sappi North America Westbrook Mill | 50447 | S D Warren Westbrook | ME | Cumberland | GEN6 | Conventional Hydroelectric | HY |  | S | X | X | 591_:_UN_PRID_CRN115_SWBK | 591_:_UN_PRID_CRN115_SWBK | 0.8 | 0.8 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 1 | 1913 |  |  | N | Industrial CHP | 7 | X T T: X; WH BLQ BLQ: WAT |  | N | N |  | 12H | [23 empty] | N
Vintage1940 | hydro | FALSE | 16721 | Sappi North America Westbrook Mill | 50447 | S D Warren Westbrook | ME | Cumberland | GEN7 | Conventional Hydroelectric | HY |  | S | X | X | 591_:_UN_PRID_CRN115_SWBK | 591_:_UN_PRID_CRN115_SWBK | 0.6 | 0.8 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 1 | 1940 |  |  | N | Industrial CHP | 7 | X T T: X; WH BLQ BLQ: WAT |  | N | N | 0 | 12H
Vintage1982 | biomass | TRUE | 16721 | Sappi North America Westbrook Mill | 50447 | S D Warren Westbrook | ME | Cumberland | GEN9 | Wood/Wood Waste Biomass | ST |  | S | X | X | 591_:_UN_PRID_CRN115_SWBK | 591_:_UN_PRID_CRN115_SWBK | 47.5 | 0.85 | 40.5 | 47.5 | 5 | N |  |  | OS | X | 1 | 1982 |  |  | Y | Industrial CHP | 7 | B | WDS | BIT | RFO | DFO |  |  | RFO | WDS |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1985 | biomass | TRUE | 16721 | Sappi North America Westbrook Mill | 50447 | S D Warren Westbrook | ME | Cumberland | GN10 | Wood/Wood Waste Biomass | ST |  | S | X | X | 591_:_UN_PRID_CRN115_SWBK | 591_:_UN_PRID_CRN115_SWBK | 15 | 0.85 | 15.8 | 15.8 | 5 | N |  |  | OS | X | 10 | 1985 |  |  | Y | Industrial CHP | 7 | B | WDS | BIT | RFO | DFO |  |  | RFO | WDS |  |  | N | N |  | OVER |  | Y |  |  | Y | N | [17 empty] | Y | Y | N
Vintage1940 | hydro | FALSE | 16721 | Sappi North America Westbrook Mill | 50447 | S D Warren Westbrook | ME | Cumberland | GN11 | Conventional Hydroelectric | HY |  | S | X | X | 591_:_UN_PRID_CRN115_SWBK | 591_:_UN_PRID_CRN115_SWBK | 0.6 | 0.8 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 1 | 1940 |  |  | N | Industrial CHP | 7 | X T T: X; WH BLQ BLQ: WAT |  | N | N |  | 12H | [23 empty] | N
Vintage1940 | hydro | FALSE | 16721 | Sappi North America Westbrook Mill | 50447 | S D Warren Westbrook | ME | Cumberland | GN12 | Conventional Hydroelectric | HY |  | S | X | X | 591_:_UN_PRID_CRN115_SWBK | 591_:_UN_PRID_CRN115_SWBK | 0.2 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1940 |  |  | N | Industrial CHP | 7 | X T T: X; WH BLQ BLQ: WAT |  | N | N |  | 12H | [23 empty] | N
Vintage1940 | hydro | FALSE | 16721 | Sappi North America Westbrook Mill | 50447 | S D Warren Westbrook | ME | Cumberland | GN13 | Conventional Hydroelectric | HY |  | S | X | X | 591_:_UN_PRID_CRN115_SWBK | 591_:_UN_PRID_CRN115_SWBK | 0.2 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1940 |  |  | N | Industrial CHP | 7 | X T T: X; WH BLQ BLQ: WAT |  | N | N |  | 12H | [23 empty] | N
Vintage1940 | hydro | FALSE | 16721 | Sappi North America Westbrook Mill | 50447 | S D Warren Westbrook | ME | Cumberland | GN14 | Conventional Hydroelectric | HY |  | S | X | X | 591_:_UN_PRID_CRN115_SWBK | 591_:_UN_PRID_CRN115_SWBK | 0.2 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1940 |  |  | N | Industrial CHP | 7 | X T T: X; WH BLQ BLQ: WAT |  | N | N |  | 12H | [23 empty] | N
Vintage1940 | hydro | FALSE | 16721 | Sappi North America Westbrook Mill | 50447 | S D Warren Westbrook | ME | Cumberland | GN15 | Conventional Hydroelectric | HY |  | S | X | X | 591_:_UN_PRID_CRN115_SWBK | 591_:_UN_PRID_CRN115_SWBK | 0.2 | 0.8 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1940 |  |  | N | Industrial CHP | 7 | X T T: X; WH BLQ BLQ: WAT |  | N | N |  | 12H | [23 empty] | N
Vintage1940 | hydro | FALSE | 16721 | Sappi North America Westbrook Mill | 50447 | S D Warren Westbrook | ME | Cumberland | GN16 | Conventional Hydroelectric | HY |  | S | X | X | 591_:_UN_PRID_CRN115_SWBK | 591_:_UN_PRID_CRN115_SWBK | 0.5 | 0.8 | 0.5 | 0.5 | 0.2 | N |  |  | OP | X | 1 | 1940 |  |  | N | Industrial CHP | 7 | X T T: X; WH BLQ BLQ: WAT |  | N | N |  | 12H | [23 empty] | N
Vintage1940 | hydro | FALSE | 16721 | Sappi North America Westbrook Mill | 50447 | S D Warren Westbrook | ME | Cumberland | GN17 | Conventional Hydroelectric | HY |  | S | X | X | 591_:_UN_PRID_CRN115_SWBK | 591_:_UN_PRID_CRN115_SWBK | 0.5 | 0.8 | 0.5 | 0.5 | 0.2 | N |  |  | OP | X | 1 | 1940 |  |  | N | Industrial CHP | 7 | X T T: X; WH BLQ BLQ: WAT |  | N | N |  | 12H | [23 empty] | N
Vintage1991 | natural gas combined cycle | TRUE | 9245 | Indeck-Energy Serv Silver Spg | 50449 | Indeck Silver Springs Energy Center | NY | Wyoming | GEN1 | Natural Gas Fired Combined Cycle | CT | G722 | S | X | N | PTID 23768 | PTID 23768 | 39.4 | 0.9 | 34.7 | 45.1 | 34 | N |  |  | OP | X | 5 | 1991 |  |  | Y | IPP CHP | 3 | X T T: T; WH BLQ BLQ: NG; WH WDS NG: DFO |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1991 | natural gas combined cycle | TRUE | 9245 | Indeck-Energy Serv Silver Spg | 50449 | Indeck Silver Springs Energy Center | NY | Wyoming | GEN2 | Natural Gas Fired Combined Cycle | CA | G722 | S | Y | X | PTID 23768 | PTID 23768 | 17.2 | 0.9 | 17.2 | 17.2 | 10 | N |  |  | OP | X | 5 | 1991 |  |  | Y | IPP CHP | 3 | X T T: T; WH BLQ BLQ: NG; WH WDS NG: DFO |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1990 | natural gas combined cycle | TRUE | 9244 | Indeck-Oswego Ltd Partnership | 50450 | Indeck Oswego Energy Center | NY | Oswego | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | 23783 | 23783 | 41.2 | 0.9 | 50.6 | 60.4 | 34.5 | N |  |  | OP | X | 6 | 1990 |  |  | Y | IPP CHP | 3 | X T T: T; WH BLQ BLQ: NG; WH WDS NG: DFO |  | N | N | 0 | 12H | [23 empty] | Y | Y | Y
Vintage1990 | natural gas combined cycle | TRUE | 9244 | Indeck-Oswego Ltd Partnership | 50450 | Indeck Oswego Energy Center | NY | Oswego | GEN2 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | 23783 | 23783 | 16.2 | 0.9 |  |  | 10 | N |  |  | OP | X | 6 | 1990 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T to WH BLQ BLQ
Vintage1989 | natural gas combined cycle | TRUE | 9243 | Indeck-Yerkes Ltd Partnership | 50451 | Indeck Yerkes Energy Center | NY | Erie | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | 23781 | 23781 | 40.6 | 0.9 | 47.3 | 56.8 | 42 | N |  |  | OP | X | 12 | 1989 |  |  | Y | IPP CHP | 3 | X T T: T; WH BLQ BLQ: NG; WH WDS NG: DFO |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1989 | natural gas combined cycle | TRUE | 9243 | Indeck-Yerkes Ltd Partnership | 50451 | Indeck Yerkes Energy Center | NY | Erie | GEN2 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 19.3 | 0.9 |  |  |  | N |  |  | OP | X | 12 | 1989 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T to WH BLQ BLQ
Vintage1965 | natural gas steam turbine | FALSE | 15400 | Procter & Gamble Co | 50456 | Procter & Gamble Cincinnati Plant | OH | Hamilton | GEN1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 12.5 | 0.8 | 11.7 | 11.8 | 1.5 | N |  |  | OP | X | 11 | 1965 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H |  | N | [21 empty] | N | N | N | bar: X T T to WH BLQ BLQ; WH RFO DFO
Vintage1995 | natural gas combined cycle | TRUE | 9263 | Indeck-Corinth Ltd Partnership | 50458 | Indeck Corinth Energy Center | NY | Saratoga | GEN1 | Natural Gas Fired Combined Cycle | CT | G723 | S | X | N | INDECK___CORINTH | INDECK___CORINTH | 92 | 0.85 | 73.1 | 91.1 | 73 | N |  |  | OP | X | 2 | 1995 |  |  | Y | IPP CHP | 3 | X T T: T; WH BLQ BLQ: NG; WH WDS NG: DFO; WH NG WDS: KER |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1995 | natural gas combined cycle | TRUE | 9263 | Indeck-Corinth Ltd Partnership | 50458 | Indeck Corinth Energy Center | NY | Saratoga | GEN2 | Natural Gas Fired Combined Cycle | CA | G723 | S | Y | X | INDECK___CORINTH | INDECK___CORINTH | 55 | 0.85 | 54.1 | 42.2 | 39 | N |  |  | OP | X | 3 | 1995 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | bar: X T T to WH BLQ BLQ
Vintage1984 | hydro | FALSE | 7857 | Great Lakes Tissue Co | 50461 | Cheboygan | MI | Cheboygan | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 0.8 | 0.7 | 1.1 | 0.1 | N |  |  | OP | X | 11 | 1984 |  |  | N | Industrial Non-CHP | 6 | X T T: X; WH BLQ BLQ: WAT |  | N | N | 0 | 1H
Vintage1985 | natural gas peaker | FALSE | 15394 | Procter & Gamble Ppr Prdts Co | 50463 | Procter & Gamble Mehoopany Mill | PA | Wyoming | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 53.6 | 0.8 | 40 | 59 | 30 | N |  |  | OP | X | 6 | 1985 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T to WH BLQ BLQ
Vintage1984 | natural gas steam turbine | FALSE | 15394 | Procter & Gamble Ppr Prdts Co | 50463 | Procter & Gamble Mehoopany Mill | PA | Wyoming | GEN2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 2.6 | 1 | 0.9 | 1.6 | 0.2 | N |  |  | OP | X | 10 | 1984 |  |  | N | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T to WH BLQ BLQ; WH RFO DFO
Vintage2013 | natural gas peaker | FALSE | 15394 | Procter & Gamble Ppr Prdts Co | 50463 | Procter & Gamble Mehoopany Mill | PA | Wyoming | GEN3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 64 | 0.85 | 64 | 64 | 20 | N |  |  | OP | X | 4 | 2013 |  |  | N | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T to WH BLQ BLQ
Vintage1982 | natural gas peaker | FALSE | 15375 | Procter&Gamble Paper Products Co-Oxnard | 50464 | Oxnard | CA | Ventura | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 19.2 | 0.9 | 22.4 | 22.4 | 17 | N |  |  | OP | X | 7 | 1982 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T to WH BLQ BLQ
Vintage1989 | natural gas peaker | FALSE | 15375 | Procter&Gamble Paper Products Co-Oxnard | 50464 | Oxnard | CA | Ventura | GEN2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 49.5 | 0.9 | 48.5 | 48.5 | 30 | N |  |  | OP | X | 11 | 1989 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T to WH BLQ BLQ
Vintage1980 | biomass | TRUE | 61982 | International Paper - Flint River Mill | 50465 | Flint River Operations | GA | Macon | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 46.6 | 0.9 | 46.6 | 46.6 | 5 | N |  |  | OP | X | 12 | 1980 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | NG |  |  |  | DFO | NG |  |  | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage2015 | biomass | TRUE | 61982 | International Paper - Flint River Mill | 50465 | Flint River Operations | GA | Macon | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 38.5 | 0.9 | 30.5 | 30.5 | 5 | N |  |  | OP | X | 4 | 2015 |  |  | Y | Industrial CHP | 7 | T | WDS | NG | BLQ | DFO |  |  | NG |  |  |  | N | N |  | 12H |  |  | N |  | N | [18 empty] | Y | Y | Y
Vintage1953 | biomass | TRUE | 2522 | Buckeye Florida Ltd Partners | 50466 | Buckeye Florida LP | FL | Taylor | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 8.2 | 0.9 | 6.2 | 6.3 | 3 | N |  |  | OP | X | 7 | 1953 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | NG | RFO | OBG |  | RFO | NG |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1965 | biomass | TRUE | 2522 | Buckeye Florida Ltd Partners | 50466 | Buckeye Florida LP | FL | Taylor | GEN3 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 10.4 | 0.95 | 8.9 | 8.2 | 3 | N |  |  | OP | X | 7 | 1965 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | NG | RFO | OBG |  | RFO | NG |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1956 | biomass | TRUE | 2522 | Buckeye Florida Ltd Partners | 50466 | Buckeye Florida LP | FL | Taylor | GEN4 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 14.8 | 0.8 | 9.9 | 8.9 | 3 | N |  |  | OP | X | 7 | 1956 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | NG | RFO | OBG |  | RFO | NG |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1964 | biomass | TRUE | 2522 | Buckeye Florida Ltd Partners | 50466 | Buckeye Florida LP | FL | Taylor | GEN5 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 11 | 0.95 | 7.2 | 7.4 | 3 | N |  |  | OP | X | 7 | 1964 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | NG | RFO | OBG |  | RFO | NG |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2011 | biomass | TRUE | 2522 | Buckeye Florida Ltd Partners | 50466 | Buckeye Florida LP | FL | Taylor | GEN6 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 25 | 0.85 | 9.1 | 6.9 | 3 | N |  |  | OP | X | 1 | 2011 |  |  | N | Industrial CHP | 7 | X | BLQ | WDS | NG | RFO | OBG |  | RFO | NG |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1949 | hydro | FALSE | 55876 | Capitol Broadcasting Company Inc | 50468 | Rocky Mount Mill | NC | Nash | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.5 | 0.5 | 0.2 | N |  |  | OS | X | 1 | 1949 |  |  | N | Industrial Non-CHP | 6 | X T T: X; WH BLQ BLQ: WAT |  | N | N | 0 | 1H
Vintage1941 | hydro | FALSE | 55876 | Capitol Broadcasting Company Inc | 50468 | Rocky Mount Mill | NC | Nash | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OA | X | 1 | 1941 |  |  | N | Industrial Non-CHP | 6 | X T T: X; WH BLQ BLQ: WAT |  | N | N | 0 | 1H
Vintage1949 | hydro | FALSE | 55876 | Capitol Broadcasting Company Inc | 50468 | Rocky Mount Mill | NC | Nash | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.2 | 0.2 | 0.2 | N |  |  | OA | X | 1 | 1949 |  |  | N | Industrial Non-CHP | 6 | X T T: X; WH BLQ BLQ: WAT |  | N | N | 0 | 1H
Vintage1980 | municipal solid waste | TRUE | 470 | Covanta Energy of Niagara LP | 50472 | Covanta Niagara I, LLC | NY | Niagara | GEN1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 25 | 0.9 | 18 | 18 | 3 | N |  |  | OP | X | 8 | 1980 |  |  | Y | IPP CHP | 3 | X T T: B; WH BLQ BLQ: MSW; WH WDS NG: NG; WH RFO DFO: NG |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1980 | municipal solid waste | TRUE | 470 | Covanta Energy of Niagara LP | 50472 | Covanta Niagara I, LLC | NY | Niagara | GEN2 | Municipal Solid Waste | ST |  | S | X | X |  |  | 25 | 0.9 | 18 | 18 | 3 | N |  |  | OP | X | 8 | 1980 |  |  | Y | IPP CHP | 3 | X T T: B; WH BLQ BLQ: MSW; WH WDS NG: NG; WH RFO DFO: NG |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1980 | other | FALSE | 20558 | White Springs Agrici Chem Inc | 50474 | Swift Creek Chemical Complex | FL | Hamilton | SCC | All Other | ST |  | S | X | X |  |  | 18.8 | 1 | 15.9 | 15.9 | 5 | N |  |  | OP | X | 1 | 1980 |  |  | Y | Industrial CHP | 7 | X T T: B; WH BLQ BLQ: OTH; WH WDS NG: DFO; WH NG WDS: NG; WH RFO DFO: NG |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1989 | natural gas peaker | FALSE | 5065 | Equistar Chemicals LP | 50475 | Corpus Christi | TX | Nueces | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 41 | 0.85 | 33 | 41 | 26 | N |  |  | OP | X | 5 | 1989 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | OVER |  |  |  | N | [19 empty] | N | N | N | bar: X T T to WH BLQ BLQ
Vintage1948 | biomass | TRUE | 14369 | PCA-Tomahawk Mill | 50476 | Packaging of America Tomahawk Mill | WI | Lincoln | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 6.3 | 1 | 5.4 | 5.8 | 0.1 | N |  |  | OP | X | 6 | 1948 |  |  | Y | Industrial CHP | 7 | T | WDS | NG | BLQ | DFO | OBS |  | NG | OBG |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1978 | biomass | TRUE | 14369 | PCA-Tomahawk Mill | 50476 | Packaging of America Tomahawk Mill | WI | Lincoln | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 9.4 | 1 | 8.2 | 8.9 | 0.1 | N |  |  | OP | X | 8 | 1978 |  |  | Y | Industrial CHP | 7 | T | WDS | NG | BLQ | DFO | OBS |  | NG | OBG |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1920 | hydro | FALSE | 14369 | PCA-Tomahawk Mill | 50476 | Packaging of America Tomahawk Mill | WI | Lincoln | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 1 | 0.5 | 0.6 | 0.1 | N |  |  | OP | X | 1 | 1920 |  |  | N | Industrial CHP | 7 | X T T: X; WH BLQ BLQ: WAT |  | N | N | 0 | 10M |  | N | N | [20 empty] | N
Vintage1920 | hydro | FALSE | 14369 | PCA-Tomahawk Mill | 50476 | Packaging of America Tomahawk Mill | WI | Lincoln | GEN4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 1 | 0.3 | 0.2 | 0.1 | N |  |  | OP | X | 1 | 1920 |  |  | N | Industrial CHP | 7 | X T T: X; WH BLQ BLQ: WAT |  | N | N | 0 | 10M | [23 empty] | N
Vintage1920 | hydro | FALSE | 14369 | PCA-Tomahawk Mill | 50476 | Packaging of America Tomahawk Mill | WI | Lincoln | GEN5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 1 | 1920 |  |  | N | Industrial CHP | 7 | X T T: X; WH BLQ BLQ: WAT |  | N | N | 0 | 10M | [23 empty] | N
Vintage1920 | hydro | FALSE | 7167 | GP Big Island LLC | 50479 | Georgia-Pacific Big Island | VA | Bedford | BHG1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 1 | 0.2 | 0.2 | 0.2 | N |  |  | OP | X | 6 | 1920 |  |  | N | Industrial CHP | 7 | X T T: X; WH BLQ BLQ: WAT |  | N | N |  | 10M | [23 empty] | N
Vintage1920 | hydro | FALSE | 7167 | GP Big Island LLC | 50479 | Georgia-Pacific Big Island | VA | Bedford | BHG2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 1 | 0.2 | 0.2 | 0.2 | N |  |  | OP | X | 6 | 1920 |  |  | N | Industrial CHP | 7 | X T T: X; WH BLQ BLQ: WAT |  | N | N |  | 10M | [23 empty] | N
Vintage1965 | biomass | TRUE | 7167 | GP Big Island LLC | 50479 | Georgia-Pacific Big Island | VA | Bedford | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 7.5 | 1 | 7 | 7 | 3.5 | N |  |  | OP | X | 6 | 1965 |  |  | Y | Industrial CHP | 7 | T | WDS | NG | OBS |  |  |  | WDS | NG |  |  | N | N |  | 12H |  | N |  |  | N | [18 empty] | Y | Y | N
Vintage1946 | hard coal | FALSE | 5610 | Eastman Chemical Co-TN Ops | 50481 | Tennessee Eastman Operations | TN | Sullivan | TG10 | Conventional Steam Coal | ST |  | S | X | X |  |  | 6 | 0.8 | 6 | 6 | 2 | N |  |  | OP | X | 2 | 1946 |  |  | Y | Industrial CHP | 7 | T | BIT | NG | SLW | OTH | OG |  | NG |  |  |  | N | N |  | 12H |  |  | Y |  | Y | [18 empty] | N | N | N
Vintage1949 | hard coal | FALSE | 5610 | Eastman Chemical Co-TN Ops | 50481 | Tennessee Eastman Operations | TN | Sullivan | TG11 | Conventional Steam Coal | ST |  | S | X | X |  |  | 6 | 0.8 | 6 | 6 | 2 | N |  |  | OP | X | 5 | 1949 |  |  | Y | Industrial CHP | 7 | B | BIT | NG | SLW | OTH | OG |  | NG |  |  |  | N | N |  | 12H |  |  | Y |  | Y | [18 empty] | N | N | N
Vintage1953 | hard coal | FALSE | 5610 | Eastman Chemical Co-TN Ops | 50481 | Tennessee Eastman Operations | TN | Sullivan | TG12 | Conventional Steam Coal | ST |  | S | X | X |  |  | 6 | 0.8 | 6 | 6 | 2 | N |  |  | OP | X | 2 | 1953 |  |  | Y | Industrial CHP | 7 | B | BIT | NG | SLW | OTH | OG |  | NG |  |  |  | N | N |  | 12H |  |  | Y |  | Y | [18 empty] | N | N | N
Vintage1960 | hard coal | FALSE | 5610 | Eastman Chemical Co-TN Ops | 50481 | Tennessee Eastman Operations | TN | Sullivan | TG13 | Conventional Steam Coal | ST |  | S | X | X |  |  | 7 | 0.8 | 7 | 7 | 2 | N |  |  | OP | X | 1 | 1960 |  |  | Y | Industrial CHP | 7 | T | BIT | NG | SLW | OTH | OG |  | NG |  |  |  | N | N |  | 12H |  |  | Y |  | Y | [18 empty] | N | N | N
Vintage1962 | hard coal | FALSE | 5610 | Eastman Chemical Co-TN Ops | 50481 | Tennessee Eastman Operations | TN | Sullivan | TG14 | Conventional Steam Coal | ST |  | S | X | X |  |  | 10 | 0.8 | 10 | 10 | 2 | N |  |  | OP | X | 4 | 1962 |  |  | Y | Industrial CHP | 7 | B | BIT | NG | SLW | OTH | OG |  | NG |  |  |  | N | N |  | 12H |  |  | Y |  | Y | [18 empty] | N | N | N
Vintage1963 | hard coal | FALSE | 5610 | Eastman Chemical Co-TN Ops | 50481 | Tennessee Eastman Operations | TN | Sullivan | TG15 | Conventional Steam Coal | ST |  | S | X | X |  |  | 7.5 | 0.8 | 7.5 | 7.5 | 2 | N |  |  | OP | X | 10 | 1963 |  |  | Y | Industrial CHP | 7 | T | BIT | NG | SLW | OTH | OG |  | NG |  |  |  | N | N |  | 12H |  |  | Y |  | Y | [18 empty] | N | N | N
Vintage1966 | natural gas steam turbine | FALSE | 5610 | Eastman Chemical Co-TN Ops | 50481 | Tennessee Eastman Operations | TN | Sullivan | TG16 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 10.4 | 0.8 | 10.4 | 10.4 | 1.5 | N |  |  | OP | X | 7 | 1966 |  |  | Y | Industrial CHP | 7 | X T T: T; WH BLQ BLQ: NG; WH WDS NG: BIT; WH RFO DFO: NG |  | N | N |  | 12H |  | N |  |  | N | [18 empty] | N | N | N
Vintage1966 | hard coal | FALSE | 5610 | Eastman Chemical Co-TN Ops | 50481 | Tennessee Eastman Operations | TN | Sullivan | TG17 | Conventional Steam Coal | ST |  | S | X | X |  |  | 10.4 | 0.8 | 10.4 | 10.4 | 1.5 | N |  |  | OP | X | 10 | 1966 |  |  | Y | Industrial CHP | 7 | T | BIT | NG | SLW | OTH | OG |  | NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1967 | natural gas steam turbine | FALSE | 5610 | Eastman Chemical Co-TN Ops | 50481 | Tennessee Eastman Operations | TN | Sullivan | TG18 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 10.4 | 0.8 | 10.4 | 10.4 | 1.5 | N |  |  | OP | X | 7 | 1967 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H |  | N |  |  | N | [18 empty] | N | N | N | bar: X T T to WH BLQ BLQ; WH RFO DFO
Vintage1970 | natural gas steam turbine | FALSE | 5610 | Eastman Chemical Co-TN Ops | 50481 | Tennessee Eastman Operations | TN | Sullivan | TG19 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 10.4 | 0.8 | 10.4 | 10.4 | 1.5 | N |  |  | OP | X | 3 | 1970 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T to WH BLQ BLQ; WH RFO DFO
Vintage1972 | hard coal | FALSE | 5610 | Eastman Chemical Co-TN Ops | 50481 | Tennessee Eastman Operations | TN | Sullivan | TG20 | Conventional Steam Coal | ST |  | S | X | X |  |  | 10.4 | 0.8 | 10.4 | 10.4 | 1.5 | N |  |  | OP | X | 4 | 1972 |  |  | Y | Industrial CHP | 7 | X T T: T; WH BLQ BLQ: BIT; WH WDS NG: NG; WH RFO DFO: NG |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1969 | natural gas steam turbine | FALSE | 5610 | Eastman Chemical Co-TN Ops | 50481 | Tennessee Eastman Operations | TN | Sullivan | TG21 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 15 | 0.8 | 15 | 15 | 2 | N |  |  | OP | X | 7 | 1969 |  |  | Y | Industrial CHP | 7 | B | NG | BIT | SLW | OTH | OG |  | NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1982 | hard coal | FALSE | 5610 | Eastman Chemical Co-TN Ops | 50481 | Tennessee Eastman Operations | TN | Sullivan | TG22 | Conventional Steam Coal | ST |  | S | X | X |  |  | 15.4 | 0.8 | 15.4 | 15.4 | 1.5 | N |  |  | OP | X | 9 | 1982 |  |  | Y | Industrial CHP | 7 | T | BIT | NG | OG | OTH |  |  | NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1983 | natural gas steam turbine | FALSE | 5610 | Eastman Chemical Co-TN Ops | 50481 | Tennessee Eastman Operations | TN | Sullivan | TG24 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 16.8 | 0.8 | 16.8 | 16.8 | 2 | N |  |  | OP | X | 7 | 1983 |  |  | Y | Industrial CHP | 7 | B | NG | BIT | SLW | OTH | OG |  | NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1994 | hard coal | FALSE | 5610 | Eastman Chemical Co-TN Ops | 50481 | Tennessee Eastman Operations | TN | Sullivan | TG25 | Conventional Steam Coal | ST |  | S | X | X |  |  | 18 | 0.8 | 18 | 18 | 2 | N |  |  | OP | X | 12 | 1994 |  |  | Y | Industrial CHP | 7 | T | BIT | NG | OG | OTH | SLW |  | NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1994 | hard coal | FALSE | 5610 | Eastman Chemical Co-TN Ops | 50481 | Tennessee Eastman Operations | TN | Sullivan | TG26 | Conventional Steam Coal | ST |  | S | X | X |  |  | 16.6 | 0.8 | 16.6 | 16.6 | 1.5 | N |  |  | OP | X | 10 | 1994 |  |  | Y | Industrial CHP | 7 | T | BIT | NG | OG | OTH |  |  | NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | N | [17 empty] | N | N | N
Vintage1936 | hard coal | FALSE | 5610 | Eastman Chemical Co-TN Ops | 50481 | Tennessee Eastman Operations | TN | Sullivan | TGO7 | Conventional Steam Coal | ST |  | S | X | X |  |  | 6 | 0.8 | 6 | 6 | 2 | N |  |  | OP | X | 9 | 1936 |  |  | Y | Industrial CHP | 7 | T | BIT | NG | SLW | OTH | OG |  | NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1939 | hard coal | FALSE | 5610 | Eastman Chemical Co-TN Ops | 50481 | Tennessee Eastman Operations | TN | Sullivan | TGO8 | Conventional Steam Coal | ST |  | S | X | X |  |  | 6 | 0.86 | 6 | 6 | 2 | N |  |  | OP | X | 9 | 1939 |  |  | Y | Industrial CHP | 7 | T | BIT | NG | SLW | OTH | OG |  | NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage1941 | hard coal | FALSE | 5610 | Eastman Chemical Co-TN Ops | 50481 | Tennessee Eastman Operations | TN | Sullivan | TGO9 | Conventional Steam Coal | ST |  | S | X | X |  |  | 6 | 0.8 | 6 | 6 | 2 | N |  |  | OP | X | 7 | 1941 |  |  | Y | Industrial CHP | 7 | T | BIT | NG | SLW | OTH | OG |  | NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | N | N | N
Vintage2004 | biomass | TRUE | 19365 | United States Sugar Corp | 50482 | Clewiston Sugar House | FL | Hendry | TG6 | Other Waste Biomass | ST |  | S | X | X |  |  | 15 | 1 | 14 | 14.1 | 5 | N |  |  | OP | X | 3 | 2004 |  |  | Y | Industrial CHP | 7 | X T T: B; WH BLQ BLQ: AB; WH WDS NG: DFO; WH RFO DFO: DFO |  | N | N |  | 12H |  |  | N | N | N | [18 empty] | Y | Y | N
Vintage2006 | biomass | TRUE | 19365 | United States Sugar Corp | 50482 | Clewiston Sugar House | FL | Hendry | TG7 | Other Waste Biomass | ST |  | S | X | X |  |  | 20 | 0.8 | 18.6 | 18.6 | 7.5 | N |  |  | OP | X | 10 | 2006 |  |  | Y | Industrial CHP | 7 | X T T: B; WH BLQ BLQ: AB; WH WDS NG: DFO; WH RFO DFO: DFO |  | N | N |  | 12H |  |  | N |  | N | [18 empty] | Y | Y | N
Vintage2007 | biomass | TRUE | 19365 | United States Sugar Corp | 50482 | Clewiston Sugar House | FL | Hendry | TG8 | Other Waste Biomass | ST |  | S | X | X |  |  | 14 | 0.9 | 12 | 12 | 5 | N |  |  | OP | X | 12 | 2007 |  |  | Y | Industrial CHP | 7 | X T T: B; WH BLQ BLQ: AB; WH WDS NG: DFO; WH RFO DFO: DFO |  | N | N |  | 12H |  |  | N |  | N | [18 empty] | Y | Y | N
Vintage1943 | other | FALSE | 14306 | Eagle 2 US LLC | 50487 | PPG Powerhouse A | LA | Calcasieu | A1 | All Other | ST |  | S | X | X |  |  | 7.5 | 0.85 | 7.5 | 7.5 | 1 | N |  |  | OS | X | 6 | 1943 |  |  | N | Industrial Non-CHP | 6 | X T T: X; WH BLQ BLQ: PUR; WH RFO DFO: NG |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1943 | other | FALSE | 14306 | Eagle 2 US LLC | 50487 | PPG Powerhouse A | LA | Calcasieu | A2 | All Other | ST |  | S | X | X |  |  | 7.5 | 0.85 | 7.5 | 7.5 | 1 | N |  |  | OS | X | 6 | 1943 |  |  | N | Industrial Non-CHP | 6 | X T T: X; WH BLQ BLQ: PUR; WH RFO DFO: NG |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1943 | other | FALSE | 14306 | Eagle 2 US LLC | 50487 | PPG Powerhouse A | LA | Calcasieu | A4 | All Other | ST |  | S | X | X |  |  | 7.5 | 0.85 | 7.5 | 7.5 | 1 | N |  |  | OS | X | 5 | 1943 |  |  | N | Industrial Non-CHP | 6 | X T T: X; WH BLQ BLQ: PUR; WH RFO DFO: NG |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1950 | other | FALSE | 14306 | Eagle 2 US LLC | 50487 | PPG Powerhouse A | LA | Calcasieu | A7 | All Other | ST |  | S | X | X | EES.AXIALL |  | 10 | 0.85 | 10 | 10 | 1 | N |  |  | OS | X | 10 | 1950 |  |  | N | Industrial Non-CHP | 6 | X T T: X; WH BLQ BLQ: PUR; WH RFO DFO: NG |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1957 | other | FALSE | 14306 | Eagle 2 US LLC | 50487 | PPG Powerhouse A | LA | Calcasieu | A9 | All Other | ST |  | S | X | X |  |  | 20 | 0.85 | 20 | 20 | 1 | N |  |  | OS | X | 8 | 1957 |  |  | N | Industrial Non-CHP | 6 | X T T: X; WH BLQ BLQ: PUR; WH RFO DFO: NG |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1947 | other | FALSE | 14306 | Eagle 2 US LLC | 50488 | PPG Riverside | LA | Calcasieu | GEN1 | All Other | ST |  | S | X | X |  |  | 35 | 0.85 | 35 | 40 | 8 | N |  |  | OS | X | 9 | 1947 |  |  | N | Industrial Non-CHP | 6 | X T T: X; WH BLQ BLQ: PUR; WH RFO DFO: NG |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1950 | other | FALSE | 14306 | Eagle 2 US LLC | 50488 | PPG Riverside | LA | Calcasieu | GEN2 | All Other | ST |  | S | X | X | EES.AXIALL |  | 45 | 0.85 | 30 | 30 | 8 | N |  |  | OP | X | 6 | 1950 |  |  | N | Industrial Non-CHP | 6 | X T T: X; WH BLQ BLQ: PUR; WH RFO DFO: NG |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1969 | other | FALSE | 14306 | Eagle 2 US LLC | 50488 | PPG Riverside | LA | Calcasieu | GEN3 | All Other | ST |  | S | X | X | EES.AXIALL |  | 82 | 0.85 | 38 | 40 | 8 | N |  |  | OP | X | 2 | 1969 |  |  | N | Industrial Non-CHP | 6 | X T T: X; WH BLQ BLQ: PUR; WH RFO DFO: NG |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1977 | natural gas peaker | FALSE | 14306 | Eagle 2 US LLC | 50489 | PPG Powerhouse C | LA | Calcasieu | C1 | Natural Gas Fired Combustion Turbine | GT | PHC | S | X | X | EES.AXIALL | EES.AXIALL | 73.1 | 0.85 | 55 | 63 | 50 | N |  |  | OP | X | 8 | 1977 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T to WH BLQ BLQ
Vintage1978 | natural gas peaker | FALSE | 14306 | Eagle 2 US LLC | 50489 | PPG Powerhouse C | LA | Calcasieu | C2 | Natural Gas Fired Combustion Turbine | GT | PHC | S | X | X | EES.AXIALL | EES.AXIALL | 73.1 | 0.85 | 55 | 63 | 50 | N |  |  | OP | X | 6 | 1978 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T to WH BLQ BLQ
Vintage1977 | natural gas steam turbine | FALSE | 14306 | Eagle 2 US LLC | 50489 | PPG Powerhouse C | LA | Calcasieu | C3 | Natural Gas Steam Turbine | ST | PHC | S | X | X | EES.AXIALL | EES.AXIALL | 57.1 | 0.85 | 52 | 52 | 25 | N |  |  | OP | X | 9 | 1977 |  |  | Y | Industrial CHP | 7 | X T T: B; WH BLQ BLQ: NG; WH WDS NG: OG; WH RFO DFO: NG |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1986 | natural gas peaker | FALSE | 14306 | Eagle 2 US LLC | 50489 | PPG Powerhouse C | LA | Calcasieu | C4 | Natural Gas Fired Combustion Turbine | GT | PHC | S | X | X | EES.AXIALL | EES.AXIALL | 77.2 | 0.85 | 70.6 | 78.6 | 38 | N |  |  | OP | X | 8 | 1986 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T to WH BLQ BLQ
Vintage1986 | natural gas peaker | FALSE | 14306 | Eagle 2 US LLC | 50489 | PPG Powerhouse C | LA | Calcasieu | C5 | Natural Gas Fired Combustion Turbine | GT | PHC | S | X | X | EES.AXIALL | EES.AXIALL | 77.2 | 0.85 | 70.6 | 78.6 | 38 | N |  |  | OP | X | 8 | 1986 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T to WH BLQ BLQ
Vintage1986 | natural gas steam turbine | FALSE | 14306 | Eagle 2 US LLC | 50490 | PPG Plant C Caustic | LA | Calcasieu | TE | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 3.4 | 0.85 | 2.7 | 2.7 | 1 | N |  |  | OP | X | 10 | 1986 |  |  | Y | Industrial CHP | 7 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | N | bar: X T T to WH BLQ BLQ; WH RFO DFO
Vintage1943 | natural gas steam turbine | FALSE | 60586 | Westlake Chemical Natrium Plant | 50491 | Axiall Natrium Plant | WV | Marshall | GEN4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 7.5 | 0.9 | 7.5 | 7.5 | 0.5 | N |  |  | OP | X | 1 | 1943 |  |  | Y | Industrial CHP | 7 | X T T: T; WH BLQ BLQ: NG; WH WDS NG: OG; WH RFO DFO: NG |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1954 | natural gas steam turbine | FALSE | 60586 | Westlake Chemical Natrium Plant | 50491 | Axiall Natrium Plant | WV | Marshall | GEN6 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 26 | 0.9 | 26 | 26 | 5 | N |  |  | OP | X | 1 | 1954 |  |  | Y | Industrial CHP | 7 | X T T: T; WH BLQ BLQ: NG; WH WDS NG: OG; WH RFO DFO: NG |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1966 | natural gas steam turbine | FALSE | 60586 | Westlake Chemical Natrium Plant | 50491 | Axiall Natrium Plant | WV | Marshall | GEN7 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 82 | 0.9 | 82 | 82 | 10 | N |  |  | OP | X | 1 | 1966 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X T T to WH BLQ BLQ; WH RFO DFO
Vintage1985 | biomass | TRUE | 16764 | City of San Diego | 50492 | Gas Utilization Facility | CA | San Diego | 1 | Other Waste Biomass | IC |  | S | X | X |  |  | 2.3 | 0.8 | 2.3 | 2.3 | 1 | N |  |  | OP | X | 6 | 1985 |  |  | Y | Commercial CHP | 5 | X T T: T; WH BLQ BLQ: OBG; WH WDS NG: NG |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1985 | biomass | TRUE | 16764 | City of San Diego | 50492 | Gas Utilization Facility | CA | San Diego | 2 | Other Waste Biomass | IC |  | S | X | X |  |  | 2.3 | 0.8 | 2.3 | 2.3 | 1 | N |  |  | OP | X | 6 | 1985 |  |  | Y | Commercial CHP | 5 | X T T: T; WH BLQ BLQ: OBG; WH WDS NG: NG |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2002 | hydro | FALSE | 16764 | City of San Diego | 50492 | Gas Utilization Facility | CA | San Diego | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 0.8 | 1 | 1.5 | 0.5 | N |  |  | OP | X | 5 | 2002 |  |  | N | Commercial CHP | 5 | X T T: X; WH BLQ BLQ: WAT |  | N | N |  | 10M | [23 empty] | N
Vintage1989 | natural gas peaker | TRUE | 60662 | WCAC Operating Company | 50493 | Double C Generation Limited Partnership | CA | Kern | DC1 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 24.9 | 0.85 | 23 | 24 | 21 | N |  |  | OP | X | 3 | 1989 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T to WH BLQ BLQ
Vintage1989 | natural gas peaker | TRUE | 60662 | WCAC Operating Company | 50493 | Double C Generation Limited Partnership | CA | Kern | DC2 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 24.9 | 0.85 | 23 | 24 | 21 | N |  |  | OP | X | 3 | 1989 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T to WH BLQ BLQ
Vintage1989 | natural gas peaker | TRUE | 60662 | WCAC Operating Company | 50494 | Kern Front Limited | CA | Kern | KF1 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 24.9 | 0.85 | 23 | 24 | 21 | N |  |  | OP | X | 2 | 1989 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | bar: X T T to WH BLQ BLQ
Vintage1989 | natural gas peaker | TRUE | 60662 | WCAC Operating Company | 50494 | Kern Front Limited | CA | Kern | KF2 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 24.9 | 0.85 | 23 | 24 | 21 | N |  |  | OP | X | 2 | 1989 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | bar: X T T to WH BLQ BLQ
Vintage1989 | natural gas peaker | TRUE | 60662 | WCAC Operating Company | 50495 | High Sierra Limited | CA | Kern | HS1 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 24.9 | 0.85 | 23 | 24 | 21 | N |  |  | OP | X | 3 | 1989 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X T T to WH BLQ BLQ
Vintage1989 | natural gas peaker | TRUE | 60662 | WCAC Operating Company | 50495 | High Sierra Limited | CA | Kern | HS2 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 24.9 | 0.85 | 23 | 24 | 21 | N |  |  | OP | X | 3 | 1989 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X T T to WH BLQ BLQ
Vintage1984 | other | FALSE | 22175 | PCS Phosphate | 50509 | PCS Phosphate | NC | Beaufort | GEN1 | All Other | ST |  | S | X | X |  |  | 54 | 0.97 | 54 | 54 | 5 | N |  |  | OP | X | 12 | 1984 |  |  | Y | Industrial CHP | 7 | X T T: B; WH BLQ BLQ: WH; WH RFO DFO: DFO; WH DFO RFO: PG |  | N | N |  | 12H |  |  |  |  | N | [18 empty] | N | N | N
Vintage1999 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50512 | Glen Park Hydroelectric Project | NY | Jefferson | GEN1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 14.5 | 0.9 | 14.5 | 14.5 | 2.2 | N |  |  | OP | X | 10 | 1999 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  | N |  |  | 10M
Vintage1999 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50512 | Glen Park Hydroelectric Project | NY | Jefferson | GEN2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 14.5 | 0.9 | 14.5 | 14.5 | 2.2 | N |  |  | OP | X | 10 | 1999 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  | N |  |  | 10M
Vintage1999 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50512 | Glen Park Hydroelectric Project | NY | Jefferson | GEN3 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 3.6 | 0.9 | 3.6 | 3.6 | 0.5 | N |  |  | OP | X | 10 | 1999 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  | N |  |  | 10M
Vintage1987 | hydro | TRUE | 18121 | Stillwater Associates | 50513 | Stillwater Reservoir Hydro | NY | Herkimer | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 1 | 2.5 | 2.5 | 0.3 | N |  |  | OP | X | 1 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  |  |  |  | 10M | [23 empty] | N |  | N
Vintage1984 | hydro | TRUE | 6495 | Fort Miller Associates | 50514 | Fort Miller Hydroelectric Facility | NY | Saratoga | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 12 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  | N |  | 0 | 10M | [20 empty] | N |  |  |  |  | N
Vintage1984 | hydro | TRUE | 6495 | Fort Miller Associates | 50514 | Fort Miller Hydroelectric Facility | NY | Saratoga | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 1 | 2.5 | 2.5 | 2.5 | N |  |  | OP | X | 12 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  | N |  | 0 | 10M | [20 empty] | N |  |  |  |  | N
Vintage1982 | other | FALSE | 55985 | Tesoro Refining and Marketing Company | 50530 | Equilon Los Angeles Refining | CA | Los Angeles | GEN1 | Other Gases | GT |  | S | X | X |  |  | 30 | 0.85 | 17.8 | 20.8 | 18 | N |  |  | OP | X | 12 | 1982 |  |  | Y | Industrial CHP | 7 | X T T: T; WH BLQ BLQ: OG; WH WDS NG: NG |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1982 | other | FALSE | 55985 | Tesoro Refining and Marketing Company | 50530 | Equilon Los Angeles Refining | CA | Los Angeles | GEN2 | Other Gases | GT |  | S | X | X |  |  | 30 | 0.85 | 19.7 | 23.7 | 18 | N |  |  | OP | X | 12 | 1982 |  |  | Y | Industrial CHP | 7 | X T T: T; WH BLQ BLQ: OG; WH WDS NG: NG |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1991 | other | FALSE | 55985 | Tesoro Refining and Marketing Company | 50530 | Equilon Los Angeles Refining | CA | Los Angeles | GEN3 | Other Gases | ST |  | S | X | X |  |  | 23 | 0.8 | 5.8 | 8.7 | 4 | N |  |  | OP | X | 4 | 1991 |  |  | Y | Industrial CHP | 7 | X T T: B; WH BLQ BLQ: OG; WH WDS NG: NG; WH RFO DFO: OG |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2000 | onshore wind | TRUE | 56899 | Wind Stream Operations LLC | 50532 | Victory Garden (Tehachapi) | CA | Kern | 15SLE | Onshore Wind Turbine | WT |  | S | X | X |  |  | 1.5 |  | 1.5 | 1.5 | 0 | N |  |  | OP | X | 5 | 2000 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WND |  | N | N | 1 | [21 empty] | N |  |  | N | N | N
Vintage1981 | onshore wind | TRUE | 56899 | Wind Stream Operations LLC | 50532 | Victory Garden (Tehachapi) | CA | Kern | WGNS | Onshore Wind Turbine | WT |  | S | X | X |  |  | 17.3 |  | 17.3 | 17.3 | 0 | N |  |  | OP | X | 12 | 1981 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WND |  | N | N | 241 | [21 empty] | N |  |  | N | N | N
Vintage2021 | onshore wind | TRUE | 63880 | Painted Hills Wind Holdings, LLC | 50533 | Painted Hills Wind Park | CA | Riverside | PHW | Onshore Wind Turbine | WT |  | S | X | X |  |  | 46.8 |  | 46.8 | 46.8 | 0 | N |  |  | OP | X | 4 | 2021 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WND |  | N | N | 13 | [24 empty] | N
Vintage1984 | onshore wind | TRUE | 63235 | Brookfield Renewable Trading and Marketing LP | 50535 | Mesa Wind Power LLC | CA | Riverside | WGNS | Onshore Wind Turbine | WT |  | W | X | X |  |  | 29.9 |  | 29.9 | 29.9 | 0 | N |  |  | OP | X | 11 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WND |  | N | N | 460 | [16 empty] | WT | WND | 29.9 | 3 | 2022 |  |  |  | N | N
Vintage2021 | onshore wind | TRUE | 64156 | Sky River Wind LLC | 50536 | Sky River Wind Energy Center | CA | Kern | SRW1 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 60.2 |  | 60.2 | 60.2 |  | N |  |  | OP | X | 9 | 2021 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WND |  |  |  | 21
Vintage1987 | natural gas peaker | FALSE | 9297 | IPT SRI Cogeneration Inc | 50537 | SRI International Cogen Project | CA | San Mateo | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 6 | 0.8 | 5.6 | 5.6 | 0.2 | N |  |  | OP | X | 4 | 1987 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: X T T to WH BLQ BLQ
Vintage1984 | hydro | TRUE | 1966 | Boltonville Hydro Associates | 50539 | Boltonville Hydro Associates | VT | Orange | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0 | N |  |  | OP | X | 7 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  | N | N | 0 | 1H | [23 empty] | N
Vintage1984 | hydro | TRUE | 1966 | Boltonville Hydro Associates | 50539 | Boltonville Hydro Associates | VT | Orange | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0 | N |  |  | OS | X | 7 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  | N | N | 0 | 1H | [23 empty] | N
Vintage1989 | hydro | TRUE | 1966 | Boltonville Hydro Associates | 50539 | Boltonville Hydro Associates | VT | Orange | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0 | N |  |  | OS | X | 12 | 1989 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  | N | N | 0 | 1H | [23 empty] | N
Vintage1984 | other | FALSE | 2696 | Tesoro Carson Refinery | 50540 | BP Carson Refinery | CA | Los Angeles | GEN1 | Other Gases | OT |  | S | X | X |  |  | 12 | 0.9 | 6.5 | 6.5 | 1 | N |  |  | SB | Y | 6 | 1984 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T to WH BLQ BLQ
Vintage1982 | natural gas steam turbine | FALSE | 2696 | Tesoro Carson Refinery | 50540 | BP Carson Refinery | CA | Los Angeles | GEN2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 1.5 | 0.9 | 1.5 | 1.5 | 0.2 | N |  |  | OS | X | 4 | 1982 |  |  | N | Industrial Non-CHP | 6 | X T T: X; WH BLQ BLQ: NG; WH WDS NG: OG; WH RFO DFO: NG |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1988 | natural gas combined cycle | TRUE | 8303 | Harbor Cogeneration Co. | 50541 | Harbor Cogen | CA | Los Angeles | GEN1 | Natural Gas Fired Combined Cycle | CT | HCCC | S | X | N | HARBGN_7_UNITS | HARBGN_7_UNITS | 82.3 | 1 | 80.8 | 84.5 | 65 | N |  |  | OP | X | 12 | 1988 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T to WH BLQ BLQ
Vintage2001 | natural gas combined cycle | TRUE | 8303 | Harbor Cogeneration Co. | 50541 | Harbor Cogen | CA | Los Angeles | ST1 | Natural Gas Fired Combined Cycle | CA | HCCC | S | N | X | HARBGN_7_UNITS | HARBGN_7_UNITS | 13.6 | 1 | 9.9 | 10.4 | 0 | N |  |  | OP | X | 6 | 2001 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T to WH BLQ BLQ
Vintage2001 | natural gas combined cycle | TRUE | 8303 | Harbor Cogeneration Co. | 50541 | Harbor Cogen | CA | Los Angeles | ST2 | Natural Gas Fired Combined Cycle | CA | HCCC | S | N | X | HARBGN_7_UNITS | HARBGN_7_UNITS | 11.5 | 1 | 11 | 11 | 0 | N |  |  | OP | X | 6 | 2001 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T to WH BLQ BLQ
Vintage1986 | biomass | TRUE | 26840 | Port Townsend Paper Co | 50544 | Port Townsend Paper | WA | Jefferson | GEN6 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 7.5 | 0.8 | 7.5 | 7.5 | 0.5 | N |  |  | OP | X | 1 | 1986 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | NG | WO | SLW |  | WO | PG |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1982 | hydro | FALSE | 26840 | Port Townsend Paper Co | 50544 | Port Townsend Paper | WA | Jefferson | HDRO | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.3 | 0.3 | 0.1 | N |  |  | OS | X | 8 | 1982 |  |  | N | Industrial CHP | 7 | X T T: X; WH BLQ BLQ: WAT |  | N | N |  | OVER
Vintage1981 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 50545 | Lawrence Hydroelectric Associates | MA | Essex | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7.4 | 1 | 7 | 6.8 | 0.1 | N |  |  | OP | X | 7 | 1981 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  |  |  | 0 | 10M
Vintage1981 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 50545 | Lawrence Hydroelectric Associates | MA | Essex | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7.4 | 1 | 7 | 6.8 | 0.1 | N |  |  | OP | X | 7 | 1981 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  |  |  | 0 | 10M
Vintage1986 | hydro | TRUE | 13402 | Nevada Irrigation District | 50546 | Bowman | CA | Nevada | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.6 | 0.99 | 3.6 | 3.6 | 0.1 | N |  |  | OP | X | 9 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WAT |  | N | N | 0 | 1H | [23 empty] | N
Vintage1999 | onshore wind | TRUE | 64407 | Huntsman Wind | 50552 | GPS Cabazon Wind LLC | CA | Riverside | WGNS | Onshore Wind Turbine | WT |  | S | X | X |  |  | 38.9 |  | 38.9 | 38.9 | 2 | N |  |  | OP | X | 1 | 1999 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WND |  | N |  | 52 | [24 empty] | N
Vintage2008 | onshore wind | TRUE | 61208 | Red Marlin Wind Ventures, LLC | 50553 | Edom Hills Project 1 LLC | CA | Riverside | 1 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 20 |  | 20 | 20 | 4 | N |  |  | OP | X | 9 | 2008 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WND |  | N | N | 8 | [24 empty] | N
Vintage1990 | petroleum | TRUE | 19876 | Virginia Electric & Power Co | 50555 | Rosemary Power Station | NC | Halifax | GEN1 | Petroleum Liquids | CT | G785 | S | X | N |  |  | 86 | 0.85 | 75 | 88 | 52 | N |  |  | OP | X | 11 | 1990 |  |  | N | Electric Utility | 1 | X T T: X; WH BLQ BLQ: DFO |  | N |  |  | 12H | [23 empty] | N | N | N
Vintage1990 | petroleum | TRUE | 19876 | Virginia Electric & Power Co | 50555 | Rosemary Power Station | NC | Halifax | GEN2 | Petroleum Liquids | CT | G785 | S | X | N |  |  | 40 | 0.85 | 36 | 44 | 24 | N |  |  | OP | X | 11 | 1990 |  |  | N | Electric Utility | 1 | X T T: X; WH BLQ BLQ: DFO |  | N |  |  | 12H | [23 empty] | N | N | N
Vintage1990 | petroleum | TRUE | 19876 | Virginia Electric & Power Co | 50555 | Rosemary Power Station | NC | Halifax | GEN3 | Petroleum Liquids | CA | G785 | S | N | X |  |  | 54 | 0.85 | 54 | 54 | 44 | N |  |  | OP | X | 11 | 1990 |  |  | N | Electric Utility | 1 | X T T: X; WH BLQ BLQ: DFO |  | N |  |  | 12H | [23 empty] | N | N | N
Vintage1989 | natural gas combined cycle | TRUE | 14063 | Oklahoma Gas & Electric Co | 50558 | Frontier | OK | Oklahoma | GT01 | Natural Gas Fired Combined Cycle | CT | CC01 | S | X | N | OKGENSCI1UN1_RA | OKGENSMITH | 87.2 | 0.9 |  |  |  | N |  |  | OP | X | 9 | 1989 |  |  | N | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T to WH BLQ BLQ; WH RFO DFO
Vintage1989 | natural gas combined cycle | TRUE | 14063 | Oklahoma Gas & Electric Co | 50558 | Frontier | OK | Oklahoma | ST01 | Natural Gas Fired Combined Cycle | CA | CC01 | S | Y | X |  |  | 44.2 | 0.9 | 120 | 120 | 70 | N |  |  | OP | X | 9 | 1989 |  |  | N | Electric Utility | 1 | [11 empty] | N | N | 0 | 12H | [23 empty] | N | N | N | bar: X T T to WH BLQ BLQ; WH RFO DFO
Vintage1986 | biomass | TRUE | 58650 | IHI Power Services Corp | 50560 | Pacific-Ultrapower Chinese Station | CA | Tuolumne | GEN1 | Wood/Wood Waste Biomass | ST |  | J | X | X |  |  | 25 | 0.85 | 18 | 18 | 15 | N |  |  | OP | X | 10 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WDS; WH RFO DFO: PG |  | N | N |  | OVER | N | [22 empty] | N | N | N
Vintage1990 | natural gas combined cycle | TRUE | 49942 | Eagle Point Power Generation LLC | 50561 | Eagle Point Power Generation | NJ | Gloucester | GTG1 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N | EAGLEGEN 13 KV EGLE#1 GEN | EAGLE CT1 | 90 | 0.85 | 85 | 90 | 82 | N |  |  | OP | X | 11 | 1990 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: NG; WH WDS NG: DFO |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1990 | natural gas combined cycle | TRUE | 49942 | Eagle Point Power Generation LLC | 50561 | Eagle Point Power Generation | NJ | Gloucester | GTG2 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N | EAGLEGEN 13 KV EGLE#2 GEN |  | 90 | 0.85 | 85 | 90 | 82 | N |  |  | OP | X | 11 | 1990 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: NG; WH WDS NG: DFO |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1991 | natural gas combined cycle | TRUE | 49942 | Eagle Point Power Generation LLC | 50561 | Eagle Point Power Generation | NJ | Gloucester | STG1 | Natural Gas Fired Combined Cycle | CA | CC1 | W | N | X | EAGLEGEN 13 KV EGLE#3 GEN |  | 45 | 0.85 | 47 | 47 | 45 | N |  |  | OP | X | 4 | 1991 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: NG; WH WDS NG: DFO |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2016 | natural gas combined cycle | TRUE | 49942 | Eagle Point Power Generation LLC | 50561 | Eagle Point Power Generation | NJ | Gloucester | STG2 | Natural Gas Fired Combined Cycle | CA | CC1 | W | N | X | EAGLEGEN 13 KV EGLE#4 GEN |  | 26.8 | 0.85 | 27 | 27 | 24 | N |  |  | OP | X | 5 | 2016 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: NG; WH WDS NG: DFO |  |  | N |  | 12H | [23 empty] | N | N | N
Vintage1988 | biomass | TRUE | 54843 | WM Illinois Renewable Energy LLC | 50563 | Settlers Hill Gas Recovery | IL | Kane | GEN1 | Landfill Gas | GT |  | S | X | X | Zonal | Zonal | 3 | 0.98 | 2.9 | 3.3 | 1 | N |  |  | OP | X | 10 | 1988 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1998 | biomass | TRUE | 54843 | WM Illinois Renewable Energy LLC | 50563 | Settlers Hill Gas Recovery | IL | Kane | GEN2 | Landfill Gas | GT |  | S | X | X | Zonal | Zonal | 3 | 0.98 | 2.9 | 3.3 | 1 | N |  |  | OP | X | 5 | 1998 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage2008 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50564 | New Milford Gas Recovery | CT | Litchfield | GEN2 | Landfill Gas | IC |  | S | X | X | Zonal | Zonal | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 5 | 2008 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2008 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50564 | New Milford Gas Recovery | CT | Litchfield | GEN4 | Landfill Gas | IC |  | S | X | X | Zonal | Zonal | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 5 | 2008 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  |  | N |  | 1H | [23 empty] | N | N | N
Vintage1991 | natural gas peaker | TRUE | 54843 | WM Illinois Renewable Energy LLC | 50566 | Milam Gas Recovery | IL | St Clair | GEN1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | Zonal | Zonal | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 4 | 1991 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N |  |  | 1H | [23 empty] | N | N | N | bar: X T T to WH BLQ BLQ
Vintage1991 | natural gas peaker | TRUE | 54843 | WM Illinois Renewable Energy LLC | 50566 | Milam Gas Recovery | IL | St Clair | GEN2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | Zonal | Zonal | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 4 | 1991 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N |  |  | 1H | [23 empty] | N | N | N | bar: X T T to WH BLQ BLQ
Vintage1993 | natural gas peaker | TRUE | 54843 | WM Illinois Renewable Energy LLC | 50566 | Milam Gas Recovery | IL | St Clair | GEN3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | Zonal | Zonal | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 3 | 1993 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N |  |  | 1H | [23 empty] | N | N | N | bar: X T T to WH BLQ BLQ
Vintage1991 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50568 | High Acres Gas Recovery | NY | Monroe | GEN1 | Landfill Gas | IC |  | S | X | X | PTID 23767 | PTID 23767 | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 5 | 1991 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1991 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50568 | High Acres Gas Recovery | NY | Monroe | GEN2 | Landfill Gas | IC |  | S | X | X | PTID 23767 | PTID 23767 | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 5 | 1991 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1991 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50568 | High Acres Gas Recovery | NY | Monroe | GEN3 | Landfill Gas | IC |  | S | X | X | PTID 23767 | PTID 23767 | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 5 | 1991 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1991 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50568 | High Acres Gas Recovery | NY | Monroe | GEN4 | Landfill Gas | IC |  | S | X | X | PTID 23767 | PTID 23767 | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 5 | 1991 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage2008 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50568 | High Acres Gas Recovery | NY | Monroe | GEN5 | Landfill Gas | IC |  | S | X | X | PTID 23767 | PTID 23767 | 1.6 | 0.98 | 1.6 | 1.6 | 0.8 | N |  |  | OP | X | 3 | 2008 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage2008 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50568 | High Acres Gas Recovery | NY | Monroe | GEN6 | Landfill Gas | IC |  | S | X | X | PTID 23767 | PTID 23767 | 1.6 | 0.98 | 1.6 | 1.6 | 0.8 | N |  |  | OP | X | 3 | 2008 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2008 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50568 | High Acres Gas Recovery | NY | Monroe | GEN7 | Landfill Gas | IC |  | S | X | X | PTID 23767 | PTID 23767 | 1.6 | 0.98 | 1.6 | 1.6 | 0.8 | N |  |  | OP | X | 3 | 2008 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2008 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50568 | High Acres Gas Recovery | NY | Monroe | GEN8 | Landfill Gas | IC |  | S | X | X | PTID 23767 | PTID 23767 | 1.6 | 0.98 | 1.6 | 1.6 | 0.8 | N |  |  | OP | X | 3 | 2008 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1988 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50569 | DFW Gas Recovery | TX | Denton | GEN1 | Landfill Gas | GT |  | S | X | X | DG_BIO2 | DG_BIO2 | 3 | 0.98 | 2.9 | 3.2 | 1 | N |  |  | OP | X | 5 | 1988 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1988 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50569 | DFW Gas Recovery | TX | Denton | GEN2 | Landfill Gas | GT |  | S | X | X | DG_BIO2 | DG_BIO2 | 3 | 0.98 | 2.9 | 3.2 | 1 | N |  |  | OP | X | 5 | 1988 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage2009 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50569 | DFW Gas Recovery | TX | Denton | GEN3 | Landfill Gas | IC |  | S | X | X | DG_BIO2 | DG_BIO2 | 1.6 | 0.98 | 1.6 | 1.6 | 0.8 | N |  |  | OP | X | 8 | 2009 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  |  |  |  | 1H | [23 empty] | N | N | N
Vintage2009 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50569 | DFW Gas Recovery | TX | Denton | GEN4 | Landfill Gas | IC |  | S | X | X | DG_BIO2 | DG_BIO2 | 1.6 | 0.98 | 1.6 | 1.6 | 0.8 | N |  |  | OP | X | 8 | 2009 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  |  |  |  | 1H | [23 empty] | N | N | N
Vintage2009 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50569 | DFW Gas Recovery | TX | Denton | GEN5 | Landfill Gas | IC |  | S | X | X | DG_BIO2 | DG_BIO2 | 1.6 | 0.98 | 1.6 | 1.6 | 0.8 | N |  |  | OP | X | 8 | 2009 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  |  |  |  | 1H | [23 empty] | N | N | N
Vintage2009 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50569 | DFW Gas Recovery | TX | Denton | GEN6 | Landfill Gas | IC |  | S | X | X | DG_BIO2 | DG_BIO2 | 1.6 | 0.98 | 1.6 | 1.6 | 0.8 | N |  |  | OP | X | 8 | 2009 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  |  |  |  | 1H | [23 empty] | N | N | N
Vintage1992 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50570 | Chestnut Ridge Gas Recovery | TN | Anderson | GEN1 | Landfill Gas | IC |  | S | X | X | TVA | TVA | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 1 | 1992 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1992 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50570 | Chestnut Ridge Gas Recovery | TN | Anderson | GEN2 | Landfill Gas | IC |  | S | X | X | TVA | TVA | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 1 | 1992 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1992 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50570 | Chestnut Ridge Gas Recovery | TN | Anderson | GEN3 | Landfill Gas | IC |  | S | X | X | TVA | TVA | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 1 | 1992 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1992 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50570 | Chestnut Ridge Gas Recovery | TN | Anderson | GEN4 | Landfill Gas | IC |  | S | X | X | TVA | TVA | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 1 | 1992 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage2011 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50570 | Chestnut Ridge Gas Recovery | TN | Anderson | GEN5 | Landfill Gas | IC |  | S | X | X | TVA | TVA | 1.6 | 0.98 | 1.6 | 1.6 | 0.8 | N |  |  | OP | X | 11 | 2011 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1989 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50571 | Altamont Gas Recovery | CA | Alameda | GEN1 | Landfill Gas | GT |  | S | X | X | PG&E | PG&E | 3 | 0.98 | 2.9 | 3.3 | 1 | N |  |  | OP | X | 3 | 1989 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1989 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50571 | Altamont Gas Recovery | CA | Alameda | GEN2 | Landfill Gas | GT |  | S | X | X | PG&E | PG&E | 3 | 0.98 | 2.9 | 3.3 | 1 | N |  |  | OP | X | 3 | 1989 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1989 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50572 | CSL Gas Recovery | FL | Broward | GEN1 | Landfill Gas | CT | CC1 | S | X | Y | FP&L | FP&L | 3 | 0.98 | 2.9 | 3 | 1 | N |  |  | OP | X | 3 | 1989 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1989 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50572 | CSL Gas Recovery | FL | Broward | GEN2 | Landfill Gas | CT | CC1 | S | X | Y | FP&L | FP&L | 3 | 0.98 | 2.9 | 3 | 1 | N |  |  | OP | X | 3 | 1989 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1989 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50572 | CSL Gas Recovery | FL | Broward | GEN3 | Landfill Gas | CT | CC1 | S | X | Y | FP&L | FP&L | 3 | 0.98 | 2.9 | 3 | 1 | N |  |  | OP | X | 3 | 1989 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage2000 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50572 | CSL Gas Recovery | FL | Broward | GEN4 | Landfill Gas | CA | CC1 | S | N | X | FP&L | FP&L | 2.2 | 0.98 | 2.2 | 2.2 | 0.2 | N |  |  | OP | X | 2 | 2000 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1989 | biomass | TRUE | 54843 | WM Illinois Renewable Energy LLC | 50573 | CID Gas Recovery | IL | Cook | GEN2 | Landfill Gas | GT |  | S | X | X | Zonal | Zonal | 3 | 0.98 | 2.9 | 3.3 | 1 | N |  |  | OP | X | 3 | 1989 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1993 | biomass | TRUE | 54843 | WM Illinois Renewable Energy LLC | 50575 | Lake Gas Recovery | IL | Cook | GEN2 | Landfill Gas | GT |  | S | X | X | Zonal | Zonal | 3 | 0.98 | 2.9 | 3.3 | 1 | N |  |  | OP | X | 8 | 1993 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1993 | biomass | TRUE | 54843 | WM Illinois Renewable Energy LLC | 50575 | Lake Gas Recovery | IL | Cook | GEN3 | Landfill Gas | GT |  | S | X | X | Zonal | Zonal | 3 | 0.98 | 2.9 | 3.3 | 1 | N |  |  | OP | X | 8 | 1993 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1985 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50576 | Metro Gas Recovery | WI | Milwaukee | GEN1 | Landfill Gas | GT |  | S | X | X | WE | WE | 3 | 0.98 | 2.9 | 3.3 | 1 | N |  |  | OP | X | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1985 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50576 | Metro Gas Recovery | WI | Milwaukee | GEN2 | Landfill Gas | GT |  | S | X | X | WE | WE | 3 | 0.98 | 2.9 | 3.3 | 1 | N |  |  | OP | X | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage2000 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50576 | Metro Gas Recovery | WI | Milwaukee | GEN3 | Landfill Gas | IC |  | S | X | X | WE | WE | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 2 | 2000 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage2000 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50576 | Metro Gas Recovery | WI | Milwaukee | GEN4 | Landfill Gas | IC |  | S | X | X | WE | WE | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 2 | 2000 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2000 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50576 | Metro Gas Recovery | WI | Milwaukee | GEN5 | Landfill Gas | IC |  | S | X | X | WE | WE | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 2 | 2000 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2000 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50576 | Metro Gas Recovery | WI | Milwaukee | GEN6 | Landfill Gas | IC |  | S | X | X | WE | WE | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 2 | 2000 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1985 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50577 | Omega Hills Gas Recovery | WI | Washington | GEN1 | Landfill Gas | GT |  | S | X | X | WE | WE | 3.1 | 0.98 | 2.9 | 3.3 | 1 | N |  |  | OP | X | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1985 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50577 | Omega Hills Gas Recovery | WI | Washington | GEN2 | Landfill Gas | GT |  | S | X | X | WE | WE | 3.1 | 0.98 | 2.9 | 3.3 | 1 | N |  |  | OP | X | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage2001 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50577 | Omega Hills Gas Recovery | WI | Washington | GEN3 | Landfill Gas | GT |  | S | X | X | WE | WE | 3.3 | 0.98 | 3 | 3 | 1 | N |  |  | OP | X | 9 | 2001 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage2010 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 50577 | Omega Hills Gas Recovery | WI | Washington | GEN5 | Landfill Gas | GT |  | S | X | X | WE | WE | 3.3 | 0.98 | 2.9 | 3.3 | 1 | N |  |  | OP | X | 9 | 2010 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: LFG |  |  |  |  | 1H | [23 empty] | N | N | N
Vintage1992 | natural gas peaker | FALSE | 39245 | Saint John's Health Center | 50610 | Saint Johns Health Center | CA | Los Angeles | 01 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 1.2 | 0.8 | 1 | 1.1 | 0.4 | N |  |  | OP | X | 2 | 1992 |  |  | Y | Commercial CHP | 5 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | N | bar: X T T to WH BLQ BLQ
Vintage1987 | hard coal | TRUE | 58224 | Rausch Creek Generation, LLC | 50611 | Westwood Generation LLC | PA | Schuylkill | GEN1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 36 | 0.9 | 30 | 30 | 24 | N |  |  | OP | X | 6 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T: X; WH BLQ BLQ: WC; WH RFO DFO: DFO |  | N | N |  | OVER | Y |  |  |  | Y | [18 empty] | N | N | N
Vintage1991 | natural gas peaker | TRUE | 60662 | WCAC Operating Company | 50612 | McKittrick Limited | CA | Kern | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 46 | 0.85 | 46 | 48 | 21 | N |  |  | OP | X | 10 | 1991 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X T T to WH BLQ BLQ
Vintage1976 | biomass | TRUE | 13008 | Ahlstrom-Munksjo NA Specialty Solutions, LLC | 50614 | Mosinee Mill | WI | Marathon | GEN1 | Wood/Wood Waste Biomass | ST |  | W | X | X |  |  | 15 | 0.8 | 13 | 13 | 2 | N |  |  | OP | X | 12 | 1976 |  |  | Y | Industrial CHP | 7 | T | BLQ | BIT | WDS | SLW | RFO | NG | RFO | NG |  |  | N |  |  | 12H |  |  | Y |  | Y | [18 empty] | Y | Y | N
Vintage1924 | hydro | FALSE | 13008 | Ahlstrom-Munksjo NA Specialty Solutions, LLC | 50614 | Mosinee Mill | WI | Marathon | HYD1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 2.2 | 0.8 | 2 | 2 | 1 | N |  |  | OP | X | 8 | 1924 |  |  | N | Industrial CHP | 7 | T T: X; NG BLQ: WAT |  |  | N |  | 0 | 1H | [7 empty] | 0.5 | 0.5 | 5 | 2023 | [12 empty] | N
Vintage1916 | hydro | FALSE | 13008 | Ahlstrom-Munksjo NA Specialty Solutions, LLC | 50614 | Mosinee Mill | WI | Marathon | HYD2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.6 | 1 | 0.7 | 0.7 | 0.5 | N |  |  | OP | X | 7 | 1916 |  |  | N | Industrial CHP | 7 | T T: X; NG BLQ: WAT |  |  | N |  | 0 | 1H | [23 empty] | N
Vintage1916 | hydro | FALSE | 13008 | Ahlstrom-Munksjo NA Specialty Solutions, LLC | 50614 | Mosinee Mill | WI | Marathon | HYD3 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.6 | 1 | 0.7 | 0.7 | 0.5 | N |  |  | OP | X | 7 | 1916 |  |  | N | Industrial CHP | 7 | T T: X; NG BLQ: WAT |  |  | N |  | 0 | 1H | [23 empty] | N
Vintage1951 | biomass | TRUE | 13008 | Ahlstrom-Munksjo NA Specialty Solutions, LLC | 50614 | Mosinee Mill | WI | Marathon | WEST | Wood/Wood Waste Biomass | ST |  | W | X | X |  |  | 5 | 0.8 | 5 | 5 | 2 | N |  |  | OP | X | 8 | 1951 |  |  | Y | Industrial CHP | 7 | T | BLQ | BIT | WDS | SLW | RFO | NG | RFO | NG |  |  | N |  |  | 12H |  |  | Y |  | Y | [18 empty] | Y | Y | N
Vintage1958 | natural gas steam turbine | FALSE | 18000 | State of Rhode Island | 50621 | Central Power Plant | RI | Providence | GEN4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 2 | 0.8 | 0.5 | 2 | 0.5 | N |  |  | SB | Y | 8 | 1958 |  |  | Y | Commercial CHP | 5 | X T: B; WAT BLQ: NG; WAT BIT: DFO; WAT RFO: DFO |  |  | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage2004 | natural gas peaker | FALSE | 18000 | State of Rhode Island | 50621 | Central Power Plant | RI | Providence | GEN5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.5 | 0.8 | 2.8 | 3.8 | 0.8 | N |  |  | OP | X | 1 | 2004 |  |  | Y | Commercial CHP | 5 | X T: T; WAT BLQ: NG; WAT BIT: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage2004 | natural gas peaker | FALSE | 18000 | State of Rhode Island | 50621 | Central Power Plant | RI | Providence | GEN6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.5 | 0.8 | 2.8 | 3.8 | 0.8 | N |  |  | OP | X | 1 | 2004 |  |  | Y | Commercial CHP | 5 | X T: T; WAT BLQ: NG; WAT BIT: DFO |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage2015 | natural gas peaker | FALSE | 18000 | State of Rhode Island | 50621 | Central Power Plant | RI | Providence | GEN7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 1.2 | N |  |  | OP | X | 4 | 2015 |  |  | N | Commercial CHP | 5 | [11 empty] | N | N |  | 10M | [20 empty] | N |  |  | N |  | N | bar: X T to WAT BLQ
Vintage1986 | natural gas peaker | FALSE | 1569 | Berry Petroleum Co | 50622 | Berry Cogen Tanne Hills 18 | CA | Kern | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | ZP26 | ZP26 | 8.8 | 0.8 | 8 | 9 | 4.5 | N |  |  | OP | X | 12 | 1986 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T to WAT BLQ
Vintage1986 | natural gas peaker | FALSE | 1569 | Berry Petroleum Co | 50622 | Berry Cogen Tanne Hills 18 | CA | Kern | GEN2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | ZP26 | Zp26 | 8.8 | 0.8 | 8 | 9 | 4.5 | N |  |  | OP | X | 12 | 1986 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T to WAT BLQ
Vintage1983 | other | FALSE | 60657 | Torrance Refining Company, LLC | 50624 | Torrance Refining Company, LLC | CA | Los Angeles | EXP1 | All Other | ST |  | S | X | X |  |  | 7.5 | 0.8 | 7.5 | 7.5 | 0 | N |  |  | OP | X | 9 | 1983 |  |  | N | Industrial CHP | 7 | [11 empty] | N | N |  | OVER | N | [22 empty] | N |  | N | bar: X T to WAT BLQ; WAT RFO
Vintage1988 | other | FALSE | 60657 | Torrance Refining Company, LLC | 50624 | Torrance Refining Company, LLC | CA | Los Angeles | GTG1 | Other Gases | GT |  | S | X | X |  |  | 22.5 | 0.8 | 22.5 | 22.5 | 10.5 | N |  |  | OP | X | 11 | 1988 |  |  | Y | Industrial CHP | 7 | X T: T; WAT BLQ: OG; WAT BIT: NG |  |  | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage1988 | other | FALSE | 60657 | Torrance Refining Company, LLC | 50624 | Torrance Refining Company, LLC | CA | Los Angeles | STG1 | All Other | ST |  | S | X | X |  |  | 19.3 | 0.8 | 19.3 | 19.3 | 1.5 | N |  |  | OP | X | 11 | 1988 |  |  | N | Industrial CHP | 7 | [11 empty] | N | N |  | OVER | [23 empty] | N |  | N | bar: X T to WAT BLQ; WAT RFO
Vintage1978 | other | FALSE | 6090 | ExxonMobil Oil Corp | 50625 | ExxonMobil Beaumont Refinery | TX | Jefferson | ETG | Other Gases | OT |  | S | X | X |  |  | 7.5 | 0.93 | 5 | 5 | 2 | N |  |  | OP | X | 1 | 1978 |  |  | N | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T to WAT BLQ
Vintage1978 | natural gas steam turbine | FALSE | 6090 | ExxonMobil Oil Corp | 50625 | ExxonMobil Beaumont Refinery | TX | Jefferson | TG22 | Natural Gas Steam Turbine | ST | PP | S | X | X |  |  | 27.2 | 0.98 | 25 | 25 | 8 | N |  |  | OP | X | 2 | 1978 |  |  | Y | Industrial CHP | 7 | X T: T; WAT BLQ: NG; WAT BIT: OG; WAT RFO: NG; WAT NG: OG |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1993 | natural gas steam turbine | FALSE | 6090 | ExxonMobil Oil Corp | 50625 | ExxonMobil Beaumont Refinery | TX | Jefferson | TG23 | Natural Gas Steam Turbine | ST | PP | S | X | X |  |  | 40.5 | 0.94 | 38.6 | 38.6 | 15 | N |  |  | OP | X | 6 | 1993 |  |  | Y | Industrial CHP | 7 | X T: T; WAT BLQ: NG; WAT BIT: OG; WAT RFO: NG; WAT NG: OG |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1993 | natural gas peaker | FALSE | 6090 | ExxonMobil Oil Corp | 50625 | ExxonMobil Beaumont Refinery | TX | Jefferson | TG24 | Natural Gas Fired Combustion Turbine | GT | PP | S | X | X |  |  | 38.6 | 0.93 | 32 | 38 | 18 | N |  |  | OP | X | 6 | 1993 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T to WAT BLQ
Vintage1970 | natural gas steam turbine | FALSE | 6090 | ExxonMobil Oil Corp | 50625 | ExxonMobil Beaumont Refinery | TX | Jefferson | TG32 | Natural Gas Steam Turbine | ST | PP | S | X | X |  |  | 25 | 0.97 | 25 | 25 | 10 | N |  |  | OP | X | 1 | 1970 |  |  | Y | Industrial CHP | 7 | X T: T; WAT BLQ: NG; WAT BIT: OG; WAT RFO: NG; WAT NG: OG |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1966 | natural gas steam turbine | FALSE | 6090 | ExxonMobil Oil Corp | 50625 | ExxonMobil Beaumont Refinery | TX | Jefferson | TG33 | Natural Gas Steam Turbine | ST | PP | S | X | X |  |  | 20 | 0.97 | 20 | 20 | 5 | N |  |  | OP | X | 1 | 1966 |  |  | Y | Industrial CHP | 7 | X T: T; WAT BLQ: NG; WAT BIT: OG; WAT RFO: NG; WAT NG: OG |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1967 | natural gas steam turbine | FALSE | 6090 | ExxonMobil Oil Corp | 50625 | ExxonMobil Beaumont Refinery | TX | Jefferson | TG34 | Natural Gas Steam Turbine | ST | PP | S | X | X |  |  | 30 | 0.96 | 30 | 30 | 10 | N |  |  | OP | X | 1 | 1967 |  |  | Y | Industrial CHP | 7 | X T: T; WAT BLQ: NG; WAT BIT: OG; WAT RFO: NG; WAT NG: OG |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2005 | natural gas peaker | FALSE | 6090 | ExxonMobil Oil Corp | 50625 | ExxonMobil Beaumont Refinery | TX | Jefferson | TG41 | Natural Gas Fired Combustion Turbine | GT | PP | S | X | X |  |  | 163 | 0.96 | 145 | 165 | 90 | N |  |  | OP | X | 6 | 2005 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T to WAT BLQ
Vintage2005 | natural gas peaker | FALSE | 6090 | ExxonMobil Oil Corp | 50625 | ExxonMobil Beaumont Refinery | TX | Jefferson | TG42 | Natural Gas Fired Combustion Turbine | GT | PP | S | X | X |  |  | 163 | 0.97 | 145 | 165 | 90 | N |  |  | OP | X | 4 | 2005 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T to WAT BLQ
Vintage2004 | natural gas peaker | FALSE | 6090 | ExxonMobil Oil Corp | 50625 | ExxonMobil Beaumont Refinery | TX | Jefferson | TG43 | Natural Gas Fired Combustion Turbine | GT | PP | S | X | X |  |  | 163 | 0.97 | 145 | 165 | 90 | N |  |  | OP | X | 12 | 2004 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T to WAT BLQ
Vintage1990 | other | FALSE | 56392 | Chalmette Refining LLC | 50626 | Chalmette Refining LLC | LA | St Bernard | GEN1 | All Other | OT |  | S | X | X |  |  | 5.7 | 0.907 | 1.7 | 1.4 | 0.8 | N |  |  | OP | X | 3 | 1990 |  |  | N | Industrial Non-CHP | 6 | X T: X; WAT BLQ: OTH |  |  | N |  |  | OVER | [23 empty] | N
Vintage1987 | other | FALSE | 5519 | ExxonMobil Oil Corp | 50627 | ExxonMobil Oil Joliet Refinery | IL | Will | GTG1 | Other Gases | GT |  | S | X | X |  |  | 22 | 0.8 | 22 | 22 | 6 | N |  |  | OP | X | 11 | 1987 |  |  | Y | Industrial CHP | 7 | X T: T; WAT BLQ: OG; WAT BIT: NG |  |  | N | N |  | 12H | [23 empty] | Y | N | N
Vintage1986 | other | FALSE | 5519 | ExxonMobil Oil Corp | 50627 | ExxonMobil Oil Joliet Refinery | IL | Will | MG | Other Gases | ST |  | S | X | X |  |  | 11.2 | 0.8 | 11.2 | 11.2 | 0 | N |  |  | OP | X | 5 | 1986 |  |  | N | Industrial CHP | 7 | X T: X; WAT BLQ: OG; WAT BIT: NG; WAT RFO: OG |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1987 | other | FALSE | 5519 | ExxonMobil Oil Corp | 50627 | ExxonMobil Oil Joliet Refinery | IL | Will | STG1 | Other Gases | ST |  | S | X | X |  |  | 6.5 | 0.8 | 3.3 | 3.3 | 2 | N |  |  | OP | X | 11 | 1987 |  |  | N | Industrial CHP | 7 | X T: X; WAT BLQ: OG; WAT BIT: NG; WAT RFO: OG |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1991 | natural gas peaker | FALSE | 19691 | Paulsboro Refining Company - LLC | 50628 | Paulsboro Refinery | NJ | Gloucester | GEN1 | Natural Gas Fired Combustion Turbine | GT | UTI1 | S | X | X |  |  | 30.5 | 0.8 | 27 | 30.5 | 2 | N |  |  | OP | X | 9 | 1991 |  |  | Y | Industrial CHP | 7 | X T: T; WAT BLQ: NG; WAT BIT: OG; WAT WDS: DFO; WAT RFO: NG |  |  | N | N |  | 12H | [23 empty] | Y | N | N
Vintage1982 | other | FALSE | 19691 | Paulsboro Refining Company - LLC | 50628 | Paulsboro Refinery | NJ | Gloucester | GEN2 | Other Gases | ST | UTI1 | S | X | X |  |  | 15 | 0.85 | 14.5 | 14.5 | 2 | N |  |  | OP | X | 8 | 1982 |  |  | Y | Industrial CHP | 7 | X T: T; WAT BLQ: OG; WAT BIT: DFO; WAT WDS: NG; WAT RFO: OG |  |  | N | N |  | 12H | [23 empty] | Y | N | N
Vintage1991 | other | FALSE | 19691 | Paulsboro Refining Company - LLC | 50628 | Paulsboro Refinery | NJ | Gloucester | GEN3 | Other Gases | ST | UTI1 | S | X | X |  |  | 15 | 0.8 | 14.5 | 14.5 | 2 | N |  |  | OP | X | 9 | 1991 |  |  | Y | Industrial CHP | 7 | X T: T; WAT BLQ: OG; WAT BIT: DFO; WAT WDS: NG; WAT RFO: OG |  |  | N | N |  | 12H | [23 empty] | Y | N | N
Vintage2006 | petroleum | FALSE | 19691 | Paulsboro Refining Company - LLC | 50628 | Paulsboro Refinery | NJ | Gloucester | GEN4 | Petroleum Coke | OT |  | S | X | X |  |  | 18 | 0.8 | 11.6 | 11.6 | 2 | N |  |  | OS | X | 11 | 2006 |  |  | N | Industrial CHP | 7 | [11 empty] | N | N | 0 | OVER | Y |  |  |  | Y | [18 empty] | N | bar: X T to WAT BLQ
Vintage1990 | municipal solid waste | TRUE | 4482 | Covanta Lake Inc | 50629 | Covanta Lake County Energy | FL | Lake | GEN1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 15.5 | 0.85 | 12.5 | 12.5 | 2.5 | N |  |  | OP | X | 9 | 1990 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: MSW; WAT RFO: NG |  |  | N | N |  | 12H | [20 empty] | N |  |  | N | N | N
Vintage1986 | municipal solid waste | TRUE | 4476 | Covanta Marion Inc | 50630 | Covanta Marion Inc | OR | MARION | GEN1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 13.1 | 0.95 | 11.5 | 11.5 | 2 | N |  |  | OP | X | 8 | 1986 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: MSW; WAT BIT: NG; WAT RFO: NG |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1988 | municipal solid waste | TRUE | 4498 | Covanta Stanislaus Inc | 50632 | Covanta Stanislaus Energy | CA | Stanislaus | GEN1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 24 | 0.85 | 19.9 | 19.9 | 3 | N |  |  | OP | X | 9 | 1988 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: MSW; WAT RFO: DFO |  |  | N | N |  | 12H |  |  | N |  | N | [18 empty] | N | N | N
Vintage1985 | other | FALSE | 3102 | Mosaic Company | 50633 | Mosaic Co Bartow Facility | FL | Polk | GEN1 | All Other | ST |  | S | X | X |  |  | 36.9 | 0.8 | 36 | 36 | 2 | N |  |  | OP | X | 12 | 1985 |  |  | Y | Industrial CHP | 7 | X T: B; WAT BLQ: WH; WAT BIT: OTH; WAT RFO: WH |  |  | N |  |  | OVER | [23 empty] | N | N
Vintage1992 | other | FALSE | 3102 | Mosaic Company | 50633 | Mosaic Co Bartow Facility | FL | Polk | GEN2 | All Other | ST |  | S | X | X |  |  | 45 | 0.85 | 44 | 44 | 2 | N |  |  | OP | X | 8 | 1992 |  |  | Y | Industrial CHP | 7 | X T: B; WAT BLQ: WH; WAT BIT: OTH; WAT RFO: WH |  |  | N |  |  | OVER | [23 empty] | N | N
Vintage1917 | hydro | TRUE | 2138 | Brainerd Public Utilities | 50636 | Brainerd Public Utilities | MN | Crow Wing | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 1 | 1917 |  |  | N | Electric Utility | 1 | X T: X; WAT BLQ: WAT |  |  | N | N |  | 12H | [23 empty] | N
Vintage1917 | hydro | TRUE | 2138 | Brainerd Public Utilities | 50636 | Brainerd Public Utilities | MN | Crow Wing | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 1 | 1917 |  |  | N | Electric Utility | 1 | X T: X; WAT BLQ: WAT |  |  | N | N |  | 12H | [23 empty] | N
Vintage1936 | hydro | TRUE | 2138 | Brainerd Public Utilities | 50636 | Brainerd Public Utilities | MN | Crow Wing | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 7 | 1936 |  |  | N | Electric Utility | 1 | X T: X; WAT BLQ: WAT |  |  | N | N | 0 | 12H | [23 empty] | N
Vintage1936 | hydro | TRUE | 2138 | Brainerd Public Utilities | 50636 | Brainerd Public Utilities | MN | Crow Wing | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 1 | 1936 |  |  | N | Electric Utility | 1 | X T: X; WAT BLQ: WAT |  |  | N |  |  | 12H | [23 empty] | N
Vintage1940 | hydro | TRUE | 2138 | Brainerd Public Utilities | 50636 | Brainerd Public Utilities | MN | Crow Wing | 5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 1 | 1940 |  |  | N | Electric Utility | 1 | X T: X; WAT BLQ: WAT |  |  | N |  |  | 12H | [23 empty] | N
Vintage1950 | biomass | TRUE | 56225 | Clearwater Paper Corporation | 50637 | Clearwater Paper IPP Lewiston | ID | Nez Perce | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 10 | 0.8 | 2 | 9.4 | 2 | N |  |  | OS | X | 1 | 1950 |  |  | Y | Industrial CHP | 7 | X T: T; WAT BLQ: BLQ; WAT BIT: NG; WAT RFO: NG |  |  | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage1977 | biomass | TRUE | 56225 | Clearwater Paper Corporation | 50637 | Clearwater Paper IPP Lewiston | ID | Nez Perce | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 10 | 0.8 | 3.3 | 9.4 | 2 | N |  |  | OS | X | 11 | 1977 |  |  | Y | Industrial CHP | 7 | X T: T; WAT BLQ: BLQ; WAT BIT: NG; WAT RFO: NG |  |  | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage1981 | biomass | TRUE | 56225 | Clearwater Paper Corporation | 50637 | Clearwater Paper IPP Lewiston | ID | Nez Perce | GEN3 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 28.8 | 0.85 | 25.2 | 25.3 | 4 | N |  |  | OP | X | 7 | 1981 |  |  | Y | Industrial CHP | 7 | X T: T; WAT BLQ: BLQ; WAT BIT: WDS; WAT WDS: NG; WAT RFO: NG |  |  | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage1991 | biomass | TRUE | 56225 | Clearwater Paper Corporation | 50637 | Clearwater Paper IPP Lewiston | ID | Nez Perce | GEN4 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 65 | 0.95 | 24 | 24 | 4 | N |  |  | OP | X | 2 | 1991 |  |  | Y | Industrial CHP | 7 | X T: T; WAT BLQ: BLQ; WAT BIT: WDS; WAT WDS: NG; WAT RFO: NG |  |  | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage1977 | biomass | TRUE | 56225 | Clearwater Paper Corporation | 50638 | Clearwater Paper APP CB | AR | Desha | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 28 | 0.95 | 28 | 28 | 2 | N |  |  | OP | X | 11 | 1977 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | DFO |  |  |  | BLQ | NG |  |  | N | N |  | 12H | [5 empty] | N | [17 empty] | Y | Y | Y
Vintage1976 | biomass | TRUE | 16653 | Sappi Cloquet LLC | 50639 | Sappi Cloquet Mill | MN | Carlton | GEN3 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 19.2 | 0.9 | 17.5 | 17.5 | 8 | N |  |  | OP | X | 1 | 1976 |  |  | Y | Industrial CHP | 7 | T | WDS | NG | SLW | DFO | BLQ |  | WDS |  |  |  | N | N |  | OVER | [23 empty] | Y | Y | Y
Vintage1997 | biomass | TRUE | 16653 | Sappi Cloquet LLC | 50639 | Sappi Cloquet Mill | MN | Carlton | GEN4 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 41.5 | 0.85 | 41.5 | 41.5 | 6 | N |  |  | OP | X | 12 | 1997 |  |  | Y | Industrial CHP | 7 | T | WDS | NG | SLW | DFO | BLQ |  | WDS |  |  |  | N | N |  | OVER | [23 empty] | Y | Y | Y
Vintage2001 | biomass | TRUE | 16653 | Sappi Cloquet LLC | 50639 | Sappi Cloquet Mill | MN | Carlton | GEN5 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 27.6 | 0.85 | 14 | 15 | 4 | N |  |  | OP | X | 5 | 2001 |  |  | Y | Industrial CHP | 7 | X T: T; WAT BLQ: BLQ; WAT BIT: NG; WAT RFO: BLQ |  |  | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage1950 | hydro | FALSE | 16653 | Sappi Cloquet LLC | 50639 | Sappi Cloquet Mill | MN | Carlton | HGN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 0.85 | 1.6 | 1.6 | 0.5 | N |  |  | OP | X | 1 | 1950 |  |  | N | Industrial CHP | 7 | X T: X; WAT BLQ: WAT |  |  | N | N | 0 | 1H
Vintage1929 | hydro | FALSE | 16653 | Sappi Cloquet LLC | 50639 | Sappi Cloquet Mill | MN | Carlton | HGN5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 1 | 1929 |  |  | N | Industrial CHP | 7 | X T: X; WAT BLQ: WAT |  |  | N | N | 0 | 1H
Vintage1929 | hydro | FALSE | 16653 | Sappi Cloquet LLC | 50639 | Sappi Cloquet Mill | MN | Carlton | HGN6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 1 | 1929 |  |  | N | Industrial CHP | 7 | X T: X; WAT BLQ: WAT |  |  | N |  | 0 | 1H
Vintage1980 | hydro | FALSE | 16653 | Sappi Cloquet LLC | 50639 | Sappi Cloquet Mill | MN | Carlton | HGN7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.8 | 0.8 | 1 | 1.4 | 0.5 | N |  |  | OP | X | 1 | 1980 |  |  | N | Industrial CHP | 7 | X T: X; WAT BLQ: WAT |  |  | N |  | 0 | 1H
Vintage1988 | municipal solid waste | FALSE | 4497 | Covanta Indianapolis Inc | 50647 | Covanta Indianapolis Energy | IN | Marion | GEN1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 6.5 | 0.8 | 5 | 5 | 1 | N |  |  | OP | X | 11 | 1988 |  |  | Y | Commercial CHP | 5 | X T: T; WAT BLQ: MSW; WAT BIT: NG; WAT RFO: MSW |  |  | N | N |  | 12H | [23 empty] | N
Vintage1987 | municipal solid waste | TRUE | 4474 | Covanta Bristol Inc | 50648 | Covanta Bristol Energy | CT | Hartford | GEN1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 16.3 | 0.9 | 13.2 | 13.2 | 0.5 | N |  |  | OP | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: MSW; WAT BIT: NG; WAT RFO: NG | [5 empty] | OVER | [23 empty] | N
Vintage1989 | municipal solid waste | FALSE | 4484 | Covanta Babylon Inc | 50649 | Covanta Babylon Inc | NY | Suffolk | GEN1 | Municipal Solid Waste | ST |  | S | X | X | 23656 | NYISO | 17 | 1 | 14.4 | 14.4 | 1 | N |  |  | OP | X | 1 | 1989 |  |  | N | Commercial Non-CHP | 4 | X T: X; WAT BLQ: MSW; WAT RFO: DFO |  |  | N | N |  | 12H | [23 empty] | N
Vintage1989 | biomass | TRUE | 1950 | ReEnergy Stratton LLC | 50650 | ReEnergy Stratton LLC | ME | Franklin | UNI1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 47 | 0.85 | 46.1 | 46.1 | 18 | N |  |  | OP | X | 11 | 1989 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WDS; WAT BIT: DFO; WAT RFO: DFO |  |  | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage1984 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50652 | Lyonsdale Associates | NY | Lewis | GEN1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.5 | 0.9 | 1.5 | 1.5 | 0.1 | N |  |  | OP | X | 7 | 1984 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WAT |  |  | N |  | 0 | 1H
Vintage1984 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50652 | Lyonsdale Associates | NY | Lewis | GEN2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.5 | 0.9 | 1.5 | 1.5 | 0.1 | N |  |  | OP | X | 7 | 1984 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WAT |  |  | N |  | 0 | 1H
Vintage2020 | geothermal | TRUE | 34691 | Ormat Nevada Inc | 50654 | Steamboat Hills LP | NV | Washoe | OEC51 | Geothermal | BT |  | S | X | X |  |  | 25.7 | 0.85 | 17.1 | 25.7 | 17.1 | N |  |  | OP | X | 6 | 2020 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: GEO |  |  | N |  |  | OVER | [23 empty] | N
Vintage2020 | geothermal | TRUE | 34691 | Ormat Nevada Inc | 50654 | Steamboat Hills LP | NV | Washoe | OEC52 | Geothermal | BT |  | S | X | X |  |  | 5.9 | 0.85 | 4 | 5.9 | 4 | N |  |  | OP | X | 6 | 2020 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: GEO |  |  | N |  |  | OVER | [23 empty] | N
Vintage1991 | municipal solid waste | TRUE | 9097 | Huntington Resource Recovery | 50656 | Huntington Resource Recovery Facility | NY | Suffolk | GEN1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 28 | 1 | 24.5 | 24.5 | 8 | N |  |  | OP | X | 12 | 1991 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: MSW; WAT RFO: PG |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1995 | municipal solid waste | TRUE | 49760 | Covanta Montgomery, Inc. | 50657 | Montgomery County Resource Recovery | MD | Montgomery | GEN1 | Municipal Solid Waste | ST |  | W | X | X | 50825 | 50825 | 67.8 | 0.97 | 54 | 56 | 1 | N |  |  | OP | X | 5 | 1995 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: MSW; WAT RFO: NG |  |  | N | N |  | 12H | [20 empty] | N |  |  | N | N | N
Vintage1990 | municipal solid waste | TRUE | 4425 | Covanta Fairfax Inc | 50658 | Covanta Fairfax Energy | VA | Fairfax | GEN1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 62 | 0.9 | 49 | 49 | 10 | N |  |  | OP | X | 3 | 1990 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: MSW; WAT BIT: NG; WAT RFO: NG |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1990 | municipal solid waste | TRUE | 4425 | Covanta Fairfax Inc | 50658 | Covanta Fairfax Energy | VA | Fairfax | GEN2 | Municipal Solid Waste | ST |  | S | X | X |  |  | 62 | 0.9 | 49 | 49 | 10 | N |  |  | OP | X | 3 | 1990 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: MSW; WAT BIT: NG; WAT RFO: NG |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1989 | municipal solid waste | FALSE | 56316 | Covanta Tulsa Renewable Energy LLC | 50660 | Covanta Tulsa Renewable Energy LLC | OK | Tulsa | GEN1 | Municipal Solid Waste | ST |  | W | X | X |  |  | 16.8 | 0.8 | 15.6 | 15.8 | 0.8 | N |  |  | OP | X | 1 | 1989 |  |  | Y | Industrial CHP | 7 | X T: B; WAT BLQ: MSW; WAT BIT: NG; WAT RFO: NG |  |  | N | N |  | 12H |  |  | N | [20 empty] | Y | Y | N
Vintage1989 | municipal solid waste | TRUE | 13982 | Ogden Projects Inc-Haverhill | 50661 | Covanta Haverhill | MA | Essex | GEN1 | Municipal Solid Waste | ST |  | S | X | X | 14174_:_LD.WARD_HIL13.2 | 14174_:_LD.WARD_HIL13.2 | 46 | 0.9 | 42.8 | 43.2 | 4.1 | N |  |  | OP | X | 5 | 1989 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: MSW; WAT RFO: DFO |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1994 | municipal solid waste | FALSE | 4487 | Covanta Onondega LP | 50662 | Onondaga County Resource Recovery | NY | Onondaga | GEN1 | Municipal Solid Waste | ST |  | S | X | X | NYISO - PTID 23987 | NYISO - PTID 23987 | 39.5 | 0.9 | 30 | 30 | 3.5 | N |  |  | OP | X | 11 | 1994 |  |  | N | Commercial Non-CHP | 4 | X T: X; WAT BLQ: MSW; WAT RFO: NG |  |  | N | N | 0 | OVER | [23 empty] | N | N | N
Vintage1987 | municipal solid waste | FALSE | 4496 | Covanta Alexandria/Arlington | 50663 | Covanta Alexandria/Arlington Energy | VA | Alexandria City | GEN1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 14.5 | 0.9 | 14.5 | 14.5 | 1.5 | N |  |  | OP | X | 10 | 1987 |  |  | N | Commercial Non-CHP | 4 | X T: X; WAT BLQ: MSW; WAT RFO: MSW |  |  | N | N |  | 12H | [23 empty] | N
Vintage1987 | municipal solid waste | FALSE | 4496 | Covanta Alexandria/Arlington | 50663 | Covanta Alexandria/Arlington Energy | VA | Alexandria City | GEN2 | Municipal Solid Waste | ST |  | S | X | X |  |  | 14.5 | 0.9 | 14.5 | 14.5 | 1.5 | N |  |  | OP | X | 10 | 1987 |  |  | N | Commercial Non-CHP | 4 | X T: X; WAT BLQ: MSW; WAT RFO: MSW |  |  | N | N |  | 12H | [23 empty] | N
Vintage1991 | municipal solid waste | TRUE | 14519 | Pasco County | 50666 | Pasco Cnty Solid Waste Resource Recovery | FL | Pasco | GEN1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 31.2 | 0.95 | 26 | 26 | 5 | N |  |  | OP | X | 5 | 1991 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: MSW; WAT RFO: NG |  |  | N |  |  | 12H | [23 empty] | N | N
Vintage2015 | natural gas peaker | FALSE | 14395 | Palm Springs City of | 50674 | Municipal Cogen Plant | CA | Riverside | GEN1A | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.2 | 1 | 1.2 | 1.2 | 0.5 | N |  |  | OP | X | 11 | 2015 |  |  | N | Commercial Non-CHP | 4 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: X T to WAT BLQ
Vintage1985 | hydro | TRUE | 56838 | KEI (Maine) Power Management (III) LLC | 50688 | Gardiner | ME | Kennebec | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.99 | 1 | 1 | 0.3 | N |  |  | OP | X | 7 | 1985 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1999 | onshore wind | TRUE | 2770 | Terra-Gen Operating Co-Wind | 50690 | San Gorgonio Westwinds II LLC | CA | Riverside | GEN1 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 43.4 |  | 43.4 | 43.4 | 0 | N |  |  | OP | X | 6 | 1999 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WND |  |  | N | N | 62
Vintage1993 | biomass | TRUE | 14155 | Orange County Sanitation Dist | 50696 | Plant No 1 Orange County | CA | Orange | GEN1 | Other Waste Biomass | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.4 | 2.4 | 1.8 | N |  |  | OP | X | 6 | 1993 |  |  | Y | Commercial CHP | 5 | X T: T; WAT BLQ: OBG; WAT BIT: NG; WAT RFO: NG; WAT NG: OBG |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1993 | biomass | TRUE | 14155 | Orange County Sanitation Dist | 50696 | Plant No 1 Orange County | CA | Orange | GEN2 | Other Waste Biomass | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.4 | 2.4 | 1.8 | N |  |  | OP | X | 6 | 1993 |  |  | Y | Commercial CHP | 5 | X T: T; WAT BLQ: OBG; WAT BIT: NG; WAT RFO: NG; WAT NG: OBG |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1993 | biomass | TRUE | 14155 | Orange County Sanitation Dist | 50696 | Plant No 1 Orange County | CA | Orange | GEN3 | Other Waste Biomass | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.4 | 2.4 | 1.8 | N |  |  | OP | X | 6 | 1993 |  |  | Y | Commercial CHP | 5 | X T: T; WAT BLQ: OBG; WAT BIT: NG; WAT RFO: NG; WAT NG: OBG |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1987 | hydro | TRUE | 56837 | KEI (Maine) Power Management (II) LLC | 50699 | Pumpkin Hill | ME | Penobscot | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.99 | 1 | 1 | 0.1 | N |  |  | OP | X | 3 | 1987 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WAT |  |  | N | N |  | 1H | [20 empty] | N |  |  | N |  | N
Vintage1986 | hydro | TRUE | 15795 | William G. Reed Jr | 50700 | Lilliwaup Falls Generating | WA | Mason | 4735 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0.2 | N |  |  | OP | X | 5 | 1986 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WAT |  |  | N |  | 0 | 10M
Vintage1986 | hydro | TRUE | 15795 | William G. Reed Jr | 50700 | Lilliwaup Falls Generating | WA | Mason | 4736 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0.2 | N |  |  | OP | X | 5 | 1986 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WAT |  |  | N |  | 0 | 10M
Vintage1986 | hydro | TRUE | 15795 | William G. Reed Jr | 50700 | Lilliwaup Falls Generating | WA | Mason | 4737 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0.2 | N |  |  | OP | X | 5 | 1986 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WAT |  |  | N |  | 0 | 10M
Vintage1986 | hydro | TRUE | 15795 | William G. Reed Jr | 50700 | Lilliwaup Falls Generating | WA | Mason | 4738 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0.2 | N |  |  | OP | X | 5 | 1986 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WAT |  |  | N |  | 0 | 10M
Vintage1986 | hydro | TRUE | 15795 | William G. Reed Jr | 50700 | Lilliwaup Falls Generating | WA | Mason | 4739 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0.2 | N |  |  | OP | X | 5 | 1986 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WAT |  |  | N |  | 0 | 10M
Vintage1986 | hydro | TRUE | 15795 | William G. Reed Jr | 50700 | Lilliwaup Falls Generating | WA | Mason | 4740 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0.2 | N |  |  | OP | X | 5 | 1986 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WAT |  |  | N |  | 0 | 10M
Vintage1986 | hydro | TRUE | 15795 | William G. Reed Jr | 50700 | Lilliwaup Falls Generating | WA | Mason | 4741 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 0.8 | 0.2 | 0.2 | 0.2 | N |  |  | OP | X | 5 | 1986 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WAT |  |  | N |  |  | 10M
Vintage1986 | hydro | TRUE | 7601 | Green Mountain Power Corp | 50702 | Salmon Falls | ME | York | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 1 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 7 | 1986 |  |  | N | Electric Utility | 1 | X T: X; WAT BLQ: WAT |  |  |  |  | 0 | 10M
Vintage1986 | hydro | TRUE | 7601 | Green Mountain Power Corp | 50702 | Salmon Falls | ME | York | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 1 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 7 | 1986 |  |  | N | Electric Utility | 1 | X T: X; WAT BLQ: WAT |  |  |  |  | 0 | 10M
Vintage1986 | hydro | TRUE | 7601 | Green Mountain Power Corp | 50702 | Salmon Falls | ME | York | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 1 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 7 | 1986 |  |  | N | Electric Utility | 1 | X T: X; WAT BLQ: WAT |  |  |  |  | 0 | 10M
Vintage1985 | hydro | TRUE | 7601 | Green Mountain Power Corp | 50704 | Somersworth Lower Great Dam | NH | Strafford | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 1 | 1.2 | 1.2 | 0.1 | N |  |  | OP | X | 7 | 1985 |  |  | N | Electric Utility | 1 | X T: X; WAT BLQ: WAT |  |  | N |  | 0 | 10M
Vintage1994 | natural gas combined cycle | TRUE | 30151 | Tri-State G & T Assn, Inc | 50707 | JM Shafer Generating Station | CO | Weld | LMA | Natural Gas Fired Combined Cycle | CT | J272 | S | X | N |  |  | 58.5 | 0.85 | 272 | 272 | 12 | N |  |  | OP | X | 6 | 1994 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T to WAT BLQ
Vintage1994 | natural gas combined cycle | TRUE | 30151 | Tri-State G & T Assn, Inc | 50707 | JM Shafer Generating Station | CO | Weld | LMB | Natural Gas Fired Combined Cycle | CT | J272 | S | X | N |  |  | 58.5 | 0.85 |  |  | 12 | N |  |  | OP | X | 6 | 1994 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T to WAT BLQ
Vintage1994 | natural gas combined cycle | TRUE | 30151 | Tri-State G & T Assn, Inc | 50707 | JM Shafer Generating Station | CO | Weld | LMC | Natural Gas Fired Combined Cycle | CT | J272 | S | X | N |  |  | 58.5 | 0.85 |  |  | 12 | N |  |  | OP | X | 7 | 1994 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T to WAT BLQ
Vintage1994 | natural gas combined cycle | TRUE | 30151 | Tri-State G & T Assn, Inc | 50707 | JM Shafer Generating Station | CO | Weld | LMD | Natural Gas Fired Combined Cycle | CT | J272 | S | X | N |  |  | 58.5 | 0.85 |  |  | 12 | N |  |  | OP | X | 7 | 1994 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T to WAT BLQ
Vintage1994 | natural gas combined cycle | TRUE | 30151 | Tri-State G & T Assn, Inc | 50707 | JM Shafer Generating Station | CO | Weld | LME | Natural Gas Fired Combined Cycle | CT | J272 | S | X | N |  |  | 58.5 | 0.85 |  |  | 12 | N |  |  | OP | X | 7 | 1994 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T to WAT BLQ
Vintage1994 | natural gas combined cycle | TRUE | 30151 | Tri-State G & T Assn, Inc | 50707 | JM Shafer Generating Station | CO | Weld | STA | Natural Gas Fired Combined Cycle | CA | J272 | S | Y | X |  |  | 52.2 | 1 |  |  | 5.2 | N |  |  | OP | X | 6 | 1994 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T to WAT BLQ
Vintage1994 | natural gas combined cycle | TRUE | 30151 | Tri-State G & T Assn, Inc | 50707 | JM Shafer Generating Station | CO | Weld | STB | Natural Gas Fired Combined Cycle | CA | J272 | S | Y | X |  |  | 52.2 | 1 |  |  | 5.2 | N |  |  | OP | X | 6 | 1994 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T to WAT BLQ
Vintage1964 | hard coal | FALSE | 19511 | University of Alaska | 50711 | University of Alaska Fairbanks | AK | Fairbanks North Star | GEN1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 1.5 | 0.8 | 0.5 | 1.4 | 0.2 | N |  |  | OS | X | 1 | 1964 |  |  | Y | Commercial CHP | 5 | T | SUB | DFO | JF |  |  |  | NG | DFO |  |  | N | N |  | 12H |  |  | N | Y | Y | [18 empty] | Y | N | N
Vintage1964 | hard coal | FALSE | 19511 | University of Alaska | 50711 | University of Alaska Fairbanks | AK | Fairbanks North Star | GEN2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 1.5 | 0.8 | 0.5 | 1.4 | 0.2 | N |  |  | OS | X | 1 | 1964 |  |  | Y | Commercial CHP | 5 | T | SUB | DFO | JF |  |  |  | NG | DFO |  |  | N | N |  | 12H |  |  | N | Y | Y | [18 empty] | Y | N | N
Vintage1981 | hard coal | FALSE | 19511 | University of Alaska | 50711 | University of Alaska Fairbanks | AK | Fairbanks North Star | GEN3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 10 | 0.85 | 8.1 | 10 | 2.5 | N |  |  | OA | X | 4 | 1981 |  |  | Y | Commercial CHP | 5 | T | SUB | DFO | NG | JF |  |  | NG | DFO |  |  | N | N |  | 12H | Y |  | N | Y | Y | [18 empty] | Y | N | N
Vintage2000 | petroleum | FALSE | 19511 | University of Alaska | 50711 | University of Alaska Fairbanks | AK | Fairbanks North Star | GEN4 | Petroleum Liquids | IC |  | S | X | X |  |  | 9.6 | 0.8 | 9.6 | 9.6 | 2 | N |  |  | SB | Y | 8 | 2000 |  |  | Y | Commercial CHP | 5 | X T: T; WAT BLQ: DFO |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2020 | hard coal | FALSE | 19511 | University of Alaska | 50711 | University of Alaska Fairbanks | AK | Fairbanks North Star | GEN5 | Conventional Steam Coal | ST |  | S | X | X |  |  | 17 | 0.94 | 17 | 17 | 4 | N |  |  | OP | X | 2 | 2020 |  |  | Y | Commercial CHP | 5 | T | SUB | DFO | NG | JF |  |  | NG | DFO |  |  | N | N |  | 12H | Y | N | N | Y | Y | [18 empty] | Y | Y | N
Vintage1988 | hydro | TRUE | 7601 | Green Mountain Power Corp | 50713 | Huntington Falls | VT | Addison | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.7 | 0.2 | N |  |  | OP | X | 10 | 1988 |  |  | N | Electric Utility | 1 | X T: X; WAT BLQ: WAT |  |  | N |  | 0 | 10M
Vintage1988 | hydro | TRUE | 7601 | Green Mountain Power Corp | 50713 | Huntington Falls | VT | Addison | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.7 | 0.2 | N |  |  | OP | X | 10 | 1988 |  |  | N | Electric Utility | 1 | X T: X; WAT BLQ: WAT |  |  | N |  | 0 | 10M
Vintage1988 | hydro | TRUE | 7601 | Green Mountain Power Corp | 50713 | Huntington Falls | VT | Addison | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.1 | 0.8 | 3.9 | 3.8 | 0.2 | N |  |  | OP | X | 10 | 1988 |  |  | N | Electric Utility | 1 | X T: X; WAT BLQ: WAT |  |  | N |  | 0 | 10M
Vintage1986 | hydro | TRUE | 64961 | Koosh, Inc. | 50718 | Notch Butte Hydro | ID | Lincoln | HYD1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 1 | 1 | 0.9 | 0.1 | N |  |  | OP | X | 9 | 1986 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WAT | [5 empty] | 10M | [20 empty] | N |  |  | N
Vintage1989 | biomass | TRUE | 54843 | WM Illinois Renewable Energy LLC | 50721 | Tazewell Gas Recovery | IL | Tazewell | GEN1 | Landfill Gas | IC |  | S | X | X | Zonal | Zonal | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 7 | 1989 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: LFG |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1989 | biomass | TRUE | 54843 | WM Illinois Renewable Energy LLC | 50721 | Tazewell Gas Recovery | IL | Tazewell | GEN2 | Landfill Gas | IC |  | S | X | X | Zonal | Zonal | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 7 | 1989 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: LFG |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1999 | biomass | TRUE | 54843 | WM Illinois Renewable Energy LLC | 50721 | Tazewell Gas Recovery | IL | Tazewell | GEN3 | Landfill Gas | IC |  | S | X | X | Zonal | Zonal | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 5 | 1999 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: LFG |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1990 | natural gas peaker | FALSE | 64451 | INEOS US Chemicals Company - Naperville Campus | 50722 | INEOS Naperville Cogeneration Plant | IL | DuPage | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 8.3 | 0.8 | 7 | 11 | 4.3 | N |  |  | OP | X | 12 | 1990 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 12H |  |  |  | N | [16 empty] | N |  |  | N | N | N | bar: X T to WAT BLQ
Vintage1955 | other | FALSE | 19517 | United States Steel- Clairton | 50729 | Clairton Works | PA | Allegheny | GEN1 | Other Gases | ST |  | S | X | X |  |  | 21 | 0.85 | 16 | 18 | 2 | N |  |  | OP | X | 1 | 1955 |  |  | Y | Industrial CHP | 7 | X T: T; WAT BLQ: OG; WAT BIT: NG; WAT RFO: OG |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1955 | other | FALSE | 19517 | United States Steel- Clairton | 50729 | Clairton Works | PA | Allegheny | GEN3 | Other Gases | ST |  | S | X | X |  |  | 10 | 0.8 | 8 | 8 | 1 | N |  |  | OP | X | 1 | 1955 |  |  | N | Industrial CHP | 7 | X T: X; WAT BLQ: OG; WAT BIT: NG; WAT RFO: OG |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1943 | other | FALSE | 19519 | United States Steel-Mon Valley | 50732 | Mon Valley Works | PA | Allegheny | GEN1 | Other Gases | ST |  | S | X | X |  |  | 25 | 0.8 | 30 | 33 | 6 | N |  |  | OP | X | 6 | 1943 |  |  | N | Industrial CHP | 7 | X T: X; WAT BLQ: BFG; WAT BIT: OG; WAT WDS: NG; WAT RFO: NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1943 | other | FALSE | 19519 | United States Steel-Mon Valley | 50732 | Mon Valley Works | PA | Allegheny | GEN2 | Other Gases | ST |  | S | X | X |  |  | 25 | 0.8 | 30 | 33 | 6 | N |  |  | OP | X | 6 | 1943 |  |  | N | Industrial CHP | 7 | X T: X; WAT BLQ: BFG; WAT BIT: OG; WAT WDS: NG; WAT RFO: NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage2002 | other | FALSE | 19519 | United States Steel-Mon Valley | 50732 | Mon Valley Works | PA | Allegheny | GEN3 | Other Gases | ST |  | S | X | X |  |  | 2.5 | 0.85 | 1.9 | 1.9 | 0.3 | N |  |  | OP | X | 2 | 2002 |  |  | Y | Industrial CHP | 7 | X T: T; WAT BLQ: BFG; WAT BIT: OG; WAT WDS: NG; WAT RFO: NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1997 | other | FALSE | 19526 | United States Steel-Gary | 50733 | Gary Works | IN | Lake | STG1 | Other Gases | ST |  | S | X | X |  |  | 161 | 0.9 | 161 | 150 | 50 | N |  |  | OP | X | 4 | 1997 |  |  | Y | Industrial CHP | 7 | B | BFG | NG | RFO | OG |  |  | BFG |  |  |  | N |  |  | 12H | [23 empty] | N | N | N
Vintage1987 | biomass | TRUE | 64003 | Stored Solar Services, LLC | 50739 | Stored Solar Tamworth, LLC | NH | Carroll | GEN1 | Wood/Wood Waste Biomass | ST |  | W | X | X | UN.TAMWORTH115.TAMW |  | 25 | 0.8 | 20 | 20 | 14 | N |  |  | OP | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WDS; WAT RFO: WDS |  |  | N | N |  | 12H | [23 empty] | N
Vintage1986 | hydro | TRUE | 15213 | Pontook Operating LP | 50741 | Pontook Hydro Facility | NH | Coos | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.5 | 0.9 | 3.5 | 3.5 | 1 | N |  |  | OP | X | 12 | 1986 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WAT |  |  | N |  |  | 1H | [23 empty] | N
Vintage1986 | hydro | TRUE | 15213 | Pontook Operating LP | 50741 | Pontook Hydro Facility | NH | Coos | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.5 | 0.9 | 3.5 | 3.5 | 1 | N |  |  | OP | X | 12 | 1986 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WAT |  |  | N |  |  | 1H | [23 empty] | N
Vintage1986 | hydro | TRUE | 15213 | Pontook Operating LP | 50741 | Pontook Hydro Facility | NH | Coos | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.5 | 0.9 | 3.5 | 3.5 | 1 | N |  |  | OP | X | 12 | 1986 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WAT |  |  | N |  |  | 1H | [23 empty] | N
Vintage1991 | natural gas combined cycle | TRUE | 14182 | Sterling Power Partners LP | 50744 | Sterling Power Plant | NY | Oneida | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | 23777 | 23777 | 47.7 | 0.9 | 38.8 | 47.6 | 35 | N |  |  | OP | X | 6 | 1991 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T to WAT BLQ; WAT RFO
Vintage1991 | natural gas combined cycle | TRUE | 14182 | Sterling Power Partners LP | 50744 | Sterling Power Plant | NY | Oneida | GEN2 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X | 23777 | 23777 | 16.5 | 0.9 | 16 | 16.5 | 12 | N |  |  | OP | X | 7 | 1991 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T to WAT BLQ
Vintage1991 | petroleum | TRUE | 14182 | Sterling Power Partners LP | 50744 | Sterling Power Plant | NY | Oneida | GEN3 | Petroleum Liquids | IC |  | S | X | X | 23777 | 23777 | 1.1 | 0.9 | 1.1 | 1.1 | 0.2 | N |  |  | OP | X | 6 | 1991 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: DFO; WAT RFO: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1990 | natural gas combined cycle | TRUE | 2871 | OLS Energy-Agnews Inc. | 50748 | Agnews Power Plant | CA | Santa Clara | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 24.4 | 0.9 | 24.4 | 24.4 | 16.5 | N |  |  | OP | X | 11 | 1990 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T to WAT BLQ
Vintage1990 | natural gas combined cycle | TRUE | 2871 | OLS Energy-Agnews Inc. | 50748 | Agnews Power Plant | CA | Santa Clara | GEN2 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X |  |  | 7.6 | 0.8 | 7.3 | 7.4 | 4 | N |  |  | OP | X | 11 | 1990 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T to WAT BLQ
Vintage1988 | natural gas peaker | FALSE | 23005 | Aera Energy LLC-Coalinga | 50750 | Coalinga Cogeneration Facility | CA | Fresno | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 3.4 | 0.8 | 3.2 | 3.3 | 1.8 | N |  |  | OP | X | 6 | 1988 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 10M |  | N | [18 empty] | N |  |  | N | N | N | bar: X T to WAT BLQ
Vintage1988 | natural gas peaker | FALSE | 23005 | Aera Energy LLC-Coalinga | 50750 | Coalinga Cogeneration Facility | CA | Fresno | GEN2 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 3.4 | 0.8 | 3.2 | 3.3 | 1.8 | N |  |  | OP | X | 6 | 1988 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 10M | N | N | N | N |  | N | N | [13 empty] | N |  |  | N | N | N | bar: X T to WAT BLQ
Vintage1989 | natural gas peaker | FALSE | 54713 | Chevron USA Inc | 50751 | Southeast Kern River Cogen | CA | Kern | GTG1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | POD_VEDDER_1_SEKRN-APND | TH_ZP26_GEN-APND | 24 | 0.9 | 20.8 | 21.7 | 12 | N |  |  | OP | X | 2 | 1989 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T to WAT BLQ; WAT RFO
Vintage1989 | natural gas peaker | FALSE | 54713 | Chevron USA Inc | 50751 | Southeast Kern River Cogen | CA | Kern | GTG2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.4 | 0.9 | 3 | 3.2 | 1.5 | N |  |  | OS | X | 2 | 1989 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T to WAT BLQ; WAT RFO
Vintage1989 | natural gas peaker | FALSE | 54713 | Chevron USA Inc | 50751 | Southeast Kern River Cogen | CA | Kern | GTG3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.4 | 0.9 | 3 | 3.2 | 1.5 | N |  |  | OS | X | 2 | 1989 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T to WAT BLQ; WAT RFO
Vintage1985 | natural gas peaker | FALSE | 164 | AERA Energy LLC | 50752 | South Belridge Cogeneration Facility | CA | Kern | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 31.4 | 0.9 | 19 | 21 | 10 | N |  |  | OP | X | 12 | 1985 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T to WAT BLQ
Vintage1985 | natural gas peaker | FALSE | 164 | AERA Energy LLC | 50752 | South Belridge Cogeneration Facility | CA | Kern | GEN2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 31.4 | 0.9 | 19 | 21 | 10 | N |  |  | OP | X | 12 | 1985 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T to WAT BLQ
Vintage1986 | natural gas peaker | FALSE | 164 | AERA Energy LLC | 50752 | South Belridge Cogeneration Facility | CA | Kern | GEN3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 31.4 | 0.9 | 19 | 21 | 10 | N |  |  | OP | X | 12 | 1986 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T to WAT BLQ
Vintage1982 | onshore wind | TRUE | 2770 | Terra-Gen Operating Co-Wind | 50754 | Oak Creek Energy Systems I | CA | Kern | GEN1 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 3.5 |  | 3.5 | 3.5 | 0 | N |  |  | OP | X | 6 | 1982 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WND |  |  | N | N | 37
Vintage1993 | onshore wind | TRUE | 2770 | Terra-Gen Operating Co-Wind | 50754 | Oak Creek Energy Systems I | CA | Kern | GEN2 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 4.2 |  | 4.2 | 4.2 | 0 | N |  |  | OP | X | 12 | 1993 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WND |  |  | N | N | 7
Vintage1999 | onshore wind | TRUE | 2770 | Terra-Gen Operating Co-Wind | 50754 | Oak Creek Energy Systems I | CA | Kern | GEN3 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 23.1 |  | 23.1 | 23.1 | 0 | N |  |  | OP | X | 6 | 1999 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WND |  |  | N | N | 33
Vintage1999 | onshore wind | TRUE | 2770 | Terra-Gen Operating Co-Wind | 50754 | Oak Creek Energy Systems I | CA | Kern | GEN4 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 3.7 |  | 3.7 | 3.7 | 0 | N |  |  | OP | X | 6 | 1999 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WND |  |  | N |  | 4
Vintage1989 | hydro | TRUE | 12745 | Modesto Irrigation District | 50755 | New Hogan Power Plant | CA | Calaveras | GEN1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 2 | 0.9 | 1.9 | 1.9 | 0.2 | N |  |  | OP | X | 4 | 1989 |  |  | N | Electric Utility | 1 | X T: X; WAT BLQ: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1989 | hydro | TRUE | 12745 | Modesto Irrigation District | 50755 | New Hogan Power Plant | CA | Calaveras | GEN2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1 | 0.9 | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 4 | 1989 |  |  | N | Electric Utility | 1 | X T: X; WAT BLQ: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1987 | hydro | TRUE | 19013 | Topsham Hydro Partners | 50758 | Pejepscot Hydroelectric Project | ME | Sagadahoc | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 12.3 | 0.95 | 11.7 | 11.3 | 1.5 | N |  |  | OP | X | 11 | 1987 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WAT | [5 empty] | 10M | [23 empty] | N
Vintage1987 | hydro | TRUE | 19013 | Topsham Hydro Partners | 50758 | Pejepscot Hydroelectric Project | ME | Sagadahoc | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.95 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 11 | 1987 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WAT | [5 empty] | 10M | [23 empty] | N
Vintage1987 | hydro | TRUE | 19013 | Topsham Hydro Partners | 50758 | Pejepscot Hydroelectric Project | ME | Sagadahoc | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.95 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 11 | 1987 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WAT | [5 empty] | 10M | [23 empty] | N
Vintage1987 | hydro | TRUE | 19013 | Topsham Hydro Partners | 50758 | Pejepscot Hydroelectric Project | ME | Sagadahoc | GEN4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.95 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 11 | 1987 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WAT |  |  |  |  | 0 | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 57144 | Northbrook Carthage LLC | 50759 | West End Dam Hydroelectric Project | NY | Jefferson | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 0.9 | 2.1 | 2 | 0.3 | N |  |  | OP | X | 10 | 1985 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WAT |  |  |  |  | 0 | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 57144 | Northbrook Carthage LLC | 50759 | West End Dam Hydroelectric Project | NY | Jefferson | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 0.9 | 2.1 | 2 | 0.3 | N |  |  | OP | X | 10 | 1985 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WAT |  |  |  |  | 0 | 10M | [23 empty] | N
Vintage2012 | solar pv | TRUE | 50131 | Enel Stillwater LLC | 50765 | Stillwater Facility | NV | Churchill | 1 | Solar Photovoltaic | PV |  | W | X | X |  |  | 22 |  | 21.8 | 21.8 |  | N |  |  | OP | X | 4 | 2012 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: SUN |  |  | N
Vintage2009 | geothermal | TRUE | 50131 | Enel Stillwater LLC | 50765 | Stillwater Facility | NV | Churchill | 1-1 | Geothermal | BT |  | S | X | X |  |  | 11.8 | 1 | 10.1 | 14.3 | 0.1 | N |  |  | OP | X | 3 | 2009 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: GEO | [5 empty] | 1H
Vintage2009 | geothermal | TRUE | 50131 | Enel Stillwater LLC | 50765 | Stillwater Facility | NV | Churchill | 1-2 | Geothermal | BT |  | S | X | X |  |  | 11.8 | 1 | 10.1 | 14.3 | 0.1 | N |  |  | OP | X | 3 | 2009 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: GEO | [5 empty] | 1H
Vintage2009 | geothermal | TRUE | 50131 | Enel Stillwater LLC | 50765 | Stillwater Facility | NV | Churchill | 2-1 | Geothermal | BT |  | S | X | X |  |  | 11.8 | 1 | 10.1 | 14.3 | 0.1 | N |  |  | OP | X | 3 | 2009 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: GEO | [5 empty] | 1H
Vintage2009 | geothermal | TRUE | 50131 | Enel Stillwater LLC | 50765 | Stillwater Facility | NV | Churchill | 2-2 | Geothermal | BT |  | S | X | X |  |  | 11.8 | 1 | 10.1 | 14.3 | 0.1 | N |  |  | OP | X | 3 | 2009 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: GEO |  |  | N |  |  | 1H
Vintage2003 | geothermal | TRUE | 34691 | Ormat Nevada Inc | 50766 | Ormesa I | CA | Imperial | ITLU1 | Geothermal | BT |  | S | X | X |  |  | 12 | 0.8 | 8 | 12 | 8 | N |  |  | OP | X | 6 | 2003 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: GEO; WAT RFO: GEO |  |  | N |  |  | OVER | [23 empty] | N
Vintage2003 | geothermal | TRUE | 34691 | Ormat Nevada Inc | 50766 | Ormesa I | CA | Imperial | ITLU2 | Geothermal | BT |  | S | X | X |  |  | 12 | 0.8 | 8 | 12 | 8 | N |  |  | OP | X | 7 | 2003 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: GEO; WAT RFO: GEO |  |  | N |  |  | OVER | [23 empty] | N
Vintage1986 | geothermal | TRUE | 34691 | Ormat Nevada Inc | 50766 | Ormesa I | CA | Imperial | OE31 | Geothermal | BT |  | S | X | X |  |  | 1.2 | 0.8 | 0.8 | 1.2 | 0.8 | N |  |  | OP | X | 12 | 1986 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: GEO; WAT RFO: GEO | [5 empty] | OVER | [23 empty] | N
Vintage1986 | geothermal | TRUE | 34691 | Ormat Nevada Inc | 50766 | Ormesa I | CA | Imperial | OE32 | Geothermal | BT |  | S | X | X |  |  | 1.2 | 0.8 | 0.8 | 1.2 | 0.8 | N |  |  | OP | X | 12 | 1986 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: GEO; WAT RFO: GEO | [5 empty] | OVER | [23 empty] | N
Vintage1987 | hydro | TRUE | 63840 | Clear Energy Capital, LLC | 50768 | Forestport | NY | Oneida | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.4 | 0.9 | 3.4 | 3.4 | 0.5 | N |  |  | OP | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WAT |  |  | N | N | 0 | 10M
Vintage1988 | biomass | TRUE | 19781 | Viking Energy Corp | 50770 | Viking Energy of McBain | MI | Missaukee | GEN1 | Wood/Wood Waste Biomass | ST |  | W | X | X |  |  | 18 | 0.9 | 16.3 | 18 | 10 | N |  |  | OP | X | 12 | 1988 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WDS; WAT BIT: TDF; WAT WDS: NG; WAT RFO: NG |  |  | N |  |  | 12H | [23 empty] | Y | Y | N
Vintage1989 | biomass | TRUE | 19781 | Viking Energy Corp | 50772 | Viking Energy of Lincoln | MI | Alcona | GEN1 | Wood/Wood Waste Biomass | ST |  | W | X | X |  |  | 18 | 0.9 | 16.3 | 18 | 10 | N |  |  | OP | X | 1 | 1989 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WDS; WAT BIT: TDF; WAT WDS: NG; WAT RFO: NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1992 | hard coal | TRUE | 14432 | Panther Creek Power Operating, LLC | 50776 | Panther Creek Energy Facility | PA | Carbon | GEN1 | Conventional Steam Coal | ST |  | S | X | X | Panther 50746 | PJM RFC | 94 | 0.85 | 80 | 80 | 35 | N |  |  | OP | X | 7 | 1992 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: WC; WAT RFO: DFO |  |  | N | N |  | 12H | Y |  |  |  | Y | [15 empty] | N |  |  | N | N | N
Vintage1991 | natural gas combined cycle | TRUE | 61536 | Consolidated Edison Energy, Inc. | 50799 | Parlin Power Plant | NJ | Middlesex | GEN1 | Natural Gas Fired Combined Cycle | CT | PEC | W | X | N | Parlin 230 KV Dupont NUG JCPL GEN 61482275 | Parlin 230 KV Dupont NUG JCPL GEN 61482275 | 45.9 | 0.85 | 35.9 | 42.2 | 30 | N |  |  | OP | X | 6 | 1991 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: NG; WAT BIT: DFO; WAT RFO: NG; WAT NG: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1991 | natural gas combined cycle | TRUE | 61536 | Consolidated Edison Energy, Inc. | 50799 | Parlin Power Plant | NJ | Middlesex | GEN2 | Natural Gas Fired Combined Cycle | CT | PEC | W | X | N | Parlin 230 KV Dupont NUG JCPL GEN 61482275 | Parlin 230 KV Dupont NUG JCPL GEN 61482275 | 45.9 | 0.85 | 37.5 | 43.7 | 30 | N |  |  | OP | X | 6 | 1991 |  |  | N | IPP Non-CHP | 2 | X T: X; WAT BLQ: NG; WAT BIT: DFO; WAT RFO: NG; WAT NG: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1991 | natural gas combined cycle | TRUE | 61536 | Consolidated Edison Energy, Inc. | 50799 | Parlin Power Plant | NJ | Middlesex | GEN3 | Natural Gas Fired Combined Cycle | CA | PEC | W | Y | X |  |  | 21.6 | 0.85 | 20.6 | 20.6 | 5 | N |  |  | OP | X | 6 | 1991 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T to WAT BLQ
Vintage1991 | natural gas combined cycle | TRUE | 61536 | Consolidated Edison Energy, Inc. | 50799 | Parlin Power Plant | NJ | Middlesex | GEN4 | Natural Gas Fired Combined Cycle | CA | PEC | W | Y | X |  |  | 21.6 | 0.9 | 20.6 | 20.6 | 5 | N |  |  | OP | X | 6 | 1991 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T to WAT BLQ
Vintage1957 | natural gas steam turbine | FALSE | 27718 | WestRock Seminole | 50803 | Seminole Mill | FL | Duval | GEN3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 30 | 0.85 | 20 | 18 | 4 | N |  |  | OP | X | 2 | 1957 |  |  | Y | Industrial CHP | 7 | X T: T; WAT BLQ: NG; WAT BIT: PUR; WAT RFO: NG |  |  | N | N |  | 12H | [23 empty] | N
Vintage1991 | biomass | TRUE | 20505 | International Paper Port Wentworth Mill | 50804 | Port Wentworth Mill | GA | Chatham | GEN4 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 47.3 | 0.85 | 35 | 47.3 | 1 | N |  |  | OP | X | 8 | 1991 |  |  | Y | Industrial CHP | 7 | B | BLQ | WDS | OBG | OBL | SLW | DFO | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage2004 | biomass | TRUE | 20505 | International Paper Port Wentworth Mill | 50804 | Port Wentworth Mill | GA | Chatham | GEN5 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 25 | 0.85 | 23.5 | 25 | 1 | N |  |  | OP | X | 1 | 2004 |  |  | N | Industrial CHP | 7 | X | BLQ | WDS | OBG | OBL | SLW | DFO | NG |  |  |  | N | N | 0 | 12H | [23 empty] | Y | Y | N
Vintage1963 | biomass | TRUE | 18162 | WestRock-Florence | 50806 | Florence Mill | SC | Florence | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 12.3 | 0.85 | 12.3 | 12.3 | 5 | N |  |  | OP | X | 11 | 1963 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | RFO | NG |  |  | BLQ |  |  |  | N | N |  | OVER |  |  |  | N | N | [18 empty] | N | N | N
Vintage1974 | biomass | TRUE | 18162 | WestRock-Florence | 50806 | Florence Mill | SC | Florence | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 15 | 0.85 | 12.5 | 12.5 | 6 | N |  |  | OP | X | 11 | 1974 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | RFO | NG |  |  | BLQ |  |  |  | N | N |  | OVER |  |  |  | N | N | [18 empty] | N | N | N
Vintage1987 | biomass | TRUE | 18162 | WestRock-Florence | 50806 | Florence Mill | SC | Florence | GEN3 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 76.5 | 0.87 | 74 | 74 | 5 | N |  |  | OP | X | 3 | 1987 |  |  | Y | Industrial CHP | 7 | T | WDS | BIT | RFO | NG |  |  | NG |  |  |  | N | N |  | OVER |  | Y |  | N | Y | [18 empty] | N | N | N
Vintage1930 | biomass | TRUE | 18157 | WestRock Corp-Panama City | 50807 | WestRock Panama City Mill | FL | Bay | GEN3 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 4 | 0.8 | 4 | 4 | 1 | N |  |  | OP | X | 5 | 1930 |  |  | Y | Industrial CHP | 7 | B | BLQ | NG | RFO |  |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1949 | biomass | TRUE | 18157 | WestRock Corp-Panama City | 50807 | WestRock Panama City Mill | FL | Bay | GEN4 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 10 | 0.8 | 10 | 10 | 3 | N |  |  | OP | X | 3 | 1949 |  |  | Y | Industrial CHP | 7 | B | BLQ | NG | RFO |  |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1956 | biomass | TRUE | 18157 | WestRock Corp-Panama City | 50807 | WestRock Panama City Mill | FL | Bay | GEN6 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 20 | 0.85 | 21.8 | 21.8 | 3 | N |  |  | OP | X | 3 | 1956 |  |  | Y | Industrial CHP | 7 | B | WDS | NG | RFO | BIT |  |  | NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1957 | biomass | TRUE | 18155 | Westrock (LA) | 50810 | Westrock Hodge (LA) | LA | Jackson | NO 7 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 15.6 | 0.85 | 15.6 | 15.6 | 1 | N |  |  | OP | X | 8 | 1957 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS |  |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1972 | biomass | TRUE | 18155 | Westrock (LA) | 50810 | Westrock Hodge (LA) | LA | Jackson | NO 8 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 27.5 | 0.9 | 27.5 | 27.5 | 1 | N |  |  | OP | X | 8 | 1972 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS |  |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1972 | biomass | TRUE | 18155 | Westrock (LA) | 50810 | Westrock Hodge (LA) | LA | Jackson | NO 9 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 23.3 | 0.9 | 23.3 | 23.3 | 1 | N |  |  | OP | X | 10 | 1972 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS |  |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1980 | biomass | TRUE | 18147 | RockTenn-Hopewell | 50813 | Hopewell Mill | VA | Hopewell City | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 47.6 | 0.85 | 40.7 | 40.7 | 8 | N |  |  | OP | X | 12 | 1980 |  |  | Y | Industrial CHP | 7 | B | BLQ | WDS | NG | BIT | RFO |  | NG | RFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | Y
Vintage1985 | natural gas combined cycle | TRUE | 55879 | Odyssey Operating Services | 50815 | Odyssey Energy Altura Cogen, LLC | TX | Harris | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N | PSA_PSA_G1 | PSA_PSA_G1 | 84.9 | 0.85 | 80 | 68.4 | 40 | N |  |  | OP | X | 11 | 1985 |  |  | Y | IPP CHP | 3 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | N | bar: B X to BLQ BLQ
Vintage1985 | natural gas combined cycle | TRUE | 55879 | Odyssey Operating Services | 50815 | Odyssey Energy Altura Cogen, LLC | TX | Harris | GEN2 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N | PSA_PSA_G2 | PSA_PSA_G2 | 84.9 | 0.85 | 80 | 68.4 | 40 | N |  |  | OP | X | 12 | 1985 |  |  | Y | IPP CHP | 3 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | N | bar: B X to BLQ BLQ
Vintage1985 | natural gas combined cycle | TRUE | 55879 | Odyssey Operating Services | 50815 | Odyssey Energy Altura Cogen, LLC | TX | Harris | GEN3 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N | PSA_PSA_G3 | PSA_PSA_G3 | 84.9 | 0.85 | 80 | 70.7 | 40 | N |  |  | OP | X | 12 | 1985 |  |  | Y | IPP CHP | 3 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | N | bar: B X to BLQ BLQ
Vintage1986 | natural gas combined cycle | TRUE | 55879 | Odyssey Operating Services | 50815 | Odyssey Energy Altura Cogen, LLC | TX | Harris | GEN4 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N | PSA_PSA_G4 | PSA_PSA_G4 | 84.9 | 0.85 | 80 | 69.6 | 40 | N |  |  | OP | X | 3 | 1986 |  |  | Y | IPP CHP | 3 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | N | bar: B X to BLQ BLQ
Vintage1986 | natural gas combined cycle | TRUE | 55879 | Odyssey Operating Services | 50815 | Odyssey Energy Altura Cogen, LLC | TX | Harris | GEN5 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N | PSA_PSA_G5 | PSA_PSA_G5 | 84.9 | 0.85 | 80 | 69.5 | 40 | N |  |  | OP | X | 4 | 1986 |  |  | Y | IPP CHP | 3 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | N | bar: B X to BLQ BLQ
Vintage1986 | natural gas combined cycle | TRUE | 55879 | Odyssey Operating Services | 50815 | Odyssey Energy Altura Cogen, LLC | TX | Harris | GEN6 | Natural Gas Fired Combined Cycle | CA | CC1 | W | Y | X | PSA_PSA_G7 | PSA_PSA_G7 | 129.2 | 0.85 | 127 | 127 | 52 | N |  |  | OP | X | 4 | 1986 |  |  | Y | IPP CHP | 3 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | N | bar: B X to BLQ BLQ
Vintage1995 | natural gas combined cycle | TRUE | 55879 | Odyssey Operating Services | 50815 | Odyssey Energy Altura Cogen, LLC | TX | Harris | GEN7 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N | PSA_PSA_G6 | PSA_PSA_G6 | 89.9 | 0.85 | 69.3 | 69.3 | 40 | N |  |  | OP | X | 6 | 1995 |  |  | Y | IPP CHP | 3 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | N | bar: B X to BLQ BLQ
Vintage1985 | onshore wind | TRUE | 2770 | Terra-Gen Operating Co-Wind | 50820 | East Winds Project | CA | Riverside | GEN1 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 3 |  | 3 | 3 | 0 | N |  |  | OP | X | 1 | 1985 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WND |  |  |  | N | N | 5 | [24 empty] | N
Vintage1989 | onshore wind | TRUE | 2770 | Terra-Gen Operating Co-Wind | 50821 | Mojave 16/17/18 | CA | Kern | GEN1 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 88.5 |  | 88.5 | 88.5 | 5.2 | N |  |  | OP | X | 12 | 1989 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WND |  |  |  | N | N | 238
Vintage1989 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 50827 | Twin Falls Hydro | WA | King | UNI1 | Conventional Hydroelectric | HY |  | J | X | X |  |  | 12 | 1 | 11.4 | 11 | 0.1 | N |  |  | OP | X | 12 | 1989 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WAT | [6 empty] | 10M
Vintage1989 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 50827 | Twin Falls Hydro | WA | King | UNI2 | Conventional Hydroelectric | HY |  | J | X | X |  |  | 12 | 1 | 11.4 | 11 | 0.1 | N |  |  | OP | X | 12 | 1989 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WAT | [6 empty] | 10M
Vintage1985 | biomass | TRUE | 13876 | Nove Investments I LLC | 50831 | Nove Power Plant | CA | Contra Costa | GEN1 | Landfill Gas | IC |  | S | X | X | RICHMN_7_BAYENV |  | 1 | 1 | 1 | 1 | 0.5 | N |  |  | OP | X | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: LFG; NG NG: LFG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1987 | biomass | TRUE | 13876 | Nove Investments I LLC | 50831 | Nove Power Plant | CA | Contra Costa | GEN2 | Landfill Gas | IC |  | S | X | X | RICHMN_7_BAYENV |  | 1 | 1 | 1 | 1 | 0.5 | N |  |  | OP | X | 5 | 1987 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: LFG; NG NG: LFG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1985 | biomass | TRUE | 13876 | Nove Investments I LLC | 50831 | Nove Power Plant | CA | Contra Costa | GEN3 | Landfill Gas | IC |  | S | X | X | RICHMN_7_BAYENV |  | 1 | 1 | 1 | 1 | 0.5 | N |  |  | OP | X | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: LFG; NG NG: LFG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1985 | hydro | TRUE | 3477 | City of Chicopee - (MA) | 50832 | Chicopee Hydroelectric Station | MA | Hampden | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.9 | 1.2 | 1.2 | 0 | N |  |  | OP | X | 5 | 1985 |  |  | N | Electric Utility | 1 | B X: X; BLQ BLQ: WAT |  |  |  | N | N |  | 10M | [20 empty] | Y | 12 | 2024 | N
Vintage1985 | hydro | TRUE | 3477 | City of Chicopee - (MA) | 50832 | Chicopee Hydroelectric Station | MA | Hampden | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.9 | 1.2 | 1.2 | 0 | N |  |  | OP | X | 5 | 1985 |  |  | N | Electric Utility | 1 | B X: X; BLQ BLQ: WAT |  |  |  | N | N |  | 10M | [20 empty] | Y | 12 | 2024 | N
Vintage1990 | hard coal | TRUE | 18414 | TES Filer City Station LP | 50835 | TES Filer City Station | MI | Manistee | GEN1 | Conventional Steam Coal | ST |  | J | X | X | cons.filercity | MISO | 70 | 0.85 | 60 | 60 | 7 | N |  |  | OP | X | 5 | 1990 | 6 | 2025 | Y | IPP CHP | 3 | T | BIT | NG | WDS | TDF |  |  | NG |  |  |  | N | N |  | 12H |  |  | Y |  | Y | [18 empty] | Y | Y | N
Vintage1988 | municipal solid waste | TRUE | 16899 | SERRF Joint Powers Authority | 50837 | Southeast Resource Recovery | CA | Los Angeles | GEN1 | Municipal Solid Waste | ST |  | J | X | X |  |  | 35.6 | 0.9 | 28 | 26 | 2 | N |  |  | OP | X | 7 | 1988 |  |  | Y | IPP CHP | 3 | B X: T; BLQ BLQ: MSW; WDS WDS: NG; NG NG: NG |  |  |  | N | N |  | 12H |  |  | N | [20 empty] | N | N | N
Vintage1969 | natural gas peaker | FALSE | 56097 | Gramercy Holdings I LLC | 50846 | Gramercy Holdings LLC | LA | St James | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 16 | 0.95 | 15 | 17 | 1 | N |  |  | OP | X | 4 | 1969 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | bar: B X to BLQ BLQ
Vintage1974 | natural gas peaker | FALSE | 56097 | Gramercy Holdings I LLC | 50846 | Gramercy Holdings LLC | LA | St James | GT4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 24.7 | 0.95 | 21 | 24 | 1 | N |  |  | OP | X | 4 | 1974 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: B X to BLQ BLQ
Vintage1958 | natural gas steam turbine | FALSE | 56097 | Gramercy Holdings I LLC | 50846 | Gramercy Holdings LLC | LA | St James | ST1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 18.7 | 0.95 | 17 | 17 | 2 | N |  |  | OP | X | 2 | 1958 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: B X to BLQ BLQ; NG NG
Vintage1958 | natural gas steam turbine | FALSE | 56097 | Gramercy Holdings I LLC | 50846 | Gramercy Holdings LLC | LA | St James | ST2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 18.7 | 0.95 | 17 | 17 | 2 | N |  |  | OP | X | 2 | 1958 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: B X to BLQ BLQ; NG NG
Vintage1969 | natural gas steam turbine | FALSE | 56097 | Gramercy Holdings I LLC | 50846 | Gramercy Holdings LLC | LA | St James | ST3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 7.2 | 0.95 | 6 | 6 | 3 | N |  |  | OP | X | 2 | 1969 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: B X to BLQ BLQ; NG NG
Vintage1987 | natural gas combined cycle | FALSE | 61261 | Berkeley Cogeneration Facility | 50849 | PE Berkeley | CA | Alameda | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | Y |  |  | 23 | 0.85 | 22 | 23 | 18 | N |  |  | OP | X | 6 | 1987 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: B X to BLQ BLQ
Vintage1987 | natural gas combined cycle | FALSE | 61261 | Berkeley Cogeneration Facility | 50849 | PE Berkeley | CA | Alameda | GEN2 | Natural Gas Fired Combined Cycle | CA | CC1 | W | Y | X |  |  | 5.5 | 0.85 | 2 | 4 | 1 | N |  |  | OP | X | 6 | 1987 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: B X to BLQ BLQ
Vintage1987 | natural gas combined cycle | TRUE | 14265 | OLS Energy-Chino | 50850 | OLS Energy Chino | CA | San Bernardino | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | CIMGEN_7_B1 | CIMGEN_7_B1 | 23.5 | 0.8 | 22.5 | 22.5 | 15 | N |  |  | OP | X | 12 | 1987 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: B X to BLQ BLQ
Vintage1987 | natural gas combined cycle | TRUE | 14265 | OLS Energy-Chino | 50850 | OLS Energy Chino | CA | San Bernardino | GEN2 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X | CIMGEN_7_B1 | CIMGEN_7_B1 | 7.3 | 0.8 | 6.5 | 6 | 2 | N |  |  | OP | X | 12 | 1987 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: B X to BLQ BLQ
Vintage1988 | natural gas combined cycle | TRUE | 56835 | CSUCI Site Authority | 50851 | CSUCI Site Authority | CA | Ventura | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 23.5 | 0.9 | 21.5 | 22.1 | 21.5 | N |  |  | OP | X | 3 | 1988 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: B X to BLQ BLQ
Vintage1988 | natural gas combined cycle | TRUE | 56835 | CSUCI Site Authority | 50851 | CSUCI Site Authority | CA | Ventura | GEN2 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X |  |  | 7.6 | 0.8 | 6.8 | 6.9 | 6.5 | N |  |  | OP | X | 3 | 1988 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: B X to BLQ BLQ
Vintage1987 | municipal solid waste | TRUE | 8633 | Hillsborough County | 50858 | Hillsborough County Resource Recovery | FL | Hillsborough | GEN1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 29 | 1 | 26 | 26 | 5 | N |  |  | OP | X | 4 | 1987 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: MSW; NG NG: NG |  |  |  | N | N |  | 12H |  |  | N |  | N | [18 empty] | N
Vintage2009 | municipal solid waste | TRUE | 8633 | Hillsborough County | 50858 | Hillsborough County Resource Recovery | FL | Hillsborough | GEN2 | Municipal Solid Waste | ST |  | S | X | X |  |  | 18 | 1 | 16 | 16 | 3 | N |  |  | OP | X | 6 | 2009 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: MSW; NG NG: NG |  |  |  | N | N |  | 12H |  |  | N |  | N | [18 empty] | N
Vintage1990 | municipal solid waste | TRUE | 4447 | Covanta Lancaster Inc | 50859 | Lancaster County Resource Recovery | PA | Lancaster | GEN1 | Municipal Solid Waste | ST |  | W | X | X | 50608 | 50608 | 35.7 | 0.9 | 32.4 | 32.4 | 1 | N |  |  | OP | X | 12 | 1990 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: MSW; NG NG: PG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1989 | municipal solid waste | FALSE | 10162 | Kent County | 50860 | Kent County Waste to Energy Facility | MI | Kent | GEN1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 18 | 0.9 | 15.7 | 15.7 | 1 | N |  |  | OP | X | 10 | 1989 |  |  | N | Commercial Non-CHP | 4 | B X: X; BLQ BLQ: MSW; NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1991 | natural gas peaker | TRUE | 16636 | Sargent Canyon Cogeneration Co | 50864 | Sargent Canyon Cogeneration | CA | Monterey | K100 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 38.2 | 1 | 30 | 34 | 30 | N |  |  | OS | X | 11 | 1991 |  |  | Y | IPP CHP | 3 | [11 empty] | N |  |  | 1H | [23 empty] | N | N | bar: B X to BLQ BLQ
Vintage1991 | natural gas peaker | TRUE | 16506 | Salinas River Cogeneration Co | 50865 | Salinas River Cogeneration | CA | Monterey | K100 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 38.9 | 1 | 33 | 35 | 30 | N |  |  | OP | X | 11 | 1991 |  |  | Y | IPP CHP | 3 | [11 empty] | N |  |  | 10M | [23 empty] | N | bar: B X to BLQ BLQ
Vintage1989 | municipal solid waste | TRUE | 20541 | Wheelabrator Environmental Systems | 50873 | Wheelabrator Concord Facility | NH | Merrimack | GEN1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 14 | 0.85 | 12 | 12 | 4 | N |  |  | OP | X | 4 | 1989 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: MSW; NG NG: WO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1985 | municipal solid waste | TRUE | 63619 | City of Tampa | 50875 | McKay Bay Facility | FL | Hillsborough | GEN1 | Municipal Solid Waste | ST |  | W | X | X |  |  | 22.1 | 0.9 | 18 | 18 | 9 | N |  |  | OP | X | 6 | 1985 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: MSW; NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | N | N
Vintage1985 | municipal solid waste | TRUE | 20541 | Wheelabrator Environmental Systems | 50877 | Wheelabrator North Andover | MA | Essex | GEN1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 40.3 | 0.85 | 30 | 30 | 8 | N |  |  | OP | X | 5 | 1985 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: MSW; NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | N | N
Vintage1987 | municipal solid waste | TRUE | 20541 | Wheelabrator Environmental Systems | 50878 | Wheelabrator Millbury Facility | MA | Worcester | GEN1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 47.6 | 0.85 | 40 | 40 | 14 | N |  |  | OP | X | 9 | 1987 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: MSW; NG NG: NG |  |  |  | N | N |  | OVER |  |  | N | N | [19 empty] | N | N | N
Vintage1985 | municipal solid waste | TRUE | 20541 | Wheelabrator Environmental Systems | 50880 | Wheelabrator Saugus | MA | Essex | GEN1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 53.7 | 0.8 | 32 | 32 | 7 | N |  |  | OP | X | 8 | 1985 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: MSW; NG NG: DFO |  |  |  | N | N |  | OVER |  |  |  | N | [19 empty] | N | N | N
Vintage1987 | biomass | TRUE | 64579 | Shasta Sustainable Resource Management, Inc. | 50881 | Wheelabrator Shasta | CA | Shasta | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 18.3 | 0.95 | 18.8 | 18.8 | 2 | N |  |  | OP | X | 10 | 1987 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WDS; WDS WDS: AB; NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1987 | biomass | TRUE | 64579 | Shasta Sustainable Resource Management, Inc. | 50881 | Wheelabrator Shasta | CA | Shasta | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 18.3 | 0.95 | 18.8 | 18.8 | 2 | N |  |  | OP | X | 11 | 1987 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WDS; WDS WDS: AB; NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1987 | biomass | TRUE | 64579 | Shasta Sustainable Resource Management, Inc. | 50881 | Wheelabrator Shasta | CA | Shasta | GEN3 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 18.3 | 0.95 | 18.8 | 18.8 | 2 | N |  |  | OP | X | 11 | 1987 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WDS; WDS WDS: AB; NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1984 | municipal solid waste | TRUE | 20541 | Wheelabrator Environmental Systems | 50882 | Wheelabrator Westchester | NY | Westchester | GEN1 | Municipal Solid Waste | ST |  | S | X | X | NYISO Zone H | NYISO Zone H | 59.7 | 0.8 | 51 | 53 | 7 | N |  |  | OP | X | 10 | 1984 |  |  | Y | IPP CHP | 3 | B X: B; BLQ BLQ: MSW; NG NG: MSW |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1988 | municipal solid waste | TRUE | 20541 | Wheelabrator Environmental Systems | 50883 | Wheelabrator Bridgeport | CT | Fairfield | GEN1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 67 | 0.85 | 58 | 59 | 10 | N |  |  | OP | X | 7 | 1988 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: MSW; NG NG: NG |  |  |  | N |  |  | OVER | [23 empty] | N | N | N
Vintage1983 | municipal solid waste | TRUE | 55871 | Covanta Projects, LLC | 50884 | Pinellas County Resource Recovery | FL | Pinellas | GEN1 | Municipal Solid Waste | ST |  | W | X | X |  |  | 50.5 | 0.85 | 41.1 | 41.1 | 7 | N |  |  | OP | X | 1 | 1983 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: MSW; NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1986 | municipal solid waste | TRUE | 55871 | Covanta Projects, LLC | 50884 | Pinellas County Resource Recovery | FL | Pinellas | GEN2 | Municipal Solid Waste | ST |  | W | X | X |  |  | 26 | 0.85 | 17 | 17 | 4 | N |  |  | OP | X | 4 | 1986 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: MSW; NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1990 | municipal solid waste | TRUE | 20541 | Wheelabrator Environmental Systems | 50885 | Wheelabrator Gloucester LP | NJ | Gloucester | GEN1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 14 | 0.85 | 12 | 12 | 4 | N |  |  | OP | X | 1 | 1990 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: MSW; NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | N | N
Vintage1991 | municipal solid waste | TRUE | 42892 | City of Spokane | 50886 | Spokane Waste to Energy | WA | Spokane | GEN1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 26 | 0.85 | 22.7 | 22.7 | 4 | N |  |  | OP | X | 9 | 1991 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: MSW; NG NG: MSW | NG |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1991 | municipal solid waste | TRUE | 20541 | Wheelabrator Environmental Systems | 50887 | Wheelabrator South Broward | FL | Broward | GEN1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 66 | 0.85 | 54 | 54 | 10 | N |  |  | OP | X | 4 | 1991 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: MSW; NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1995 | hard coal | TRUE | 23013 | EIF Northampton GP, LLC | 50888 | Northampton Generating Company LP | PA | Northampton | GEN1 | Conventional Steam Coal | ST |  | S | X | X | 50630 | 50630 | 134.1 | 0.85 | 112 | 112 | 65 | N |  |  | OP | X | 8 | 1995 |  |  | N | IPP Non-CHP | 2 | X | WC | TDF | WDS | PC | WO |  | WO |  |  |  | N | N |  | OVER | Y |  |  |  | Y | [18 empty] | Y | Y | N
Vintage1985 | hydro | TRUE | 11468 | Madison Hydro Partners | 50890 | Ivy River Hydro | NC | Madison | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 1 | 0.2 | 0.2 | 0 | N |  |  | OP | X | 11 | 1985 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WAT |  |  |  | N |  |  | 10M
Vintage1985 | hydro | TRUE | 11468 | Madison Hydro Partners | 50890 | Ivy River Hydro | NC | Madison | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 1 | 0.2 | 0.2 | 0 | N |  |  | OP | X | 11 | 1985 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WAT |  |  |  | N |  |  | 10M
Vintage1985 | hydro | TRUE | 11468 | Madison Hydro Partners | 50890 | Ivy River Hydro | NC | Madison | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 1 | 0.2 | 0.2 | 0 | N |  |  | OP | X | 11 | 1985 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WAT |  |  |  | N |  |  | 10M
Vintage1985 | hydro | TRUE | 11468 | Madison Hydro Partners | 50890 | Ivy River Hydro | NC | Madison | GEN4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 1 | 0.2 | 0.2 | 0 | N |  |  | OP | X | 11 | 1985 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WAT | [6 empty] | 10M
Vintage1985 | hydro | TRUE | 11468 | Madison Hydro Partners | 50890 | Ivy River Hydro | NC | Madison | GEN5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 1 | 0.2 | 0.2 | 0 | N |  |  | OS | X | 11 | 1985 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WAT | [6 empty] | 10M
Vintage1985 | hydro | TRUE | 11468 | Madison Hydro Partners | 50890 | Ivy River Hydro | NC | Madison | GEN6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.2 | 1 | 0.2 | 0.2 | 0 | N |  |  | OS | X | 11 | 1985 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WAT | [6 empty] | 10M
Vintage1986 | hydro | TRUE | 63985 | Hydroland Omega LLC | 50891 | El Dorado Hydro Elk Creek | ID | Idaho | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.6 | 1 | 2.3 | 2.3 | 0.1 | N |  |  | OP | X | 4 | 1986 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WAT | [5 empty] | 0 | 10M
Vintage1986 | hydro | TRUE | 63985 | Hydroland Omega LLC | 50892 | Rock Creek LP | CA | El Dorado | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 1 | 1.5 | 1.5 | 0.1 | N |  |  | OP | X | 4 | 1986 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WAT | [5 empty] | 0 | 10M
Vintage1986 | hydro | TRUE | 63985 | Hydroland Omega LLC | 50892 | Rock Creek LP | CA | El Dorado | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.5 | 1 | 1.5 | 1.5 | 0.1 | N |  |  | OP | X | 4 | 1986 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WAT | [5 empty] | 0 | 10M
Vintage1988 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50893 | Allegheny No. 5 Hydro Station | PA | Armstrong | GEN1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 4.6 | 0.9 | 3 | 5 | 2 | N |  |  | OP | X | 10 | 1988 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M
Vintage1988 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50893 | Allegheny No. 5 Hydro Station | PA | Armstrong | GEN2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 4.6 | 0.9 | 3 | 5 | 2 | N |  |  | OP | X | 10 | 1988 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WAT |  |  |  | N | N |  | 10M
Vintage1988 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50894 | Allegheny No 6 Hydro Station | PA | Armstrong | GEN1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 4.6 | 0.9 | 4 | 6 | 2 | N |  |  | OP | X | 11 | 1988 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M
Vintage1988 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 50894 | Allegheny No 6 Hydro Station | PA | Armstrong | GEN2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 4.6 | 0.9 | 4 | 6 | 2 | N |  |  | OP | X | 11 | 1988 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M
Vintage1987 | hydro | TRUE | 60851 | North Side Energy Company | 50895 | Bypass | ID | Jerome | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.3 | 1 | 3.3 | 3.3 | 0.1 | N |  |  | SB | Y | 3 | 1987 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1987 | hydro | TRUE | 60851 | North Side Energy Company | 50895 | Bypass | ID | Jerome | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.3 | 1 | 3.3 | 3.3 | 0.1 | N |  |  | SB | Y | 3 | 1987 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1987 | hydro | TRUE | 60851 | North Side Energy Company | 50895 | Bypass | ID | Jerome | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.3 | 1 | 3.3 | 3.3 | 0.1 | N |  |  | SB | Y | 3 | 1987 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1990 | hydro | TRUE | 60851 | North Side Energy Company | 50896 | S E Hazelton A | ID | Jerome | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.8 | 1 | 2.8 | 2.8 | 0.1 | N |  |  | SB | Y | 6 | 1990 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1990 | hydro | TRUE | 60851 | North Side Energy Company | 50896 | S E Hazelton A | ID | Jerome | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.8 | 1 | 2.8 | 2.8 | 0.1 | N |  |  | SB | Y | 6 | 1990 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1990 | hydro | TRUE | 60851 | North Side Energy Company | 50896 | S E Hazelton A | ID | Jerome | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.8 | 1 | 2.8 | 2.8 | 0.1 | N |  |  | SB | Y | 6 | 1990 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1990 | hydro | TRUE | 56813 | Allegheny Hydro LP | 50897 | Allegheny Hydro No 8 | PA | Armstrong | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.8 | 0.9 | 6.8 | 6.8 | 1 | N |  |  | OP | X | 12 | 1990 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage1990 | hydro | TRUE | 56813 | Allegheny Hydro LP | 50897 | Allegheny Hydro No 8 | PA | Armstrong | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.8 | 0.9 | 6.8 | 6.8 | 1 | N |  |  | OP | X | 12 | 1990 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage1990 | hydro | TRUE | 56813 | Allegheny Hydro LP | 50898 | Allegheny Hydro No 9 | PA | Armstrong | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8.9 | 0.9 | 8.9 | 8.9 | 1 | N |  |  | OP | X | 12 | 1990 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage1990 | hydro | TRUE | 56813 | Allegheny Hydro LP | 50898 | Allegheny Hydro No 9 | PA | Armstrong | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 8.9 | 0.9 | 8.9 | 8.9 | 1 | N |  |  | OP | X | 12 | 1990 |  |  | N | IPP Non-CHP | 2 | B X: X; BLQ BLQ: WAT |  |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage1951 | hard coal | FALSE | 20508 | WestRock Corp | 50900 | Covington Facility | VA | Covington City | GEN3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 10.5 | 0.85 | 10.5 | 10.5 | 5 | N |  |  | OP | X | 1 | 1951 |  |  | Y | Industrial CHP | 7 | T | BIT | NG | WDS | RFO | DFO | BLQ | NG | RFO |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | Y | Y | Y
Vintage1980 | biomass | TRUE | 20508 | WestRock Corp | 50900 | Covington Facility | VA | Covington City | GEN4 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 34 | 0.85 | 32.5 | 32.5 | 3 | N |  |  | OP | X | 9 | 1980 |  |  | Y | Industrial CHP | 7 | T | BLQ | BIT | WDS | RFO | NG | DFO | RFO | NG |  |  | N | N |  | 12H |  | N |  |  | N | [18 empty] | Y | Y | Y
Vintage1989 | hard coal | FALSE | 20508 | WestRock Corp | 50900 | Covington Facility | VA | Covington City | GEN5 | Conventional Steam Coal | ST |  | S | X | X |  |  | 34 | 0.85 | 32.5 | 32.5 | 3 | N |  |  | OP | X | 9 | 1989 |  |  | Y | Industrial CHP | 7 | T | BIT | WDS | RFO | NG | DFO | BLQ | DFO | NG |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | Y | Y | Y
Vintage2013 | biomass | TRUE | 20508 | WestRock Corp | 50900 | Covington Facility | VA | Covington City | GEN7 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 82.4 | 0.85 | 81 | 82.4 | 7 | N |  |  | OP | X | 11 | 2013 |  |  | Y | Industrial CHP | 7 | T | WDS | BLQ | NG | RFO |  |  | NG |  |  |  | N | N | 0 | 12H | N | [22 empty] | Y | Y | Y
Vintage1984 | natural gas steam turbine | FALSE | 8 | Tate & Lyle Ingredients Americas Inc | 50903 | Sagamore Plant Cogeneration | IN | Tippecanoe | GEN1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 7.4 | 0.85 | 7.4 | 7.4 | 1.5 | N |  |  | OP | X | 10 | 1984 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT; WAT NG RFO DFO
Vintage2005 | natural gas peaker | FALSE | 21964 | University of New Mexico | 50906 | Ford Utilities Center | NM | Bernalillo | 3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 7 | 0.9 | 6 | 6.3 | 0.1 | N |  |  | OP | X | 3 | 2005 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage2011 | other | FALSE | 21964 | University of New Mexico | 50906 | Ford Utilities Center | NM | Bernalillo | 4 | All Other | ST |  | S | X | X |  |  | 1.1 | 0.8 | 0.7 | 0.7 | 0.2 | N |  |  | OP | X | 10 | 2011 |  |  | N | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT; WAT NG RFO DFO
Vintage2014 | natural gas peaker | FALSE | 21964 | University of New Mexico | 50906 | Ford Utilities Center | NM | Bernalillo | 5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 6.7 | 0.9 | 6.2 | 7 | 0.1 | N |  |  | OP | X | 1 | 2014 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H |  |  |  |  | N | [18 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1986 | municipal solid waste | FALSE | 14222 | Oswego County | 50907 | Oswego County Energy Recovery | NY | Oswego | UNT1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 1.8 | 0.8 | 1.7 | 1.7 | 0.6 | N |  |  | OP | X | 2 | 1986 |  |  | Y | Commercial CHP | 5 | X T T T: B; WAT BIT BLQ BIT: MSW; WAT NG BIT WDS: NG; WAT NG RFO DFO: NG |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1986 | municipal solid waste | FALSE | 14222 | Oswego County | 50907 | Oswego County Energy Recovery | NY | Oswego | UNT2 | Municipal Solid Waste | ST |  | S | X | X |  |  | 1.8 | 0.8 | 1.7 | 1.7 | 0.6 | N |  |  | OP | X | 2 | 1986 |  |  | Y | Commercial CHP | 5 | X T T T: B; WAT BIT BLQ BIT: MSW; WAT NG BIT WDS: NG; WAT NG RFO DFO: NG |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1986 | hydro | TRUE | 12502 | Middle Fork Irrigation Dist | 50917 | Middle Fork Irrigation District | OR | Hood River | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.97 | 2 | 2 | 0.2 | N |  |  | OP | X | 3 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1986 | hydro | TRUE | 12502 | Middle Fork Irrigation Dist | 50917 | Middle Fork Irrigation District | OR | Hood River | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.95 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 3 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1986 | hydro | TRUE | 12502 | Middle Fork Irrigation Dist | 50917 | Middle Fork Irrigation District | OR | Hood River | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.95 | 0.8 | 0.8 | 0.1 | N |  |  | OP | X | 3 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1986 | biomass | TRUE | 3770 | Co-Generation Co | 50921 | Co-Gen LLC | OR | Grant | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 7.5 | 0.9 | 7.5 | 7.5 | 4 | N |  |  | SB | Y | 5 | 1986 |  |  | Y | IPP CHP | 3 | X T T T: T; WAT BIT BLQ BIT: WDS; WAT NG RFO DFO: WDS |  |  | N |  |  | OVER | [23 empty] | N | N | N
Vintage1995 | petroleum | TRUE | 21773 | Yellowstone Energy LP | 50931 | Yellowstone Energy LP | MT | Yellowstone | GEN1 | Petroleum Coke | ST |  | S | X | X |  |  | 68 | 0.9 | 52 | 55 | 22 | N |  |  | OP | X | 6 | 1995 |  |  | Y | IPP CHP | 3 | X T T T: T; WAT BIT BLQ BIT: PC; WAT NG BIT WDS: OG; WAT NG RFO DFO: DFO |  |  | N | N |  | OVER | Y |  |  |  | Y | [18 empty] | Y | N | N
Vintage2015 | biomass | TRUE | 5089 | Des Moines Metro WRF | 50932 | Des Moines Wastewater Reclamation Fac | IA | Polk | 72-04 | Other Waste Biomass | IC |  | S | X | X |  |  | 1.4 | 0.8 | 1.4 | 1.4 | 0.7 | N |  |  | SB | N | 9 | 2015 |  |  | Y | Commercial CHP | 5 | X T T T: T; WAT BIT BLQ BIT: OBG; WAT NG BIT WDS: NG |  |  | N | N |  | 10M | [23 empty] | Y | N | N
Vintage2015 | biomass | TRUE | 5089 | Des Moines Metro WRF | 50932 | Des Moines Wastewater Reclamation Fac | IA | Polk | 72-05 | Other Waste Biomass | IC |  | S | X | X |  |  | 1.4 | 0.8 | 1.4 | 1.4 | 0.7 | N |  |  | SB | N | 9 | 2015 |  |  | Y | Commercial CHP | 5 | X T T T: T; WAT BIT BLQ BIT: OBG; WAT NG BIT WDS: NG |  |  | N | N |  | 10M | [23 empty] | Y | N | N
Vintage1951 | natural gas steam turbine | FALSE | 61707 | Ahlstrom-Munksjo | 50933 | Rhinelander Mill | WI | Oneida | GEN5 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 10 | 0.85 | 4 | 7 | 3 | N |  |  | SB | N | 2 | 1951 |  |  | Y | Industrial CHP | 7 | X T T T: B; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO; WAT NG RFO DFO: NG; WAT RFO NG NG: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1958 | hard coal | FALSE | 61707 | Ahlstrom-Munksjo | 50933 | Rhinelander Mill | WI | Oneida | GEN6 | Conventional Steam Coal | ST |  | S | X | X |  |  | 9.3 | 0.8 | 6.3 | 8.5 | 3.8 | N |  |  | OP | X | 7 | 1958 |  |  | Y | Industrial CHP | 7 | X T T T: B; WAT BIT BLQ BIT: BIT; WAT NG RFO DFO: DFO |  |  | N | N |  | 12H |  |  |  | Y | Y | [18 empty] | N | N | N
Vintage1917 | hydro | FALSE | 61707 | Ahlstrom-Munksjo | 50933 | Rhinelander Mill | WI | Oneida | HYD1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.3 | N |  |  | OP | X | 12 | 1917 |  |  | N | Industrial CHP | 7 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  | N | N |  | 10M
Vintage1917 | hydro | FALSE | 61707 | Ahlstrom-Munksjo | 50933 | Rhinelander Mill | WI | Oneida | HYD2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.3 | N |  |  | OP | X | 12 | 1917 |  |  | N | Industrial CHP | 7 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  | N | N |  | 10M
Vintage1926 | hydro | FALSE | 61707 | Ahlstrom-Munksjo | 50933 | Rhinelander Mill | WI | Oneida | HYD3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.6 | N |  |  | OP | X | 12 | 1926 |  |  | N | Industrial CHP | 7 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  | N | N |  | 10M
Vintage1983 | petroleum | FALSE | 3179 | Caterpillar Inc | 50935 | Caterpillar | IN | Tippecanoe | 3512 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.8 | 0.8 | 0.2 | N |  |  | OP | X | 12 | 1983 |  |  | N | Industrial Non-CHP | 6 | X T T T: X; WAT BIT BLQ BIT: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1987 | petroleum | FALSE | 3179 | Caterpillar Inc | 50935 | Caterpillar | IN | Tippecanoe | 3516 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.8 | 0.8 | 0.8 | 0.3 | N |  |  | SB | N | 7 | 1987 |  |  | N | Industrial Non-CHP | 6 | X T T T: X; WAT BIT BLQ BIT: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1996 | petroleum | FALSE | 3179 | Caterpillar Inc | 50935 | Caterpillar | IN | Tippecanoe | 516A | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.5 | N |  |  | OP | X | 3 | 1996 |  |  | N | Industrial Non-CHP | 6 | X T T T: X; WAT BIT BLQ BIT: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2011 | natural gas peaker | FALSE | 3179 | Caterpillar Inc | 50935 | Caterpillar | IN | Tippecanoe | ET1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.5 | N |  |  | OP | X | 4 | 2011 | 1 | 2022 | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage2011 | natural gas peaker | FALSE | 3179 | Caterpillar Inc | 50935 | Caterpillar | IN | Tippecanoe | ET2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.5 | N |  |  | OP | X | 4 | 2011 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage2013 | natural gas peaker | FALSE | 3179 | Caterpillar Inc | 50935 | Caterpillar | IN | Tippecanoe | ET4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 0.6 | N |  |  | OP | X | 4 | 2013 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage2001 | petroleum | FALSE | 3179 | Caterpillar Inc | 50935 | Caterpillar | IN | Tippecanoe | R12 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.4 | 0.8 | 0.3 | 0.3 | 0.1 | N |  |  | SB | N | 6 | 2001 |  |  | N | Industrial Non-CHP | 6 | X T T T: X; WAT BIT BLQ BIT: DFO |  |  | N | N | 0 | 10M | [23 empty] | N | N | N
Vintage2020 | biomass | TRUE | 20854 | Winnebago County | 50936 | Winnebago County Landfill Gas | WI | Winnebago | EG2R | Landfill Gas | IC |  | S | X | X |  |  | 0.6 | 1 | 0.6 | 0.6 | 0.4 | N |  |  | OP | X | 1 | 2020 |  |  | N | IPP CHP | 3 | X T T T: X; WAT BIT BLQ BIT: LFG |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2000 | biomass | TRUE | 20854 | Winnebago County | 50936 | Winnebago County Landfill Gas | WI | Winnebago | EG3 | Landfill Gas | IC |  | S | X | X |  |  | 0.9 | 1 | 0.9 | 0.9 | 0.7 | N |  |  | OP | X | 2 | 2000 |  |  | N | IPP CHP | 3 | X T T T: X; WAT BIT BLQ BIT: LFG; WAT NG BIT WDS: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage2007 | biomass | TRUE | 20854 | Winnebago County | 50936 | Winnebago County Landfill Gas | WI | Winnebago | EG4 | Landfill Gas | IC |  | S | X | X |  |  | 1 | 1 | 1 | 1 | 0.7 | N |  |  | OP | X | 4 | 2007 |  |  | Y | IPP CHP | 3 | X T T T: T; WAT BIT BLQ BIT: LFG |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2010 | biomass | TRUE | 20854 | Winnebago County | 50936 | Winnebago County Landfill Gas | WI | Winnebago | EG5 | Landfill Gas | IC |  | S | X | X |  |  | 1.4 | 1 | 1.4 | 1.4 | 1 | N |  |  | OP | X | 5 | 2010 |  |  | Y | IPP CHP | 3 | X T T T: T; WAT BIT BLQ BIT: LFG |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1992 | petroleum | FALSE | 20680 | William Beaumont Hospital | 50937 | William Beaumont Hospital | MI | Oakland | GENA | Petroleum Liquids | IC |  | S | X | X |  |  | 1.9 | 0.8 | 1.9 | 1.9 | 0.5 | N |  |  | SB | Y | 10 | 1992 | 9 | 2022 | N | Commercial Non-CHP | 4 | X T T T: X; WAT BIT BLQ BIT: DFO; WAT NG BIT WDS: NG |  |  | N |  |  | 10M | [20 empty] | N |  |  | Y | Y | Y
Vintage1992 | petroleum | FALSE | 20680 | William Beaumont Hospital | 50937 | William Beaumont Hospital | MI | Oakland | GENB | Petroleum Liquids | IC |  | S | X | X |  |  | 1.9 | 0.8 | 1.9 | 1.9 | 0.5 | N |  |  | SB | Y | 10 | 1992 | 9 | 2022 | N | Commercial Non-CHP | 4 | X T T T: X; WAT BIT BLQ BIT: DFO; WAT NG BIT WDS: NG |  |  | N |  |  | 10M | [20 empty] | N |  |  | Y | Y | Y
Vintage1987 | hydro | TRUE | 5187 | Douglas County | 50938 | Galesville Project | OR | Douglas | GV1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.9 | 0.8 | 1 | 0.1 | N |  |  | OP | X | 2 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1987 | hydro | TRUE | 5187 | Douglas County | 50938 | Galesville Project | OR | Douglas | GV2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.9 | 0.8 | 1 | 0.1 | N |  |  | OP | X | 2 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1996 | natural gas peaker | FALSE | 10657 | Lagoon Corp | 50942 | Lagoon Cogeneration Facility | UT | Davis | 1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1 | 0.8 | 0.5 | 0.1 | 0.1 | N |  |  | SB | N | 5 | 1996 |  |  | Y | Commercial CHP | 5 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO |  |  | N | N |  | OVER | [23 empty] | Y | N | N
Vintage1989 | natural gas peaker | FALSE | 10657 | Lagoon Corp | 50942 | Lagoon Cogeneration Facility | UT | Davis | 2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1 | 0.8 | 0.5 | 0.1 | 0.1 | N |  |  | SB | N | 7 | 1989 |  |  | Y | Commercial CHP | 5 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO |  |  | N | N |  | OVER | [23 empty] | Y | N | N
Vintage1989 | natural gas peaker | FALSE | 10657 | Lagoon Corp | 50942 | Lagoon Cogeneration Facility | UT | Davis | 3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1 | 0.8 | 0.5 | 0.1 | 0.1 | N |  |  | SB | N | 7 | 1989 |  |  | Y | Commercial CHP | 5 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO |  |  | N | N |  | OVER | [23 empty] | Y | N | N
Vintage1993 | natural gas combined cycle | TRUE | 49893 | Invenergy Services LLC | 50949 | Hardee Power Station | FL | Hardee | GEN1 | Natural Gas Fired Combined Cycle | CT | CC01 | W | X | Y |  |  | 95.9 | 0.85 | 70 | 85 | 20 | N |  |  | OP | X | 1 | 1993 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1993 | natural gas combined cycle | TRUE | 49893 | Invenergy Services LLC | 50949 | Hardee Power Station | FL | Hardee | GEN2 | Natural Gas Fired Combined Cycle | CT | CC01 | W | X | Y |  |  | 95.9 | 0.85 | 70 | 85 | 20 | N |  |  | OP | X | 1 | 1993 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1993 | natural gas combined cycle | TRUE | 49893 | Invenergy Services LLC | 50949 | Hardee Power Station | FL | Hardee | GEN3 | Natural Gas Fired Combined Cycle | CA | CC01 | W | N | X |  |  | 95.9 | 0.85 | 78 | 85 | 25 | N |  |  | OP | X | 1 | 1993 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO; WAT NG RFO DFO: NG; WAT RFO NG NG: DFO |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1993 | natural gas peaker | TRUE | 49893 | Invenergy Services LLC | 50949 | Hardee Power Station | FL | Hardee | GEN4 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 86.5 | 0.85 | 70 | 84 | 20 | N |  |  | OP | X | 1 | 1993 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2000 | natural gas peaker | TRUE | 49893 | Invenergy Services LLC | 50949 | Hardee Power Station | FL | Hardee | GEN5 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 95.9 | 0.85 | 85 | 85 | 55 | N |  |  | OP | X | 5 | 2000 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1993 | hard coal | TRUE | 21734 | Sunnyside Cogeneration Assoc | 50951 | Sunnyside Cogen Associates | UT | Carbon | GEN1 | Conventional Steam Coal | ST |  | J | X | X |  |  | 58.1 | 0.95 | 51 | 51 | 35 | N |  |  | OP | X | 2 | 1993 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WC; WAT NG RFO DFO: DFO |  |  | N | N |  | 12H | Y |  |  |  | Y | [18 empty] | N | N | N
Vintage1990 | natural gas peaker | FALSE | 16548 | St Francis Hospital | 50952 | Saint Francis Hospital | IL | Cook | GEN1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.1 | N |  |  | OS | X | 2 | 1990 |  |  | Y | Commercial CHP | 5 | [11 empty] | N |  |  | 10M | [23 empty] | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1990 | natural gas peaker | FALSE | 16548 | St Francis Hospital | 50952 | Saint Francis Hospital | IL | Cook | GEN2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.1 | N |  |  | OS | X | 2 | 1990 |  |  | Y | Commercial CHP | 5 | [11 empty] | N |  |  | 10M | [23 empty] | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1947 | natural gas steam turbine | FALSE | 5623 | Rousselot Inc | 50955 | Rousselot Inc | MA | Essex | GEN1 | Natural Gas Steam Turbine | ST |  | S | X | X | LD.BARTH_ST115 | LD.BARTH_ST115 | 1.5 | 1 | 1.5 | 1.5 | 0.4 | N |  |  | SB | Y | 5 | 1947 |  |  | Y | Industrial CHP | 7 | X T T T: B; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: RFO; WAT NG RFO DFO: PG |  |  | N | N |  | 12H |  |  |  |  | N | [18 empty] | Y | N | Y
Vintage1947 | natural gas steam turbine | FALSE | 5623 | Rousselot Inc | 50955 | Rousselot Inc | MA | Essex | GEN2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.4 | N |  |  | SB | Y | 5 | 1947 |  |  | Y | Industrial CHP | 7 | X T T T: B; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: RFO; WAT NG RFO DFO: PG |  |  | N | N |  | 12H |  |  |  |  | N | [18 empty] | Y | N | Y
Vintage1969 | natural gas steam turbine | FALSE | 5623 | Rousselot Inc | 50955 | Rousselot Inc | MA | Essex | GEN3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 3.7 | 0.8 | 3.3 | 3.3 | 0.5 | N |  |  | OP | X | 4 | 1969 |  |  | Y | Industrial CHP | 7 | X T T T: B; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: RFO; WAT NG RFO DFO: PG |  |  | N | N |  | 12H |  |  |  |  | N | [18 empty] | Y | N | Y
Vintage1954 | biomass | TRUE | 23931 | Resolute Forest Products | 50956 | Bowater Newsprint Calhoun Operation | TN | McMinn | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 19 | 0.95 | 17 | 17 | 2 | N |  |  | OP | X | 5 | 1954 |  |  | Y | Industrial CHP | 7 | B | BLQ | NG | WDS | TDF | SLW |  | BLQ |  |  |  | N | N |  | 12H | N | N |  |  | N | N | N | [16 empty] | Y | Y | N
Vintage1954 | biomass | TRUE | 23931 | Resolute Forest Products | 50956 | Bowater Newsprint Calhoun Operation | TN | McMinn | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 19.2 | 0.95 | 19 | 19 | 2 | N |  |  | OP | X | 7 | 1954 |  |  | Y | Industrial CHP | 7 | B | BLQ | NG | WDS | TDF | SLW |  | BLQ |  |  |  | N | N |  | 12H | N | N |  |  | N | N | N | [16 empty] | Y | Y | N
Vintage1957 | biomass | TRUE | 23931 | Resolute Forest Products | 50956 | Bowater Newsprint Calhoun Operation | TN | McMinn | GEN3 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 25 | 0.95 | 27 | 27 | 2 | N |  |  | OP | X | 7 | 1957 |  |  | Y | Industrial CHP | 7 | B | BLQ | NG | WDS | TDF | SLW |  | BLQ |  |  |  | N | N |  | 12H | N | N |  |  | N | N | N | [16 empty] | Y | Y | N
Vintage1994 | municipal solid waste | FALSE | 4440 | Covanta Union Operations LLC | 50960 | Union County Resource Recovery | NJ | Union | GEN1 | Municipal Solid Waste | ST |  | W | X | X |  |  | 45 | 0.9 | 37.5 | 38.5 | 18 | N |  |  | OP | X | 2 | 1994 |  |  | N | Commercial Non-CHP | 4 | X T T T: X; WAT BIT BLQ BIT: MSW; WAT NG RFO DFO: NG |  |  | N | N |  | 12H | [23 empty] | N
Vintage1990 | hydro | TRUE | 64078 | Central Rivers Power US, LLC | 50961 | Slate Creek | CA | Shasta | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.2 | 1 | 4 | 3.9 | 0.1 | N |  |  | OP | X | 5 | 1990 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  |  |  | 0 | 10M
Vintage2003 | natural gas peaker | FALSE | 2844 | Department of the Navy | 50963 | Naval Hospital Medical Center | CA | San Diego | 4TG | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 5.3 | 0.97 | 4.4 | 4.4 | 2.7 | N |  |  | OP | X | 12 | 2003 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1988 | geothermal | TRUE | 472 | Amedee Gethrm Venture I LP | 50964 | Amedee Geothermal Venture I | CA | Lassen | IND | Geothermal | ST |  | S | X | X |  |  | 1.5 | 1 | 1.1 | 0.7 | 0.1 | N |  |  | OP | X | 8 | 1988 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: GEO; WAT NG RFO DFO: GEO | [5 empty] | 1H | [23 empty] | N
Vintage1988 | geothermal | TRUE | 472 | Amedee Gethrm Venture I LP | 50964 | Amedee Geothermal Venture I | CA | Lassen | SYN | Geothermal | ST |  | S | X | X |  |  | 1.5 | 1 | 1.1 | 0.7 | 0.1 | N |  |  | OP | X | 8 | 1988 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: GEO; WAT NG RFO DFO: GEO | [5 empty] | 1H | [23 empty] | N
Vintage1986 | petroleum | FALSE | 18323 | Toledo Refining Company | 50965 | Toledo Ref Power Recovery Train | OH | Lucas | GEN1 | Petroleum Coke | OT |  | S | X | X |  |  | 6 | 0.922 | 6 | 6 | 0 | N |  |  | OP | X | 6 | 1986 |  |  | Y | Industrial CHP | 7 | X T T T: B; WAT BIT BLQ BIT: PC; WAT NG BIT WDS: OG; WAT WDS WDS RFO: NG |  |  | N | N | [5 empty] | Y | Y | [18 empty] | Y | Y | N
Vintage2017 | natural gas steam turbine | FALSE | 34359 | Curators of the University of Missouri | 50969 | MU Combined Heat and Power Plant | MO | Boone | 6025 | Natural Gas Steam Turbine | ST |  | S | X | X | CWLD.UMC |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 12 | 2017 |  |  | Y | Commercial CHP | 5 | B | NG | WDS | DFO | BIT |  |  | NG |  |  |  | N | N |  | 1H |  |  | Y |  | Y | [18 empty] | Y | Y | Y
Vintage2002 | petroleum | FALSE | 34359 | Curators of the University of Missouri | 50969 | MU Combined Heat and Power Plant | MO | Boone | DGT1 | Petroleum Liquids | IC |  | S | X | X | CWLD.UMC |  | 2 | 0.8 | 2 | 2 | 1 | N |  |  | SB | Y | 9 | 2002 |  |  | N | Commercial CHP | 5 | X T T T: X; WAT BIT BLQ BIT: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1961 | natural gas steam turbine | FALSE | 34359 | Curators of the University of Missouri | 50969 | MU Combined Heat and Power Plant | MO | Boone | GEN1 | Natural Gas Steam Turbine | ST |  | S | X | X | CWLD.UMC |  | 6.2 | 0.8 | 6 | 6.1 | 2 | N |  |  | OP | X | 7 | 1961 |  |  | Y | Commercial CHP | 5 | T | NG | WDS | DFO | BIT |  |  | NG |  |  |  | N | N |  | 12H | N |  | Y |  | Y | [18 empty] | Y | Y | Y
Vintage1974 | natural gas steam turbine | FALSE | 34359 | Curators of the University of Missouri | 50969 | MU Combined Heat and Power Plant | MO | Boone | GEN2 | Natural Gas Steam Turbine | ST |  | S | X | X | CWLD.UMC |  | 12.5 | 0.8 | 12.2 | 12.3 | 3 | N |  |  | OP | X | 7 | 1974 |  |  | Y | Commercial CHP | 5 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO; WAT WDS WDS RFO: BIT; WAT NG RFO DFO: NG |  |  | N | N |  | 12H | N |  | Y |  | Y | [18 empty] | Y | Y | Y
Vintage1986 | natural gas steam turbine | FALSE | 34359 | Curators of the University of Missouri | 50969 | MU Combined Heat and Power Plant | MO | Boone | GEN3 | Natural Gas Steam Turbine | ST |  | S | X | X | CWLD.UMC |  | 19.8 | 0.85 | 19.2 | 19.4 | 3 | N |  |  | OP | X | 8 | 1986 |  |  | Y | Commercial CHP | 5 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO; WAT WDS WDS RFO: BIT; WAT NG RFO DFO: NG |  |  | N | N |  | 12H | N |  | Y |  | Y | [18 empty] | Y | Y | Y
Vintage1988 | natural gas steam turbine | FALSE | 34359 | Curators of the University of Missouri | 50969 | MU Combined Heat and Power Plant | MO | Boone | GEN4 | Natural Gas Steam Turbine | ST |  | S | X | X | CWLD.UMC |  | 14.5 | 0.85 | 13.3 | 13.4 | 3 | N |  |  | OP | X | 7 | 1988 |  |  | Y | Commercial CHP | 5 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO; WAT WDS WDS RFO: BIT; WAT NG RFO DFO: NG |  |  | N | N |  | 12H | N |  | Y |  | Y | [18 empty] | Y | Y | Y
Vintage1994 | petroleum | FALSE | 34359 | Curators of the University of Missouri | 50969 | MU Combined Heat and Power Plant | MO | Boone | GEN6 | Petroleum Liquids | IC |  | S | X | X | CWLD.UMC |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.3 | N |  |  | SB | Y | 5 | 1994 |  |  | N | Commercial CHP | 5 | X T T T: X; WAT BIT BLQ BIT: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1997 | petroleum | FALSE | 34359 | Curators of the University of Missouri | 50969 | MU Combined Heat and Power Plant | MO | Boone | GEN7 | Petroleum Liquids | IC |  | S | X | X | CWLD.UMC |  | 1 | 0.8 | 1 | 1 | 0.5 | N |  |  | SB | Y | 6 | 1997 |  |  | N | Commercial CHP | 5 | X T T T: X; WAT BIT BLQ BIT: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage2002 | natural gas peaker | FALSE | 34359 | Curators of the University of Missouri | 50969 | MU Combined Heat and Power Plant | MO | Boone | NTG1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | CWLD.UMC |  | 17.3 | 0.8 | 11.4 | 14.5 | 2 | N |  |  | OP | X | 9 | 2002 |  |  | Y | Commercial CHP | 5 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2002 | natural gas peaker | FALSE | 34359 | Curators of the University of Missouri | 50969 | MU Combined Heat and Power Plant | MO | Boone | NTG2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | CWLD.UMC |  | 17.3 | 0.8 | 11.4 | 14.5 | 2 | N |  |  | OP | X | 9 | 2002 |  |  | Y | Commercial CHP | 5 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1990 | natural gas peaker | FALSE | 19216 | Tropicana Products Inc | 50971 | Tropicana Products Bradent | FL | Manatee | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 46.8 | 0.85 | 31 | 35 | 10 | N |  |  | OP | X | 2 | 1990 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1993 | hydro | TRUE | 11716 | Marsh Valley Development Inc | 50972 | Marsh Valley Development | ID | Bannock | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 1 | 1.5 | 1.5 | 0.1 | N |  |  | OP | X | 4 | 1993 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  |  |  | 0 | 10M
Vintage1962 | natural gas combined cycle | FALSE | 12981 | Motiva Enterprises LLC | 50973 | Motiva Enterprises Port Arthur Refinery | TX | Jefferson | GN31 | Natural Gas Fired Combined Cycle | CA | BLK1 | S | Y | X |  |  | 10 | 0.8 | 8.4 | 8.6 | 3 | N |  |  | OP | X | 6 | 1962 |  |  | Y | Industrial CHP | 7 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: OG |  |  | N | N |  | 12H | [23 empty] | N
Vintage1957 | natural gas combined cycle | FALSE | 12981 | Motiva Enterprises LLC | 50973 | Motiva Enterprises Port Arthur Refinery | TX | Jefferson | GN32 | Natural Gas Fired Combined Cycle | CA | BLK1 | S | Y | X |  |  | 15.6 | 0.8 | 10.5 | 10.7 | 3 | N |  |  | OP | X | 6 | 1957 |  |  | Y | Industrial CHP | 7 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: OG |  |  | N | N |  | 12H | [23 empty] | N
Vintage1978 | natural gas combined cycle | FALSE | 12981 | Motiva Enterprises LLC | 50973 | Motiva Enterprises Port Arthur Refinery | TX | Jefferson | GN33 | Natural Gas Fired Combined Cycle | CA | BLK1 | S | Y | X |  |  | 25.5 | 0.8 | 21.5 | 22 | 3 | N |  |  | OP | X | 6 | 1978 |  |  | Y | Industrial CHP | 7 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: OG |  |  | N | N |  | 12H | [23 empty] | N
Vintage1970 | natural gas peaker | FALSE | 12981 | Motiva Enterprises LLC | 50973 | Motiva Enterprises Port Arthur Refinery | TX | Jefferson | GN34 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 18.8 | 0.8 | 15.6 | 16 | 3 | N |  |  | OP | X | 6 | 1970 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1983 | natural gas combined cycle | FALSE | 12981 | Motiva Enterprises LLC | 50973 | Motiva Enterprises Port Arthur Refinery | TX | Jefferson | GN35 | Natural Gas Fired Combined Cycle | CT | BLK1 | S | X | N |  |  | 40.5 | 0.85 | 39 | 38 | 3 | N |  |  | OP | X | 12 | 1983 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X T T T to WAT BIT BLQ BIT
Vintage2011 | natural gas combined cycle | FALSE | 12981 | Motiva Enterprises LLC | 50973 | Motiva Enterprises Port Arthur Refinery | TX | Jefferson | GN41 | Natural Gas Fired Combined Cycle | CT | BLK1 | S | X | N |  |  | 41.6 | 0.85 | 36.1 | 46.4 | 3 | N |  |  | OP | X | 12 | 2011 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X T T T to WAT BIT BLQ BIT
Vintage2011 | natural gas combined cycle | FALSE | 12981 | Motiva Enterprises LLC | 50973 | Motiva Enterprises Port Arthur Refinery | TX | Jefferson | GN42 | Natural Gas Fired Combined Cycle | CT | BLK1 | S | X | N |  |  | 41.6 | 0.85 | 36.1 | 46.4 | 3 | N |  |  | OP | X | 11 | 2011 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X T T T to WAT BIT BLQ BIT
Vintage2011 | natural gas combined cycle | FALSE | 12981 | Motiva Enterprises LLC | 50973 | Motiva Enterprises Port Arthur Refinery | TX | Jefferson | GN43 | Natural Gas Fired Combined Cycle | CT | BLK1 | S | X | N |  |  | 41.6 | 0.85 | 36.1 | 46.4 | 3 | N |  |  | OP | X | 11 | 2011 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X T T T to WAT BIT BLQ BIT
Vintage2011 | natural gas combined cycle | FALSE | 12981 | Motiva Enterprises LLC | 50973 | Motiva Enterprises Port Arthur Refinery | TX | Jefferson | GN44 | Natural Gas Fired Combined Cycle | CT | BLK1 | S | X | N |  |  | 41.6 | 0.85 | 36.1 | 46.4 | 3 | N |  |  | OP | X | 10 | 2011 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1993 | hard coal | TRUE | 16814 | Scrubgrass Reclamation CO. LP. | 50974 | Scrubgrass Reclamation CO. LP. | PA | Venango | GEN1 | Conventional Steam Coal | ST |  | S | X | X | 50789 Scrubgrs-13kv-gen | 50789 scrubgrs-13kv-gen | 94.7 | 0.85 | 83.2 | 85.9 | 0 | N |  |  | OP | X | 6 | 1993 |  |  | N | IPP Non-CHP | 2 | X | WC | BIT | SUB | WDS |  |  | DFO | BIT |  |  | N | N | 0 | OVER | Y |  |  |  | Y | [18 empty] | N | N | N
Vintage1993 | natural gas combined cycle | TRUE | 24202 | Carr Street Generating Sta LP | 50978 | Carr Street Generating Station | NY | Onondaga | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N | PTID 24060 | PTID 24060 | 48.8 | 0.85 | 35 | 40 | 16 | N |  |  | OP | X | 7 | 1993 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1993 | natural gas combined cycle | TRUE | 24202 | Carr Street Generating Sta LP | 50978 | Carr Street Generating Station | NY | Onondaga | GEN2 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N | PTID 24060 | PTID 24060 | 48.8 | 0.85 | 35 | 40 | 16 | N |  |  | OP | X | 7 | 1993 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1993 | natural gas combined cycle | TRUE | 24202 | Carr Street Generating Sta LP | 50978 | Carr Street Generating Station | NY | Onondaga | GEN3 | Natural Gas Fired Combined Cycle | CA | CC1 | W | N | X | PTID 24060 | PTID 24060 | 25 | 0.9 | 23 | 25 | 10 | N |  |  | OP | X | 7 | 1993 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1989 | hydro | TRUE | 3220 | Central Oregon Irrigation Dist | 50980 | Siphon Power Project | OR | Deschutes | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.7 | 0.9 | 2.7 | 2.7 | 0.8 | N |  |  | OP | X | 8 | 1989 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  | N | N |  | 10M
Vintage1989 | hydro | TRUE | 3220 | Central Oregon Irrigation Dist | 50980 | Siphon Power Project | OR | Deschutes | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.7 | 0.9 | 2.7 | 2.7 | 0.8 | N |  |  | OP | X | 8 | 1989 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  | N | N |  | 10M
Vintage1989 | natural gas peaker | FALSE | 17711 | Solano County | 50985 | Solano County Cogen Plant | CA | Solano | 3163 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1 | 1 | 1 | 1 | 0.5 | N |  |  | OP | X | 6 | 1989 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1989 | natural gas peaker | FALSE | 17711 | Solano County | 50985 | Solano County Cogen Plant | CA | Solano | 3164 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.4 | 1 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 6 | 1989 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage2004 | natural gas peaker | FALSE | 17711 | Solano County | 50985 | Solano County Cogen Plant | CA | Solano | 3165 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.4 | 1 | 1.4 | 1 | 0.7 | N |  |  | OP | X | 12 | 2004 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1983 | hydro | TRUE | 17150 | Shorock Hydro Inc | 50987 | Rock Creek I | ID | Twin Falls | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.1 | 0.8 | 2 | 1 | 0.2 | N |  |  | OP | X | 9 | 1983 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  |  |  | 0 | 10M
Vintage1987 | biomass | TRUE | 3930 | Co-Gen II | 50993 | Co-Gen II LLC | OR | Douglas | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 7.5 | 0.9 | 7.8 | 7.3 | 4 | N |  |  | SB | Y | 10 | 1987 |  |  | Y | IPP CHP | 3 | X T T T: T; WAT BIT BLQ BIT: WDS; WAT NG BIT WDS: NG; WAT NG RFO DFO: WDS |  |  | N | N |  | OVER | [23 empty] | N |  | N
Vintage1988 | hydro | TRUE | 39006 | Brookfield White Pine Hydro LLC | 50999 | Aziscohos Hydroelectric Project | ME | Oxford | GEN1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 6.7 | 0.9 | 6.8 | 6.8 | 0.1 | N |  |  | OP | X | 6 | 1988 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT | [5 empty] | 10M
Vintage1981 | biomass | TRUE | 11415 | M.A. Patout & Son Limited, LLC | 51008 | Enterprise Sugar Factory | LA | Iberia | 1000 | Other Waste Biomass | ST |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0 | N |  |  | OP | X | 10 | 1981 |  |  | Y | Industrial CHP | 7 | X T T T: T; WAT BIT BLQ BIT: AB; WAT NG BIT WDS: NG; WAT NG RFO DFO: AB; WAT RFO NG NG: NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1981 | biomass | TRUE | 11415 | M.A. Patout & Son Limited, LLC | 51008 | Enterprise Sugar Factory | LA | Iberia | 2000 | Other Waste Biomass | ST |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0 | N |  |  | SB | N | 10 | 1981 |  |  | Y | Industrial CHP | 7 | X T T T: T; WAT BIT BLQ BIT: AB; WAT NG BIT WDS: NG; WAT NG RFO DFO: AB; WAT RFO NG NG: NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1992 | biomass | TRUE | 64003 | Stored Solar Services, LLC | 51026 | Ryegate Associates, LLC | VT | CALEDONIA | GEN1 | Wood/Wood Waste Biomass | ST |  | W | X | X |  |  | 21.5 | 1 | 20 | 20 | 13.2 | N |  |  | OP | X | 9 | 1992 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WDS; WAT NG RFO DFO: WDS |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1990 | natural gas combined cycle | TRUE | 27769 | Ocean State Power Co | 51030 | Ocean State Power | RI | Providence | GEN1 | Natural Gas Fired Combined Cycle | CT | OSP1 | S | X | N | UN.OCEAN_ST13.8OSP1 | UN.OCEAN_ST13.8OSP1 | 82.8 | 0.85 | 71.2 | 77.8 | 45 | N |  |  | OP | X | 12 | 1990 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1990 | natural gas combined cycle | TRUE | 27769 | Ocean State Power Co | 51030 | Ocean State Power | RI | Providence | GEN2 | Natural Gas Fired Combined Cycle | CT | OSP1 | S | X | N | UN.OCEAN_ST13.8OSP1 | UN.OCEAN_ST13.8OSP1 | 82.8 | 0.85 | 71.2 | 77.8 | 45 | N |  |  | OP | X | 12 | 1990 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1990 | natural gas combined cycle | TRUE | 27769 | Ocean State Power Co | 51030 | Ocean State Power | RI | Providence | GEN3 | Natural Gas Fired Combined Cycle | CA | OSP1 | S | Y | X | UN.OCEAN_ST13.8OSP1 | UN.OCEAN_ST13.8OSP1 | 88.6 | 0.85 | 76.2 | 83.3 | 38 | N |  |  | OP | X | 12 | 1990 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO |  |  | N | N |  | 12H | [23 empty] | N |  | N
Vintage1988 | hydro | TRUE | 5914 | Erie Boulevard Hydropower LP | 51033 | West Delaware Tunnel Plant | NY | Sullivan | GEN1 | Conventional Hydroelectric | HY |  | S | X | X | 323627 | 323627 | 7.5 | 0.8 | 7 | 7.6 | 5 | N |  |  | OP | X | 12 | 1988 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  | N |  | 0 | 10M
Vintage1987 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 51034 | Little Falls Hydro | NY | Herkimer | GEN1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 6.5 | 0.9 | 6.5 | 6.5 | 0.8 | N |  |  | OP | X | 1 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  | N |  | 0 | 1H
Vintage1987 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 51034 | Little Falls Hydro | NY | Herkimer | GEN2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 6.5 | 0.9 | 6.5 | 6.5 | 0.8 | N |  |  | OP | X | 1 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  | N |  | 0 | 1H
Vintage1990 | municipal solid waste | FALSE | 56601 | Covanta MacArthur Renewable Energy | 51038 | MacArthur Waste to Energy Facility | NY | Suffolk | GEN1 | Municipal Solid Waste | ST |  | W | X | X | 323679 | NYISO | 12.5 | 1 | 11 | 11 | 1 | N |  |  | OP | X | 3 | 1990 |  |  | N | Commercial Non-CHP | 4 | X T T T: X; WAT BIT BLQ BIT: MSW; WAT NG RFO DFO: NG |  |  | N | N |  | 12H | [23 empty] | N
Vintage1958 | natural gas combined cycle | FALSE | 5347 | Dow Chemical Co | 52006 | LaO Energy Systems | LA | Iberville | GEN1 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | EES,DOWCHEM | EES,DOWCHEM | 57 | 0.85 | 57 | 57 | 8 | N |  |  | OP | X | 6 | 1958 |  |  | Y | Industrial CHP | 7 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: OG; WAT WDS WDS RFO: OTH |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1962 | natural gas combined cycle | FALSE | 5347 | Dow Chemical Co | 52006 | LaO Energy Systems | LA | Iberville | GEN2 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | EES,DOWCHEM | EES,DOWCHEM | 88 | 0.85 | 80 | 80 | 22 | N |  |  | OP | X | 6 | 1962 |  |  | Y | Industrial CHP | 7 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: OG; WAT WDS WDS RFO: OTH |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1966 | natural gas combined cycle | FALSE | 5347 | Dow Chemical Co | 52006 | LaO Energy Systems | LA | Iberville | GEN3 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | EES,DOWCHEM | EES,DOWCHEM | 90 | 0.85 | 94 | 94 | 13 | N |  |  | OP | X | 6 | 1966 |  |  | Y | Industrial CHP | 7 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: OG; WAT WDS WDS RFO: OTH |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1969 | natural gas combined cycle | FALSE | 5347 | Dow Chemical Co | 52006 | LaO Energy Systems | LA | Iberville | GEN4 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | EES,DOWCHEM | EES,DOWCHEM | 76.5 | 0.9 | 49 | 49 | 3 | N |  |  | OP | X | 6 | 1969 |  |  | Y | Industrial CHP | 7 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: OG; WAT WDS WDS RFO: OTH |  |  | N | N |  | 12H | [23 empty] | N
Vintage1978 | natural gas combined cycle | FALSE | 5347 | Dow Chemical Co | 52006 | LaO Energy Systems | LA | Iberville | GEN5 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | EES,DOWCHEM | EES,DOWCHEM | 76.5 | 0.9 | 52 | 65 | 45 | N |  |  | OP | X | 11 | 1978 |  |  | Y | Industrial CHP | 7 | [11 empty] | N |  |  | 12H | [23 empty] | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1979 | natural gas combined cycle | FALSE | 5347 | Dow Chemical Co | 52006 | LaO Energy Systems | LA | Iberville | GEN6 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | EES,DOWCHEM | EES,DOWCHEM | 76.5 | 0.9 | 52 | 65 | 45 | N |  |  | OP | X | 2 | 1979 |  |  | Y | Industrial CHP | 7 | [11 empty] | N |  |  | 12H | [23 empty] | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1994 | municipal solid waste | TRUE | 10875 | Lee County Board-Commissioners | 52010 | Lee County Solid Waste Energy | FL | Lee | GEN1 | Municipal Solid Waste | ST |  | S | X | X |  |  | 39 | 0.85 | 39 | 39 | 19 | N |  |  | OP | X | 9 | 1994 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: MSW; WAT NG RFO DFO: PG |  |  | N | N |  | 12H | [20 empty] | N |  |  | N | N | N
Vintage2007 | municipal solid waste | TRUE | 10875 | Lee County Board-Commissioners | 52010 | Lee County Solid Waste Energy | FL | Lee | GEN2 | Municipal Solid Waste | ST |  | S | X | X |  |  | 20 | 0.85 | 16 | 16 | 10 | N |  |  | OP | X | 8 | 2007 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: MSW; WAT NG RFO DFO: PG |  |  | N | N |  | 12H | [20 empty] | N |  |  | N | N | N
Vintage1988 | geothermal | TRUE | 34691 | Ormat Nevada Inc | 52015 | Dixie Valley | NV | Churchill | GEN1 | Geothermal | ST |  | S | X | X | CONTRL_1_OXBOW | CONTRL_1_OXBOW | 64.7 | 0.963 | 56 | 57 | 5 | N |  |  | OP | X | 6 | 1988 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: GEO; WAT NG RFO DFO: GEO |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2012 | geothermal | TRUE | 34691 | Ormat Nevada Inc | 52015 | Dixie Valley | NV | Churchill | GEN2 | Geothermal | BT |  | S | X | X | CONTRL_1_OXBOW | CONTRL_1_OXBOW | 6.2 | 0.8 | 2.5 | 5.1 | 1 | N |  |  | OP | X | 4 | 2012 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: GEO; WAT NG RFO DFO: GEO |  |  | N | N |  | 12H | [23 empty] | N
Vintage1991 | natural gas combined cycle | TRUE | 5310 | Doswell Ltd Partnership | 52019 | Doswell Energy Center | VA | Hanover | GEN1 | Natural Gas Fired Combined Cycle | CT | UNT5 | S | X | N | 71856749 | 71856749 | 122 | 0.85 | 104.7 | 122 | 73.3 | N |  |  | OP | X | 11 | 1991 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1991 | natural gas combined cycle | TRUE | 5310 | Doswell Ltd Partnership | 52019 | Doswell Energy Center | VA | Hanover | GEN2 | Natural Gas Fired Combined Cycle | CT | UNT5 | S | X | N | 71856749 | 71856749 | 122 | 0.85 | 104.7 | 122 | 73.3 | N |  |  | OP | X | 12 | 1991 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1991 | natural gas combined cycle | TRUE | 5310 | Doswell Ltd Partnership | 52019 | Doswell Energy Center | VA | Hanover | GEN3 | Natural Gas Fired Combined Cycle | CA | UNT5 | S | Y | X | 71856749 | 71856749 | 132 | 0.9 | 123 | 132 | 28.7 | N |  |  | OP | X | 12 | 1991 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1992 | natural gas combined cycle | TRUE | 5310 | Doswell Ltd Partnership | 52019 | Doswell Energy Center | VA | Hanover | GEN4 | Natural Gas Fired Combined Cycle | CT | UNT6 | S | X | N | 71856755 | 71856755 | 122 | 0.85 | 104.7 | 122 | 73.3 | N |  |  | OP | X | 1 | 1992 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1992 | natural gas combined cycle | TRUE | 5310 | Doswell Ltd Partnership | 52019 | Doswell Energy Center | VA | Hanover | GEN5 | Natural Gas Fired Combined Cycle | CT | UNT6 | S | X | N | 71856755 | 71856755 | 122 | 0.85 | 104.7 | 122 | 73.3 | N |  |  | OP | X | 1 | 1992 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1992 | natural gas combined cycle | TRUE | 5310 | Doswell Ltd Partnership | 52019 | Doswell Energy Center | VA | Hanover | GEN6 | Natural Gas Fired Combined Cycle | CA | UNT6 | S | Y | X | 71856755 | 71856755 | 132 | 0.9 | 123 | 132 | 28.7 | N |  |  | OP | X | 1 | 1992 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage2001 | natural gas peaker | TRUE | 5310 | Doswell Ltd Partnership | 52019 | Doswell Energy Center | VA | Hanover | GEN7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 71856761 | 71856761 | 187 | 0.9 | 170 | 188 | 74.5 | N |  |  | OP | X | 3 | 2001 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2018 | natural gas peaker | TRUE | 5310 | Doswell Ltd Partnership | 52019 | Doswell Energy Center | VA | Hanover | GEN8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 1379268472 | 1379268472 | 187 | 0.9 | 165 | 188 | 90 | N |  |  | OP | X | 3 | 2018 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage2018 | natural gas peaker | TRUE | 5310 | Doswell Ltd Partnership | 52019 | Doswell Energy Center | VA | Hanover | GEN9 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 1379268471 | 1379268471 | 187 | 0.9 | 165 | 188 | 90 | N |  |  | OP | X | 4 | 2018 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1991 | natural gas peaker | FALSE | 29767 | Illinois Institute-Technology | 52021 | ITT Cogen Facility | IL | Cook | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 33092313 | 33092313 | 3.7 | 0.8 | 3.5 | 3.7 | 0.1 | N |  |  | SB | Y | 5 | 1991 |  |  | Y | Commercial CHP | 5 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO; WAT NG RFO DFO: NG |  |  | N | N | 0 | 1H | [23 empty] | Y | N | Y
Vintage1991 | natural gas peaker | FALSE | 29767 | Illinois Institute-Technology | 52021 | ITT Cogen Facility | IL | Cook | GEN2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 33092313 | 33092313 | 3.7 | 0.8 | 3.5 | 3.7 | 0.1 | N |  |  | SB | Y | 5 | 1991 |  |  | Y | Commercial CHP | 5 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO; WAT NG RFO DFO: NG |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1974 | natural gas steam turbine | FALSE | 16001 | Rhode Island Hospital | 52024 | Rhode Island Hospital | RI | Providence | GEN2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 1.7 | 0.8 | 1.7 | 1.7 | 0.3 | N |  |  | OP | X | 10 | 1974 |  |  | Y | Commercial CHP | 5 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: RFO; WAT NG RFO DFO: NG |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1974 | natural gas steam turbine | FALSE | 16001 | Rhode Island Hospital | 52024 | Rhode Island Hospital | RI | Providence | GEN4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 1.7 | 0.8 | 1.7 | 1.7 | 0.3 | N |  |  | OP | X | 10 | 1974 |  |  | Y | Commercial CHP | 5 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: RFO; WAT NG RFO DFO: NG |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | N | Y
Vintage1993 | natural gas steam turbine | FALSE | 16001 | Rhode Island Hospital | 52024 | Rhode Island Hospital | RI | Providence | NEW1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 3.5 | 0.8 | 3.5 | 3.5 | 0.3 | N |  |  | OP | X | 12 | 1993 |  |  | Y | Commercial CHP | 5 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: RFO; WAT NG RFO DFO: NG |  |  | N | N |  | 12H | [20 empty] | N |  |  | Y | N | Y
Vintage1993 | natural gas steam turbine | FALSE | 16001 | Rhode Island Hospital | 52024 | Rhode Island Hospital | RI | Providence | NEW3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 3.5 | 0.8 | 3.5 | 3.5 | 0.3 | N |  |  | OP | X | 9 | 1993 |  |  | Y | Commercial CHP | 5 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: RFO; WAT NG RFO DFO: NG |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1992 | natural gas combined cycle | TRUE | 56516 | Morris Energy Operations Company, LLC | 52026 | Dartmouth Power Associates LP | MA | Bristol | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N | 388 | 388 | 41.9 | 0.9 | 62.1 | 67.7 | 24 | N |  |  | OP | X | 3 | 1992 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1992 | natural gas combined cycle | TRUE | 56516 | Morris Energy Operations Company, LLC | 52026 | Dartmouth Power Associates LP | MA | Bristol | GEN2 | Natural Gas Fired Combined Cycle | CA | CC1 | W | Y | X | 388 | 388 | 32.2 | 0.9 |  |  | 12 | N |  |  | OP | X | 3 | 1992 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2009 | natural gas peaker | TRUE | 56516 | Morris Energy Operations Company, LLC | 52026 | Dartmouth Power Associates LP | MA | Bristol | GEN3 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X | 15940 | 15940 | 23.3 | 0.85 | 19.6 | 21.8 | 19 | N |  |  | OP | X | 9 | 2009 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1992 | geothermal | TRUE | 3608 | Puna Geothermal Venture | 52028 | Puna Geothermal Venture I | HI | Hawaii | OEC11 | Geothermal | ST |  | S | X | X |  |  | 3.5 | 0.8 | 3.1 | 3.1 | 0.5 | N |  |  | OP | X | 8 | 1992 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: GEO; WAT NG RFO DFO: GEO |  |  | N |  |  | OVER | [23 empty] | N
Vintage1992 | geothermal | TRUE | 3608 | Puna Geothermal Venture | 52028 | Puna Geothermal Venture I | HI | Hawaii | OEC12 | Geothermal | ST |  | S | X | X |  |  | 3.5 | 0.8 | 3.1 | 3.1 | 0.5 | N |  |  | OP | X | 8 | 1992 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: GEO; WAT NG RFO DFO: GEO |  |  | N |  |  | OVER | [23 empty] | N
Vintage1992 | geothermal | TRUE | 3608 | Puna Geothermal Venture | 52028 | Puna Geothermal Venture I | HI | Hawaii | OEC13 | Geothermal | ST |  | S | X | X |  |  | 3.5 | 0.8 | 3.1 | 3.1 | 0.5 | N |  |  | OP | X | 8 | 1992 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: GEO; WAT NG RFO DFO: GEO |  |  | N |  |  | OVER | [23 empty] | N
Vintage1992 | geothermal | TRUE | 3608 | Puna Geothermal Venture | 52028 | Puna Geothermal Venture I | HI | Hawaii | OEC14 | Geothermal | ST |  | S | X | X |  |  | 3.5 | 0.8 | 3.1 | 3.1 | 0.5 | N |  |  | OP | X | 8 | 1992 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: GEO; WAT NG RFO DFO: GEO |  |  | N |  |  | OVER | [23 empty] | N
Vintage1992 | geothermal | TRUE | 3608 | Puna Geothermal Venture | 52028 | Puna Geothermal Venture I | HI | Hawaii | OEC15 | Geothermal | ST |  | S | X | X |  |  | 3.5 | 0.8 | 3.1 | 3.1 | 0.5 | N |  |  | OP | X | 8 | 1992 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: GEO; WAT NG RFO DFO: GEO |  |  | N |  |  | OVER | [23 empty] | N
Vintage1992 | geothermal | TRUE | 3608 | Puna Geothermal Venture | 52028 | Puna Geothermal Venture I | HI | Hawaii | OEC21 | Geothermal | ST |  | S | X | X |  |  | 3.5 | 0.8 | 3.1 | 3.1 | 0.5 | N |  |  | OP | X | 8 | 1992 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: GEO; WAT NG RFO DFO: GEO |  |  | N |  |  | OVER | [23 empty] | N
Vintage1992 | geothermal | TRUE | 3608 | Puna Geothermal Venture | 52028 | Puna Geothermal Venture I | HI | Hawaii | OEC22 | Geothermal | ST |  | S | X | X |  |  | 3.5 | 0.8 | 3.1 | 3.1 | 0.5 | N |  |  | OP | X | 8 | 1992 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: GEO; WAT NG RFO DFO: GEO |  |  | N |  |  | OVER | [23 empty] | N
Vintage1992 | geothermal | TRUE | 3608 | Puna Geothermal Venture | 52028 | Puna Geothermal Venture I | HI | Hawaii | OEC23 | Geothermal | ST |  | S | X | X |  |  | 3.5 | 0.8 | 3.1 | 3.1 | 0.5 | N |  |  | OP | X | 8 | 1992 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: GEO; WAT NG RFO DFO: GEO |  |  | N |  |  | OVER | [23 empty] | N
Vintage1992 | geothermal | TRUE | 3608 | Puna Geothermal Venture | 52028 | Puna Geothermal Venture I | HI | Hawaii | OEC24 | Geothermal | ST |  | S | X | X |  |  | 3.5 | 0.8 | 3.1 | 3.1 | 0.5 | N |  |  | OP | X | 8 | 1992 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: GEO; WAT NG RFO DFO: GEO |  |  | N |  |  | OVER | [23 empty] | N
Vintage1992 | geothermal | TRUE | 3608 | Puna Geothermal Venture | 52028 | Puna Geothermal Venture I | HI | Hawaii | OEC25 | Geothermal | ST |  | S | X | X |  |  | 3.5 | 0.8 | 3.1 | 3.1 | 0.5 | N |  |  | OP | X | 8 | 1992 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: GEO; WAT NG RFO DFO: GEO |  |  | N |  |  | OVER | [23 empty] | N
Vintage2012 | geothermal | TRUE | 3608 | Puna Geothermal Venture | 52028 | Puna Geothermal Venture I | HI | Hawaii | OEC31 | Geothermal | BT |  | S | X | X |  |  | 8 | 0.8 | 6 | 6 | 0.5 | N |  |  | OP | X | 2 | 2012 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: GEO; WAT NG RFO DFO: GEO |  |  | N |  |  | OVER | [23 empty] | N
Vintage2012 | geothermal | TRUE | 3608 | Puna Geothermal Venture | 52028 | Puna Geothermal Venture I | HI | Hawaii | OEC32 | Geothermal | BT |  | S | X | X |  |  | 8 | 0.8 | 6 | 6 | 0.5 | N |  |  | OP | X | 2 | 2012 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: GEO; WAT NG RFO DFO: GEO |  |  | N |  |  | OVER | [23 empty] | N
Vintage1989 | hydro | TRUE | 59092 | Ampersand Moretown Hydro LLC | 52033 | Moretown Generating Station | VT | Washington | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 1 | 0.3 | 0.1 | 0.1 | N |  |  | OS | X | 1 | 1989 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  | N | N |  | 10M
Vintage1989 | hydro | TRUE | 4713 | D/R Hydro Co | 52036 | Yough Hydro Power | PA | Somerset | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.1 | 0.9 | 6.1 | 5 | 1 | N |  |  | OP | X | 12 | 1989 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1989 | hydro | TRUE | 4713 | D/R Hydro Co | 52036 | Yough Hydro Power | PA | Somerset | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 6.1 | 0.9 | 6.1 | 5 | 1 | N |  |  | OP | X | 12 | 1989 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1985 | hydro | TRUE | 31613 | Washington Cnty Wtr Consv Dist | 52039 | Quail Creek Hydro Plant #1 | UT | Washington | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.3 | 0.95 | 2.3 | 2.3 | 0.5 | N |  |  | OP | X | 6 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage2017 | natural gas peaker | FALSE | 19724 | Vanderbilt University | 52048 | Vanderbilt University Power Plant | TN | Davidson | GT1B | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 6.3 | 0.8 | 5.8 | 6.5 | 1 | N |  |  | OP | X | 7 | 2017 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT; WAT NG RFO DFO
Vintage2002 | natural gas peaker | FALSE | 19724 | Vanderbilt University | 52048 | Vanderbilt University Power Plant | TN | Davidson | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 5.2 | 0.93 | 4 | 5 | 1 | N |  |  | OS | X | 7 | 2002 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT; WAT NG RFO DFO
Vintage2015 | natural gas peaker | FALSE | 19724 | Vanderbilt University | 52048 | Vanderbilt University Power Plant | TN | Davidson | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 7.2 | 0.8 | 7.8 | 8.7 | 1 | N |  |  | OP | X | 8 | 2015 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT; WAT NG RFO DFO
Vintage1987 | hydro | TRUE | 4277 | Converse Energy Inc | 52049 | Clifton Dam 3 Power Station | SC | Spartanburg | 1H | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.8 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 4 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT | [5 empty] | 1H
Vintage1985 | hydro | TRUE | 4277 | Converse Energy Inc | 52049 | Clifton Dam 3 Power Station | SC | Spartanburg | 2V | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 8 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT | [5 empty] | 1H
Vintage1984 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 52054 | Rapidan Hydro Facility | MN | Blue Earth | GEN1 | Conventional Hydroelectric | HY |  | W | X | X | NSP.RAPIDA1 |  | 3.4 | 1 | 3.2 | 3.1 | 1 | N |  |  | OS | X | 8 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  | N |  |  | 10M
Vintage1984 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 52054 | Rapidan Hydro Facility | MN | Blue Earth | GEN2 | Conventional Hydroelectric | HY |  | W | X | X | NSP.RAPIDA1 |  | 3.4 | 1 | 3.2 | 3.1 | 1 | N |  |  | OS | X | 8 | 1984 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  | N |  | 0 | 10M
Vintage1991 | natural gas combined cycle | TRUE | 19153 | Nassau Energy Corp | 52056 | Nassau Energy Corp | NY | Nassau | GT1 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N |  |  | 43 | 0.85 | 38 | 45 | 28.5 | N |  |  | OP | X | 3 | 1991 | 7 | 2022 | Y | IPP CHP | 3 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1991 | natural gas combined cycle | TRUE | 19153 | Nassau Energy Corp | 52056 | Nassau Energy Corp | NY | Nassau | ST1 | Natural Gas Fired Combined Cycle | CA | CC1 | W | Y | X |  |  | 12 | 0.85 | 12 | 12 | 5.6 | N |  |  | OP | X | 3 | 1991 | 7 | 2022 | Y | IPP CHP | 3 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1987 | hydro | TRUE | 60082 | ECOsponsible LLC | 52057 | Herkimer | NY | Herkimer | 01 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 |  | 0.1 | 0.1 | 0.1 | N |  |  | OS | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  | N |  | 0 | 10M
Vintage1987 | hydro | TRUE | 60082 | ECOsponsible LLC | 52057 | Herkimer | NY | Herkimer | 02 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 |  | 0.1 | 0.1 |  | N |  |  | OS | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  | N |  | 0 | 10M
Vintage1987 | hydro | TRUE | 60082 | ECOsponsible LLC | 52057 | Herkimer | NY | Herkimer | 03 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 |  | 0.1 | 0.1 |  | N |  |  | OS | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  | N |  | 0 | 10M
Vintage1987 | hydro | TRUE | 60082 | ECOsponsible LLC | 52057 | Herkimer | NY | Herkimer | 04 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 |  | 0.1 | 0.1 |  | N |  |  | OS | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  | N |  | 0 | 10M
Vintage1987 | hydro | TRUE | 57184 | Ampersand Mount Ida Hydro LLC | 52058 | Ogdensburg | NY | St Lawrence | 01 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.9 | 0.2 | 0.2 | 0.1 | N |  |  | OP | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  | N |  | 0 | 10M
Vintage1987 | hydro | TRUE | 57184 | Ampersand Mount Ida Hydro LLC | 52058 | Ogdensburg | NY | St Lawrence | 02 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.9 | 0.2 | 0.1 | 0.1 | N |  |  | OP | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  | N |  | 0 | 10M
Vintage1987 | hydro | TRUE | 57184 | Ampersand Mount Ida Hydro LLC | 52058 | Ogdensburg | NY | St Lawrence | 03 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.9 | 0.2 | 0.1 | 0.1 | N |  |  | OP | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  | N |  | 0 | 10M
Vintage1987 | hydro | TRUE | 57184 | Ampersand Mount Ida Hydro LLC | 52058 | Ogdensburg | NY | St Lawrence | 04 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.9 | 0.2 | 0.1 | 0.1 | N |  |  | OP | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  | N |  | 0 | 10M
Vintage1987 | hydro | TRUE | 57184 | Ampersand Mount Ida Hydro LLC | 52058 | Ogdensburg | NY | St Lawrence | 05 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.9 | 0.2 | 0.1 | 0.1 | N |  |  | OP | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT |  |  | N |  | 0 | 10M
Vintage1988 | natural gas combined cycle | FALSE | 8153 | Hartford Steam Co | 52061 | Hartford Hospital Cogeneration | CT | Hartford | GEN2 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | 980 | 980 | 4.2 | 1 | 2.4 | 2.4 | 0.3 | N |  |  | OP | X | 7 | 1988 | 12 | 2025 | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1988 | natural gas combined cycle | FALSE | 8153 | Hartford Steam Co | 52061 | Hartford Hospital Cogeneration | CT | Hartford | GEN3 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 6.2 | 0.95 | 6.2 | 6.2 | 3 | N |  |  | OP | X | 7 | 1988 | 12 | 2025 | Y | Commercial CHP | 5 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO |  |  | N | N |  | 12H | N | [19 empty] | N |  |  | Y | N | Y
Vintage2014 | other | FALSE | 8153 | Hartford Steam Co | 52061 | Hartford Hospital Cogeneration | CT | Hartford | GEN4 | Other Natural Gas | FC |  | S | X | X |  |  | 1.4 |  | 1.4 | 1.4 | 0 | N |  |  | OP | X | 5 | 2014 | 6 | 2029 | N | Commercial CHP | 5 | [11 empty] | N | N |  | OVER | [20 empty] | N |  |  | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1978 | other | FALSE | 59409 | Eco Services Corp. | 52063 | Martinez Sulfuric Acid Regeneration Plt | CA | Contra Costa | GEN1 | All Other | ST |  | S | X | X |  |  | 4 | 0.8 | 4 | 4 | 0.3 | N |  |  | OP | X | 1 | 1978 |  |  | Y | Industrial CHP | 7 | X T T T: B; WAT BIT BLQ BIT: WH; WAT NG BIT WDS: NG; WAT NG RFO DFO: NG |  |  | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage1976 | other | FALSE | 59409 | Eco Services Corp. | 52064 | Dominguez Plant | CA | Los Angeles | GEN1 | All Other | ST |  | S | X | X |  |  | 5 | 0.8 | 3.5 | 3.5 | 1 | N |  |  | OP | X | 8 | 1976 |  |  | Y | Industrial CHP | 7 | X T T T: B; WAT BIT BLQ BIT: WH; WAT NG BIT WDS: NG; WAT NG RFO DFO: NG |  |  | N | N |  | OVER | [23 empty] | Y | N | N
Vintage1977 | other | FALSE | 59409 | Eco Services Corp. | 52065 | Houston Plant | TX | Harris | GEN1 | All Other | ST |  | S | X | X |  |  | 6 | 0.8 | 5.5 | 6.1 | 5 | N |  |  | OP | X | 1 | 1977 |  |  | Y | Industrial CHP | 7 | X T T T: B; WAT BIT BLQ BIT: WH; WAT NG RFO DFO: NG |  |  | N | N |  | OVER | [23 empty] | N |  | N
Vintage1970 | other | FALSE | 59409 | Eco Services Corp. | 52065 | Houston Plant | TX | Harris | GEN2 | All Other | ST |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 1.2 | N |  |  | OP | X | 1 | 1970 |  |  | Y | Industrial CHP | 7 | X T T T: B; WAT BIT BLQ BIT: WH; WAT NG RFO DFO: NG |  |  | N | N |  | OVER | [23 empty] | N |  | N
Vintage1985 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 52068 | Great Falls Hydro Project | NJ | Passaic | GEN1 | Conventional Hydroelectric | HY |  | W | X | X | 50390 | 50390 | 4.1 | 0.9 | 3.3 | 3.3 | 0.3 | N |  |  | OP | X | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT | [5 empty] | 10M
Vintage1985 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 52068 | Great Falls Hydro Project | NJ | Passaic | GEN2 | Conventional Hydroelectric | HY |  | W | X | X | 50390 | 50390 | 4.1 | 0.9 | 3.3 | 3.3 | 0.3 | N |  |  | OP | X | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT | [5 empty] | 10M
Vintage1985 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 52068 | Great Falls Hydro Project | NJ | Passaic | GEN3 | Conventional Hydroelectric | HY |  | W | X | X | 50390 | 50390 | 4.1 | 0.9 | 3.3 | 3.3 | 0.3 | N |  |  | OP | X | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: WAT | [5 empty] | 10M
Vintage1990 | natural gas steam turbine | FALSE | 22218 | U S Army-Radford | 52072 | Radford Army Ammunition Plant | VA | Montgomery | GEN1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 6 | 0.85 | 5.6 | 5.6 | 2 | N |  |  | OP | X | 1 | 1990 |  |  | N | Industrial Non-CHP | 6 | X T T T: X; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO; WAT NG RFO DFO: NG |  |  | N | N |  | 12H |  | N | [21 empty] | Y | N | N
Vintage1990 | natural gas steam turbine | FALSE | 22218 | U S Army-Radford | 52072 | Radford Army Ammunition Plant | VA | Montgomery | GEN2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 6 | 0.85 | 5.6 | 5.6 | 2 | N |  |  | OP | X | 1 | 1990 |  |  | N | Industrial Non-CHP | 6 | X T T T: X; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO; WAT NG RFO DFO: NG |  |  | N | N |  | 12H |  | N | [21 empty] | Y | N | N
Vintage1990 | natural gas steam turbine | FALSE | 22218 | U S Army-Radford | 52072 | Radford Army Ammunition Plant | VA | Montgomery | GEN3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 6 | 0.85 | 5.6 | 5.6 | 2 | N |  |  | OP | X | 1 | 1990 |  |  | N | Industrial Non-CHP | 6 | X T T T: X; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO; WAT NG RFO DFO: NG |  |  | N | N |  | 12H |  | N | [21 empty] | Y | N | N
Vintage1993 | natural gas combined cycle | FALSE | 19524 | University of California-LA | 52073 | UCLA So Campus Cogen Project | CA | Los Angeles | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 14.5 | 0.8 | 12.5 | 13.5 | 5 | N |  |  | OP | X | 10 | 1993 |  |  | Y | Commercial CHP | 5 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO; WAT NG RFO DFO: NG |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1993 | natural gas combined cycle | FALSE | 19524 | University of California-LA | 52073 | UCLA So Campus Cogen Project | CA | Los Angeles | GEN2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 14.5 | 0.8 | 12.5 | 13.5 | 5 | N |  |  | OP | X | 10 | 1993 |  |  | Y | Commercial CHP | 5 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO; WAT NG RFO DFO: NG |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1993 | natural gas combined cycle | FALSE | 19524 | University of California-LA | 52073 | UCLA So Campus Cogen Project | CA | Los Angeles | GEN3 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 14 | 0.8 | 11 | 12 | 1 | N |  |  | OP | X | 10 | 1993 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | bar: X T T T to WAT BIT BLQ BIT; WAT NG RFO DFO
Vintage2012 | natural gas peaker | FALSE | 54713 | Chevron USA Inc | 52076 | McKittrick Cogen | CA | Kern | UNIT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | TEXMCKT_1_N101 | TH_ZP26_GEN-APND | 6 | 0.9 | 4.8 | 5.5 | 1.5 | N |  |  | OP | X | 6 | 2012 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT; WAT NG RFO DFO
Vintage2012 | natural gas peaker | FALSE | 54713 | Chevron USA Inc | 52076 | McKittrick Cogen | CA | Kern | UNIT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | TEXMCKT_1_N101 | TH_ZP26_GEN-APND | 6 | 0.9 | 4.8 | 5.5 | 1.5 | N |  |  | OP | X | 6 | 2012 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT; WAT NG RFO DFO
Vintage1985 | natural gas peaker | FALSE | 164 | AERA Energy LLC | 52077 | Lost Hills Cogeneration Plant | CA | Kern | GEN5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.5 | 0.9 | 2.7 | 3 | 2.5 | N |  |  | OP | X | 10 | 1985 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1985 | natural gas peaker | FALSE | 164 | AERA Energy LLC | 52077 | Lost Hills Cogeneration Plant | CA | Kern | GEN6 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.5 | 0.9 | 2.7 | 3 | 2.5 | N |  |  | OP | X | 10 | 1985 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1986 | natural gas peaker | FALSE | 54713 | Chevron USA Inc | 52078 | North Midway Cogen | CA | Kern | GEN7 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.5 | 0.9 | 3 | 3.2 | 1.5 | N |  |  | OS | X | 10 | 1986 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT; WAT NG RFO DFO
Vintage1986 | natural gas peaker | FALSE | 54713 | Chevron USA Inc | 52078 | North Midway Cogen | CA | Kern | GEN8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.5 | 0.9 | 3 | 3.2 | 1.5 | N |  |  | OS | X | 10 | 1986 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT; WAT NG RFO DFO
Vintage1986 | natural gas peaker | FALSE | 54713 | Chevron USA Inc | 52078 | North Midway Cogen | CA | Kern | GEN9 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.5 | 0.9 | 3 | 3.2 | 1.5 | N |  |  | OS | X | 10 | 1986 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT; WAT NG RFO DFO
Vintage1988 | natural gas peaker | FALSE | 54713 | Chevron USA Inc | 52081 | Cymric 31X Cogen | CA | Kern | TG1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | CYMRIC_1_N004 | TH_ZP26_GEN-APND | 3.4 | 0.9 | 2.7 | 2.9 | 1.5 | N |  |  | OP | X | 10 | 1988 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1988 | natural gas peaker | FALSE | 54713 | Chevron USA Inc | 52081 | Cymric 31X Cogen | CA | Kern | TG2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | CYMRIC_1_N004 | TH_ZP26_GEN-APND | 3.4 | 0.9 | 2.7 | 2.9 | 1.5 | N |  |  | OP | X | 10 | 1988 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1986 | natural gas peaker | FALSE | 54713 | Chevron USA Inc | 52082 | Cymric 6Z Cogen | CA | Kern | TG1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | CYMRIC_1_N004 | TH_ZP26_GEN-APND | 3.4 | 0.9 | 2.7 | 2.9 | 1.5 | N |  |  | OP | X | 7 | 1986 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1986 | natural gas peaker | FALSE | 54713 | Chevron USA Inc | 52082 | Cymric 6Z Cogen | CA | Kern | TG2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | CYMRIC_1_N004 | TH_ZP26_GEN-APND | 3.4 | 0.9 | 2.7 | 2.9 | 1.5 | N |  |  | OP | X | 7 | 1986 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1989 | natural gas peaker | FALSE | 54713 | Chevron USA Inc | 52083 | Coalinga 6C Cogen | CA | Fresno | TG1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.4 | 0.9 | 2.7 | 2.9 | 1.5 | N |  |  | OS | X | 9 | 1989 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1989 | natural gas peaker | FALSE | 54713 | Chevron USA Inc | 52083 | Coalinga 6C Cogen | CA | Fresno | TG2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.4 | 0.9 | 2.7 | 2.9 | 1.5 | N |  |  | OS | X | 9 | 1989 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1982 | natural gas peaker | FALSE | 54713 | Chevron USA Inc | 52085 | Taft 26C Cogen | CA | Kern | TG1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | CADET_6_N002 | TH_ZP26_GEN-APND | 3.1 | 0.9 | 2.7 | 2.9 | 1.5 | N |  |  | OP | X | 7 | 1982 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1982 | natural gas peaker | FALSE | 54713 | Chevron USA Inc | 52085 | Taft 26C Cogen | CA | Kern | TG2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | CADET_6_N002 | TH_ZP26_GEN-APND | 3.1 | 0.9 | 2.7 | 2.9 | 1.5 | N |  |  | OP | X | 7 | 1982 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1982 | natural gas peaker | FALSE | 54713 | Chevron USA Inc | 52085 | Taft 26C Cogen | CA | Kern | TG3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | CADET_6_N002 | TH_ZP26_GEN-APND | 3.1 | 0.9 | 2.7 | 2.9 | 1.5 | N |  |  | OP | X | 7 | 1982 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1982 | natural gas peaker | FALSE | 54713 | Chevron USA Inc | 52085 | Taft 26C Cogen | CA | Kern | TG4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | CADET_6_N002 | TH_ZP26_GEN-APND | 3.1 | 0.9 | 2.7 | 2.9 | 1.5 | N |  |  | OP | X | 7 | 1982 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1986 | natural gas peaker | FALSE | 54713 | Chevron USA Inc | 52086 | Coalinga 25D Cogen | CA | Fresno | TG1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | DERRICK_6_N003 | TH_ZP26_GEN-APND | 3.4 | 0.9 | 2.7 | 2.9 | 1.5 | N |  |  | OP | X | 10 | 1986 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1986 | natural gas peaker | FALSE | 54713 | Chevron USA Inc | 52086 | Coalinga 25D Cogen | CA | Fresno | TG2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | DERRICK_6_N003 | TH_ZP26_GEN-APND | 3.4 | 0.9 | 2.7 | 2.9 | 1.5 | N |  |  | OP | X | 10 | 1986 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1987 | natural gas peaker | FALSE | 54713 | Chevron USA Inc | 52086 | Coalinga 25D Cogen | CA | Fresno | TG3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | DERRICK_6_N003 | TH_ZP26_GEN-APND | 3.4 | 0.9 | 2.7 | 2.9 | 1.5 | N |  |  | OP | X | 12 | 1987 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1987 | natural gas peaker | FALSE | 54713 | Chevron USA Inc | 52086 | Coalinga 25D Cogen | CA | Fresno | TG4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | DERRICK_6_N003 | TH_ZP26_GEN-APND | 3.4 | 0.9 | 2.7 | 2.9 | 1.5 | N |  |  | OP | X | 12 | 1987 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1992 | natural gas peaker | TRUE | 19876 | Virginia Electric & Power Co | 52087 | Elizabeth River Power Station | VA | Chesapeake City | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 129.6 | 0.9 | 116 | 121 | 78 | N |  |  | SB | Y | 6 | 1992 |  |  | N | Electric Utility | 1 | X T T T: X; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1992 | natural gas peaker | TRUE | 19876 | Virginia Electric & Power Co | 52087 | Elizabeth River Power Station | VA | Chesapeake City | GEN2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 129.6 | 0.9 | 116 | 120 | 78 | N |  |  | SB | Y | 6 | 1992 |  |  | N | Electric Utility | 1 | X T T T: X; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1992 | natural gas peaker | TRUE | 19876 | Virginia Electric & Power Co | 52087 | Elizabeth River Power Station | VA | Chesapeake City | GEN3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 129.6 | 0.9 | 116 | 124 | 78 | N |  |  | SB | Y | 6 | 1992 |  |  | N | Electric Utility | 1 | X T T T: X; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO |  |  | N |  |  | 1H | [23 empty] | Y | N | Y
Vintage1987 | natural gas combined cycle | TRUE | 22652 | Texas City Cogeneration LLC | 52088 | Texas City Power Plant | TX | Galveston | GEN1 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | TXCTY_CC1 | TXCTY_CC1 | 141 | 0.95 | 139 | 139 | 5 | N |  |  | OP | X | 5 | 1987 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1987 | natural gas combined cycle | TRUE | 22652 | Texas City Cogeneration LLC | 52088 | Texas City Power Plant | TX | Galveston | GEN2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | TXCTY_CTA | TXCTY_CTA | 103 | 0.95 | 104 | 115 | 65 | N |  |  | OP | X | 5 | 1987 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1987 | natural gas combined cycle | TRUE | 22652 | Texas City Cogeneration LLC | 52088 | Texas City Power Plant | TX | Galveston | GEN3 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | TXCTY_CTB | TXCTY_CTB | 103 | 0.95 | 104 | 115 | 65 | N |  |  | OP | X | 5 | 1987 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1987 | natural gas combined cycle | TRUE | 22652 | Texas City Cogeneration LLC | 52088 | Texas City Power Plant | TX | Galveston | GEN4 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | TXCTY_CTC | TXCTY_CTC | 103 | 0.95 | 104 | 115 | 65 | N |  |  | OP | X | 5 | 1987 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1942 | natural gas steam turbine | FALSE | 57151 | Celanese Acetate LLC | 52089 | Celanese Acetate LLC | VA | Giles | GEN1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 6 | 0.7 | 6 | 6 | 2 | N |  |  | OP | X | 1 | 1942 |  |  | Y | Industrial CHP | 7 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO; WAT NG RFO DFO: NG |  |  | N | N |  | 12H |  | N |  |  | N | [18 empty] | Y | Y | Y
Vintage1942 | natural gas steam turbine | FALSE | 57151 | Celanese Acetate LLC | 52089 | Celanese Acetate LLC | VA | Giles | GEN2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 6 | 0.7 | 6 | 6 | 2 | N |  |  | OP | X | 1 | 1942 |  |  | Y | Industrial CHP | 7 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO; WAT NG RFO DFO: NG |  |  | N | N |  | 12H |  | N |  |  | N | [18 empty] | Y | Y | Y
Vintage1944 | natural gas steam turbine | FALSE | 57151 | Celanese Acetate LLC | 52089 | Celanese Acetate LLC | VA | Giles | GEN3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 6 | 0.7 | 6 | 6 | 2 | N |  |  | OP | X | 1 | 1944 |  |  | Y | Industrial CHP | 7 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO; WAT NG RFO DFO: NG |  |  | N | N |  | 12H |  | N |  |  | N | [18 empty] | Y | Y | Y
Vintage1966 | natural gas steam turbine | FALSE | 57151 | Celanese Acetate LLC | 52089 | Celanese Acetate LLC | VA | Giles | GEN4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 9.2 | 0.9 | 9.2 | 9.2 | 2 | N |  |  | OP | X | 1 | 1966 |  |  | Y | Industrial CHP | 7 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: DFO; WAT NG RFO DFO: NG |  |  | N | N |  | 12H |  | N |  |  | N | [18 empty] | Y | Y | Y
Vintage2006 | petroleum | TRUE | 13484 | NewYork-Presbyterian Brooklyn Methodist Hospital | 52091 | NewYork-Presbyterian Brooklyn Methodist Hospital | NY | Kings | 01-8N | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.1 | N |  |  | OP | X | 1 | 2006 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage2006 | petroleum | TRUE | 13484 | NewYork-Presbyterian Brooklyn Methodist Hospital | 52091 | NewYork-Presbyterian Brooklyn Methodist Hospital | NY | Kings | 02-8P | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 1 | 1 | 1 | 0.1 | N |  |  | OP | X | 1 | 2006 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage2008 | petroleum | TRUE | 13484 | NewYork-Presbyterian Brooklyn Methodist Hospital | 52091 | NewYork-Presbyterian Brooklyn Methodist Hospital | NY | Kings | 03-8L | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 1 | 1 | 1 | 0.1 | N |  |  | OP | X | 1 | 2008 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage2006 | petroleum | TRUE | 13484 | NewYork-Presbyterian Brooklyn Methodist Hospital | 52091 | NewYork-Presbyterian Brooklyn Methodist Hospital | NY | Kings | 04-6Z | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.1 | N |  |  | SB | N | 1 | 2006 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage2006 | petroleum | TRUE | 13484 | NewYork-Presbyterian Brooklyn Methodist Hospital | 52091 | NewYork-Presbyterian Brooklyn Methodist Hospital | NY | Kings | 05-6Z | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.1 | N |  |  | SB | N | 1 | 2006 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage2020 | petroleum | TRUE | 13484 | NewYork-Presbyterian Brooklyn Methodist Hospital | 52091 | NewYork-Presbyterian Brooklyn Methodist Hospital | NY | Kings | CCHEG | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.4 | N |  |  | SB | N | 6 | 2020 |  |  | N | IPP Non-CHP | 2 | X T T T: X; WAT BIT BLQ BIT: DFO |  |  | N |  |  | 1H | [23 empty] | N
Vintage1990 | natural gas peaker | FALSE | 1569 | Berry Petroleum Co | 52096 | Berry Placerita Cogen | CA | Los Angeles | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SP15 | SP15 | 21.4 | 0.85 | 20 | 20.7 | 3 | N |  |  | OP | X | 3 | 1990 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1990 | natural gas peaker | FALSE | 1569 | Berry Petroleum Co | 52096 | Berry Placerita Cogen | CA | Los Angeles | GEN2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SP15 | SP15 | 21.4 | 0.85 | 20 | 20.7 | 3 | N |  |  | OP | X | 5 | 1990 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1993 | biomass | TRUE | 14155 | Orange County Sanitation Dist | 52099 | Plant No 2 Orange County | CA | Orange | GEN1 | Other Waste Biomass | IC |  | S | X | X |  |  | 3 | 0.8 | 2.7 | 2.7 | 2.2 | N |  |  | OP | X | 6 | 1993 |  |  | Y | Commercial CHP | 5 | X T T T: T; WAT BIT BLQ BIT: OBG; WAT NG BIT WDS: NG; WAT NG RFO DFO: NG; WAT RFO NG NG: OBG |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1993 | biomass | TRUE | 14155 | Orange County Sanitation Dist | 52099 | Plant No 2 Orange County | CA | Orange | GEN2 | Other Waste Biomass | IC |  | S | X | X |  |  | 3 | 0.8 | 2.7 | 2.7 | 2.2 | N |  |  | OP | X | 6 | 1993 |  |  | Y | Commercial CHP | 5 | X T T T: T; WAT BIT BLQ BIT: OBG; WAT NG BIT WDS: NG; WAT NG RFO DFO: NG; WAT RFO NG NG: OBG |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1993 | biomass | TRUE | 14155 | Orange County Sanitation Dist | 52099 | Plant No 2 Orange County | CA | Orange | GEN3 | Other Waste Biomass | IC |  | S | X | X |  |  | 3 | 0.8 | 2.7 | 2.7 | 2.2 | N |  |  | OP | X | 6 | 1993 |  |  | Y | Commercial CHP | 5 | X T T T: T; WAT BIT BLQ BIT: OBG; WAT NG BIT WDS: NG; WAT NG RFO DFO: NG; WAT RFO NG NG: OBG |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1993 | biomass | TRUE | 14155 | Orange County Sanitation Dist | 52099 | Plant No 2 Orange County | CA | Orange | GEN4 | Other Waste Biomass | IC |  | S | X | X |  |  | 3 | 0.8 | 2.7 | 2.7 | 2.2 | N |  |  | OP | X | 6 | 1993 |  |  | Y | Commercial CHP | 5 | X T T T: T; WAT BIT BLQ BIT: OBG; WAT NG BIT WDS: NG; WAT NG RFO DFO: NG; WAT RFO NG NG: OBG |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1993 | biomass | TRUE | 14155 | Orange County Sanitation Dist | 52099 | Plant No 2 Orange County | CA | Orange | GEN5 | Other Waste Biomass | IC |  | S | X | X |  |  | 3 | 0.8 | 2.7 | 2.7 | 2.2 | N |  |  | OP | X | 6 | 1993 |  |  | Y | Commercial CHP | 5 | X T T T: T; WAT BIT BLQ BIT: OBG; WAT NG BIT WDS: NG; WAT NG RFO DFO: NG; WAT RFO NG NG: OBG |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1993 | other | FALSE | 14155 | Orange County Sanitation Dist | 52099 | Plant No 2 Orange County | CA | Orange | GEN6 | All Other | ST |  | S | X | X |  |  | 1 | 0.8 | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 6 | 1993 |  |  | Y | Commercial CHP | 5 | X T T T: B; WAT BIT BLQ BIT: OTH; WAT NG RFO DFO: WH |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1982 | natural gas peaker | FALSE | 54713 | Chevron USA Inc | 52104 | Cymric 36W Cogen | CA | Kern | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | CYMRIC_1_N004 | TH_ZP26_GEN-APND | 3.1 | 0.9 | 2.7 | 2.9 | 1.5 | N |  |  | OP | X | 10 | 1982 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1982 | natural gas peaker | FALSE | 54713 | Chevron USA Inc | 52104 | Cymric 36W Cogen | CA | Kern | GEN2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | CYMRIC_1_N004 | TH_ZP26_GEN-APND | 3.1 | 0.9 | 2.7 | 2.9 | 1.5 | N |  |  | OP | X | 10 | 1982 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1982 | natural gas peaker | FALSE | 54713 | Chevron USA Inc | 52104 | Cymric 36W Cogen | CA | Kern | GEN3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | CYMRIC_1_N004 | TH_ZP26_GEN-APND | 3.1 | 0.9 | 2.7 | 2.9 | 1.5 | N |  |  | OP | X | 10 | 1982 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1982 | natural gas peaker | FALSE | 54713 | Chevron USA Inc | 52104 | Cymric 36W Cogen | CA | Kern | GEN4 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | CYMRIC_1_N004 | TH_ZP26_GEN-APND | 3.1 | 0.9 | 2.7 | 2.9 | 1.5 | N |  |  | OP | X | 10 | 1982 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1988 | natural gas peaker | FALSE | 54713 | Chevron USA Inc | 52107 | Kern River Eastridge Cogen | CA | Kern | 101A | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | POD_DISCOV_1_CHEVRON-APND | TH_ZP26_GEN-APND | 24.4 | 0.9 | 20.8 | 21.7 | 12 | N |  |  | OP | X | 6 | 1988 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT; WAT NG RFO DFO
Vintage1988 | natural gas peaker | FALSE | 54713 | Chevron USA Inc | 52107 | Kern River Eastridge Cogen | CA | Kern | 101B | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | POD_DISCOV_1_CHEVRON-APND | TH_ZP26_GEN-APND | 24.4 | 0.9 | 20.8 | 21.7 | 12 | N |  |  | OP | X | 6 | 1988 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT; WAT NG RFO DFO
Vintage1992 | natural gas combined cycle | FALSE | 49732 | Chevron Products Company-Richmond | 52109 | Richmond Cogen | CA | Contra Costa | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 62.6 | 0.8 | 50 | 52 | 25 | N |  |  | OP | X | 8 | 1992 |  |  | Y | Industrial CHP | 7 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: OG |  |  | N |  |  | 1H | [23 empty] | Y | Y | N
Vintage1992 | natural gas combined cycle | FALSE | 49732 | Chevron Products Company-Richmond | 52109 | Richmond Cogen | CA | Contra Costa | GEN2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 62.6 | 0.8 | 50 | 52 | 25 | N |  |  | OP | X | 9 | 1992 |  |  | Y | Industrial CHP | 7 | X T T T: T; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: OG |  |  | N |  |  | 1H | [23 empty] | Y | Y | N
Vintage2006 | natural gas combined cycle | FALSE | 49732 | Chevron Products Company-Richmond | 52109 | Richmond Cogen | CA | Contra Costa | GEN5 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 30.4 | 0.85 | 30.4 | 30.4 | 1.5 | N |  |  | OP | X | 3 | 2006 |  |  | N | Industrial CHP | 7 | X T T T: X; WAT BIT BLQ BIT: NG; WAT NG BIT WDS: OG |  |  | N | N |  | 12H | [23 empty] | Y | N | N
Vintage2019 | other | FALSE | 49732 | Chevron Products Company-Richmond | 52109 | Richmond Cogen | CA | Contra Costa | GEN6 | All Other | ST |  | S | X | X |  |  | 17.9 | 0.85 | 17.9 | 17.9 | 1 | N |  |  | OP | X | 4 | 2019 |  |  | N | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: X T T T to WAT BIT BLQ BIT; WAT NG RFO DFO
Vintage1978 | natural gas peaker | FALSE | 59875 | Olin Blue Cube Operations | 52120 | Freeport Energy | TX | Brazoria | G-37 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 75 | 0.85 | 59.2 | 65.9 | 40 | N |  |  | OP | X | 4 | 1978 |  |  | Y | Industrial CHP | 7 | [11 empty] | N |  |  | 12H | [23 empty] | N |  | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1982 | natural gas combined cycle | FALSE | 59875 | Olin Blue Cube Operations | 52120 | Freeport Energy | TX | Brazoria | G-61 | Natural Gas Fired Combined Cycle | CT | PLTB | S | X | N |  |  | 94.5 | 0.85 | 68.3 | 76.1 | 50 | N |  |  | OP | X | 10 | 1982 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1982 | natural gas combined cycle | FALSE | 59875 | Olin Blue Cube Operations | 52120 | Freeport Energy | TX | Brazoria | G-63 | Natural Gas Fired Combined Cycle | CT | PLTB | S | X | N |  |  | 94.5 | 0.85 | 68.3 | 80 | 50 | N |  |  | OP | X | 8 | 1982 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1982 | natural gas combined cycle | FALSE | 59875 | Olin Blue Cube Operations | 52120 | Freeport Energy | TX | Brazoria | G-64 | Natural Gas Fired Combined Cycle | CA | PLTB | S | N | X |  |  | 64.8 | 0.9 | 35 | 35 | 9 | N |  |  | OP | X | 9 | 1982 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | OVER | [23 empty] | N |  | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1984 | natural gas combined cycle | FALSE | 59875 | Olin Blue Cube Operations | 52120 | Freeport Energy | TX | Brazoria | G-65 | Natural Gas Fired Combined Cycle | CA | PLTB | S | N | X | Dow_Gen_1 and Dow_Gen_2 |  | 111.3 | 0.85 | 95.2 | 95.2 | 30 | N |  |  | OP | X | 2 | 1984 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | OVER | [20 empty] | N |  |  | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1983 | natural gas combined cycle | FALSE | 59875 | Olin Blue Cube Operations | 52120 | Freeport Energy | TX | Brazoria | G-66 | Natural Gas Fired Combined Cycle | CT | PLTB | S | X | N |  |  | 119 | 0.85 | 95.6 | 106.5 | 45 | N |  |  | OP | X | 12 | 1983 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1984 | natural gas combined cycle | FALSE | 59875 | Olin Blue Cube Operations | 52120 | Freeport Energy | TX | Brazoria | G-67 | Natural Gas Fired Combined Cycle | CT | PLTB | S | X | N |  |  | 119 | 0.85 | 95.6 | 106.5 | 45 | N |  |  | OP | X | 3 | 1984 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1988 | natural gas peaker | FALSE | 429 | Occidental Permian Ltd | 52122 | Wasson CO2 Removal Plant | TX | Yoakum | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 23.4 | 0.85 | 18.4 | 18.8 | 10 | N |  |  | OP | X | 2 | 1988 |  |  | Y | Industrial CHP | 7 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT; WAT NG RFO DFO
Vintage1948 | other | FALSE | 64954 | Contango Oil and Gas | 52127 | Elk Basin Gasoline Plant | WY | Park | GEN1 | Other Gases | ST |  | J | X | X |  |  | 1 | 0.7 | 0.8 | 0.8 | 0.2 | N |  |  | OP | X | 1 | 1948 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H |  |  |  | N | [19 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT; WAT NG RFO DFO
Vintage1948 | other | FALSE | 64954 | Contango Oil and Gas | 52127 | Elk Basin Gasoline Plant | WY | Park | GEN2 | Other Gases | ST |  | J | X | X |  |  | 1 | 0.7 | 0.8 | 0.8 | 0.2 | N |  |  | OP | X | 1 | 1948 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT; WAT NG RFO DFO
Vintage1948 | other | FALSE | 44466 | BP PLC | 52130 | Whiting Refinery | IN | Lake | 31TG | Other Gases | ST |  | S | X | X |  |  | 12.5 | 0.95 | 11.2 | 11.2 | 5 | N |  |  | OP | X | 1 | 1948 |  |  | Y | Industrial CHP | 7 | X T T T: T; WAT BIT BLQ BIT: OG; WAT NG BIT WDS: NG; WAT WDS WDS RFO: PUR; WAT NG RFO DFO: OG |  |  | N | N |  | OVER | [23 empty] | N
Vintage1948 | other | FALSE | 44466 | BP PLC | 52130 | Whiting Refinery | IN | Lake | 32TG | Other Gases | ST |  | S | X | X |  |  | 12.5 | 0.95 | 11.2 | 11.2 | 5 | N |  |  | OP | X | 1 | 1948 |  |  | Y | Industrial CHP | 7 | X T T T: T; WAT BIT BLQ BIT: OG; WAT NG BIT WDS: NG; WAT WDS WDS RFO: PUR; WAT NG RFO DFO: OG |  |  | N | N |  | OVER | [23 empty] | N
Vintage1955 | other | FALSE | 44466 | BP PLC | 52130 | Whiting Refinery | IN | Lake | 33TG | Other Gases | ST |  | S | X | X |  |  | 18.8 | 0.95 | 16.4 | 16.4 | 5 | N |  |  | OP | X | 1 | 1955 |  |  | Y | Industrial CHP | 7 | X T T T: T; WAT BIT BLQ BIT: OG; WAT NG BIT WDS: NG; WAT WDS WDS RFO: PUR; WAT NG RFO DFO: OG |  |  | N | N |  | OVER | [23 empty] | N
Vintage1955 | other | FALSE | 44466 | BP PLC | 52130 | Whiting Refinery | IN | Lake | 34TG | Other Gases | ST |  | S | X | X |  |  | 10 | 0.95 | 11.8 | 11.8 | 5 | N |  |  | OP | X | 1 | 1955 |  |  | Y | Industrial CHP | 7 | X T T T: T; WAT BIT BLQ BIT: OG; WAT NG BIT WDS: NG; WAT WDS WDS RFO: PUR; WAT NG RFO DFO: OG |  |  | N | N |  | OVER | [23 empty] | N
Vintage1980 | other | FALSE | 44466 | BP PLC | 52130 | Whiting Refinery | IN | Lake | 35TG | Other Gases | ST |  | S | X | X |  |  | 30 | 0.95 | 38 | 38 | 5 | N |  |  | OP | X | 1 | 1980 |  |  | Y | Industrial CHP | 7 | X T T T: T; WAT BIT BLQ BIT: OG; WAT NG BIT WDS: NG; WAT WDS WDS RFO: PUR; WAT NG RFO DFO: OG |  |  | N | N |  | OVER | [23 empty] | N
Vintage1986 | natural gas combined cycle | FALSE | 17566 | South Houston Green Power LLC | 52132 | Power Station 4 | TX | Galveston | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N | AMOCOOIL | AMOCOOIL | 78.2 | 0.85 | 69 | 78 | 50 | N |  |  | OP | X | 9 | 1986 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1986 | natural gas combined cycle | FALSE | 17566 | South Houston Green Power LLC | 52132 | Power Station 4 | TX | Galveston | GEN2 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N | AMOCOOIL | AMOCOOIL | 78.2 | 0.85 | 69 | 78 | 50 | N |  |  | OP | X | 9 | 1986 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1986 | natural gas combined cycle | FALSE | 17566 | South Houston Green Power LLC | 52132 | Power Station 4 | TX | Galveston | GEN3 | Natural Gas Fired Combined Cycle | CA | CC1 | W | Y | X | AMOCOOIL | AMOCOOIL | 34.7 | 0.85 | 34 | 34 | 34 | N |  |  | OS | X | 9 | 1986 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T to WAT BIT BLQ BIT
Vintage1954 | other | FALSE | 18668 | Tesoro Refining and Marketing Co LLC | 52133 | Tesoro Mandan Cogeneration Plant | ND | Morton | GEN1 | Other Gases | ST |  | S | X | X |  |  | 2.5 | 0.8 | 2.8 | 2.8 | 0.3 | N |  |  | OP | X | 10 | 1954 |  |  | Y | Industrial CHP | 7 | T | OG | NG | WO |  |  |  | OG | NG |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1954 | other | FALSE | 18668 | Tesoro Refining and Marketing Co LLC | 52133 | Tesoro Mandan Cogeneration Plant | ND | Morton | GEN2 | Other Gases | ST |  | S | X | X |  |  | 2.5 | 0.8 | 2.8 | 2.8 | 0.3 | N |  |  | OP | X | 10 | 1954 |  |  | Y | Industrial CHP | 7 | T | OG | NG | WO |  |  |  | OG | NG |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1958 | other | FALSE | 18668 | Tesoro Refining and Marketing Co LLC | 52133 | Tesoro Mandan Cogeneration Plant | ND | Morton | GEN3 | Other Gases | ST |  | S | X | X |  |  | 2.5 | 0.8 | 2.8 | 2.8 | 0.3 | N |  |  | OP | X | 5 | 1958 |  |  | Y | Industrial CHP | 7 | T | OG | NG | WO | RFO |  |  | OG | NG |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1967 | biomass | TRUE | 8009 | International Paper Co | 52140 | International Paper Prattville Mill | AL | Autauga | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 40.5 | 0.9 | 37 | 38 | 8 | N |  |  | OP | X | 2 | 1967 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | NG | OBG | WO |  | NG | WO |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1980 | biomass | TRUE | 8009 | International Paper Co | 52140 | International Paper Prattville Mill | AL | Autauga | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 49.3 | 0.85 | 48 | 48 | 10 | N |  |  | OP | X | 5 | 1980 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | BIT | OBG | WO | NG | NG | WO |  |  | N | N |  | 12H |  | Y | N |  | Y | [18 empty] | Y | Y | N
Vintage1990 | onshore wind | TRUE | 2770 | Terra-Gen Operating Co-Wind | 52142 | Mojave 3/4/5 | CA | Kern | GEN1 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 75 |  | 67 | 67 | 5.2 | N |  |  | OP | X | 12 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WND |  |  | N | N | 300 | [24 empty] | N
Vintage1983 | natural gas peaker | FALSE | 3221 | CPKelco U S Inc | 52147 | C P Kelco San Diego Plant | CA | San Diego | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 9.2 | 0.9 | 9.2 | 9.2 | 7 | N |  |  | OP | X | 10 | 1983 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1983 | natural gas peaker | FALSE | 3221 | CPKelco U S Inc | 52147 | C P Kelco San Diego Plant | CA | San Diego | GEN2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 10 | 0.8 | 9.3 | 9.3 | 7 | N |  |  | OP | X | 10 | 1983 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1983 | natural gas peaker | FALSE | 3221 | CPKelco U S Inc | 52147 | C P Kelco San Diego Plant | CA | San Diego | GEN3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 10 | 0.8 | 9.3 | 9.3 | 7 | N |  |  | OS | X | 10 | 1983 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1982 | natural gas steam turbine | FALSE | 12320 | Merck & Co Inc | 52148 | Elkton | VA | Rockingham | GEN1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 7.2 | 0.8 | 6 | 6 | 0.5 | N |  |  | OP | X | 6 | 1982 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: NG; WDS: DFO; NG: NG |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2016 | natural gas peaker | FALSE | 12320 | Merck & Co Inc | 52148 | Elkton | VA | Rockingham | GEN3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1 | 1 | 0.1 | N |  |  | OP | X | 3 | 2016 |  |  | N | Industrial CHP | 7 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: T to BLQ
Vintage2016 | natural gas peaker | FALSE | 12320 | Merck & Co Inc | 52148 | Elkton | VA | Rockingham | GEN4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 3 | 2016 |  |  | N | Industrial CHP | 7 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: T to BLQ
Vintage1982 | natural gas steam turbine | FALSE | 12320 | Merck & Co Inc | 52148 | Elkton | VA | Rockingham | GEN5 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 6 | 1982 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: NG; WDS: DFO; NG: NG |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2021 | natural gas steam turbine | FALSE | 12320 | Merck & Co Inc | 52148 | Elkton | VA | Rockingham | GEN6 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 0.1 | N |  |  | OP | X | 12 | 2021 |  |  | N | Industrial CHP | 7 | T: X; BLQ: NG; WDS: DFO; NG: NG |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2021 | natural gas steam turbine | FALSE | 12320 | Merck & Co Inc | 52148 | Elkton | VA | Rockingham | GEN7 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 1 | N |  |  | OP | X | 12 | 2021 |  |  | N | Industrial CHP | 7 | T: X; BLQ: NG; WDS: DFO; NG: NG |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2001 | natural gas peaker | FALSE | 12303 | Merck & Co Inc-West Point | 52149 | West Point (PA) | PA | Montgomery | COG3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MERCK 13 KV MERCK1-2 | MERCK 13 KV MERCK1-2 | 38.4 | 0.85 | 38.5 | 40 | 20 | N |  |  | OP | X | 4 | 2001 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage2016 | natural gas peaker | FALSE | 12303 | Merck & Co Inc-West Point | 52149 | West Point (PA) | PA | Montgomery | GEN14 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | MERCK 13 KV MERCK1-2 | MERCK 13 KV MERCK1-2 | 1.5 | 0.8 | 1.5 | 1.5 | 0.8 | N |  |  | SB | N | 8 | 2016 |  |  | N | Industrial CHP | 7 | [11 empty] | N | N |  | 10M | [23 empty] | N |  | N | bar: T to BLQ
Vintage2017 | natural gas peaker | FALSE | 12303 | Merck & Co Inc-West Point | 52149 | West Point (PA) | PA | Montgomery | GEN15 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | MERCK 13 KV MERCK1-2 | MERCK 13 KV MERCK1-2 | 1.3 | 0.8 | 1.1 | 1.3 | 0.8 | N |  |  | SB | N | 5 | 2017 |  |  | N | Industrial CHP | 7 | [11 empty] | N | N |  | 10M | [23 empty] | N |  | N | bar: T to BLQ
Vintage2020 | natural gas peaker | FALSE | 12303 | Merck & Co Inc-West Point | 52149 | West Point (PA) | PA | Montgomery | GEN16 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | MERCK 13 KV MERCK | MERCK 13 KV MERCK | 1.3 | 0.8 | 1.1 | 1.3 | 0.8 | N |  |  | SB | N | 5 | 2020 |  |  | N | Industrial CHP | 7 | [14 empty] | 10M | [23 empty] | N | bar: T to BLQ
Vintage1989 | natural gas peaker | FALSE | 12303 | Merck & Co Inc-West Point | 52149 | West Point (PA) | PA | Montgomery | GEN2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | MERCK 13 KV MERCK1-2 | MERCK 13 KV MERCK1-2 | 32.3 | 0.9 | 24.5 | 26 | 15 | N |  |  | OP | X | 1 | 1989 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1972 | petroleum | FALSE | 12303 | Merck & Co Inc-West Point | 52149 | West Point (PA) | PA | Montgomery | GEN3 | Petroleum Liquids | IC |  | S | X | X | MERCK 13 KV MERCK1-2 | MERCK 13 KV MERCK1-2 | 2.5 | 0.85 | 2.4 | 2.5 | 1.8 | N |  |  | OS | X | 1 | 1972 |  |  | N | Industrial CHP | 7 | T: X; BLQ: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1995 | natural gas peaker | FALSE | 12303 | Merck & Co Inc-West Point | 52149 | West Point (PA) | PA | Montgomery | GEN4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | MERCK 13 KV MERCK1-2 | MERCK 13 KV MERCK1-2 | 1.7 | 0.85 | 1.7 | 1.7 | 1 | N |  |  | OS | X | 6 | 1995 |  |  | N | Industrial CHP | 7 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: T to BLQ
Vintage1994 | petroleum | FALSE | 12303 | Merck & Co Inc-West Point | 52149 | West Point (PA) | PA | Montgomery | GEN5 | Petroleum Liquids | IC |  | S | X | X | MERCK 13 KV MERCK1-2 | MERCK 13 KV MERCK1-2 | 1.2 | 0.85 | 1.2 | 1.2 | 0.8 | N |  |  | OS | X | 6 | 1994 |  |  | N | Industrial CHP | 7 | T: X; BLQ: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1994 | natural gas peaker | FALSE | 12303 | Merck & Co Inc-West Point | 52149 | West Point (PA) | PA | Montgomery | GEN7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | MERCK 13 KV MERCK1-2 | MERCK 13 KV MERCK1-2 | 0.7 | 0.85 | 0.7 | 0.7 | 0.7 | N |  |  | OS | X | 6 | 1994 |  |  | N | Industrial CHP | 7 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | N | bar: T to BLQ
Vintage1999 | natural gas peaker | FALSE | 12303 | Merck & Co Inc-West Point | 52149 | West Point (PA) | PA | Montgomery | GEN8 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | MERCK 13 KV MERCK1-2 | MERCK 13 KV MERCK1-2 | 1 | 0.85 | 1 | 1 | 0.8 | N |  |  | SB | N | 8 | 1999 |  |  | N | Industrial CHP | 7 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: T to BLQ
Vintage2004 | natural gas peaker | FALSE | 12303 | Merck & Co Inc-West Point | 52149 | West Point (PA) | PA | Montgomery | GEN9 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | MERCK 13 KV MERCK1-2 | MERCK 13 KV MERCK1-2 | 1.3 | 0.85 | 0.9 | 0.9 | 0.8 | N |  |  | SB | N | 2 | 2004 |  |  | N | Industrial CHP | 7 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: T to BLQ
Vintage2004 | natural gas peaker | FALSE | 12303 | Merck & Co Inc-West Point | 52149 | West Point (PA) | PA | Montgomery | GN10 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | MERCK 13 KV MERCK1-2 | MERCK 13 KV MERCK1-2 | 1.3 | 0.85 | 0.9 | 0.9 | 0.8 | N |  |  | SB | N | 2 | 2004 |  |  | N | Industrial CHP | 7 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: T to BLQ
Vintage2010 | petroleum | FALSE | 12303 | Merck & Co Inc-West Point | 52149 | West Point (PA) | PA | Montgomery | GN11 | Petroleum Liquids | IC |  | S | X | X | MERCK 13 KV MERCK1-2 | MERCK 13 KV MERCK1-2 | 1 | 0.85 | 0.9 | 0.9 | 0.8 | N |  |  | SB | N | 11 | 2010 |  |  | N | Industrial CHP | 7 | T: X; BLQ: DFO |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2015 | petroleum | FALSE | 12303 | Merck & Co Inc-West Point | 52149 | West Point (PA) | PA | Montgomery | GN12 | Petroleum Liquids | IC |  | S | X | X | MERCK 13 KV MERCK1-2 | MERCK 13 KV MERCK1-2 | 2 | 0.8 | 2 | 2 | 0.8 | N |  |  | SB | N | 1 | 2015 |  |  | N | Industrial CHP | 7 | T: X; BLQ: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage2015 | petroleum | FALSE | 12303 | Merck & Co Inc-West Point | 52149 | West Point (PA) | PA | Montgomery | GN13 | Petroleum Liquids | IC |  | S | X | X | MERCK 13 KV MERCK1-2 | MERCK 13 KV MERCK1-2 | 2 | 0.8 | 2 | 2 | 0.8 | N |  |  | OA | X | 1 | 2015 |  |  | N | Industrial CHP | 7 | T: X; BLQ: DFO |  |  | N | N |  | 10M | [23 empty] | N
Vintage1984 | biomass | TRUE | 9424 | Sylvamo Corporation - Eastover | 52151 | Sylvamo Corporation Eastover Facility | SC | Richland | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 48.4 | 0.85 | 46 | 46 | 30 | N |  |  | OP | X | 4 | 1984 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | DFO | TDF |  | RFO | WO |  |  | N | N |  | 12H |  | N | [21 empty] | Y | Y | N
Vintage1991 | biomass | TRUE | 9424 | Sylvamo Corporation - Eastover | 52151 | Sylvamo Corporation Eastover Facility | SC | Richland | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 61.2 | 0.85 | 57 | 57 | 30 | N |  |  | OP | X | 6 | 1991 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | DFO | TDF |  | RFO | WO |  |  | N | N |  | 12H |  | N | [21 empty] | Y | Y | N
Vintage1997 | natural gas peaker | FALSE | 9348 | International Paper | 52152 | International Paper Franklin Mill | VA | Isle of Wight | GE10 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 1075455179 | 35010337 | 46.4 | 0.85 | 38 | 59.5 | 25 | N |  |  | OP | X | 11 | 1997 |  |  | Y | Industrial CHP | 7 | [11 empty] | N |  |  | 12H | [23 empty] | N | N | N | bar: T to BLQ; NG
Vintage1977 | biomass | TRUE | 9348 | International Paper | 52152 | International Paper Franklin Mill | VA | Isle of Wight | GEN9 | Wood/Wood Waste Biomass | ST |  | S | X | X | 1075455179 | 35010337 | 36.1 | 0.85 | 36.1 | 36.1 | 5 | N |  |  | OP | X | 11 | 1977 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: BLQ; WDS: NG; NG: NG |  |  | N |  |  | 12H |  | N | [21 empty] | Y | Y
Vintage1986 | hydro | TRUE | 11290 | Lacomb Irrigation Dist | 52155 | Lacomb Irrigation District | OR | Linn | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.96 | 1 | 1 | 0.2 | N |  |  | OP | X | 12 | 1986 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1989 | geothermal | TRUE | 7160 | Geysers Power Co LLC | 52158 | Aidlin Geothermal Power Plant | CA | Sonoma | GEN1 | Geothermal | ST |  | S | X | X |  |  | 12.5 | 1 | 9 | 10 | 8 | N |  |  | OP | X | 5 | 1989 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: GEO; NG: GEO |  |  | N |  |  | 12H | [23 empty] | N | N
Vintage1989 | geothermal | TRUE | 7160 | Geysers Power Co LLC | 52158 | Aidlin Geothermal Power Plant | CA | Sonoma | GEN2 | Geothermal | ST |  | S | X | X |  |  | 12.5 | 1 | 9 | 10 | 8 | N |  |  | OP | X | 5 | 1989 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: GEO; NG: GEO |  |  | N |  |  | 12H | [23 empty] | N | N
Vintage2021 | onshore wind | TRUE | 64311 | Wind Wall 1 LLC | 52162 | 85 A | CA | Kern | MON1 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 21.3 |  | 21.3 | 21.3 | 2 | N |  |  | OP | X | 3 | 2021 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WND |  |  |  |  | 6
Vintage2021 | onshore wind | TRUE | 64311 | Wind Wall 1 LLC | 52163 | 85 B | CA | Kern | MON2 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 25.2 |  | 25.2 | 25.2 | 2 | N |  |  | OP | X | 3 | 2021 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WND |  |  |  |  | 7
Vintage1985 | hydro | TRUE | 63181 | Dichotomy Collins Hydro LLC | 52166 | Collins Facility | MA | Hampden | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.83 | 0.8 | 0.8 | 0.2 | N |  |  | OP | X | 3 | 1985 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 63181 | Dichotomy Collins Hydro LLC | 52166 | Collins Facility | MA | Hampden | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.83 | 0.8 | 0.8 | 0.2 | N |  |  | OP | X | 3 | 1985 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage2011 | natural gas combined cycle | FALSE | 24210 | Riverbay Corp | 52168 | Riverbay | NY | Bronx | GEN2 | Natural Gas Fired Combined Cycle | CA | COG1 | S | Y | X |  |  | 16 | 0.8 | 13.8 | 15 | 3 | N |  |  | OP | X | 3 | 2011 |  |  | Y | Commercial CHP | 5 | T: B; BLQ: NG; WDS: DFO; NG: NG; WO: DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | N
Vintage2011 | natural gas combined cycle | FALSE | 24210 | Riverbay Corp | 52168 | Riverbay | NY | Bronx | GEN3 | Natural Gas Fired Combined Cycle | CT | COG1 | S | X | N |  |  | 12.9 | 0.8 | 12.3 | 12.6 | 10.3 | N |  |  | OP | X | 3 | 2011 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: NG; WDS: DFO; NG: NG |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2011 | natural gas combined cycle | FALSE | 24210 | Riverbay Corp | 52168 | Riverbay | NY | Bronx | GEN4 | Natural Gas Fired Combined Cycle | CT | COG1 | S | X | N |  |  | 12.9 | 0.8 | 12.3 | 12.6 | 10.3 | N |  |  | OP | X | 3 | 2011 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: NG; WDS: DFO; NG: NG |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2011 | petroleum | FALSE | 24210 | Riverbay Corp | 52168 | Riverbay | NY | Bronx | U0007 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.7 | 0.8 | 1.5 | 1.5 | 0.3 | N |  |  | OP | X | 6 | 2011 |  |  | N | Commercial CHP | 5 | T: X; BLQ: DFO |  |  | N |  |  | 10M | [23 empty] | N | N | N
Vintage1989 | natural gas peaker | TRUE | 12687 | Midway-Sunset Cogeneration Co | 52169 | Midway Sunset Cogen | CA | Kern | A | Natural Gas Fired Combustion Turbine | GT |  | J | X | X | POD SUNSET_2_UNITS APND | ZP 26 Hub | 78 | 0.9 | 73 | 83 | 50 | N |  |  | OP | X | 5 | 1989 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 1H | [23 empty] | N |  | N | bar: T to BLQ
Vintage1989 | natural gas peaker | TRUE | 12687 | Midway-Sunset Cogeneration Co | 52169 | Midway Sunset Cogen | CA | Kern | B | Natural Gas Fired Combustion Turbine | GT |  | J | X | X | POD SUNSET_2_UNITS APND | ZP 26 Hub | 78 | 0.9 | 73 | 83 | 50 | N |  |  | OP | X | 5 | 1989 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 1H | [23 empty] | N |  | N | bar: T to BLQ
Vintage1989 | natural gas peaker | TRUE | 12687 | Midway-Sunset Cogeneration Co | 52169 | Midway Sunset Cogen | CA | Kern | C | Natural Gas Fired Combustion Turbine | GT |  | J | X | X | POD SUNSET_2_UNITS POD | ZP 26 Hub | 78 | 0.9 | 73 | 83 | 50 | N |  |  | OA | X | 5 | 1989 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 1H | [23 empty] | N |  | N | bar: T to BLQ
Vintage1987 | hydro | TRUE | 56838 | KEI (Maine) Power Management (III) LLC | 52171 | Upper Barker | ME | Androscoggin | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.99 | 1 | 1 | 0.2 | N |  |  | OP | X | 5 | 1987 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage1989 | hydro | TRUE | 42659 | Pennsylvania Renewable Resources | 52173 | Conemaugh Hydro Plant | PA | Westmoreland | GEN1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 7.5 | 0.9 | 2 | 4 | 1.1 | N |  |  | OP | X | 2 | 1989 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1989 | hydro | TRUE | 42659 | Pennsylvania Renewable Resources | 52173 | Conemaugh Hydro Plant | PA | Westmoreland | GEN2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 7.5 | 0.9 | 2 | 4 | 1.1 | N |  |  | OP | X | 2 | 1989 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  | N | N |  | 10M | [23 empty] | N
Vintage1990 | geothermal | TRUE | 56677 | Cyrq Energy Corp | 52174 | Soda Lake Geothermal No I II | NV | Churchill | OEC4 | Geothermal | ST |  | S | X | X |  |  | 3.5 | 0.8 | 1.3 | 1.8 | 0.4 | N |  |  | SB | Y | 10 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: GEO; NG: GEO |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage1990 | geothermal | TRUE | 56677 | Cyrq Energy Corp | 52174 | Soda Lake Geothermal No I II | NV | Churchill | OEC5 | Geothermal | ST |  | S | X | X |  |  | 3.5 | 0.8 | 1.3 | 1.7 | 0.4 | N |  |  | SB | Y | 10 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: GEO; NG: GEO |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage1990 | geothermal | TRUE | 56677 | Cyrq Energy Corp | 52174 | Soda Lake Geothermal No I II | NV | Churchill | OEC6 | Geothermal | ST |  | S | X | X |  |  | 3.5 | 0.8 | 1.3 | 1.7 | 0.4 | N |  |  | SB | Y | 10 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: GEO; NG: GEO |  |  | N |  |  | 1H | [23 empty] | N | N
Vintage1942 | other | FALSE | 7168 | CITGO Petroleum Corp | 52175 | CITGO Refinery Powerhouse | LA | Calcasieu | GEN1 | Other Gases | ST |  | S | X | X |  |  | 25 | 0.9 | 5.6 | 5.5 | 0 | N |  |  | OS | X | 1 | 1942 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: OG; WDS: NG; NG: NG |  |  | N |  |  | 12H | [23 empty] | Y | N | N
Vintage1942 | other | FALSE | 7168 | CITGO Petroleum Corp | 52175 | CITGO Refinery Powerhouse | LA | Calcasieu | GEN2 | Other Gases | ST |  | S | X | X |  |  | 25 | 0.9 | 8.5 | 8.9 | 3.5 | N |  |  | OP | X | 1 | 1942 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: OG; WDS: NG; NG: NG |  |  | N |  |  | 12H | [23 empty] | Y | N | N
Vintage1969 | other | FALSE | 7168 | CITGO Petroleum Corp | 52175 | CITGO Refinery Powerhouse | LA | Calcasieu | GEN3 | Other Gases | ST |  | S | X | X |  |  | 25 | 0.9 | 17.4 | 24.2 | 3.5 | N |  |  | OP | X | 3 | 1969 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: OG; WDS: NG; NG: NG |  |  | N |  |  | 12H | [23 empty] | Y | N | N
Vintage1987 | natural gas combined cycle | TRUE | 15300 | BHER Power Resources, Inc | 52176 | C R Wing Cogen Plant | TX | Howard | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | FLCNS_CC1 |  | 77.5 | 0.85 | 71 | 71 | 45 | N |  |  | OP | X | 7 | 1987 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: T to BLQ
Vintage1987 | natural gas combined cycle | TRUE | 15300 | BHER Power Resources, Inc | 52176 | C R Wing Cogen Plant | TX | Howard | GEN2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | FLCNS-CC1 |  | 77.5 | 0.85 | 71 | 71 | 45 | N |  |  | OP | X | 7 | 1987 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: T to BLQ
Vintage1988 | natural gas combined cycle | TRUE | 15300 | BHER Power Resources, Inc | 52176 | C R Wing Cogen Plant | TX | Howard | GEN3 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | FLCNS-CC1 |  | 75 | 0.85 | 70 | 70 | 40 | N |  |  | OP | X | 4 | 1988 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: T to BLQ
Vintage1988 | natural gas peaker | FALSE | 18617 | Tesoro Alaska Company LLC | 52184 | Tesoro Kenai Cogeneration Plant | AK | Kenai Peninsula | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 4.3 | 0.8 | 4.2 | 4.7 | 0.4 | N |  |  | OP | X | 11 | 1988 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: NG; WDS: DFO; NG: NG |  |  | N | N |  | 10M | [23 empty] | Y | N | Y
Vintage1988 | natural gas peaker | FALSE | 18617 | Tesoro Alaska Company LLC | 52184 | Tesoro Kenai Cogeneration Plant | AK | Kenai Peninsula | GEN2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 4.3 | 0.8 | 4.2 | 4.7 | 0.4 | N |  |  | OP | X | 11 | 1988 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: NG; WDS: DFO; NG: NG |  |  | N | N | 0 | 10M | [23 empty] | Y | N | Y
Vintage1990 | natural gas peaker | TRUE | 20323 | Wellhead Services, Inc | 52186 | Yuba City Cogen Partners | CA | Sutter | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 49.9 | 0.9 | 49.9 | 49.9 | 42 | N |  |  | OP | X | 12 | 1990 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: T to BLQ
Vintage1984 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 52187 | Falls Creek | OR | Linn | GE-1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 4.1 | 0.85 | 3.9 | 4.8 | 0.2 | N |  |  | OP | X | 12 | 1984 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  | N | N |  | 1H | [23 empty] | N
Vintage2000 | natural gas peaker | FALSE | 56605 | Delaware City Refining Company LLC | 52193 | Delaware City Plant | DE | New Castle | CT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | Motiva | Motiva | 92 | 1 | 65 | 72 | 45 | N |  |  | OP | X | 5 | 2000 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | bar: T to BLQ; NG
Vintage2000 | natural gas peaker | FALSE | 56605 | Delaware City Refining Company LLC | 52193 | Delaware City Plant | DE | New Castle | CT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | Motiva | Motiva | 92 | 1 | 65 | 72 | 45 | N |  |  | OP | X | 5 | 2000 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | bar: T to BLQ; NG
Vintage1956 | other | FALSE | 56605 | Delaware City Refining Company LLC | 52193 | Delaware City Plant | DE | New Castle | G1 | Other Gases | ST |  | S | X | X | Motiva | Motiva | 27.5 | 1 | 29.5 | 29.5 | 15 | N |  |  | OP | X | 10 | 1956 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: OG; WDS: NG; NG: OG |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1956 | other | FALSE | 56605 | Delaware City Refining Company LLC | 52193 | Delaware City Plant | DE | New Castle | G2 | Other Gases | ST |  | S | X | X | Motiva | Motiva | 27.5 | 1 | 29.5 | 29.5 | 15 | N |  |  | OP | X | 10 | 1956 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: OG; WDS: NG; NG: OG |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1961 | other | FALSE | 56605 | Delaware City Refining Company LLC | 52193 | Delaware City Plant | DE | New Castle | G3 | Other Gases | ST |  | S | X | X | Motiva | Motiva | 75 | 1 | 66 | 66 | 17 | N |  |  | SB | Y | 11 | 1961 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: OG; WDS: NG; NG: OG |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1982 | other | FALSE | 56605 | Delaware City Refining Company LLC | 52193 | Delaware City Plant | DE | New Castle | G4 | Other Gases | ST |  | S | X | X | Motiva | Motiva | 10 | 1 | 10 | 10 | 3 | N |  |  | OP | X | 6 | 1982 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: OG; WDS: NG; NG: OG |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1989 | other | FALSE | 17610 | WestRock Southeast, LLC | 54004 | WestRock Southeast, LLC. | GA | Laurens | GEN1 | All Other | ST |  | S | X | X |  |  | 45 | 0.94 | 44 | 44 | 3 | N |  |  | OP | X | 7 | 1989 |  |  | Y | Industrial CHP | 7 | B | TDF | WDS | BIT | SLW | OBS | NG | NG |  |  |  | N |  |  | 12H | Y |  |  |  | N | Y | [17 empty] | Y | Y | N
Vintage1989 | natural gas peaker | FALSE | 17610 | WestRock Southeast, LLC | 54004 | WestRock Southeast, LLC. | GA | Laurens | GEN2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 37.1 | 0.94 | 40 | 42 | 3 | N |  |  | OP | X | 6 | 1989 |  |  | Y | Industrial CHP | 7 | B: T; TDF: NG; WDS: DFO |  |  |  | N |  |  | 1H | [23 empty] | Y | Y | Y
Vintage1989 | hydro | TRUE | 12380 | Montana Dept-Natural Res&Consv | 54006 | Broadwater Power Project | MT | Broadwater | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 9.7 | 1 | 9.7 | 9.7 | 1.5 | N |  |  | OP | X | 6 | 1989 |  |  | N | IPP Non-CHP | 2 | B: X; TDF: WAT |  |  |  | N | N |  | 1H
Vintage1993 | biomass | TRUE | 57224 | MM West Covina Energy LLC | 54015 | MM West Covina | CA | Los Angeles | GEN2 | Landfill Gas | ST |  | S | X | X |  |  | 6.8 | 0.98 | 5.4 | 5.4 | 5.2 | N |  |  | OP | X | 6 | 1993 |  |  | N | IPP Non-CHP | 2 | B: X; TDF: LFG; WDS: NG; NG: NG |  |  |  | N |  |  | 1H | [23 empty] | Y | Y | N
Vintage1987 | hydro | TRUE | 11295 | Los Angeles County-San Gabriel | 54017 | San Gabriel Hydro Project | CA | Los Angeles | U1 | Conventional Hydroelectric | HY |  | S | X | X | N/A | N/A | 3.9 | 0.9 | 3.7 | 3.6 | 0.8 | N |  |  | OP | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | B: X; TDF: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1987 | hydro | TRUE | 11295 | Los Angeles County-San Gabriel | 54017 | San Gabriel Hydro Project | CA | Los Angeles | U2 | Conventional Hydroelectric | HY |  | S | X | X | N/A | N/A | 1.1 | 0.9 | 1.1 | 1 | 0.1 | N |  |  | OP | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | B: X; TDF: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1994 | natural gas combined cycle | TRUE | 6838 | Rensselaer Generating LLC | 54034 | Rensselaer Cogen | NY | Rensselaer | GEN1 | Natural Gas Fired Combined Cycle | CT | G701 | S | X | N | PTID 23796 | PTID 23796 | 49.2 | 0.85 | 47 | 58 | 45 | N |  |  | OP | X | 4 | 1994 |  |  | N | IPP Non-CHP | 2 | B: X; TDF: NG; WDS: DFO; NG: NG |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | Y | N | Y
Vintage1994 | natural gas combined cycle | TRUE | 6838 | Rensselaer Generating LLC | 54034 | Rensselaer Cogen | NY | Rensselaer | GEN2 | Natural Gas Fired Combined Cycle | CA | G701 | S | Y | X | PTID 23796 | PTID 23796 | 39 | 0.85 | 33.4 | 30 | 15 | N |  |  | OP | X | 4 | 1994 |  |  | N | IPP Non-CHP | 2 | B: X; TDF: NG; WDS: DFO; NG: NG |  |  |  | N | N |  | 12H | [20 empty] | N |  |  | Y | N | Y
Vintage1989 | geothermal | TRUE | 34691 | Ormat Nevada Inc | 54038 | Geo East Mesa II | CA | Imperial | GEN1 | Geothermal | ST |  | S | X | X |  |  | 21.6 | 0.9 | 14.4 | 21.6 | 13.5 | N |  |  | OS | X | 4 | 1989 |  |  | N | IPP Non-CHP | 2 | B: X; TDF: GEO; NG: GEO |  |  |  | N |  |  | OVER | [23 empty] | N
Vintage1992 | natural gas combined cycle | TRUE | 11127 | Lockport Energy Associates LP | 54041 | Lockport Energy Associates LP | NY | Niagara | GEN1 | Natural Gas Fired Combined Cycle | CT | LEA1 | S | X | Y | nyiso ptid 23791 | nyiso ptid 23791 | 48.7 | 0.85 | 42.3 | 50.8 | 30 | N |  |  | OP | X | 7 | 1992 |  |  | Y | IPP CHP | 3 | B: T; TDF: NG; WDS: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1992 | natural gas combined cycle | TRUE | 11127 | Lockport Energy Associates LP | 54041 | Lockport Energy Associates LP | NY | Niagara | GEN2 | Natural Gas Fired Combined Cycle | CT | LEA1 | S | X | Y | nyiso ptid 23791 | nyiso ptid 23791 | 48.7 | 0.85 | 42.3 | 50.8 | 30 | N |  |  | OP | X | 7 | 1992 |  |  | Y | IPP CHP | 3 | B: T; TDF: NG; WDS: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1992 | natural gas combined cycle | TRUE | 11127 | Lockport Energy Associates LP | 54041 | Lockport Energy Associates LP | NY | Niagara | GEN3 | Natural Gas Fired Combined Cycle | CT | LEA1 | S | X | Y | nyiso ptid 23791 | nyiso ptid 23791 | 48.7 | 0.85 | 42.3 | 50.8 | 30 | N |  |  | OP | X | 7 | 1992 |  |  | Y | IPP CHP | 3 | B: T; TDF: NG; WDS: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1992 | natural gas combined cycle | TRUE | 11127 | Lockport Energy Associates LP | 54041 | Lockport Energy Associates LP | NY | Niagara | GEN4 | Natural Gas Fired Combined Cycle | CA | LEA1 | S | Y | X |  |  | 75.2 | 0.98 | 78 | 80 | 14 | N |  |  | OP | X | 9 | 1992 |  |  | Y | IPP CHP | 3 | B: T; TDF: NG; WDS: DFO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2002 | natural gas peaker | FALSE | 19528 | University of Illinois | 54044 | University of Illinois Cogen Facility | IL | Cook | CT1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 7.8 | 0.86 | 6.4 | 7.8 | 0.5 | N |  |  | OP | X | 1 | 2002 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | bar: B to TDF
Vintage2002 | natural gas peaker | FALSE | 19528 | University of Illinois | 54044 | University of Illinois Cogen Facility | IL | Cook | CT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 7.8 | 0.86 | 6.4 | 7.8 | 0.5 | N |  |  | OP | X | 1 | 2002 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: B to TDF
Vintage2002 | natural gas peaker | FALSE | 19528 | University of Illinois | 54044 | University of Illinois Cogen Facility | IL | Cook | CT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 7.8 | 0.86 | 6.4 | 7.8 | 0.5 | N |  |  | OP | X | 1 | 2002 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: B to TDF
Vintage1993 | natural gas peaker | FALSE | 19528 | University of Illinois | 54044 | University of Illinois Cogen Facility | IL | Cook | GEN1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 6.3 | 0.8 | 6.3 | 6.3 | 3 | N |  |  | OP | X | 4 | 1993 |  |  | Y | Commercial CHP | 5 | B: T; TDF: NG; WDS: DFO; NG: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | Y | Y
Vintage1993 | natural gas peaker | FALSE | 19528 | University of Illinois | 54044 | University of Illinois Cogen Facility | IL | Cook | GEN2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 6.3 | 0.8 | 6.3 | 6.3 | 3 | N |  |  | OP | X | 5 | 1993 |  |  | Y | Commercial CHP | 5 | B: T; TDF: NG; WDS: DFO; NG: DFO |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | Y | Y | Y
Vintage2000 | natural gas peaker | FALSE | 19528 | University of Illinois | 54044 | University of Illinois Cogen Facility | IL | Cook | GEN3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.7 | 0.8 | 3.7 | 3.7 | 1 | N |  |  | OS | X | 7 | 2000 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: B to TDF
Vintage2000 | natural gas peaker | FALSE | 19528 | University of Illinois | 54044 | University of Illinois Cogen Facility | IL | Cook | GEN4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 3.7 | 0.8 | 3.7 | 3.7 | 1 | N |  |  | OS | X | 7 | 2000 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | bar: B to TDF
Vintage2002 | natural gas peaker | FALSE | 19528 | University of Illinois | 54044 | University of Illinois Cogen Facility | IL | Cook | RE1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 5.5 | 0.95 | 5.5 | 5.5 | 1 | N |  |  | OP | X | 1 | 2002 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | bar: B to TDF
Vintage2002 | natural gas peaker | FALSE | 19528 | University of Illinois | 54044 | University of Illinois Cogen Facility | IL | Cook | RE2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 5.5 | 0.95 | 5.5 | 5.5 | 1 | N |  |  | OP | X | 1 | 2002 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N |  | N | bar: B to TDF
Vintage2002 | natural gas peaker | FALSE | 19528 | University of Illinois | 54044 | University of Illinois Cogen Facility | IL | Cook | RE3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 5.5 | 0.95 | 5.5 | 5.5 | 1 | N |  |  | OP | X | 1 | 2002 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N |  | N | bar: B to TDF
Vintage1988 | biomass | TRUE | 16073 | Riverview Energy Systems | 54057 | Riverview Energy Systems | MI | Wayne | GEN1 | Landfill Gas | GT |  | S | X | X | n/a | n/a | 3.3 | 0.8 | 2.8 | 3.2 | 1.1 | N |  |  | OP | X | 1 | 1988 |  |  | N | IPP Non-CHP | 2 | B: X; TDF: LFG |  |  |  | N | N |  | 1H |  |  |  |  | N | [18 empty] | N | N | N
Vintage1988 | biomass | TRUE | 16073 | Riverview Energy Systems | 54057 | Riverview Energy Systems | MI | Wayne | GEN2 | Landfill Gas | GT |  | S | X | X |  |  | 3.3 | 0.8 | 2.8 | 3.2 | 1.1 | N |  |  | OP | X | 1 | 1988 |  |  | N | IPP Non-CHP | 2 | B: X; TDF: LFG |  |  |  | N | N |  | 1H |  |  |  |  | N | [18 empty] | N | N | N
Vintage1994 | natural gas combined cycle | TRUE | 9261 | Indeck-Olean Ltd Partnership | 54076 | Indeck Olean Energy Center | NY | Cattaraugus | GEN1 | Natural Gas Fired Combined Cycle | CT | G721 | S | X | N | PTID# 23982 | PTID# 23982 | 46 | 0.9 | 34.1 | 43.2 | 29 | N |  |  | OP | X | 1 | 1994 |  |  | Y | IPP CHP | 3 | B: T; TDF: NG; WDS: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1994 | natural gas combined cycle | TRUE | 9261 | Indeck-Olean Ltd Partnership | 54076 | Indeck Olean Energy Center | NY | Cattaraugus | GEN2 | Natural Gas Fired Combined Cycle | CA | G721 | S | Y | X | PTID# 23982 | PTID# 23982 | 44.6 | 0.9 | 44.6 | 44.6 | 34 | N |  |  | OP | X | 1 | 1994 |  |  | Y | IPP CHP | 3 | B: T; TDF: NG; WDS: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1992 | natural gas steam turbine | TRUE | 61854 | Veolia Energy Operating Service | 54081 | Spruance Operating Services LLC | VA | Richmond City | GEN3 | Natural Gas Steam Turbine | ST |  | W | X | X | 76427823 | 76427823 | 57.4 | 0.85 | 42.5 | 42.5 | 5 | N |  |  | OP | X | 8 | 1992 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H |  |  | N |  | N | [18 empty] | N | N | N | bar: B to TDF; NG
Vintage1992 | natural gas steam turbine | TRUE | 61854 | Veolia Energy Operating Service | 54081 | Spruance Operating Services LLC | VA | Richmond City | GEN4 | Natural Gas Steam Turbine | ST |  | W | X | X | 76427825 | 76427825 | 57.4 | 0.85 | 12.5 | 12.5 | 5 | N |  |  | OP | X | 8 | 1992 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H |  |  | N | N | N | [18 empty] | N | N | N | bar: B to TDF; NG
Vintage1964 | natural gas steam turbine | FALSE | 55738 | Pixelle Androscoggin LLC | 54085 | Androscoggin Mill | ME | Franklin | GEN1 | Natural Gas Steam Turbine | ST |  | S | X | X | 4001 | 4168 | 25 | 0.9 | 25 | 25 | 9 | N |  |  | OP | X | 1 | 1964 |  |  | Y | Industrial CHP | 7 | T | NG | WDS | SLW | WO | BLQ |  | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1966 | natural gas steam turbine | FALSE | 55738 | Pixelle Androscoggin LLC | 54085 | Androscoggin Mill | ME | Franklin | GEN2 | Natural Gas Steam Turbine | ST |  | S | X | X | 4001 | 4168 | 25 | 0.9 | 25 | 25 | 9 | N |  |  | OP | X | 1 | 1966 |  |  | Y | Industrial CHP | 7 | T | NG | WDS | SLW | WO | BLQ |  | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1974 | natural gas steam turbine | FALSE | 55738 | Pixelle Androscoggin LLC | 54085 | Androscoggin Mill | ME | Franklin | GEN3 | Natural Gas Steam Turbine | ST |  | S | X | X | 4001 | 4168 | 30 | 0.9 | 30 | 30 | 8 | N |  |  | OP | X | 1 | 1974 |  |  | Y | Industrial CHP | 7 | T | NG | WDS | SLW | WO | BLQ |  | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1966 | biomass | TRUE | 9390 | International Paper Co-GT Mill | 54087 | International Paper Georgetown Mill | SC | Georgetown | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 25.6 | 0.85 | 25.3 | 25.6 | 10 | N |  |  | OP | X | 1 | 1966 |  |  | Y | Industrial CHP | 7 | B: T; TDF: BLQ; WDS: RFO; NG: BLQ |  |  |  | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage1984 | biomass | TRUE | 9390 | International Paper Co-GT Mill | 54087 | International Paper Georgetown Mill | SC | Georgetown | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 29.5 | 0.85 | 27.4 | 27.7 | 10 | N |  |  | OP | X | 9 | 1984 |  |  | Y | Industrial CHP | 7 | T | WDS | TDF | NG | RFO | BIT |  | WDS |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1984 | biomass | TRUE | 9390 | International Paper Co-GT Mill | 54087 | International Paper Georgetown Mill | SC | Georgetown | GEN3 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 40.5 | 0.85 | 37.7 | 38.1 | 10 | N |  |  | OP | X | 9 | 1984 |  |  | Y | Industrial CHP | 7 | T | WDS | TDF | NG | RFO | BIT |  | WDS |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1981 | biomass | TRUE | 9312 | IPC-Mansfield Mill | 54091 | Mansfield Mill | LA | DeSoto | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 40 | 0.9 | 24.6 | 27.8 | 10 | N |  |  | OP | X | 10 | 1981 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | TDF | WO |  | RFO |  |  |  | N |  |  | 1H | [23 empty] | Y | Y | N
Vintage1981 | biomass | TRUE | 9312 | IPC-Mansfield Mill | 54091 | Mansfield Mill | LA | DeSoto | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 40 | 0.9 | 25.6 | 27.7 | 10 | N |  |  | OP | X | 12 | 1981 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | TDF | WO |  | RFO |  |  |  | N |  |  | 1H | [23 empty] | Y | Y | N
Vintage1981 | biomass | TRUE | 9312 | IPC-Mansfield Mill | 54091 | Mansfield Mill | LA | DeSoto | GEN3 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 30 | 0.9 | 22.1 | 25 | 10 | N |  |  | OP | X | 12 | 1981 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | TDF | WO |  | RFO |  |  |  | N |  |  | 1H | [23 empty] | Y | Y | N
Vintage2019 | natural gas peaker | FALSE | 9312 | IPC-Mansfield Mill | 54091 | Mansfield Mill | LA | DeSoto | GEN5 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 62 | 0.85 | 45 | 48 | 10 | N |  |  | OP | X | 7 | 2019 |  |  | N | Industrial CHP | 7 | [11 empty] | N |  |  | 1H | [23 empty] | N | bar: B to TDF
Vintage1967 | natural gas steam turbine | FALSE | 9393 | International Paper Co-Riverdl | 54096 | International Paper Riverdale Mill | AL | Dallas | GEN1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 11.6 | 0.85 | 11.6 | 11.6 | 2 | N |  |  | OP | X | 1 | 1967 |  |  | N | Industrial CHP | 7 | X | NG | BLQ | WDS | DFO |  |  | NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1985 | biomass | TRUE | 9393 | International Paper Co-Riverdl | 54096 | International Paper Riverdale Mill | AL | Dallas | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 37.4 | 0.85 | 37.4 | 37.4 | 10 | N |  |  | OP | X | 1 | 1985 |  |  | N | Industrial CHP | 7 | X | BLQ | NG | WDS | DFO |  |  | NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1994 | natural gas combined cycle | FALSE | 9393 | International Paper Co-Riverdl | 54096 | International Paper Riverdale Mill | AL | Dallas | GEN3 | Natural Gas Fired Combined Cycle | CA | CC01 | S | Y | X |  |  | 17 | 1 | 17 | 17 | 2 | N |  |  | OP | X | 11 | 1994 |  |  | N | Industrial CHP | 7 | X | NG | BFG | WDS | DFO | [6 empty] | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1994 | natural gas combined cycle | FALSE | 9393 | International Paper Co-Riverdl | 54096 | International Paper Riverdale Mill | AL | Dallas | GEN4 | Natural Gas Fired Combined Cycle | CT | CC01 | S | X | Y |  |  | 38.2 | 0.85 | 38.2 | 38.2 | 17 | N |  |  | SB | Y | 11 | 1994 |  |  | Y | Industrial CHP | 7 | B: T; TDF: NG; WDS: DFO; NG: NG |  |  |  | N |  |  | 1H | [23 empty] | Y | Y | N
Vintage1972 | biomass | TRUE | 61963 | Graphic Packaging International - Texarkana | 54097 | International Paper Texarkana Mill | TX | Cass | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 25 | 0.85 | 25 | 25 | 5 | N |  |  | OP | X | 1 | 1972 |  |  | Y | Industrial CHP | 7 | B: T; TDF: BLQ; WDS: NG; NG: WDS |  |  |  | N | N | 0 | 1H | [23 empty] | Y | Y | N
Vintage1977 | biomass | TRUE | 61963 | Graphic Packaging International - Texarkana | 54097 | International Paper Texarkana Mill | TX | Cass | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 40 | 0.85 | 40 | 40 | 5 | N |  |  | OP | X | 1 | 1977 |  |  | Y | Industrial CHP | 7 | T | BLQ | OBS | NG | WDS |  |  | NG | WDS |  |  | N | N | 0 | 1H | [23 empty] | Y | Y | N
Vintage1951 | biomass | TRUE | 54738 | Thilmany LLC | 54098 | Kaukauna Paper Mill | WI | Outagamie | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 6 | 0.8 | 6 | 6 | 1 | N |  |  | OP | X | 1 | 1951 |  |  | Y | Industrial CHP | 7 | T | BLQ | BIT | WDS | NG | TDF | RFO | NG | RFO |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | Y | Y | Y
Vintage1977 | biomass | TRUE | 54738 | Thilmany LLC | 54098 | Kaukauna Paper Mill | WI | Outagamie | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 11 | 0.89 | 11 | 11 | 1 | N |  |  | OP | X | 1 | 1977 |  |  | Y | Industrial CHP | 7 | T | BLQ | BIT | WDS | NG | TDF | RFO | NG | RFO |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | Y | Y | Y
Vintage1962 | biomass | TRUE | 54738 | Thilmany LLC | 54098 | Kaukauna Paper Mill | WI | Outagamie | GEN3 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 15.6 | 0.85 | 15.6 | 15.6 | 2 | N |  |  | OP | X | 1 | 1962 |  |  | N | Industrial CHP | 7 | X | BLQ | BIT | WDS | NG | TDF | RFO | NG | RFO |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | Y
Vintage1967 | hard coal | FALSE | 54738 | Thilmany LLC | 54098 | Kaukauna Paper Mill | WI | Outagamie | GEN4 | Conventional Steam Coal | ST |  | S | X | X |  |  | 12 | 0.8 | 12 | 12 | 1 | N |  |  | OP | X | 1 | 1967 |  |  | Y | Industrial CHP | 7 | T | BIT | TDF | NG | RFO |  |  | NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | Y
Vintage1970 | natural gas steam turbine | FALSE | 9350 | IPC-Ticonderoga | 54099 | Ticonderoga Mill | NY | Essex | GEN1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 42.1 | 0.9 | 41 | 39 | 2 | N |  |  | OP | X | 1 | 1970 |  |  | Y | Industrial CHP | 7 | B | NG | BLQ | WDS | RFO | OG |  | PG | RFO | NG |  | N | N |  | 12H | [23 empty] | N |  | N
Vintage1967 | biomass | TRUE | 9382 | International Paper Co-Vicksbg | 54100 | International Paper Vicksburg Mill | MS | Warren | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 2.5 | 0.8 | 1.5 | 1.5 | 0.5 | N |  |  | OP | X | 1 | 1967 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | RFO | AB | TDF |  | BLQ |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1967 | biomass | TRUE | 9382 | International Paper Co-Vicksbg | 54100 | International Paper Vicksburg Mill | MS | Warren | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 48 | 0.95 | 37 | 37 | 6 | N |  |  | OP | X | 1 | 1967 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | RFO | AB | TDF |  | BLQ |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1963 | biomass | TRUE | 7172 | Georgia-Pacific Cedar Springs LLC | 54101 | Georgia-Pacific Cedar Springs | GA | Early | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 50 | 0.85 | 45 | 50 | 5 | N |  |  | OP | X | 10 | 1963 |  |  | Y | Industrial CHP | 7 | T | BLQ | BIT | WDS | RFO | DFO |  | NG |  |  |  | N | N | 0 | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1965 | biomass | TRUE | 7172 | Georgia-Pacific Cedar Springs LLC | 54101 | Georgia-Pacific Cedar Springs | GA | Early | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 51.2 | 0.85 | 45 | 50 | 5 | N |  |  | OP | X | 8 | 1965 |  |  | Y | Industrial CHP | 7 | T | BLQ | BIT | WDS | RFO | DFO |  | NG |  |  |  | N | N |  | OVER |  | Y |  |  | Y | [18 empty] | Y | Y | N
Vintage1913 | hydro | FALSE | 5033 | Domtar Industries Inc | 54103 | Port Edwards Mill | WI | Wood | HG1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 1 | 1913 |  |  | N | Industrial Non-CHP | 6 | T T X: X; BLQ BLQ BLQ: WAT |  |  | N |  | 0 | 1H
Vintage1913 | hydro | FALSE | 5033 | Domtar Industries Inc | 54103 | Port Edwards Mill | WI | Wood | HG2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OA | X | 1 | 1913 |  |  | N | Industrial Non-CHP | 6 | T T X: X; BLQ BLQ BLQ: WAT |  |  | N |  | 0 | 1H
Vintage1913 | hydro | FALSE | 5033 | Domtar Industries Inc | 54103 | Port Edwards Mill | WI | Wood | HG3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 1 | 1913 |  |  | N | Industrial Non-CHP | 6 | T T X: X; BLQ BLQ BLQ: WAT |  |  | N |  | 0 | 1H
Vintage1913 | hydro | FALSE | 5033 | Domtar Industries Inc | 54103 | Port Edwards Mill | WI | Wood | HG4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OP | X | 1 | 1913 |  |  | N | Industrial Non-CHP | 6 | T T X: X; BLQ BLQ BLQ: WAT |  |  | N |  | 0 | 1H
Vintage1926 | hydro | FALSE | 5033 | Domtar Industries Inc | 54103 | Port Edwards Mill | WI | Wood | HG5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | N |  |  | OP | X | 1 | 1926 |  |  | N | Industrial Non-CHP | 6 | T T X: X; BLQ BLQ BLQ: WAT |  |  | N |  | 0 | 1H
Vintage1926 | hydro | FALSE | 5033 | Domtar Industries Inc | 54103 | Port Edwards Mill | WI | Wood | HG6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | N |  |  | OA | X | 1 | 1926 |  |  | N | Industrial Non-CHP | 6 | T T X: X; BLQ BLQ BLQ: WAT |  |  | N |  | 0 | 1H
Vintage1926 | hydro | FALSE | 5033 | Domtar Industries Inc | 54103 | Port Edwards Mill | WI | Wood | JHG1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 1 | 1.2 | 1.2 | 0.6 | N |  |  | OP | X | 1 | 1926 |  |  | N | Industrial Non-CHP | 6 | T T X: X; BLQ BLQ BLQ: WAT |  |  | N |  | 0 | 1H
Vintage1938 | hydro | FALSE | 5033 | Domtar Industries Inc | 54103 | Port Edwards Mill | WI | Wood | JHG2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.3 | N |  |  | OP | X | 1 | 1938 |  |  | N | Industrial Non-CHP | 6 | T T X: X; BLQ BLQ BLQ: WAT |  |  | N |  | 0 | 1H
Vintage1939 | hydro | FALSE | 5033 | Domtar Industries Inc | 54103 | Port Edwards Mill | WI | Wood | JHG3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.3 | N |  |  | OP | X | 1 | 1939 |  |  | N | Industrial Non-CHP | 6 | T T X: X; BLQ BLQ BLQ: WAT |  |  | N |  | 0 | 1H
Vintage1943 | hydro | FALSE | 5033 | Domtar Industries Inc | 54103 | Port Edwards Mill | WI | Wood | JHG4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.2 | N |  |  | OA | X | 1 | 1943 |  |  | N | Industrial Non-CHP | 6 | T T X: X; BLQ BLQ BLQ: WAT |  |  | N |  | 0 | 1H
Vintage1977 | hydro | FALSE | 5033 | Domtar Industries Inc | 54103 | Port Edwards Mill | WI | Wood | JHG5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.3 | N |  |  | OS | X | 1 | 1977 |  |  | N | Industrial Non-CHP | 6 | T T X: X; BLQ BLQ BLQ: WAT |  |  | N |  | 0 | 1H
Vintage1968 | biomass | TRUE | 5262 | Domtar Industries Inc | 54104 | Ashdown | AR | Little River | GEN1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 19.5 | 0.9 | 17 | 17 | 5 | N |  |  | OP | X | 1 | 1968 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | BIT | RFO | TDF | NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | Y | Y | Y
Vintage1979 | biomass | TRUE | 5262 | Domtar Industries Inc | 54104 | Ashdown | AR | Little River | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 47 | 0.9 | 40 | 40 | 5 | N |  |  | OP | X | 10 | 1979 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | BIT | RFO | TDF | NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | Y | Y | Y
Vintage1991 | biomass | TRUE | 5262 | Domtar Industries Inc | 54104 | Ashdown | AR | Little River | GEN3 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 45 | 0.9 | 33 | 33 | 5 | N |  |  | OP | X | 4 | 1991 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | BIT | RFO | TDF | NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | Y | Y | Y
Vintage1991 | biomass | TRUE | 5262 | Domtar Industries Inc | 54104 | Ashdown | AR | Little River | GEN4 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 45 | 0.9 | 38 | 38 | 5 | N |  |  | OP | X | 4 | 1991 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | BIT | RFO | TDF | NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [18 empty] | Y | Y | Y
Vintage1993 | geothermal | TRUE | 49748 | ORCAL Geothermal, Inc | 54111 | Second Imperial Geothermal | CA | Imperial | GE10 | Geothermal | BT |  | W | X | X |  |  | 4.5 | 0.8 | 3.8 | 4.5 | 3.8 | N |  |  | OP | X | 6 | 1993 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: GEO |  |  |  | N |  |  | OVER | [23 empty] | N
Vintage1993 | geothermal | TRUE | 49748 | ORCAL Geothermal, Inc | 54111 | Second Imperial Geothermal | CA | Imperial | GE11 | Geothermal | BT |  | W | X | X |  |  | 4.5 | 0.8 | 3.8 | 4.5 | 3.8 | N |  |  | OP | X | 6 | 1993 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: GEO |  |  |  | N |  |  | OVER | [23 empty] | N
Vintage1993 | geothermal | TRUE | 49748 | ORCAL Geothermal, Inc | 54111 | Second Imperial Geothermal | CA | Imperial | GE12 | Geothermal | BT |  | W | X | X |  |  | 4.5 | 0.8 | 3.8 | 4.5 | 3.8 | N |  |  | OP | X | 6 | 1993 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: GEO |  |  |  | N |  |  | OVER | [23 empty] | N
Vintage2006 | geothermal | TRUE | 49748 | ORCAL Geothermal, Inc | 54111 | Second Imperial Geothermal | CA | Imperial | GE13 | Geothermal | BT |  | W | X | X |  |  | 16 | 0.8 | 12 | 16 | 12 | N |  |  | OP | X | 1 | 2006 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: GEO |  |  |  | N |  |  | OVER
Vintage1993 | geothermal | TRUE | 49748 | ORCAL Geothermal, Inc | 54111 | Second Imperial Geothermal | CA | Imperial | GEN1 | Geothermal | BT |  | W | X | X |  |  | 3.5 | 0.8 | 3 | 3.5 | 3 | N |  |  | OP | X | 6 | 1993 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: GEO |  |  |  | N |  |  | OVER
Vintage2008 | geothermal | TRUE | 49748 | ORCAL Geothermal, Inc | 54111 | Second Imperial Geothermal | CA | Imperial | GEN14 | Geothermal | BT |  | W | X | X |  |  | 16 | 0.8 | 12 | 16 | 12 | N |  |  | OP | X | 4 | 2008 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: GEO | [6 empty] | OVER
Vintage1993 | geothermal | TRUE | 49748 | ORCAL Geothermal, Inc | 54111 | Second Imperial Geothermal | CA | Imperial | GEN2 | Geothermal | BT |  | W | X | X |  |  | 3.5 | 0.8 | 3 | 3.5 | 3 | N |  |  | OP | X | 6 | 1993 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: GEO |  |  |  | N |  |  | OVER
Vintage1993 | geothermal | TRUE | 49748 | ORCAL Geothermal, Inc | 54111 | Second Imperial Geothermal | CA | Imperial | GEN3 | Geothermal | BT |  | W | X | X |  |  | 3.5 | 0.8 | 3 | 3.5 | 3 | N |  |  | OP | X | 6 | 1993 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: GEO |  |  |  | N |  |  | OVER
Vintage1993 | geothermal | TRUE | 49748 | ORCAL Geothermal, Inc | 54111 | Second Imperial Geothermal | CA | Imperial | GEN4 | Geothermal | BT |  | W | X | X |  |  | 3.5 | 0.8 | 3 | 3.5 | 3 | N |  |  | OP | X | 6 | 1993 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: GEO |  |  |  | N |  |  | OVER
Vintage1993 | geothermal | TRUE | 49748 | ORCAL Geothermal, Inc | 54111 | Second Imperial Geothermal | CA | Imperial | GEN5 | Geothermal | BT |  | W | X | X |  |  | 3.5 | 0.8 | 3 | 3.5 | 3 | N |  |  | OP | X | 6 | 1993 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: GEO |  |  |  | N |  |  | OVER
Vintage1993 | geothermal | TRUE | 49748 | ORCAL Geothermal, Inc | 54111 | Second Imperial Geothermal | CA | Imperial | GEN6 | Geothermal | BT |  | W | X | X |  |  | 3.5 | 0.8 | 3 | 3.5 | 3 | N |  |  | OP | X | 6 | 1993 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: GEO |  |  |  | N |  |  | OVER
Vintage1993 | geothermal | TRUE | 49748 | ORCAL Geothermal, Inc | 54111 | Second Imperial Geothermal | CA | Imperial | GEN7 | Geothermal | BT |  | W | X | X |  |  | 4.5 | 0.8 | 3.8 | 4.5 | 3.8 | N |  |  | OP | X | 6 | 1993 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: GEO |  |  |  | N |  |  | OVER
Vintage1993 | geothermal | TRUE | 49748 | ORCAL Geothermal, Inc | 54111 | Second Imperial Geothermal | CA | Imperial | GEN8 | Geothermal | BT |  | W | X | X |  |  | 4.5 | 0.8 | 3.8 | 4.5 | 3.8 | N |  |  | OP | X | 6 | 1993 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: GEO |  |  |  | N |  |  | OVER
Vintage1993 | geothermal | TRUE | 49748 | ORCAL Geothermal, Inc | 54111 | Second Imperial Geothermal | CA | Imperial | GEN9 | Geothermal | BT |  | W | X | X |  |  | 4.5 | 0.8 | 3.8 | 4.5 | 3.8 | N |  |  | OP | X | 6 | 1993 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: GEO |  |  |  | N |  |  | OVER
Vintage1994 | natural gas combined cycle | TRUE | 10349 | KIAC Partners | 54114 | Kennedy International Airport Cogen | NY | Queens | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N |  |  | 47.1 | 0.85 | 50.1 | 48.9 | 30 | N |  |  | OP | X | 12 | 1994 |  |  | Y | IPP CHP | 3 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1994 | natural gas combined cycle | TRUE | 10349 | KIAC Partners | 54114 | Kennedy International Airport Cogen | NY | Queens | GEN2 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N |  |  | 47.1 | 0.85 | 48.6 | 47.9 | 30 | N |  |  | OP | X | 12 | 1994 |  |  | Y | IPP CHP | 3 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1995 | natural gas combined cycle | TRUE | 10349 | KIAC Partners | 54114 | Kennedy International Airport Cogen | NY | Queens | GEN3 | Natural Gas Fired Combined Cycle | CA | CC1 | W | Y | X |  |  | 27 | 0.85 | 27.4 | 25.8 | 6 | N |  |  | OP | X | 1 | 1995 |  |  | Y | IPP CHP | 3 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1986 | hydro | TRUE | 56839 | KEI (Maine) Power Management (IV) LLC | 54123 | Mechanic Falls | ME | Androscoggin | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.99 | 1 | 1 | 0.1 | N |  |  | OP | X | 4 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N |  | N
Vintage1986 | hydro | TRUE | 56839 | KEI (Maine) Power Management (IV) LLC | 54123 | Mechanic Falls | ME | Androscoggin | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.99 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 4 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1986 | hydro | TRUE | 56837 | KEI (Maine) Power Management (II) LLC | 54124 | Pittsfield Hydro | ME | Somerset | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.99 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 7 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1986 | hydro | TRUE | 56837 | KEI (Maine) Power Management (II) LLC | 54124 | Pittsfield Hydro | ME | Somerset | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.3 | 0.99 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 7 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1986 | hydro | TRUE | 56837 | KEI (Maine) Power Management (II) LLC | 54124 | Pittsfield Hydro | ME | Somerset | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.99 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 7 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1993 | natural gas combined cycle | TRUE | 50136 | North American Energy Services | 54131 | Fortistar North Tonawanda | NY | Niagara | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N | 24026 | 24026 | 48.7 | 0.9 | 36.8 | 44.7 | 30.6 | N |  |  | OP | X | 7 | 1993 |  |  | Y | IPP CHP | 3 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1993 | natural gas combined cycle | TRUE | 50136 | North American Energy Services | 54131 | Fortistar North Tonawanda | NY | Niagara | GEN2 | Natural Gas Fired Combined Cycle | CA | CC1 | W | Y | X | 24026 | 24026 | 17 | 0.9 | 20 | 20 | 10 | N |  |  | OP | X | 7 | 1993 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: X T T T T to WAT BLQ BLQ BLQ BLQ
Vintage2020 | other | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | BES1 | Batteries | BA |  | S | X | X | 69256 | 69256 | 10 | 0.95 | 9.4 | 9.4 | 0.1 | N |  |  | OP | X | 12 | 2020 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: MWH |  |  |  | N | N |  | 10M
Vintage2020 | other | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | BES2 | Batteries | BA |  | S | X | X | 69256 | 69256 | 10 | 0.95 | 9.4 | 9.4 | 0.1 | N |  |  | OP | X | 12 | 2020 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: MWH |  |  |  | N | N |  | 10M
Vintage1925 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | DOH2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 0.9 | 1.3 | 1.3 | 0.2 | N |  |  | OS | X | 7 | 1925 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1925 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | DOH3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 0.9 | 1.3 | 1.3 | 0.2 | N |  |  | OS | X | 7 | 1925 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1925 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | DOH4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 0.9 | 1.8 | 1.8 | 0.2 | N |  |  | OS | X | 7 | 1925 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1988 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | DOH5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.3 | 0.9 | 5 | 4.9 | 0.5 | N |  |  | OP | X | 7 | 1988 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1975 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | DOH6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.1 | 0.9 | 3.9 | 3.8 | 0.5 | N |  |  | OP | X | 7 | 1975 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1975 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | DOH7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.1 | 0.9 | 3.9 | 3.8 | 0.5 | N |  |  | OP | X | 7 | 1975 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1930 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | DOH8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.9 | 3.4 | 3.3 | 0.2 | N |  |  | OP | X | 7 | 1930 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1948 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | EMH1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.9 | 1.5 | 1.5 | 0.2 | N |  |  | OP | X | 7 | 1948 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1948 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | EMH2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.9 | 1.5 | 1.5 | 0.2 | N |  |  | OP | X | 7 | 1948 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1948 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | EMH3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.9 | 1.5 | 1.5 | 0.2 | N |  |  | OP | X | 7 | 1948 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1948 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | EMH4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.9 | 1.5 | 1.5 | 0.2 | N |  |  | OP | X | 7 | 1948 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1948 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | EMH5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.9 | 1.5 | 1.5 | 0.2 | N |  |  | OP | X | 7 | 1948 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1948 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | EMH6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.6 | 0.9 | 1.5 | 1.5 | 0.2 | N |  |  | OP | X | 7 | 1948 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1953 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | MCH1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 12.2 | 0.9 | 11.6 | 11.2 | 8 | N |  |  | OP | X | 7 | 1953 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1953 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | MCH2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 12.2 | 0.9 | 11.6 | 11.2 | 8 | N |  |  | OP | X | 7 | 1953 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1967 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | MCH3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 13.2 | 0.9 | 12.5 | 12.1 | 9 | N |  |  | OP | X | 7 | 1967 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1917 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | MIH2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.5 | 0.9 | 5.3 | 5.8 | 0.5 | N |  |  | OP | X | 7 | 1917 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1917 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | MIH3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.5 | 0.9 | 5.3 | 5.8 | 0.5 | N |  |  | OP | X | 7 | 1917 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1917 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | MIH4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.1 | 0.9 | 5.5 | 5.5 | 0.5 | N |  |  | OP | X | 7 | 1917 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1921 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | MIH5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.1 | 0.9 | 4.9 | 4.7 | 0.5 | N |  |  | OP | X | 7 | 1921 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1921 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | MIH6 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.1 | 0.9 | 4.9 | 4.7 | 0.5 | N |  |  | OP | X | 7 | 1921 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1921 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | MIH7 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4 | 0.9 | 5.5 | 5.5 | 0.5 | N |  |  | OP | X | 7 | 1921 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1987 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | MIH8 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.4 | 0.9 | 5.1 | 5 | 0.5 | N |  |  | OP | X | 7 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1987 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | MIHI | Conventional Hydroelectric | HY |  | S | X | X |  |  | 5.4 | 0.9 | 5.1 | 5 | 0.5 | N |  |  | OP | X | 7 | 1987 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1986 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | NOH1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.2 | 0.9 | 3 | 2.9 | 0.5 | N |  |  | OP | X | 7 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1986 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | NOH2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.2 | 0.9 | 3 | 2.9 | 0.5 | N |  |  | OP | X | 7 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1986 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | NOH3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.2 | 0.9 | 3 | 2.9 | 0.5 | N |  |  | OP | X | 7 | 1986 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1940 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | WEH1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.8 | 0.9 | 4.6 | 4.4 | 0.5 | N |  |  | OP | X | 7 | 1940 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1940 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | WEH2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.8 | 0.9 | 4.6 | 4.4 | 0.5 | N |  |  | OP | X | 7 | 1940 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1940 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | WEH3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.8 | 0.9 | 4.6 | 4.4 | 0.5 | N |  |  | OP | X | 7 | 1940 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1940 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54134 | Great Lakes Hydro America - ME | ME | Penobscot | WEH4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.8 | 0.9 | 4.6 | 4.4 | 0.5 | N |  |  | OP | X | 7 | 1940 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1993 | hydro | TRUE | 5068 | Denver City & County of | 54142 | Hillcrest Pump Station | CO | Denver | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2 | 0.9 | 2 | 2 | 0.2 | N |  |  | OP | X | 6 | 1993 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1989 | hydro | TRUE | 56597 | Hydro Kennebec LLC | 54148 | Hydro Kennebec Project | ME | Kennebec | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7.7 | 0.9 | 7.7 | 7.7 | 0.5 | N |  |  | OP | X | 1 | 1989 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M
Vintage1989 | hydro | TRUE | 56597 | Hydro Kennebec LLC | 54148 | Hydro Kennebec Project | ME | Kennebec | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 7.7 | 0.9 | 7.7 | 7.7 | 0.5 | N |  |  | OP | X | 1 | 1989 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 10M
Vintage1995 | natural gas peaker | TRUE | 13587 | Nissequoque Cogen Partners | 54149 | Stony Brook Cogen Plant | NY | Suffolk | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | NYISO_STONY_BROOK_DA | NYISO_STONY_BROOK_DA | 47 | 0.85 | 44.5 | 47.1 | 23 | N |  |  | OP | X | 4 | 1995 |  |  | Y | IPP CHP | 3 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1978 | natural gas steam turbine | FALSE | 9434 | Iowa State University | 54201 | Iowa State University | IA | Story | GEN3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 13.2 | 0.85 | 13.3 | 13.3 | 2 | N |  |  | OP | X | 9 | 1978 |  |  | Y | Commercial CHP | 5 | T | NG | BIT | DFO |  |  |  | NG |  |  |  | N | N |  | 12H | Y |  |  |  | Y | [18 empty] | N | N | N
Vintage1970 | natural gas steam turbine | FALSE | 9434 | Iowa State University | 54201 | Iowa State University | IA | Story | GEN5 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 11.5 | 0.85 | 11.5 | 11.5 | 2 | N |  |  | OP | X | 3 | 1970 |  |  | Y | Commercial CHP | 5 | T | NG | BIT | DFO |  |  |  | NG |  |  |  | N | N |  | 12H | Y |  |  |  | Y | [18 empty] | N | N | N
Vintage2005 | natural gas steam turbine | FALSE | 9434 | Iowa State University | 54201 | Iowa State University | IA | Story | GEN6 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 15.1 | 0.85 | 15.1 | 15.1 | 3 | N |  |  | OP | X | 5 | 2005 |  |  | Y | Commercial CHP | 5 | T | NG | BIT | DFO |  |  |  | NG |  |  |  | N | N |  | 12H | Y |  |  |  | Y | [18 empty] | N | N | N
Vintage1920 | hydro | TRUE | 10963 | Lewiston City of | 54202 | Upper Androscoggin | ME | Androscoggin | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.8 | 0.7 | 0.7 | 0.2 | N |  |  | OS | X | 4 | 1920 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 12H
Vintage1920 | hydro | TRUE | 10963 | Lewiston City of | 54202 | Upper Androscoggin | ME | Androscoggin | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.2 | N |  |  | OS | X | 4 | 1920 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 12H
Vintage1920 | hydro | TRUE | 10963 | Lewiston City of | 54202 | Upper Androscoggin | ME | Androscoggin | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.8 | 0.5 | 0.5 | 0.2 | N |  |  | OS | X | 4 | 1920 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 12H
Vintage1991 | natural gas peaker | FALSE | 12704 | Mississippi Baptist Medical | 54203 | Mississippi Baptist Medical Center | MS | Hinds | A | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 4.2 | 0.8 | 4 | 4 | 2 | N |  |  | SB | Y | 1 | 1991 |  |  | Y | Commercial CHP | 5 | [11 empty] | N |  |  | 1H | [23 empty] | N | bar: X T T T T to WAT BLQ BLQ BLQ BLQ
Vintage1934 | other | FALSE | 56616 | Clevelandcliffs Warren | 54207 | Clevelandcliffs Warren | OH | Trumbull | GEN1 | Other Gases | ST |  | S | X | X |  |  | 3 | 0.8 | 2.8 | 2.8 | 1 | N |  |  | OP | X | 10 | 1934 |  |  | Y | Industrial CHP | 7 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: OG; WAT NG NG NG NG: NG; WAT NG NG NG NG: OG |  |  |  | N | N |  | 12H | [23 empty] | Y | N | N
Vintage1940 | other | FALSE | 56616 | Clevelandcliffs Warren | 54207 | Clevelandcliffs Warren | OH | Trumbull | GEN2 | Other Gases | ST |  | S | X | X |  |  | 7.5 | 0.8 | 7 | 7.1 | 1 | N |  |  | OP | X | 3 | 1940 |  |  | Y | Industrial CHP | 7 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: OG; WAT NG NG NG NG: NG; WAT NG NG NG NG: OG |  |  |  | N | N |  | 12H | [23 empty] | Y | N | N
Vintage1981 | other | FALSE | 56616 | Clevelandcliffs Warren | 54207 | Clevelandcliffs Warren | OH | Trumbull | GEN3 | Other Gases | ST |  | S | X | X |  |  | 10 | 0.8 | 9.3 | 9.4 | 1 | N |  |  | OP | X | 12 | 1981 |  |  | Y | Industrial CHP | 7 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: OG; WAT NG NG NG NG: NG; WAT NG NG NG NG: OG |  |  |  | N | N |  | 12H | [23 empty] | Y | N | N
Vintage1990 | hard coal | FALSE | 491 | American Crystal Sugar Co | 54210 | American Crystal Sugar Hillsboro | ND | Traill | G1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 13.3 | 0.8 | 13.3 | 13.3 | 0.5 | N |  |  | OP | X | 9 | 1990 |  |  | Y | Industrial CHP | 7 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: SUB; WAT NG NG NG NG: SUB |  |  |  | N | N |  | OVER | Y |  |  |  | Y | [18 empty] | N | N | N
Vintage1948 | hard coal | FALSE | 491 | American Crystal Sugar Co | 54211 | American Crystal Sugar Moorhead | MN | Clay | G1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 0.5 | N |  |  | OP | X | 9 | 1948 |  |  | Y | Industrial CHP | 7 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: SUB; WAT NG NG NG NG: SUB |  |  |  | N | N |  | OVER | Y |  |  |  | Y | [18 empty] | N | N | N
Vintage1961 | hard coal | FALSE | 491 | American Crystal Sugar Co | 54211 | American Crystal Sugar Moorhead | MN | Clay | G2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.5 | N |  |  | OP | X | 9 | 1961 |  |  | Y | Industrial CHP | 7 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: SUB; WAT NG NG NG NG: SUB |  |  |  | N | N |  | OVER | Y |  |  |  | Y | [18 empty] | N | N | N
Vintage1954 | hard coal | FALSE | 491 | American Crystal Sugar Co | 54212 | American Crystal Sugar Crookston | MN | Polk | G1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 3.5 | 0.8 | 3.5 | 3.5 | 0.5 | N |  |  | OP | X | 9 | 1954 |  |  | Y | Industrial CHP | 7 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: SUB; WAT NG NG NG NG: SUB |  |  |  | N | N |  | OVER | Y |  |  |  | Y | [18 empty] | N | N | N
Vintage1975 | hard coal | FALSE | 491 | American Crystal Sugar Co | 54212 | American Crystal Sugar Crookston | MN | Polk | G2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 0.5 | N |  |  | OP | X | 9 | 1975 |  |  | Y | Industrial CHP | 7 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: SUB; WAT NG NG NG NG: SUB |  |  |  | N | N |  | OVER | Y |  |  |  | Y | [18 empty] | N | N | N
Vintage1965 | hard coal | FALSE | 491 | American Crystal Sugar Co | 54213 | American Crystal Sugar Drayton | ND | Pembina | G1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 6 | 0.8 | 6 | 6 | 0.5 | N |  |  | OP | X | 9 | 1965 |  |  | Y | Industrial CHP | 7 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: SUB; WAT NG NG NG NG: SUB |  |  |  | N | N |  | OVER | Y |  |  |  | Y | [18 empty] | N | N | N
Vintage1990 | hard coal | FALSE | 491 | American Crystal Sugar Co | 54214 | American Crystal Sugar East Grand Forks | MN | Polk | G1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 9 | 1990 |  |  | Y | Industrial CHP | 7 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: SUB; WAT NG NG NG NG: SUB |  |  |  | N | N |  | OVER | Y |  |  |  | Y | [18 empty] | N | N | N
Vintage1990 | hard coal | FALSE | 491 | American Crystal Sugar Co | 54214 | American Crystal Sugar East Grand Forks | MN | Polk | G2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 5 | 0.8 | 5 | 5 | 0.5 | N |  |  | OP | X | 9 | 1990 |  |  | Y | Industrial CHP | 7 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: SUB; WAT NG NG NG NG: SUB |  |  |  | N | N |  | OVER | Y |  |  |  | Y | [18 empty] | N | N | N
Vintage2007 | biomass | TRUE | 2053 | Bowater Newport Coosa Pines Op | 54216 | U S Alliance Coosa Pines | AL | Talladega | GEN7 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 25.9 | 0.85 | 24.9 | 24.9 | 4 | N |  |  | OP | X | 11 | 2007 |  |  | Y | Industrial CHP | 7 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: BLQ; WAT NG NG NG NG: NG; WAT NG NG NG NG: NG | DFO |  |  | N | N |  | 12H |  | N | [18 empty] | N |  |  | N
Vintage2021 | petroleum | FALSE | 6738 | Franklin Heating Station | 54224 | Franklin Heating Station | MN | Olmsted | DG10 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.1 | 0.8 | 3.1 | 3.1 | 0.6 | N |  |  | SB | Y | 7 | 2021 |  |  | N | Commercial CHP | 5 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: DFO |  |  |  |  | N |  | 10M | [23 empty] | N | N | N
Vintage2009 | petroleum | FALSE | 6738 | Franklin Heating Station | 54224 | Franklin Heating Station | MN | Olmsted | DG4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | OP | X | 5 | 2009 |  |  | N | Commercial CHP | 5 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N |  | N
Vintage2011 | petroleum | FALSE | 6738 | Franklin Heating Station | 54224 | Franklin Heating Station | MN | Olmsted | DG5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | OP | X | 4 | 2011 |  |  | N | Commercial CHP | 5 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N |  | N
Vintage2021 | petroleum | FALSE | 6738 | Franklin Heating Station | 54224 | Franklin Heating Station | MN | Olmsted | DG8 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.1 | 0.8 | 3.1 | 3.1 | 0.6 | N |  |  | SB | Y | 12 | 2021 |  |  | N | Commercial CHP | 5 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2001 | petroleum | FALSE | 6738 | Franklin Heating Station | 54224 | Franklin Heating Station | MN | Olmsted | EG1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | SB | Y | 6 | 2001 |  |  | N | Commercial CHP | 5 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2001 | petroleum | FALSE | 6738 | Franklin Heating Station | 54224 | Franklin Heating Station | MN | Olmsted | EG2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | SB | Y | 6 | 2001 |  |  | N | Commercial CHP | 5 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2001 | petroleum | FALSE | 6738 | Franklin Heating Station | 54224 | Franklin Heating Station | MN | Olmsted | EG3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | SB | Y | 6 | 2001 |  |  | N | Commercial CHP | 5 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1951 | natural gas steam turbine | FALSE | 6738 | Franklin Heating Station | 54224 | Franklin Heating Station | MN | Olmsted | GEN1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 2.5 | 0.8 | 2 | 2 | 0.6 | N |  |  | OP | X | 1 | 1951 |  |  | Y | Commercial CHP | 5 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG: DFO; WAT NG NG NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1951 | natural gas steam turbine | FALSE | 6738 | Franklin Heating Station | 54224 | Franklin Heating Station | MN | Olmsted | GEN2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 2.5 | 0.8 | 2 | 2 | 0.6 | N |  |  | OP | X | 1 | 1951 |  |  | Y | Commercial CHP | 5 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG: DFO; WAT NG NG NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1968 | natural gas steam turbine | FALSE | 6738 | Franklin Heating Station | 54224 | Franklin Heating Station | MN | Olmsted | GEN3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 6.3 | 0.85 | 6.1 | 6.1 | 1 | N |  |  | OP | X | 1 | 1968 |  |  | Y | Commercial CHP | 5 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG: DFO; WAT NG NG NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage2006 | other | FALSE | 6738 | Franklin Heating Station | 54224 | Franklin Heating Station | MN | Olmsted | GEN6 | All Other | ST |  | S | X | X |  |  | 6.5 | 0.85 | 2.8 | 2.8 | 0.6 | N |  |  | OP | X | 1 | 2006 |  |  | Y | Commercial CHP | 5 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: PUR; WAT NG NG NG NG: PUR |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage2011 | natural gas peaker | FALSE | 7209 | The Gillette Company | 54225 | Gillette SBMC | MA | Suffolk | CTG3 | Natural Gas Fired Combustion Turbine | GT | 1 | S | X | X |  |  | 7.2 | 0.95 | 7.2 | 7.2 | 3.8 | N |  |  | OP | X | 7 | 2011 |  |  | Y | Industrial CHP | 7 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG: DFO; WAT NG NG NG NG: NG | DFO |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1991 | petroleum | FALSE | 7209 | The Gillette Company | 54225 | Gillette SBMC | MA | Suffolk | DG | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.9 | 0.5 | 0.5 | 0.1 | N |  |  | SB | N | 9 | 1991 |  |  | N | Industrial CHP | 7 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1997 | petroleum | FALSE | 7209 | The Gillette Company | 54225 | Gillette SBMC | MA | Suffolk | DG2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.9 | 0.5 | 0.5 | 0.1 | N |  |  | SB | N | 3 | 1997 |  |  | N | Industrial CHP | 7 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2000 | petroleum | FALSE | 7209 | The Gillette Company | 54225 | Gillette SBMC | MA | Suffolk | DG3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.9 | 1 | 1 | 0.3 | N |  |  | SB | N | 3 | 2000 |  |  | N | Industrial CHP | 7 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: DFO | [6 empty] | 10M | [23 empty] | N | N | N
Vintage1971 | natural gas steam turbine | FALSE | 7209 | The Gillette Company | 54225 | Gillette SBMC | MA | Suffolk | TG2 | Natural Gas Steam Turbine | ST | 1 | S | X | X |  |  | 5 | 0.8 | 5 | 5 | 0.5 | N |  |  | OP | X | 2 | 1971 |  |  | Y | Industrial CHP | 7 | X T T T T: B; WAT BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG: DFO; WAT NG NG NG NG: NG |  |  |  | N | N |  | 12H | [23 empty] | N |  | N
Vintage2013 | natural gas steam turbine | FALSE | 5989 | Erving Paper Mills Inc | 54228 | Erving Paper Mills | MA | Franklin | 2 | Natural Gas Steam Turbine | ST | CC | S | X | X |  |  | 0.6 | 1 | 0.6 | 0.6 | 0 | N |  |  | OP | X | 12 | 2013 |  |  | Y | Industrial CHP | 7 | T | NG | OTH | DFO |  |  |  | NG | DFO |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2015 | natural gas peaker | FALSE | 5989 | Erving Paper Mills Inc | 54228 | Erving Paper Mills | MA | Franklin | 3 | Natural Gas Fired Combustion Turbine | GT | CC | S | X | X |  |  | 5.6 | 1 | 5.5 | 6 | 2.8 | N |  |  | OP | X | 11 | 2015 |  |  | Y | Industrial CHP | 7 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage2009 | natural gas peaker | FALSE | 14928 | Pfizer Inc | 54236 | Pfizer Groton Plant | CT | New London | GT-1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 10 | 0.8 | 9.5 | 10.5 | 4.5 | N |  |  | OP | X | 9 | 2009 |  |  | Y | Industrial CHP | 7 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG: DFO; WAT NG NG NG NG: NG | DFO |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1952 | natural gas steam turbine | FALSE | 14928 | Pfizer Inc | 54236 | Pfizer Groton Plant | CT | New London | TG 3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 10 | 0.97 | 10 | 10 | 0.8 | N |  |  | OP | X | 1 | 1952 |  |  | Y | Industrial CHP | 7 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG: DFO; WAT NG NG NG NG: NG | PG |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1994 | natural gas steam turbine | FALSE | 14928 | Pfizer Inc | 54236 | Pfizer Groton Plant | CT | New London | TG 4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 10 | 0.94 | 5 | 5 | 0.8 | N |  |  | OP | X | 1 | 1994 |  |  | Y | Industrial CHP | 7 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG: DFO; WAT NG NG NG NG: NG | PG |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage2001 | natural gas steam turbine | FALSE | 14928 | Pfizer Inc | 54236 | Pfizer Groton Plant | CT | New London | TG5 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 7.5 | 0.8 | 7.5 | 7.5 | 0.5 | N |  |  | OP | X | 8 | 2001 |  |  | Y | Industrial CHP | 7 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG: DFO; WAT NG NG NG NG: NG | PG |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1987 | biomass | TRUE | 56652 | DTE Stockton LLC | 54238 | Stockton Biomass | CA | San Joaquin | STG | Wood/Wood Waste Biomass | ST |  | S | X | X | COGNAT_1_UNIT | COGNAT_1_UNIT | 54 | 0.85 | 45 | 45 | 22 | N |  |  | OP | X | 12 | 1987 |  |  | Y | IPP CHP | 3 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: WDS; WAT NG NG NG NG: NG; WAT NG NG NG NG: NG |  |  |  | N | N |  | 12H | N | N | [21 empty] | Y | Y | N
Vintage1984 | petroleum | FALSE | 10339 | Kings Bay Naval Base | 54239 | Naval Submarine Base Kings Bay | GA | Camden | 3023 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 2.5 | N |  |  | SB | Y | 12 | 1984 |  |  | N | Commercial Non-CHP | 4 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1984 | petroleum | FALSE | 10339 | Kings Bay Naval Base | 54239 | Naval Submarine Base Kings Bay | GA | Camden | 3024 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 2.5 | N |  |  | SB | Y | 12 | 1984 |  |  | N | Commercial Non-CHP | 4 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1984 | petroleum | FALSE | 10339 | Kings Bay Naval Base | 54239 | Naval Submarine Base Kings Bay | GA | Camden | 3025 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 2.5 | N |  |  | SB | Y | 12 | 1984 |  |  | N | Commercial Non-CHP | 4 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1988 | petroleum | FALSE | 10339 | Kings Bay Naval Base | 54239 | Naval Submarine Base Kings Bay | GA | Camden | 3027 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 2.5 | N |  |  | SB | Y | 1 | 1988 |  |  | N | Commercial Non-CHP | 4 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1988 | petroleum | FALSE | 10339 | Kings Bay Naval Base | 54239 | Naval Submarine Base Kings Bay | GA | Camden | 3028 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 2.5 | N |  |  | SB | Y | 9 | 1988 |  |  | N | Commercial Non-CHP | 4 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1989 | petroleum | FALSE | 10339 | Kings Bay Naval Base | 54239 | Naval Submarine Base Kings Bay | GA | Camden | 3029 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 2.5 | N |  |  | SB | Y | 5 | 1989 |  |  | N | Commercial Non-CHP | 4 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1988 | petroleum | FALSE | 10339 | Kings Bay Naval Base | 54239 | Naval Submarine Base Kings Bay | GA | Camden | 5876 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 2.5 | N |  |  | SB | Y | 12 | 1988 |  |  | N | Commercial Non-CHP | 4 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1989 | petroleum | FALSE | 10339 | Kings Bay Naval Base | 54239 | Naval Submarine Base Kings Bay | GA | Camden | 5877 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 2.5 | N |  |  | SB | Y | 5 | 1989 |  |  | N | Commercial Non-CHP | 4 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1989 | petroleum | FALSE | 10339 | Kings Bay Naval Base | 54239 | Naval Submarine Base Kings Bay | GA | Camden | 5878 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 2.5 | N |  |  | SB | Y | 5 | 1989 |  |  | N | Commercial Non-CHP | 4 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1989 | petroleum | FALSE | 10339 | Kings Bay Naval Base | 54239 | Naval Submarine Base Kings Bay | GA | Camden | 5879 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 2.5 | N |  |  | SB | Y | 5 | 1989 |  |  | N | Commercial Non-CHP | 4 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1989 | petroleum | FALSE | 10339 | Kings Bay Naval Base | 54239 | Naval Submarine Base Kings Bay | GA | Camden | 5880 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 2.5 | N |  |  | SB | Y | 5 | 1989 |  |  | N | Commercial Non-CHP | 4 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1988 | petroleum | FALSE | 10339 | Kings Bay Naval Base | 54239 | Naval Submarine Base Kings Bay | GA | Camden | 5881 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 2.5 | N |  |  | SB | Y | 12 | 1988 |  |  | N | Commercial Non-CHP | 4 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage2004 | natural gas peaker | FALSE | 11233 | Louisiana Tech University | 54240 | Louisiana Tech University Power Plant | LA | Lincoln | TG3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 7.5 | 0.8 | 6.4 | 7.4 | 3.6 | N |  |  | OP | X | 7 | 2004 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H |  | N | [21 empty] | N | N | N | bar: X T T T T to WAT BLQ BLQ BLQ BLQ
Vintage1990 | hydro | TRUE | 60900 | Smith Creek Hydro, LLC | 54249 | Smith Falls Hydro Project | ID | Boundary | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18 | 0.9 | 9 | 18 | 4.5 | N |  |  | OP | X | 1 | 1990 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N |  |  | 1H
Vintage1990 | hydro | TRUE | 60900 | Smith Creek Hydro, LLC | 54249 | Smith Falls Hydro Project | ID | Boundary | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 18 | 0.9 | 9 | 18 | 4.5 | N |  |  | OP | X | 1 | 1990 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N |  |  | 1H
Vintage1989 | hydro | TRUE | 60900 | Smith Creek Hydro, LLC | 54249 | Smith Falls Hydro Project | ID | Boundary | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.1 | 0.9 | 2.1 | 2.1 | 1 | N |  |  | OP | X | 12 | 1989 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N |  |  | 1H
Vintage1964 | natural gas steam turbine | FALSE | 13542 | Newman & Co Inc | 54250 | Newman (PA) | PA | Philadelphia | 001 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 1.6 | N |  |  | OP | X | 5 | 1964 |  |  | Y | Industrial CHP | 7 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG: DFO; WAT NG NG NG NG: NG |  |  |  | N | N | 0 | 12H | [23 empty] | Y | N | Y
Vintage1985 | hydro | TRUE | 42744 | Deschutes Valley Water District | 54251 | Opal Springs Hydro | OR | Jefferson | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.3 | 1 | 3.3 | 5 | 2 | N |  |  | OP | X | 1 | 1985 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT | [5 empty] | 0 | 10M | [23 empty] | N
Vintage1988 | hydro | TRUE | 21944 | Sonoma County Water Agency | 54261 | Warm Springs Hydro Project | CA | Sonoma | 3385 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.7 | 0.9 | 1.2 | 1.2 | 0.4 | N |  |  | OP | X | 12 | 1988 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1996 | natural gas peaker | FALSE | 17897 | St Mary's Hospital | 54262 | Saint Marys Hospital Power Plant | MN | Olmsted | 1 | Natural Gas Fired Combustion Turbine | GT | CC1 | S | X | X |  |  | 4.7 | 0.8 | 4.5 | 4.5 | 1.5 | N |  |  | OP | X | 6 | 1996 |  |  | Y | Commercial CHP | 5 | [11 empty] | N |  |  | 12H | [20 empty] | N |  |  | N | N | N | bar: X T T T T to WAT BLQ BLQ BLQ BLQ
Vintage1971 | natural gas steam turbine | FALSE | 17897 | St Mary's Hospital | 54262 | Saint Marys Hospital Power Plant | MN | Olmsted | 4 | Natural Gas Steam Turbine | ST | CC1 | S | X | X |  |  | 3 | 0.8 | 2.7 | 2.7 | 0.3 | N |  |  | OP | X | 1 | 1971 |  |  | Y | Commercial CHP | 5 | X T T T T: B; WAT BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG: DFO; WAT NG NG NG NG: NG |  |  |  | N |  |  | 12H | [20 empty] | N |  |  | Y | N | Y
Vintage1978 | petroleum | FALSE | 17897 | St Mary's Hospital | 54262 | Saint Marys Hospital Power Plant | MN | Olmsted | 5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 0.3 | N |  |  | SB | Y | 1 | 1978 |  |  | N | Commercial CHP | 5 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: DFO |  |  |  | N |  |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage2020 | petroleum | FALSE | 17897 | St Mary's Hospital | 54262 | Saint Marys Hospital Power Plant | MN | Olmsted | 6B | Petroleum Liquids | IC |  | S | X | X |  |  | 3.3 | 0.8 | 3.3 | 3.3 | 0.3 | N |  |  | OP | X | 7 | 2020 |  |  | N | Commercial CHP | 5 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: DFO | [6 empty] | 10M | [23 empty] | N
Vintage2011 | petroleum | FALSE | 17897 | St Mary's Hospital | 54262 | Saint Marys Hospital Power Plant | MN | Olmsted | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.8 | 2.8 | 0.3 | N |  |  | OP | X | 3 | 2011 |  |  | N | Commercial CHP | 5 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: DFO |  |  |  | N |  |  | 10M | [23 empty] | N |  | N
Vintage1979 | natural gas steam turbine | FALSE | 58835 | Akron Energy Systems LLC | 54265 | Akron Recycle Energy Plant | OH | Summit | 1 | Natural Gas Steam Turbine | ST |  | W | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.5 | N |  |  | OS | X | 6 | 1979 |  |  | Y | Commercial CHP | 5 | T | NG | WDS | TDF | WO |  |  | NG |  |  |  | N | N |  | OVER |  |  |  |  | N | [18 empty] | Y | Y | Y
Vintage1979 | natural gas steam turbine | FALSE | 58835 | Akron Energy Systems LLC | 54265 | Akron Recycle Energy Plant | OH | Summit | 2 | Natural Gas Steam Turbine | ST |  | W | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.5 | N |  |  | OS | X | 6 | 1979 |  |  | Y | Commercial CHP | 5 | T | NG | WDS | TDF | WO |  |  | NG |  |  |  | N | N |  | OVER |  |  |  |  | N | [18 empty] | Y | Y | Y
Vintage1990 | hydro | TRUE | 63987 | Koma Kulshan Associates | 54267 | Koma Kulshan Associates | WA | Whatcom | GEN1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 12 | 1 | 12.4 | 12.4 | 0.3 | N |  |  | OP | X | 10 | 1990 |  |  | N | IPP Non-CHP | 2 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: WAT |  |  |  | N | N | 0 | 12H | [23 empty] | N
Vintage1991 | natural gas peaker | FALSE | 64469 | HollyFrontier Corporation | 54268 | Puget Sound Refinery | WA | Skagit | GTG1 | Natural Gas Fired Combustion Turbine | GT | CC1 | S | X | X |  |  | 46.6 | 0.9 | 40 | 46 | 35 | N |  |  | OP | X | 9 | 1991 |  |  | Y | Industrial CHP | 7 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG: OG |  |  |  | N | N |  | 12H | [20 empty] | Y | 5 | 2022 | N | N | N
Vintage1991 | natural gas peaker | FALSE | 64469 | HollyFrontier Corporation | 54268 | Puget Sound Refinery | WA | Skagit | GTG2 | Natural Gas Fired Combustion Turbine | GT | CC1 | S | X | X |  |  | 46.6 | 0.9 | 40 | 46 | 35 | N |  |  | OP | X | 10 | 1991 |  |  | Y | Industrial CHP | 7 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG: OG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1993 | natural gas peaker | FALSE | 64469 | HollyFrontier Corporation | 54268 | Puget Sound Refinery | WA | Skagit | GTG3 | Natural Gas Fired Combustion Turbine | GT | CC1 | S | X | X |  |  | 46.6 | 0.9 | 40 | 46 | 35 | N |  |  | OP | X | 1 | 1993 |  |  | Y | Industrial CHP | 7 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG: OG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1991 | natural gas combined cycle | TRUE | 16553 | Saguaro Power Co | 54271 | Saguaro Power | NV | Clark | CTG1 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N |  |  | 45.1 | 0.85 | 36 | 38 | 33 | N |  |  | OP | X | 9 | 1991 |  |  | Y | IPP CHP | 3 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1991 | natural gas combined cycle | TRUE | 16553 | Saguaro Power Co | 54271 | Saguaro Power | NV | Clark | CTG2 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N |  |  | 45.1 | 0.85 | 36 | 38 | 33 | N |  |  | OP | X | 9 | 1991 |  |  | Y | IPP CHP | 3 | X T T T T: T; WAT BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | Y
Vintage1991 | natural gas combined cycle | TRUE | 16553 | Saguaro Power Co | 54271 | Saguaro Power | NV | Clark | STG | Natural Gas Fired Combined Cycle | CA | CC1 | W | Y | X |  |  | 37 | 0.85 | 29 | 29 | 22 | N |  |  | OP | X | 9 | 1991 |  |  | Y | IPP CHP | 3 | X T T T T: B; WAT BLQ BLQ BLQ BLQ: NG; WAT NG NG NG NG: OG |  |  |  | N | N |  | 12H | [23 empty] | N | N
Vintage2007 | petroleum | FALSE | 19541 | University of North Carolina | 54276 | Univ of NC Chapel Hill Cogen Facility | NC | Orange | ES001 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 2 | 0.5 | N |  |  | SB | Y | 10 | 2007 |  |  | N | Commercial CHP | 5 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2007 | petroleum | FALSE | 19541 | University of North Carolina | 54276 | Univ of NC Chapel Hill Cogen Facility | NC | Orange | ES002 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 1.8 | 2 | 0.5 | N |  |  | SB | Y | 10 | 2007 |  |  | N | Commercial CHP | 5 | X T T T T: X; WAT BLQ BLQ BLQ BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1991 | hard coal | FALSE | 19541 | University of North Carolina | 54276 | Univ of NC Chapel Hill Cogen Facility | NC | Orange | TG3 | Conventional Steam Coal | ST |  | S | X | X |  |  | 28 | 0.85 | 28.7 | 28.7 | 7 | N |  |  | OP | X | 7 | 1991 |  |  | Y | Commercial CHP | 5 | T | BIT | NG | DFO |  |  |  | NG | DFO |  |  | N | N |  | 12H | Y |  |  | Y | Y | [18 empty] | N | N | N
Vintage1968 | biomass | TRUE | 9394 | Interstate Paper LLC | 54281 | Interstate Paper LLC Riceboro | GA | Liberty | 577A | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 14.5 | 0.97 | 14.5 | 14.5 | 2 | N |  |  | OP | X | 3 | 1968 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | NG | RFO | TDF | SLW | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1992 | hydro | TRUE | 31518 | Fort Smith City of | 54283 | Lee Creek Water Treatment Facility | AR | Crawford | 0209 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 1 | 1.3 | 1.3 | 0.5 | N |  |  | OS | X | 11 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 1H
Vintage1992 | hydro | TRUE | 8248 | Hastings Lock & Dam | 54285 | Hastings City Hydroelectric | MN | Dakota | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 0.9 | 2 | 2 | 0.2 | N |  |  | OP | X | 1 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  |  | N |  | 10M | [23 empty] | N
Vintage1992 | hydro | TRUE | 8248 | Hastings Lock & Dam | 54285 | Hastings City Hydroelectric | MN | Dakota | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.2 | 0.9 | 2 | 2 | 0.2 | N |  |  | OP | X | 1 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  |  | N |  | 10M | [23 empty] | N
Vintage1989 | petroleum | FALSE | 61186 | DCII-250 Williams Street NW, LLC | 54290 | Inforum | GA | Fulton | BUG1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 0 | N |  |  | OP | X | 10 | 1989 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2005 | petroleum | FALSE | 18981 | Thomson Corp | 54294 | West Group Data Center | MN | Dakota | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 0.6 | 0.4 | 0 | N |  |  | SB | N | 5 | 2005 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2005 | petroleum | FALSE | 18981 | Thomson Corp | 54294 | West Group Data Center | MN | Dakota | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 0.6 | 0.4 | 0 | N |  |  | SB | N | 5 | 2005 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2005 | petroleum | FALSE | 18981 | Thomson Corp | 54294 | West Group Data Center | MN | Dakota | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 0.6 | 0.4 | 0 | N |  |  | SB | N | 5 | 2005 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2005 | petroleum | FALSE | 18981 | Thomson Corp | 54294 | West Group Data Center | MN | Dakota | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 0.6 | 0.4 | 0 | N |  |  | SB | N | 5 | 2005 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2018 | other | FALSE | 1752 | Biola University | 54296 | Biola University Hybrid | CA | Los Angeles | BATT | Batteries | BA |  | S | X | X |  |  | 0.3 | 1 | 0.3 | 0.3 | 0 | N |  |  | OP | X | 2 | 2018 |  |  | N | Commercial CHP | 5 | T: X; BLQ: MWH |  |  |  | N |  |  | 10M
Vintage2002 | natural gas peaker | FALSE | 1752 | Biola University | 54296 | Biola University Hybrid | CA | Los Angeles | EG3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1 | 0.9 | 1 | 1 | 0.8 | N |  |  | OP | X | 9 | 2002 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage2005 | onshore wind | TRUE | 63235 | Brookfield Renewable Trading and Marketing LP | 54298 | Coram Energy LLC (ECT) | CA | Kern | GEWE | Onshore Wind Turbine | WT |  | W | X | X |  |  | 7.5 |  | 7.5 | 7.5 | 1 | N |  |  | OP | X | 5 | 2005 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WND |  |  |  | N | N | 5
Vintage2005 | onshore wind | TRUE | 63235 | Brookfield Renewable Trading and Marketing LP | 54299 | Coram Energy LLC | CA | Kern | GEWE | Onshore Wind Turbine | WT |  | W | X | X |  |  | 3 |  | 3 | 3 | 1 | N |  |  | OP | X | 1 | 2005 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WND |  |  |  |  | N | 2
Vintage2004 | onshore wind | TRUE | 63235 | Brookfield Renewable Trading and Marketing LP | 54300 | CTV Power Purchase Contract Trust | CA | Kern | GEWE | Onshore Wind Turbine | WT |  | W | X | X |  |  | 4.5 |  | 4.5 | 4.5 | 1 | N |  |  | OP | X | 1 | 2004 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WND |  |  |  | N | N | 3
Vintage1985 | onshore wind | TRUE | 63235 | Brookfield Renewable Trading and Marketing LP | 54300 | CTV Power Purchase Contract Trust | CA | Kern | SX1S | Onshore Wind Turbine | WT |  | J | X | X |  |  | 0.1 |  | 0.1 | 0.1 | 0.1 | N |  |  | OS | X | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WND |  |  |  | N |  | 3
Vintage1986 | hydro | TRUE | 12382 | Metropolitan Dist of Hartford | 54302 | Goodwin Hydroelectric | CT | Hartford | G1 | Conventional Hydroelectric | HY |  | S | X | X | 4004 | 4004 | 1.6 | 0.9 | 1.6 | 1.6 | 0.6 | N |  |  | OP | X | 4 | 1986 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 1H | [20 empty] | N |  |  | N
Vintage1986 | hydro | TRUE | 12382 | Metropolitan Dist of Hartford | 54302 | Goodwin Hydroelectric | CT | Hartford | G2 | Conventional Hydroelectric | HY |  | S | X | X | 4004 | 4004 | 1.6 | 0.9 | 1.6 | 1.6 | 0.6 | N |  |  | OP | X | 4 | 1986 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 1H | [20 empty] | N |  |  | N
Vintage1991 | petroleum | FALSE | 20523 | Westward Seafoods Inc | 54305 | Westward Seafoods | AK | Aleutians West | 2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.2 | 0.8 | 2.2 | 2.2 | 1 | N |  |  | OP | X | 3 | 1991 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1991 | petroleum | FALSE | 20523 | Westward Seafoods Inc | 54305 | Westward Seafoods | AK | Aleutians West | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.2 | 0.8 | 2.2 | 2.2 | 1 | N |  |  | OP | X | 3 | 1991 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1991 | petroleum | FALSE | 20523 | Westward Seafoods Inc | 54305 | Westward Seafoods | AK | Aleutians West | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.2 | 0.8 | 2.2 | 2.2 | 1 | N |  |  | OP | X | 3 | 1991 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N | N
Vintage1993 | hydro | TRUE | 8365 | Hazelton/Wilson Joint Venture | 54306 | Wilson Lake Hydroelectric Project | ID | Jerome | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.2 | 0.9 | 4.2 | 4.2 | 1.6 | N |  |  | OP | X | 5 | 1993 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 1H | [23 empty] | N
Vintage1993 | hydro | TRUE | 8365 | Hazelton/Wilson Joint Venture | 54306 | Wilson Lake Hydroelectric Project | ID | Jerome | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.2 | 0.9 | 4.2 | 4.2 | 1.6 | N |  |  | OP | X | 5 | 1993 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 1H | [23 empty] | N
Vintage1984 | hydro | TRUE | 54722 | Grizzly Mountain Ranch | 54308 | Three Forks Water Power Project | CA | Trinity | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 0.8 | 1.2 | 1.2 | 0.1 | N |  |  | OP | X | 12 | 1984 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 10M | [23 empty] | N
Vintage1992 | natural gas peaker | FALSE | 772 | Archer Daniels Midland Co | 54316 | Archer Daniels Midland Southport | NC | Brunswick | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | No Sales | No sales | 18 | 0.85 | 15 | 18 | 5 | N |  |  | SB | Y | 9 | 1992 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: NG; WDS: DFO |  |  |  | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage1992 | natural gas peaker | FALSE | 772 | Archer Daniels Midland Co | 54316 | Archer Daniels Midland Southport | NC | Brunswick | GEN2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 17.5 | 0.85 | 15 | 17.5 | 5 | N |  |  | SB | Y | 10 | 1992 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: NG; WDS: DFO |  |  |  | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage1995 | natural gas peaker | FALSE | 772 | Archer Daniels Midland Co | 54316 | Archer Daniels Midland Southport | NC | Brunswick | GEN3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 17 | 0.85 | 15 | 17 | 5 | N |  |  | SB | Y | 4 | 1995 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: NG; WDS: DFO |  |  |  | N |  |  | 12H | [23 empty] | Y | N | Y
Vintage1968 | hard coal | FALSE | 7067 | Tata Chemicals Partners | 54318 | General Chemical | WY | Sweetwater | TG1 | Conventional Steam Coal | ST |  | S | X | X |  |  | 15 | 0.85 | 15 | 15 | 2 | N |  |  | OP | X | 5 | 1968 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: BIT; WDS: NG; NG: NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [15 empty] | N |  |  | N | N | N
Vintage1977 | hard coal | FALSE | 7067 | Tata Chemicals Partners | 54318 | General Chemical | WY | Sweetwater | TG2 | Conventional Steam Coal | ST |  | S | X | X |  |  | 15 | 0.85 | 15 | 15 | 2 | N |  |  | OP | X | 1 | 1977 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: BIT; WDS: NG; NG: NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | [15 empty] | N |  |  | N | N | N
Vintage1999 | natural gas peaker | FALSE | 7375 | Goodyear Tire & Rubber Co | 54321 | Goodyear Beaumont Chemical Plant | TX | Jefferson | 2N80 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 5 | 0.9 | 4 | 4.5 | 2 | N |  |  | OP | X | 8 | 1999 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ; NG
Vintage1987 | natural gas steam turbine | FALSE | 7375 | Goodyear Tire & Rubber Co | 54321 | Goodyear Beaumont Chemical Plant | TX | Jefferson | 3N80 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 14.8 | 0.9 | 13 | 13.5 | 5 | N |  |  | OP | X | 3 | 1987 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: NG; WDS: WO; NG: NG |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1999 | natural gas peaker | FALSE | 7375 | Goodyear Tire & Rubber Co | 54321 | Goodyear Beaumont Chemical Plant | TX | Jefferson | N802 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 5 | 0.9 | 4 | 4.5 | 2 | N |  |  | OP | X | 8 | 1999 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1999 | natural gas peaker | FALSE | 7375 | Goodyear Tire & Rubber Co | 54321 | Goodyear Beaumont Chemical Plant | TX | Jefferson | N803 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 5 | 0.9 | 4 | 4.5 | 2 | N |  |  | OP | X | 10 | 1999 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1999 | natural gas peaker | FALSE | 7375 | Goodyear Tire & Rubber Co | 54321 | Goodyear Beaumont Chemical Plant | TX | Jefferson | N804 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 5 | 0.9 | 4 | 4.5 | 2 | N |  |  | OP | X | 10 | 1999 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1946 | hydro | FALSE | 55810 | Augusta Canal Authority | 54322 | Sibley Mill | GA | Richmond | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.9 | 0.6 | 0.6 | 0.4 | N |  |  | OP | X | 1 | 1946 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 1H | [23 empty] | N
Vintage1946 | hydro | FALSE | 55810 | Augusta Canal Authority | 54322 | Sibley Mill | GA | Richmond | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.9 | 0.7 | 0.7 | 0.4 | N |  |  | OP | X | 1 | 1946 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 1H | [23 empty] | N
Vintage1946 | hydro | FALSE | 55810 | Augusta Canal Authority | 54322 | Sibley Mill | GA | Richmond | 4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.9 | 0.8 | 0.8 | 0.4 | N |  |  | OP | X | 1 | 1946 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 1H | [23 empty] | N
Vintage2001 | petroleum | FALSE | 18452 | Turner Properties Inc | 54323 | CNN Center | GA | Fulton | D4_1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.4 | N |  |  | SB | Y | 2 | 2001 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: DFO; NG: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2001 | petroleum | FALSE | 18452 | Turner Properties Inc | 54323 | CNN Center | GA | Fulton | D4_2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.5 | N |  |  | SB | Y | 2 | 2001 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: DFO; NG: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2003 | petroleum | FALSE | 18452 | Turner Properties Inc | 54323 | CNN Center | GA | Fulton | D4_3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.5 | N |  |  | SB | Y | 6 | 2003 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: DFO; NG: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2001 | petroleum | FALSE | 18452 | Turner Properties Inc | 54323 | CNN Center | GA | Fulton | D5_1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.5 | N |  |  | SB | Y | 2 | 2001 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: DFO; NG: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2003 | petroleum | FALSE | 18452 | Turner Properties Inc | 54323 | CNN Center | GA | Fulton | D5_2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.5 | N |  |  | SB | Y | 6 | 2003 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: DFO; NG: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2003 | petroleum | FALSE | 18452 | Turner Properties Inc | 54323 | CNN Center | GA | Fulton | D5_3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.5 | N |  |  | SB | Y | 6 | 2003 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: DFO; NG: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1986 | petroleum | FALSE | 18452 | Turner Properties Inc | 54323 | CNN Center | GA | Fulton | DK2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.3 | 1.5 | 0.4 | N |  |  | SB | N | 6 | 1986 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: DFO; NG: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1991 | natural gas combined cycle | TRUE | 27770 | Ocean State Power II | 54324 | Ocean State Power II | RI | Providence | GEN1 | Natural Gas Fired Combined Cycle | CT | OSP2 | W | X | N |  |  | 82.8 | 0.85 | 71.2 | 77.8 | 45 | N |  |  | OP | X | 10 | 1991 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: NG; WDS: DFO |  |  |  | N |  |  | 12H | [7 empty] | 26.1 | 0 | 5 | 2024 | [12 empty] | Y | Y | Y
Vintage1991 | natural gas combined cycle | TRUE | 27770 | Ocean State Power II | 54324 | Ocean State Power II | RI | Providence | GEN2 | Natural Gas Fired Combined Cycle | CT | OSP2 | W | X | N |  |  | 82.8 | 0.85 | 71.2 | 77.8 | 45 | N |  |  | OP | X | 10 | 1991 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: NG; WDS: DFO |  |  |  | N |  |  | 12H | [7 empty] | 26.1 | 0 | 5 | 2024 | [12 empty] | Y | Y | Y
Vintage1991 | natural gas combined cycle | TRUE | 27770 | Ocean State Power II | 54324 | Ocean State Power II | RI | Providence | GEN3 | Natural Gas Fired Combined Cycle | CA | OSP2 | W | Y | X |  |  | 88.6 | 0.85 | 76.2 | 83.3 | 35 | N |  |  | OP | X | 10 | 1991 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N |  |  | 12H | [7 empty] | 63.8 | 0 | 5 | 2024 | [12 empty] | N | N | N | bar: T to BLQ
Vintage1988 | natural gas peaker | FALSE | 17052 | Shell Chemical LP | 54330 | Westhollow Technology Center | TX | Harris | 1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.7 | 0.9 | 3.7 | 3.7 | 2.3 | N |  |  | OP | X | 1 | 1988 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [20 empty] | N |  |  | N | N | N | bar: T to BLQ
Vintage1998 | natural gas combined cycle | FALSE | 2468 | Bucknell University | 54333 | Bucknell University | PA | Union | G001 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y | Citizens | Citizens | 4.7 | 0.9 | 4.5 | 5.5 | 2.5 | N |  |  | OP | X | 6 | 1998 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: NG; WDS: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1991 | natural gas combined cycle | FALSE | 2468 | Bucknell University | 54333 | Bucknell University | PA | Union | G502 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 1.2 | 0.9 | 0.8 | 1.2 | 0.3 | N |  |  | OP | X | 10 | 1991 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: NG; WDS: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2015 | natural gas steam turbine | FALSE | 12986 | Morton Salt Inc | 54335 | Morton Salt Rittman | OH | Wayne | GEN2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 2 | 2015 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H |  |  |  |  | N | [18 empty] | N | N | N | bar: T to BLQ; NG
Vintage1973 | biomass | TRUE | 16098 | Rio Grande Valley Sugar Growers, Inc. | 54338 | Rio Grande Valley Sugar Growers | TX | Hidalgo | GENA | Other Waste Biomass | ST |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 10 | 1973 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: AB; WDS: NG; NG: AB | NG |  |  | N |  |  | 12H | [23 empty] | Y | Y | N
Vintage1973 | biomass | TRUE | 16098 | Rio Grande Valley Sugar Growers, Inc. | 54338 | Rio Grande Valley Sugar Growers | TX | Hidalgo | GENB | Other Waste Biomass | ST |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 10 | 1973 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: AB; WDS: NG; NG: AB | NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1995 | biomass | TRUE | 16098 | Rio Grande Valley Sugar Growers, Inc. | 54338 | Rio Grande Valley Sugar Growers | TX | Hidalgo | GENC | Other Waste Biomass | ST |  | S | X | X |  |  | 2.5 | 0.8 | 2.5 | 2.5 | 0.5 | N |  |  | OP | X | 1 | 1995 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: AB; WDS: NG; NG: AB | NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage2009 | biomass | TRUE | 16098 | Rio Grande Valley Sugar Growers, Inc. | 54338 | Rio Grande Valley Sugar Growers | TX | Hidalgo | GEND | Other Waste Biomass | ST |  | S | X | X |  |  | 16 | 0.8 | 10 | 10 | 4 | N |  |  | OP | X | 8 | 2009 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: AB; WDS: NG; NG: AB | NG |  |  | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage2011 | petroleum | FALSE | 16098 | Rio Grande Valley Sugar Growers, Inc. | 54338 | Rio Grande Valley Sugar Growers | TX | Hidalgo | GENE | Petroleum Liquids | IC |  | S | X | X |  |  | 1.4 | 0.8 | 1.4 | 1.4 | 0 | N |  |  | OP | X | 9 | 2011 |  |  | N | Industrial CHP | 7 | T: X; BLQ: DFO; NG: DFO |  |  |  | N | N |  | 1H |  |  |  |  | N | [18 empty] | N | N | N
Vintage1990 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 54340 | Norway Point Hydropower Project | MI | Alpena | 1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 2.8 | 1 | 2.8 | 2.8 | 0.8 | N |  |  | OP | X | 9 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT | [6 empty] | 10M
Vintage1990 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 54340 | Norway Point Hydropower Project | MI | Alpena | 2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.2 | 1 | 1.2 | 1.2 | 0.4 | N |  |  | OP | X | 9 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT | [6 empty] | 10M
Vintage1990 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 54341 | Four Mile Hydropower Project | MI | Alpena | 1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.6 | 1 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 9 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N |  |  | 10M
Vintage1990 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 54341 | Four Mile Hydropower Project | MI | Alpena | 2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.6 | 1 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 9 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N |  |  | 10M
Vintage1990 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 54341 | Four Mile Hydropower Project | MI | Alpena | 3 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.6 | 1 | 0.6 | 0.6 | 0.2 | N |  |  | OP | X | 9 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N |  |  | 10M
Vintage2005 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 54341 | Four Mile Hydropower Project | MI | Alpena | 4 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.2 | 1 | 0.2 | 0.2 | 0.2 | N |  |  | OP | X | 10 | 2005 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N |  |  | 10M
Vintage1990 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 54342 | Ninth Street Hydropower Project | MI | Alpena | 1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.4 | 1 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 9 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT | [6 empty] | 10M
Vintage1990 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 54342 | Ninth Street Hydropower Project | MI | Alpena | 2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.4 | 1 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 9 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT | [6 empty] | 10M
Vintage1990 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 54342 | Ninth Street Hydropower Project | MI | Alpena | 3 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.4 | 1 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 9 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT | [6 empty] | 10M
Vintage1990 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 54343 | Terminus Hydroelectric Project | CA | Tulare | GEN1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 20.1 | 1 | 20 | 20 | 6 | N |  |  | OP | X | 3 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 1H
Vintage1986 | biomass | TRUE | 18483 | Tampa Wastewater Department | 54347 | Howard F Curren Advncd Wastewater Plant | FL | Hillsborough | 1 | Other Waste Biomass | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.4 | N |  |  | OS | X | 9 | 1986 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: OBG |  |  |  | N |  |  | 10M | [23 empty] | N | N | N
Vintage1986 | biomass | TRUE | 18483 | Tampa Wastewater Department | 54347 | Howard F Curren Advncd Wastewater Plant | FL | Hillsborough | 2 | Other Waste Biomass | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.4 | N |  |  | OS | X | 9 | 1986 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: OBG |  |  |  | N |  |  | 10M | [23 empty] | N | N | N
Vintage1986 | biomass | TRUE | 18483 | Tampa Wastewater Department | 54347 | Howard F Curren Advncd Wastewater Plant | FL | Hillsborough | 3 | Other Waste Biomass | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.4 | N |  |  | OS | X | 9 | 1986 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: OBG |  |  |  | N |  |  | 10M | [23 empty] | N | N | N
Vintage1989 | biomass | TRUE | 18483 | Tampa Wastewater Department | 54347 | Howard F Curren Advncd Wastewater Plant | FL | Hillsborough | 4 | Other Waste Biomass | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.4 | N |  |  | OS | X | 2 | 1989 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: OBG |  |  |  | N |  |  | 10M | [23 empty] | N | N | N
Vintage1989 | biomass | TRUE | 18483 | Tampa Wastewater Department | 54347 | Howard F Curren Advncd Wastewater Plant | FL | Hillsborough | 5 | Other Waste Biomass | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.4 | N |  |  | OS | X | 2 | 1989 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: OBG |  |  |  | N |  |  | 10M | [23 empty] | N | N | N
Vintage1992 | natural gas combined cycle | TRUE | 13365 | Nevada Cogeneration Assoc # 2 | 54349 | Nevada Cogen Associates 2 Black Mountain | NV | Clark | GTA | Natural Gas Fired Combined Cycle | CT | STG1 | W | X | N |  |  | 22.2 | 0.9 | 21.7 | 21.7 | 19 | N |  |  | OP | X | 11 | 1992 | 10 | 2030 | Y | IPP CHP | 3 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ; NG
Vintage1992 | natural gas combined cycle | TRUE | 13365 | Nevada Cogeneration Assoc # 2 | 54349 | Nevada Cogen Associates 2 Black Mountain | NV | Clark | GTB | Natural Gas Fired Combined Cycle | CT | STG1 | W | X | N |  |  | 22.2 | 0.9 | 21.7 | 21.7 | 19 | N |  |  | OP | X | 12 | 1992 | 10 | 2030 | Y | IPP CHP | 3 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ; NG
Vintage1992 | natural gas combined cycle | TRUE | 13365 | Nevada Cogeneration Assoc # 2 | 54349 | Nevada Cogen Associates 2 Black Mountain | NV | Clark | GTC | Natural Gas Fired Combined Cycle | CT | STG1 | W | X | N |  |  | 22.2 | 0.9 | 21.7 | 21.7 | 19 | N |  |  | OP | X | 12 | 1992 | 10 | 2030 | Y | IPP CHP | 3 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ; NG
Vintage1992 | natural gas combined cycle | TRUE | 13365 | Nevada Cogeneration Assoc # 2 | 54349 | Nevada Cogen Associates 2 Black Mountain | NV | Clark | STM | Natural Gas Fired Combined Cycle | CA | STG1 | W | Y | X |  |  | 29.7 | 0.9 | 28 | 28 | 5 | N |  |  | OP | X | 12 | 1992 | 10 | 2030 | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1992 | natural gas combined cycle | TRUE | 13399 | Nevada Cogeneration Assoc # 1 | 54350 | Nevada Cogen Assoc#1 GarnetVly | NV | Clark | GTA | Natural Gas Fired Combined Cycle | CT | CC1 | J | X | N |  |  | 21.7 | 0.9 | 20.5 | 22 | 19 | N |  |  | OP | X | 4 | 1992 | 5 | 2023 | Y | IPP CHP | 3 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ; NG
Vintage1992 | natural gas combined cycle | TRUE | 13399 | Nevada Cogeneration Assoc # 1 | 54350 | Nevada Cogen Assoc#1 GarnetVly | NV | Clark | GTB | Natural Gas Fired Combined Cycle | CT | CC1 | J | X | N |  |  | 21.7 | 0.9 | 20.5 | 22 | 19 | N |  |  | OP | X | 4 | 1992 | 5 | 2023 | Y | IPP CHP | 3 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ; NG
Vintage1992 | natural gas combined cycle | TRUE | 13399 | Nevada Cogeneration Assoc # 1 | 54350 | Nevada Cogen Assoc#1 GarnetVly | NV | Clark | GTC | Natural Gas Fired Combined Cycle | CT | CC1 | J | X | N |  |  | 21.7 | 0.9 | 20.5 | 22 | 19 | N |  |  | OP | X | 4 | 1992 | 5 | 2023 | Y | IPP CHP | 3 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ; NG
Vintage1992 | natural gas combined cycle | TRUE | 13399 | Nevada Cogeneration Assoc # 1 | 54350 | Nevada Cogen Assoc#1 GarnetVly | NV | Clark | STM | Natural Gas Fired Combined Cycle | CA | CC1 | J | Y | X |  |  | 29.7 | 0.9 | 24 | 19 | 5 | N |  |  | OP | X | 5 | 1992 | 5 | 2023 | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T to BLQ; NG
Vintage1993 | hydro | TRUE | 2548 | City of Burlington Electric - (VT) | 54355 | Chace Mill Winooski One | VT | Chittenden | GEN1 | Conventional Hydroelectric | HY |  | S | X | X | 622 | 622 | 2.5 | 0.99 | 2.5 | 2.5 | 0.3 | N |  |  | OP | X | 4 | 1993 |  |  | N | Electric Utility | 1 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M
Vintage1993 | hydro | TRUE | 2548 | City of Burlington Electric - (VT) | 54355 | Chace Mill Winooski One | VT | Chittenden | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 0.99 | 2.5 | 2.5 | 0.3 | N |  |  | OP | X | 4 | 1993 |  |  | N | Electric Utility | 1 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M
Vintage1993 | hydro | TRUE | 2548 | City of Burlington Electric - (VT) | 54355 | Chace Mill Winooski One | VT | Chittenden | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.5 | 0.99 | 2.5 | 2.5 | 0.3 | N |  |  | OP | X | 4 | 1993 |  |  | N | Electric Utility | 1 | T: X; BLQ: WAT |  |  |  | N | N |  | 10M
Vintage1960 | biomass | TRUE | 61880 | Graphic Packaging International - Augusta | 54358 | Graphic Packaging International Augusta Mill | GA | Richmond | 1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 27 | 1 | 25.3 | 25.4 | 10 | N |  |  | OP | X | 8 | 1960 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: WDS; WDS: NG; NG: NG | WDS | ANT |  | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage1965 | natural gas steam turbine | FALSE | 61880 | Graphic Packaging International - Augusta | 54358 | Graphic Packaging International Augusta Mill | GA | Richmond | 2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 39 | 1 | 36.5 | 36.7 | 10 | N |  |  | OP | X | 1 | 1965 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: NG; WDS: DFO; NG: NG |  |  |  | N | N |  | OVER | [23 empty] | N | N | N
Vintage1965 | biomass | TRUE | 61880 | Graphic Packaging International - Augusta | 54358 | Graphic Packaging International Augusta Mill | GA | Richmond | 3 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 18.7 | 1 | 17.5 | 17.6 | 5 | N |  |  | OP | X | 1 | 1965 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: WDS; WDS: NG; NG: NG | WDS |  |  | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage1980 | petroleum | FALSE | 60194 | Fuyao Glass Illinois, Inc | 54360 | Fuyao Glass Illinois Inc. | IL | Macon | PORT | Petroleum Liquids | IC |  | S | X | X | 0 | 0 | 0.7 | 0.8 | 0.7 | 0.7 | 0.4 | N |  |  | SB | Y | 12 | 1980 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1980 | petroleum | FALSE | 60194 | Fuyao Glass Illinois, Inc | 54360 | Fuyao Glass Illinois Inc. | IL | Macon | TK1 | Petroleum Liquids | IC |  | S | X | X | 0 | 0 | 2 | 0.8 | 2 | 2 | 0.8 | N |  |  | SB | Y | 12 | 1980 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1980 | petroleum | FALSE | 60194 | Fuyao Glass Illinois, Inc | 54360 | Fuyao Glass Illinois Inc. | IL | Macon | TK2 | Petroleum Liquids | IC |  | S | X | X | 0 | 0 | 2 | 0.8 | 2 | 2 | 0.8 | N |  |  | SB | Y | 12 | 1980 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1972 | petroleum | FALSE | 50035 | Electric Glass Fiber America, LLC. | 54363 | Shelby, NC | NC | Cleveland | GEN2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.6 | 0.7 | 0.1 | N |  |  | SB | N | 1 | 1972 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N
Vintage1972 | petroleum | FALSE | 50035 | Electric Glass Fiber America, LLC. | 54363 | Shelby, NC | NC | Cleveland | GEN3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.6 | 0.7 | 0.1 | N |  |  | SB | N | 1 | 1972 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N
Vintage1972 | petroleum | FALSE | 50035 | Electric Glass Fiber America, LLC. | 54363 | Shelby, NC | NC | Cleveland | GEN4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.8 | 0.8 | 0.9 | 0.1 | N |  |  | SB | N | 1 | 1972 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N
Vintage1972 | petroleum | FALSE | 50035 | Electric Glass Fiber America, LLC. | 54363 | Shelby, NC | NC | Cleveland | GEN5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.2 | 0.8 | 0.8 | 0.9 | 0.1 | N |  |  | SB | N | 1 | 1972 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N | N
Vintage1975 | petroleum | FALSE | 60538 | Vitro Architectural Glass | 54364 | Works 4 | TX | Wichita | L1G | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | SB | Y | 6 | 1975 | 11 | 2023 | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1980 | petroleum | FALSE | 60538 | Vitro Architectural Glass | 54364 | Works 4 | TX | Wichita | L1PG | Petroleum Liquids | IC |  | S | X | X |  |  | 0.9 | 0.8 | 0.9 | 0.9 | 0.1 | N |  |  | SB | Y | 10 | 1980 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M |  |  |  | N | [19 empty] | N | N | N
Vintage1974 | petroleum | FALSE | 60538 | Vitro Architectural Glass | 54364 | Works 4 | TX | Wichita | L2G | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | SB | Y | 6 | 1974 | 11 | 2024 | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M |  |  |  | N | [19 empty] | N | N | N
Vintage1995 | natural gas combined cycle | TRUE | 49901 | Northern Star Generation Services Co LLC | 54365 | Orange Cogeneration Facility | FL | Polk | APC1 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N |  |  | 54 | 0.9 | 43 | 43 | 10 | N |  |  | OP | X | 3 | 1995 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T to BLQ; NG
Vintage1995 | natural gas combined cycle | TRUE | 49901 | Northern Star Generation Services Co LLC | 54365 | Orange Cogeneration Facility | FL | Polk | APC2 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N |  |  | 54 | 0.9 | 43 | 43 | 10 | N |  |  | OP | X | 2 | 1995 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T to BLQ; NG
Vintage1995 | natural gas combined cycle | TRUE | 49901 | Northern Star Generation Services Co LLC | 54365 | Orange Cogeneration Facility | FL | Polk | APC3 | Natural Gas Fired Combined Cycle | CA | CC1 | W | N | X |  |  | 28.6 | 0.85 | 24.6 | 24.6 | 5 | N |  |  | OP | X | 3 | 1995 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T to BLQ; NG
Vintage1992 | natural gas combined cycle | FALSE | 22208 | University of Colorado | 54372 | University of Colorado | CO | Boulder | GT1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 16 | 1 | 15 | 16 | 2.5 | N |  |  | OP | X | 8 | 1992 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: NG; WDS: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1992 | natural gas combined cycle | FALSE | 22208 | University of Colorado | 54372 | University of Colorado | CO | Boulder | GT2 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 16 | 1 | 15 | 16 | 2.5 | N |  |  | OP | X | 8 | 1992 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: NG; WDS: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1992 | natural gas combined cycle | FALSE | 22208 | University of Colorado | 54372 | University of Colorado | CO | Boulder | ST1 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 1 | 1 | 1 | 1 | 1 | N |  |  | OP | X | 8 | 1992 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T to BLQ
Vintage2012 | natural gas peaker | FALSE | 24205 | Sinclair Oil Corp | 54374 | Sinclair Oil Refinery | WY | Carbon | 2004 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 0.6 | N |  |  | OP | X | 1 | 2012 | 4 | 2022 | N | Industrial CHP | 7 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: T to BLQ
Vintage2012 | natural gas peaker | FALSE | 24205 | Sinclair Oil Corp | 54374 | Sinclair Oil Refinery | WY | Carbon | 2006 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 0.6 | N |  |  | OP | X | 1 | 2012 | 4 | 2022 | N | Industrial CHP | 7 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: T to BLQ
Vintage2012 | natural gas peaker | FALSE | 24205 | Sinclair Oil Corp | 54374 | Sinclair Oil Refinery | WY | Carbon | 2008 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 0.6 | N |  |  | OP | X | 1 | 2012 | 4 | 2022 | N | Industrial CHP | 7 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: T to BLQ
Vintage1925 | other | FALSE | 24205 | Sinclair Oil Corp | 54374 | Sinclair Oil Refinery | WY | Carbon | NO2 | Other Gases | ST |  | S | X | X |  |  | 0.4 | 0.8 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 1 | 1925 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: OG; WDS: NG; NG: OG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1954 | other | FALSE | 24205 | Sinclair Oil Corp | 54374 | Sinclair Oil Refinery | WY | Carbon | NO3 | Other Gases | ST |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 0.1 | N |  |  | OP | X | 1 | 1954 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: OG; WDS: NG; NG: OG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1955 | petroleum | FALSE | 24205 | Sinclair Oil Corp | 54374 | Sinclair Oil Refinery | WY | Carbon | NO5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.6 | N |  |  | SB | Y | 1 | 1955 |  |  | N | Industrial CHP | 7 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1985 | hydro | TRUE | 7601 | Green Mountain Power Corp | 54384 | EHC West Hopkinton | NH | Merrimack | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 1 | 1 | 0.9 | 0.1 | N |  |  | OP | X | 7 | 1985 |  |  | N | Electric Utility | 1 | T: X; BLQ: WAT | [5 empty] | 0 | 10M
Vintage1986 | hydro | TRUE | 63985 | Hydroland Omega LLC | 54385 | Kinneytown New Old | CT | New Haven | GEN1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.8 | 1 | 0.8 | 0.7 | 0.1 | N |  |  | OP | X | 11 | 1986 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1995 | hydro | TRUE | 63985 | Hydroland Omega LLC | 54385 | Kinneytown New Old | CT | New Haven | GEN2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.5 | 1 | 1.4 | 1.4 | 0.1 | N |  |  | OP | X | 1 | 1995 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1985 | hydro | TRUE | 11082 | Littlewood Irrigation District | 54386 | Little Wood Hydro Project | ID | Blaine | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.8 | 0.85 | 2.4 | 2.6 | 0.4 | N |  |  | SB | Y | 2 | 1985 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 1H
Vintage1990 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 54387 | Weeks Falls | WA | King | GEN1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 4.3 | 0.95 | 4.2 | 4.2 | 0.3 | N |  |  | OP | X | 6 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1991 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 54391 | Alice Falls Hydro Project | NY | Clinton | 1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.5 | 0.9 | 1.5 | 1.5 | 0.5 | N |  |  | OP | X | 11 | 1991 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT | [5 empty] | 0 | 10M | [23 empty] | N
Vintage1991 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 54391 | Alice Falls Hydro Project | NY | Clinton | 2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.6 | 0.9 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 11 | 1991 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT | [5 empty] | 0 | 10M | [23 empty] | N
Vintage1987 | hydro | TRUE | 5385 | Dry Creek LLC | 54394 | Dry Creek Project | ID | Butte | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.6 | 1 | 2.2 | 1.5 | 0.2 | N |  |  | OP | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT | [5 empty] | 0 | 10M
Vintage1993 | hydro | TRUE | 59834 | GR Catalyst One, LLC | 54395 | Stillwater Hydro Electric Project | NY | Saratoga | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.7 | 0.9 | 1.7 | 1.7 | 0.4 | N |  |  | OP | X | 4 | 1993 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1993 | hydro | TRUE | 59834 | GR Catalyst One, LLC | 54395 | Stillwater Hydro Electric Project | NY | Saratoga | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.7 | 0.9 | 1.7 | 1.7 | 0.4 | N |  |  | OP | X | 4 | 1993 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage2011 | petroleum | FALSE | 18028 | State of Wisconsin | 54406 | Capitol Heat and Power | WI | Dane | P31 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.1 | N |  |  | SB | Y | 7 | 2011 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: DFO; NG: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2011 | petroleum | FALSE | 18028 | State of Wisconsin | 54406 | Capitol Heat and Power | WI | Dane | P32 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.1 | N |  |  | SB | Y | 7 | 2011 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: DFO; NG: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1951 | natural gas steam turbine | FALSE | 18028 | State of Wisconsin | 54407 | Waupun Correctional Central Heating Plt | WI | Dodge | 1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.1 | N |  |  | OP | X | 5 | 1951 |  |  | Y | Commercial CHP | 5 | T: B; BLQ: NG; WDS: DFO; NG: NG | DFO |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1951 | natural gas steam turbine | FALSE | 18028 | State of Wisconsin | 54407 | Waupun Correctional Central Heating Plt | WI | Dodge | 2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.2 | N |  |  | OP | X | 5 | 1951 |  |  | Y | Commercial CHP | 5 | T: B; BLQ: NG; WDS: DFO; NG: NG | DFO |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1991 | petroleum | FALSE | 18028 | State of Wisconsin | 54407 | Waupun Correctional Central Heating Plt | WI | Dodge | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.1 | N |  |  | SB | Y | 6 | 1991 |  |  | N | Commercial CHP | 5 | T: X; BLQ: DFO; NG: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1998 | petroleum | FALSE | 18028 | State of Wisconsin | 54407 | Waupun Correctional Central Heating Plt | WI | Dodge | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.2 | N |  |  | SB | Y | 6 | 1998 |  |  | N | Commercial CHP | 5 | T: X; BLQ: DFO; NG: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1965 | natural gas steam turbine | FALSE | 18028 | State of Wisconsin | 54408 | UW Madison Charter Street Plant | WI | Dane | 1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 9.7 | 0.9 | 9.7 | 9.7 | 0.1 | N |  |  | OP | X | 1 | 1965 |  |  | Y | Commercial CHP | 5 | T: B; BLQ: NG; WDS: DFO; NG: NG | DFO |  |  | N | N |  | 1H |  |  |  |  | N | [18 empty] | Y | Y | Y
Vintage1965 | petroleum | FALSE | 18028 | State of Wisconsin | 54408 | UW Madison Charter Street Plant | WI | Dane | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.3 | 0.9 | 1.3 | 1.3 | 0.1 | N |  |  | SB | Y | 1 | 1965 |  |  | N | Commercial CHP | 5 | T: X; BLQ: DFO; NG: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1970 | petroleum | FALSE | 4823 | Dartmouth College | 54409 | Dartmouth College Heating Plant | NH | Grafton | GEN1 | Petroleum Liquids | ST |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.2 | N |  |  | OP | X | 1 | 1970 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: RFO; NG: RFO | PG |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1970 | petroleum | FALSE | 4823 | Dartmouth College | 54409 | Dartmouth College Heating Plant | NH | Grafton | GEN2 | Petroleum Liquids | ST |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.2 | N |  |  | OP | X | 1 | 1970 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: RFO; NG: RFO | PG |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1992 | petroleum | FALSE | 4823 | Dartmouth College | 54409 | Dartmouth College Heating Plant | NH | Grafton | GEN3 | Petroleum Liquids | ST |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 0.2 | N |  |  | OP | X | 1 | 1992 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: RFO; NG: RFO | PG |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1990 | natural gas peaker | FALSE | 63997 | Western Power and Steam II LLC | 54410 | Western Power & Steam Inc | CA | Kern | CTG | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 27.7 | 0.9 | 19.6 | 19.5 | 12 | N |  |  | OP | X | 3 | 1990 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N | 0 | 12H | [20 empty] | N |  |  | N | N | N | bar: T to BLQ
Vintage1994 | petroleum | FALSE | 9765 | John Deere Dubuque Works | 54414 | John Deere Dubuque Works | IA | Dubuque | GE10 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.4 | 1.4 | 1 | N |  |  | SB | Y | 6 | 1994 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO |  |  |  | N | N |  | 1H |  |  |  | N | [19 empty] | N | N | N
Vintage1994 | petroleum | FALSE | 9765 | John Deere Dubuque Works | 54414 | John Deere Dubuque Works | IA | Dubuque | GEN5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.4 | 1.4 | 1 | N |  |  | SB | Y | 6 | 1994 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1994 | petroleum | FALSE | 9765 | John Deere Dubuque Works | 54414 | John Deere Dubuque Works | IA | Dubuque | GEN6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.4 | 1.4 | 1 | N |  |  | SB | Y | 6 | 1994 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1994 | petroleum | FALSE | 9765 | John Deere Dubuque Works | 54414 | John Deere Dubuque Works | IA | Dubuque | GEN7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.4 | 1.4 | 1 | N |  |  | SB | Y | 6 | 1994 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1994 | petroleum | FALSE | 9765 | John Deere Dubuque Works | 54414 | John Deere Dubuque Works | IA | Dubuque | GEN8 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.4 | 1.4 | 1 | N |  |  | SB | Y | 6 | 1994 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage1994 | petroleum | FALSE | 9765 | John Deere Dubuque Works | 54414 | John Deere Dubuque Works | IA | Dubuque | GEN9 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.4 | 1.4 | 1 | N |  |  | SB | Y | 6 | 1994 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage2020 | biomass | TRUE | 55600 | Cadillac Renewable Energy LLC | 54415 | Cadillac Renewable Energy | MI | Wexford | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 44 | 0.9 | 38 | 38 | 10 | N |  |  | OP | X | 8 | 2020 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WDS; NG: NG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1986 | hydro | TRUE | 7601 | Green Mountain Power Corp | 54418 | Rollinsford | NH | Strafford | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 1 | 0.7 | 0.6 | 0.1 | N |  |  | OP | X | 10 | 1986 |  |  | N | Electric Utility | 1 | T: X; BLQ: WAT | [5 empty] | 0 | 10M
Vintage1995 | hydro | TRUE | 7601 | Green Mountain Power Corp | 54418 | Rollinsford | NH | Strafford | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 1 | 0.7 | 0.6 | 0.1 | N |  |  | OP | X | 1 | 1995 |  |  | N | Electric Utility | 1 | T: X; BLQ: WAT | [5 empty] | 0 | 10M
Vintage2012 | petroleum | FALSE | 19553 | Unisea Inc | 54422 | Unisea G 2 | AK | Aleutians West | CAT4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.9 | 1 | 1 | 0.3 | N |  |  | OP | X | 5 | 2012 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2012 | petroleum | FALSE | 19553 | Unisea Inc | 54422 | Unisea G 2 | AK | Aleutians West | CAT5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.9 | 1 | 1 | 0.3 | N |  |  | OP | X | 5 | 2012 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1990 | petroleum | FALSE | 19553 | Unisea Inc | 54422 | Unisea G 2 | AK | Aleutians West | GEN1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.2 | 2.2 | 1.5 | N |  |  | OP | X | 8 | 1990 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO; WDS: OBL |  |  |  | N | N |  | 10M | [23 empty] | Y | Y | N
Vintage1990 | petroleum | FALSE | 19553 | Unisea Inc | 54422 | Unisea G 2 | AK | Aleutians West | GEN2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.6 | 0.8 | 2.3 | 2.3 | 1.5 | N |  |  | OP | X | 8 | 1990 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO; WDS: OBL |  |  |  | N | N |  | 10M | [23 empty] | Y | Y | N
Vintage1990 | petroleum | FALSE | 19553 | Unisea Inc | 54422 | Unisea G 2 | AK | Aleutians West | GEN3 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2.3 | 2.3 | 1.5 | N |  |  | OP | X | 8 | 1990 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO; WDS: OBL |  |  |  | N | N |  | 10M | [23 empty] | Y | Y | N
Vintage1990 | petroleum | FALSE | 19553 | Unisea Inc | 54422 | Unisea G 2 | AK | Aleutians West | GEN4 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.2 | 2.2 | 1.5 | N |  |  | OP | X | 8 | 1990 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO; WDS: OBL |  |  |  | N | N |  | 10M | [23 empty] | Y | Y | N
Vintage1990 | petroleum | FALSE | 19553 | Unisea Inc | 54422 | Unisea G 2 | AK | Aleutians West | GEN5 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.7 | 0.8 | 2.3 | 2.3 | 1.5 | N |  |  | OP | X | 8 | 1990 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO; WDS: OBL |  |  |  | N | N |  | 10M | [23 empty] | Y | Y | N
Vintage1990 | petroleum | FALSE | 19553 | Unisea Inc | 54422 | Unisea G 2 | AK | Aleutians West | GEN6 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.5 | 0.8 | 2.2 | 2.2 | 1.5 | N |  |  | OP | X | 8 | 1990 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO; WDS: OBL |  |  |  | N | N |  | 10M | [23 empty] | Y | Y | N
Vintage1994 | natural gas combined cycle | TRUE | 49901 | Northern Star Generation Services Co LLC | 54426 | Mulberry Cogeneration Facility | FL | Polk | GT1 | Natural Gas Fired Combined Cycle | CT | CC1 | W | X | N |  |  | 82 | 0.9 | 78 | 80 | 40 | N |  |  | OP | X | 5 | 1994 |  |  | Y | IPP CHP | 3 | T: T; BLQ: NG; WDS: DFO; NG: NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1994 | natural gas combined cycle | TRUE | 49901 | Northern Star Generation Services Co LLC | 54426 | Mulberry Cogeneration Facility | FL | Polk | ST1 | Natural Gas Fired Combined Cycle | CA | CC1 | W | N | X |  |  | 43.3 | 0.9 | 37 | 40 | 20 | N |  |  | OP | X | 7 | 1994 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1999 | biomass | TRUE | 7043 | Temple-Inland Corp | 54427 | Gaylord Container Bogalusa | LA | Washington | NO10 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 37 | 0.9 | 34.4 | 34.8 | 4 | N |  |  | OP | X | 4 | 1999 |  |  | Y | Industrial CHP | 7 | B | BLQ | WDS | RFO | NG |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1981 | biomass | TRUE | 7043 | Temple-Inland Corp | 54427 | Gaylord Container Bogalusa | LA | Washington | NO8 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 25 | 0.8 | 22.5 | 23.5 | 4 | N |  |  | OP | X | 3 | 1981 |  |  | N | Industrial CHP | 7 | X | BLQ | WDS | RFO | NG |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1979 | biomass | TRUE | 7043 | Temple-Inland Corp | 54427 | Gaylord Container Bogalusa | LA | Washington | NO9 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 37.5 | 0.85 | 34.9 | 35.3 | 4 | N |  |  | OP | X | 6 | 1979 |  |  | N | Industrial CHP | 7 | X | BLQ | WDS | RFO | NG |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1991 | biomass | TRUE | 57356 | Alabama River Cellulose LLC | 54429 | Alabama Pine Pulp | AL | Monroe | GEN2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 69 | 0.9 | 68.7 | 70.1 | 5 | N |  |  | OP | X | 11 | 1991 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: BLQ; WDS: WDS; NG: NG | DFO |  |  | N | N |  | OVER |  |  |  |  | N | [18 empty] | N | N | N
Vintage1990 | natural gas peaker | FALSE | 60637 | Sentinel Peak Resources California, LLC | 54447 | Welport Lease Project | CA | Kern | TI | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | N004 | N004 | 5 | 0.8 | 4 | 4.7 | 4 | N |  |  | OP | X | 3 | 1990 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1988 | natural gas peaker | FALSE | 60637 | Sentinel Peak Resources California, LLC | 54449 | Dome Project | CA | Kern | T1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SO#1 | SO#1 | 3 | 0.8 | 2.5 | 2.7 | 2.4 | N |  |  | OP | X | 8 | 1988 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1988 | natural gas peaker | FALSE | 60637 | Sentinel Peak Resources California, LLC | 54449 | Dome Project | CA | Kern | T2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | SO#1 | SO#1 | 3 | 0.8 | 2.5 | 2.7 | 2.4 | N |  |  | OP | X | 8 | 1988 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1984 | other | FALSE | 38215 | Phillips 66 - Los Angeles | 54451 | Los Angeles Refinery Wilmington | CA | Los Angeles | G1 | Other Natural Gas | OT |  | S | X | X |  |  | 10 | 1 | 6.1 | 7 | 6.1 | N |  |  | OS | X | 5 | 1984 |  |  | N | Industrial CHP | 7 | [11 empty] | N | N |  | OVER | [23 empty] | N | bar: T to BLQ
Vintage1988 | other | FALSE | 38215 | Phillips 66 - Los Angeles | 54451 | Los Angeles Refinery Wilmington | CA | Los Angeles | G2 | Other Gases | GT |  | S | X | X |  |  | 58.5 | 0.8 | 45 | 48 | 35 | N |  |  | OP | X | 5 | 1988 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: OG; WDS: NG |  |  |  | N | N |  | OVER |  | N | [21 empty] | Y | Y | N
Vintage1977 | natural gas peaker | FALSE | 179 | Agrium US Inc | 54452 | Agrium Kenai Nitrogen Operations | AK | Kenai Peninsula | 744A | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 0.1 | N |  |  | OS | X | 10 | 1977 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1977 | natural gas peaker | FALSE | 179 | Agrium US Inc | 54452 | Agrium Kenai Nitrogen Operations | AK | Kenai Peninsula | 744B | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 0.1 | N |  |  | OS | X | 10 | 1977 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1977 | natural gas peaker | FALSE | 179 | Agrium US Inc | 54452 | Agrium Kenai Nitrogen Operations | AK | Kenai Peninsula | 744C | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 0.1 | N |  |  | OS | X | 10 | 1977 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1977 | natural gas peaker | FALSE | 179 | Agrium US Inc | 54452 | Agrium Kenai Nitrogen Operations | AK | Kenai Peninsula | 744D | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 0.1 | N |  |  | OS | X | 10 | 1977 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1977 | natural gas peaker | FALSE | 179 | Agrium US Inc | 54452 | Agrium Kenai Nitrogen Operations | AK | Kenai Peninsula | 744E | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 2.5 | 0.9 | 2.5 | 2.5 | 0.1 | N |  |  | OS | X | 10 | 1977 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1990 | onshore wind | TRUE | 57170 | EDF Renewable Asset Holdings, Inc. | 54453 | EDF Renewable Windfarm V Inc | CA | Solano | GEN2 | Onshore Wind Turbine | WT |  | W | X | X |  |  | 15.5 |  | 15.5 | 15.5 | 0 | N |  |  | OP | X | 1 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WND |  |  |  | N | N | 71
Vintage2011 | onshore wind | TRUE | 49963 | FPL Energy Operating Services, Inc. | 54454 | San Gorgonio Windplant WPP1993 | CA | Riverside | GEN11 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 49.5 |  | 49.5 | 49.5 | 2.5 | N |  |  | OP | X | 12 | 2011 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WND |  |  |  | N | N | 33 | [24 empty] | N
Vintage1989 | petroleum | FALSE | 64432 | SWVP Alpharetta Owners, LLC | 54457 | Hewlett Packard Enterprise | GA | Fulton | ALF1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.9 | 1 | 1 | 0 | N |  |  | SB | N | 5 | 1989 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1989 | petroleum | FALSE | 64432 | SWVP Alpharetta Owners, LLC | 54457 | Hewlett Packard Enterprise | GA | Fulton | ALF2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.9 | 1 | 1 | 0 | N |  |  | SB | N | 5 | 1989 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1989 | petroleum | FALSE | 64432 | SWVP Alpharetta Owners, LLC | 54457 | Hewlett Packard Enterprise | GA | Fulton | ALF3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.9 | 1 | 1 | 0 | N |  |  | SB | N | 5 | 1989 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [12 empty] | 0 | [10 empty] | N | N | N
Vintage1989 | petroleum | FALSE | 64432 | SWVP Alpharetta Owners, LLC | 54457 | Hewlett Packard Enterprise | GA | Fulton | ALF4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.9 | 1 | 1 | 0 | N |  |  | SB | N | 5 | 1989 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1991 | petroleum | FALSE | 64432 | SWVP Alpharetta Owners, LLC | 54457 | Hewlett Packard Enterprise | GA | Fulton | ALF5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.9 | 1 | 1 | 0 | N |  |  | SB | N | 5 | 1991 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2005 | petroleum | FALSE | 64432 | SWVP Alpharetta Owners, LLC | 54457 | Hewlett Packard Enterprise | GA | Fulton | B1GN1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.9 | 1.4 | 1.5 | 0 | N |  |  | SB | N | 5 | 2005 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2005 | petroleum | FALSE | 64432 | SWVP Alpharetta Owners, LLC | 54457 | Hewlett Packard Enterprise | GA | Fulton | B1GN2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.9 | 1.4 | 1.5 | 0 | N |  |  | SB | N | 5 | 2005 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1921 | hydro | FALSE | 55810 | Augusta Canal Authority | 54462 | Graniteville Enterprise Division | GA | Richmond | 1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.6 | 0.95 | 0.5 | 0.5 | 0.3 | N |  |  | OP | X | 1 | 1921 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 1H
Vintage1921 | hydro | FALSE | 55810 | Augusta Canal Authority | 54462 | Graniteville Enterprise Division | GA | Richmond | 2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.6 | 0.95 | 0.5 | 0.5 | 0.3 | N |  |  | OP | X | 1 | 1921 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 1H
Vintage1948 | biomass | TRUE | 16024 | Riverwood Intl USA Inc | 54464 | Riverwood International Macon Mill | GA | Bibb | 0001 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 7.5 | 0.95 | 7.5 | 7.5 | 4 | N |  |  | OP | X | 6 | 1948 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | WO | SLW | NG |  | NG |  |  |  | N | N |  | 12H |  | N |  |  | N | N | [17 empty] | Y | Y | Y
Vintage1948 | biomass | TRUE | 16024 | Riverwood Intl USA Inc | 54464 | Riverwood International Macon Mill | GA | Bibb | 0002 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 5 | 0.95 | 4.7 | 4.7 | 0.5 | N |  |  | OP | X | 6 | 1948 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | WO | SLW | NG |  | NG |  |  |  | N | N |  | 12H |  | N |  |  | N | N | [17 empty] | Y | Y | Y
Vintage1948 | biomass | TRUE | 16024 | Riverwood Intl USA Inc | 54464 | Riverwood International Macon Mill | GA | Bibb | 0003 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 5 | 0.95 | 4.7 | 4.7 | 3 | N |  |  | OP | X | 6 | 1948 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | WO | SLW | NG |  | NG |  |  |  | N | N | 0 | 12H |  | N |  |  | N | N | [17 empty] | Y | Y | Y
Vintage1981 | biomass | TRUE | 16024 | Riverwood Intl USA Inc | 54464 | Riverwood International Macon Mill | GA | Bibb | 0004 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 15.9 | 0.95 | 20 | 20 | 10 | N |  |  | OP | X | 6 | 1981 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | WO | SLW | NG |  | NG |  |  |  | N | N |  | 12H | [5 empty] | N | [17 empty] | Y | Y | Y
Vintage2013 | biomass | TRUE | 16024 | Riverwood Intl USA Inc | 54464 | Riverwood International Macon Mill | GA | Bibb | 0005 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 40 | 0.95 | 39.5 | 39.5 | 15 | N |  |  | OP | X | 9 | 2013 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: WDS; WDS: NG; NG: NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1993 | natural gas combined cycle | TRUE | 14184 | Orlando CoGen Ltd LP | 54466 | Orlando Cogen LP | FL | Orange | GEN1 | Natural Gas Fired Combined Cycle | CS |  | J | Y | N |  |  | 122.4 | 0.85 | 120 | 130 | 95 | N |  |  | OP | X | 9 | 1993 |  |  | Y | IPP CHP | 3 | [11 empty] | N |  |  | 12H | [23 empty] | N | bar: T to BLQ
Vintage1988 | hydro | TRUE | 7601 | Green Mountain Power Corp | 54471 | Mascoma Hydro | NH | Grafton | 01 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.5 | 1 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 12 | 1988 |  |  | N | Electric Utility | 1 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1988 | hydro | TRUE | 7601 | Green Mountain Power Corp | 54471 | Mascoma Hydro | NH | Grafton | 02 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.5 | 1 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 12 | 1988 |  |  | N | Electric Utility | 1 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1988 | hydro | TRUE | 7601 | Green Mountain Power Corp | 54471 | Mascoma Hydro | NH | Grafton | 03 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 0.5 | 1 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 12 | 1988 |  |  | N | Electric Utility | 1 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1986 | other | FALSE | 16968 | Simplot Phosphates LLC | 54472 | Simplot Phosphates | WY | Sweetwater | GEN1 | All Other | ST |  | S | X | X |  |  | 11.5 | 0.85 | 11.5 | 11.5 | 2 | N |  |  | OP | X | 8 | 1986 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: OTH; WDS: NG; NG: NG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1993 | natural gas combined cycle | TRUE | 15500 | Puget Sound Energy Inc | 54476 | Sumas Power Plant | WA | Whatcom | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 87.8 | 0.9 | 84.7 | 96.5 | 50 | N |  |  | OP | X | 3 | 1993 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T to BLQ; NG
Vintage1993 | natural gas combined cycle | TRUE | 15500 | Puget Sound Energy Inc | 54476 | Sumas Power Plant | WA | Whatcom | GEN2 | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X |  |  | 37.7 | 0.9 | 40.8 | 40.8 | 20 | N |  |  | OP | X | 3 | 1993 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1990 | natural gas peaker | FALSE | 14173 | Oroville Cogeneration LP | 54477 | Oroville Cogeneration LP | CA | Butte | GEN1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.1 | 0.95 | 1.1 | 1.1 | 0.1 | N |  |  | SB | Y | 1 | 1990 | 1 | 2025 | Y | Industrial CHP | 7 | [11 empty] | N |  |  | 10M | [23 empty] | N | N | N | bar: T to BLQ
Vintage1990 | natural gas peaker | FALSE | 14173 | Oroville Cogeneration LP | 54477 | Oroville Cogeneration LP | CA | Butte | GEN2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.1 | 0.95 | 1.1 | 1.1 | 0.1 | N |  |  | SB | Y | 1 | 1990 | 1 | 2025 | Y | Industrial CHP | 7 | [11 empty] | N |  |  | 10M | [23 empty] | N | N | N | bar: T to BLQ
Vintage1990 | natural gas peaker | FALSE | 14173 | Oroville Cogeneration LP | 54477 | Oroville Cogeneration LP | CA | Butte | GEN3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.1 | 0.95 | 1.1 | 1.1 | 0.1 | N |  |  | SB | Y | 1 | 1990 | 1 | 2025 | Y | Industrial CHP | 7 | [11 empty] | N |  |  | 10M | [23 empty] | N | N | N | bar: T to BLQ
Vintage1990 | natural gas peaker | FALSE | 14173 | Oroville Cogeneration LP | 54477 | Oroville Cogeneration LP | CA | Butte | GEN4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.1 | 0.95 | 1.1 | 1.1 | 0.1 | N |  |  | SB | Y | 1 | 1990 | 1 | 2025 | Y | Industrial CHP | 7 | [11 empty] | N |  |  | 10M | [23 empty] | N | bar: T to BLQ
Vintage1990 | natural gas peaker | FALSE | 14173 | Oroville Cogeneration LP | 54477 | Oroville Cogeneration LP | CA | Butte | GEN5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.1 | 0.95 | 1.1 | 1.1 | 0.1 | N |  |  | SB | Y | 1 | 1990 | 1 | 2025 | Y | Industrial CHP | 7 | [11 empty] | N |  |  | 12H | [23 empty] | N | bar: T to BLQ
Vintage1990 | natural gas peaker | FALSE | 14173 | Oroville Cogeneration LP | 54477 | Oroville Cogeneration LP | CA | Butte | GEN6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.1 | 0.95 | 1.1 | 1.1 | 0.1 | N |  |  | SB | Y | 1 | 1990 | 1 | 2025 | Y | Industrial CHP | 7 | [11 empty] | N |  |  | 12H | [23 empty] | N | bar: T to BLQ
Vintage1990 | natural gas peaker | FALSE | 14173 | Oroville Cogeneration LP | 54477 | Oroville Cogeneration LP | CA | Butte | GEN7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.1 | 0.95 | 1.1 | 1.1 | 0.1 | N |  |  | SB | Y | 1 | 1990 | 1 | 2025 | Y | Industrial CHP | 7 | [11 empty] | N |  |  | 12H | [23 empty] | N | bar: T to BLQ
Vintage1949 | natural gas steam turbine | FALSE | 547 | American Sugar Refining Inc. | 54512 | Domino Sugar Arabi Plant | LA | St Bernard | TG1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 5 | 0.8 | 3.4 | 3.1 | 1 | N |  |  | OP | X | 1 | 1949 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T to BLQ; NG
Vintage2003 | natural gas steam turbine | FALSE | 547 | American Sugar Refining Inc. | 54512 | Domino Sugar Arabi Plant | LA | St Bernard | TG2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 5 | 0.8 | 2.3 | 2.3 | 1 | N |  |  | OA | X | 6 | 2003 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T to BLQ; NG
Vintage1949 | natural gas steam turbine | FALSE | 547 | American Sugar Refining Inc. | 54512 | Domino Sugar Arabi Plant | LA | St Bernard | TG3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 4 | 1 | 2 | 1.4 | 1 | N |  |  | OP | X | 1 | 1949 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T to BLQ; NG
Vintage1992 | natural gas peaker | FALSE | 30038 | WestRock (IL) | 54513 | WestRock (IL) | IL | Kane | E-1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | N/A | N/A | 0.7 | 0.8 | 0.7 | 0.7 | 0.1 | N |  |  | SB | Y | 6 | 1992 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1992 | natural gas peaker | FALSE | 30038 | WestRock (IL) | 54513 | WestRock (IL) | IL | Kane | E2-A | Natural Gas Internal Combustion Engine | IC |  | S | X | X | N/A | N/A | 0.7 | 0.8 | 0.7 | 0.7 | 0.1 | N |  |  | SB | Y | 6 | 1992 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1992 | natural gas peaker | FALSE | 30038 | WestRock (IL) | 54513 | WestRock (IL) | IL | Kane | E2-B | Natural Gas Internal Combustion Engine | IC |  | S | X | X | N/A | N/A | 0.7 | 0.8 | 0.7 | 0.7 | 0.1 | N |  |  | SB | Y | 6 | 1992 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1992 | natural gas peaker | FALSE | 30038 | WestRock (IL) | 54513 | WestRock (IL) | IL | Kane | E3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | N/A | N/A | 0.8 | 0.8 | 0.8 | 0.8 | 0.1 | N |  |  | SB | Y | 6 | 1992 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1992 | hydro | TRUE | 1851 | Blind Canyon Aquaranch, Inc. | 54514 | Blind Canyon Hydro | ID | Gooding | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.3 | 0.8 | 1.3 | 1.3 | 1.3 | N |  |  | OP | X | 4 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 12H | [20 empty] | N |  |  | N
Vintage1990 | petroleum | FALSE | 4566 | Crotched Mt Rehab Ctr Inc | 54515 | Crotched Mountain Rehabilitation Center | NH | Hillsborough | GEN1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.7 | 1 | 0.7 | 0.7 | 0.7 | N |  |  | SB | N | 2 | 1990 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1990 | petroleum | FALSE | 4566 | Crotched Mt Rehab Ctr Inc | 54515 | Crotched Mountain Rehabilitation Center | NH | Hillsborough | GEN2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.7 | 1 | 0.7 | 0.7 | 0.7 | N |  |  | SB | N | 2 | 1990 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1990 | petroleum | FALSE | 4566 | Crotched Mt Rehab Ctr Inc | 54515 | Crotched Mountain Rehabilitation Center | NH | Hillsborough | GEN3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.7 | 1 | 0.7 | 0.7 | 0.7 | N |  |  | SB | N | 2 | 1990 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2018 | biomass | TRUE | 17164 | Sierra Pacific Industries | 54517 | Sierra Pacific Sonora | CA | Tuolumne | GEN3 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 7.5 | 0.8 | 6 | 6.4 | 1 | N |  |  | OP | X | 4 | 2018 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: WDS; NG: DFO |  |  |  | N | N |  | 12H | [23 empty] | N |  | N
Vintage1990 | natural gas peaker | FALSE | 6564 | Formosa Plastics Corp | 54518 | Formosa Plastics | LA | East Baton Rouge | GT2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 38 | 0.8 | 33 | 37 | 28 | N |  |  | SB | Y | 7 | 1990 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | bar: T to BLQ
Vintage1996 | natural gas peaker | FALSE | 6564 | Formosa Plastics Corp | 54518 | Formosa Plastics | LA | East Baton Rouge | GT3 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 38.8 | 0.85 | 33 | 37 | 28 | N |  |  | OP | X | 7 | 1996 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1985 | natural gas steam turbine | FALSE | 6564 | Formosa Plastics Corp | 54518 | Formosa Plastics | LA | East Baton Rouge | ST1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 12 | 0.848 | 8 | 8 | 2 | N |  |  | OP | X | 5 | 1985 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T to BLQ; NG
Vintage1990 | natural gas steam turbine | FALSE | 6564 | Formosa Plastics Corp | 54518 | Formosa Plastics | LA | East Baton Rouge | ST2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 12 | 0.85 | 8 | 8 | 2 | N |  |  | OP | X | 10 | 1990 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T to BLQ; NG
Vintage1994 | natural gas peaker | FALSE | 6831 | Ft Worth City of | 54520 | Village Creek Water Reclamation Facility | TX | Tarrant | SD1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | NA | NA | 0.9 | 0.8 | 0.9 | 0.9 | 0.1 | N |  |  | SB | N | 4 | 1994 |  |  | N | Commercial CHP | 5 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: T to BLQ
Vintage1994 | natural gas peaker | FALSE | 6831 | Ft Worth City of | 54520 | Village Creek Water Reclamation Facility | TX | Tarrant | SD2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X | NA | NA | 0.9 | 0.8 | 0.9 | 0.9 | 0.1 | N |  |  | SB | N | 4 | 1994 |  |  | N | Commercial CHP | 5 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: T to BLQ
Vintage2001 | natural gas peaker | FALSE | 6831 | Ft Worth City of | 54520 | Village Creek Water Reclamation Facility | TX | Tarrant | TG1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | NA | NA | 5.3 | 0.8 | 4.2 | 5.3 | 0.1 | N |  |  | OP | X | 6 | 2001 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ; NG
Vintage2001 | natural gas peaker | FALSE | 6831 | Ft Worth City of | 54520 | Village Creek Water Reclamation Facility | TX | Tarrant | TG2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | NA | NA | 5.3 | 0.8 | 4.2 | 5.3 | 0.1 | N |  |  | OP | X | 9 | 2001 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ; NG
Vintage1992 | natural gas peaker | FALSE | 8705 | Hoffer Plastics | 54523 | Hoffer Plastics | IL | Kane | GEN1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.4 | N |  |  | OP | X | 4 | 1992 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: T to BLQ
Vintage1992 | natural gas peaker | FALSE | 8705 | Hoffer Plastics | 54523 | Hoffer Plastics | IL | Kane | GEN2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.4 | N |  |  | OP | X | 4 | 1992 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: T to BLQ
Vintage1992 | natural gas peaker | FALSE | 8705 | Hoffer Plastics | 54523 | Hoffer Plastics | IL | Kane | GEN3 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.4 | N |  |  | OP | X | 4 | 1992 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: T to BLQ
Vintage1992 | natural gas peaker | FALSE | 8705 | Hoffer Plastics | 54523 | Hoffer Plastics | IL | Kane | GEN4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.4 | N |  |  | OP | X | 4 | 1992 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: T to BLQ
Vintage1992 | natural gas peaker | FALSE | 8705 | Hoffer Plastics | 54523 | Hoffer Plastics | IL | Kane | GEN5 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.4 | N |  |  | OP | X | 4 | 1992 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: T to BLQ
Vintage1992 | natural gas peaker | FALSE | 8705 | Hoffer Plastics | 54523 | Hoffer Plastics | IL | Kane | GEN6 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.4 | N |  |  | OP | X | 4 | 1992 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: T to BLQ
Vintage1992 | natural gas peaker | FALSE | 8705 | Hoffer Plastics | 54523 | Hoffer Plastics | IL | Kane | GEN7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.4 | N |  |  | OP | X | 4 | 1992 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: T to BLQ
Vintage1992 | natural gas peaker | FALSE | 8705 | Hoffer Plastics | 54523 | Hoffer Plastics | IL | Kane | GEN8 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.4 | N |  |  | OP | X | 4 | 1992 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: T to BLQ
Vintage1995 | natural gas peaker | FALSE | 8705 | Hoffer Plastics | 54523 | Hoffer Plastics | IL | Kane | GEN9 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.4 | N |  |  | OP | X | 4 | 1995 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: T to BLQ
Vintage1995 | hydro | TRUE | 8862 | Horseshoe Bend Hydroelectric Co | 54524 | Horseshoe Bend Hydroelectric Co | ID | Boise | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.7 | 0.95 | 4.7 | 4.7 | 0.5 | N |  |  | OP | X | 4 | 1995 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1995 | hydro | TRUE | 8862 | Horseshoe Bend Hydroelectric Co | 54524 | Horseshoe Bend Hydroelectric Co | ID | Boise | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.7 | 0.95 | 4.7 | 4.7 | 0.5 | N |  |  | OP | X | 4 | 1995 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [20 empty] | N |  |  | N
Vintage1991 | hydro | FALSE | 26003 | Kankakee City of | 54525 | Kankakee Hydro Facility | IL | Kankakee | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.85 | 0.4 | 0.4 | 0.1 | N |  |  | OS | X | 7 | 1991 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 10M | [20 empty] | Y | 5 | 2023 | N
Vintage1991 | hydro | FALSE | 26003 | Kankakee City of | 54525 | Kankakee Hydro Facility | IL | Kankakee | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.85 | 0.4 | 0.4 | 0.1 | N |  |  | OS | X | 7 | 1991 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 10M | [20 empty] | Y | 5 | 2023 | N
Vintage1991 | hydro | FALSE | 26003 | Kankakee City of | 54525 | Kankakee Hydro Facility | IL | Kankakee | 3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 0.85 | 0.4 | 0.4 | 0.1 | N |  |  | OP | X | 7 | 1991 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: WAT |  |  |  | N |  |  | 10M | [20 empty] | Y | 5 | 2023 | N
Vintage1976 | hard coal | FALSE | 17604 | Southern Minnesota Beet Sugar | 54533 | Southern Minnesota Beet Sugar | MN | Renville | 0001 | Conventional Steam Coal | ST |  | S | X | X |  |  | 7.5 | 0.8 | 7.5 | 7.5 | 1.5 | N |  |  | OP | X | 9 | 1976 |  |  | Y | Industrial CHP | 7 | T: B; BLQ: SUB; WDS: NG; NG: SUB | NG |  |  | N | N |  | 12H |  | Y |  | N |  | Y | [17 empty] | Y | Y | N
Vintage1998 | biomass | TRUE | 57249 | EPP Renewable Energy | 54536 | Sumpter Energy Associates | MI | Wayne | 0202 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.95 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 7 | 1998 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1998 | biomass | TRUE | 57249 | EPP Renewable Energy | 54536 | Sumpter Energy Associates | MI | Wayne | 0203 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.95 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 7 | 1998 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1998 | biomass | TRUE | 57249 | EPP Renewable Energy | 54536 | Sumpter Energy Associates | MI | Wayne | 0204 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.95 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 7 | 1998 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1998 | biomass | TRUE | 57249 | EPP Renewable Energy | 54536 | Sumpter Energy Associates | MI | Wayne | 0205 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.95 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 7 | 1998 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1992 | biomass | TRUE | 57249 | EPP Renewable Energy | 54536 | Sumpter Energy Associates | MI | Wayne | 0386 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.95 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 7 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1992 | biomass | TRUE | 57249 | EPP Renewable Energy | 54536 | Sumpter Energy Associates | MI | Wayne | 0388 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.95 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 7 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1992 | biomass | TRUE | 57249 | EPP Renewable Energy | 54536 | Sumpter Energy Associates | MI | Wayne | 0389 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.95 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 7 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1992 | biomass | TRUE | 57249 | EPP Renewable Energy | 54536 | Sumpter Energy Associates | MI | Wayne | 0392 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.95 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 7 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1992 | biomass | TRUE | 57249 | EPP Renewable Energy | 54536 | Sumpter Energy Associates | MI | Wayne | 0435 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.95 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 7 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1992 | biomass | TRUE | 57249 | EPP Renewable Energy | 54536 | Sumpter Energy Associates | MI | Wayne | 0437 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.95 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 7 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1992 | biomass | TRUE | 57249 | EPP Renewable Energy | 54536 | Sumpter Energy Associates | MI | Wayne | 0440 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.95 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 7 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1992 | biomass | TRUE | 57249 | EPP Renewable Energy | 54536 | Sumpter Energy Associates | MI | Wayne | 0447 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.95 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 7 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1992 | biomass | TRUE | 57249 | EPP Renewable Energy | 54536 | Sumpter Energy Associates | MI | Wayne | 0464 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.95 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 7 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1992 | biomass | TRUE | 57249 | EPP Renewable Energy | 54536 | Sumpter Energy Associates | MI | Wayne | 0467 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.95 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 7 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1994 | natural gas combined cycle | TRUE | 15500 | Puget Sound Energy Inc | 54537 | Ferndale Generating Station | WA | Whatcom | CT1A | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 95.9 | 0.9 | 86 | 94 | 35 | N |  |  | OP | X | 4 | 1994 |  |  | Y | Electric Utility | 1 | T: T; BLQ: NG; WDS: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1994 | natural gas combined cycle | TRUE | 15500 | Puget Sound Energy Inc | 54537 | Ferndale Generating Station | WA | Whatcom | CT1B | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N |  |  | 95.9 | 0.9 | 86 | 94 | 35 | N |  |  | OP | X | 4 | 1994 |  |  | Y | Electric Utility | 1 | T: T; BLQ: NG; WDS: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1994 | natural gas combined cycle | TRUE | 15500 | Puget Sound Energy Inc | 54537 | Ferndale Generating Station | WA | Whatcom | ST1 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 93.7 | 0.9 | 98 | 98 | 30 | N |  |  | OP | X | 4 | 1994 |  |  | Y | Electric Utility | 1 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T to BLQ; NG
Vintage1994 | natural gas peaker | TRUE | 13994 | Oglethorpe Power Corporation | 54538 | Hartwell Energy Facility | GA | Hart | MAG1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 180 | 0.85 | 149.5 | 176.8 | 75 | N |  |  | OP | X | 4 | 1994 |  |  | N | Electric Utility | 1 | T: X; BLQ: NG; WDS: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1994 | natural gas peaker | TRUE | 13994 | Oglethorpe Power Corporation | 54538 | Hartwell Energy Facility | GA | Hart | MAG2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 180 | 0.85 | 148.6 | 176.8 | 75 | N |  |  | OP | X | 4 | 1994 |  |  | N | Electric Utility | 1 | T: X; BLQ: NG; WDS: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1992 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54539 | Venice Resources Gas Recovery | MI | Shiawassee | GEN1 | Landfill Gas | IC |  | S | X | X | Zonal | Zonal | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 3 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1992 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54539 | Venice Resources Gas Recovery | MI | Shiawassee | GEN2 | Landfill Gas | IC |  | S | X | X | Zonal | Zonal | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 3 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N | 0 | 1H | [23 empty] | N | N | N
Vintage1992 | natural gas peaker | FALSE | 20328 | Wells Manufacturing Co | 54540 | Charter Dura-Bar | IL | McHenry | 1A | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1 | 0.8 | 0.9 | 1 | 0.7 | N |  |  | OP | X | 4 | 1992 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1992 | natural gas peaker | FALSE | 20328 | Wells Manufacturing Co | 54540 | Charter Dura-Bar | IL | McHenry | 1B | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1 | 0.8 | 0.9 | 1 | 0.7 | N |  |  | OP | X | 4 | 1992 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1992 | natural gas peaker | FALSE | 20328 | Wells Manufacturing Co | 54540 | Charter Dura-Bar | IL | McHenry | 2A | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1 | 0.8 | 0.9 | 1 | 0.7 | N |  |  | OP | X | 4 | 1992 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1992 | natural gas peaker | FALSE | 20328 | Wells Manufacturing Co | 54540 | Charter Dura-Bar | IL | McHenry | 2B | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1 | 0.8 | 0.9 | 1 | 0.7 | N |  |  | OP | X | 4 | 1992 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1992 | natural gas peaker | FALSE | 20328 | Wells Manufacturing Co | 54540 | Charter Dura-Bar | IL | McHenry | 3A | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1 | 0.8 | 0.9 | 1 | 0.7 | N |  |  | OP | X | 4 | 1992 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 1H | [23 empty] | N |  | N | bar: T to BLQ
Vintage1992 | natural gas peaker | FALSE | 20328 | Wells Manufacturing Co | 54540 | Charter Dura-Bar | IL | McHenry | 3B | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1 | 0.8 | 0.9 | 1 | 0.7 | N |  |  | OP | X | 4 | 1992 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 1H | [23 empty] | N |  | N | bar: T to BLQ
Vintage1994 | natural gas combined cycle | TRUE | 17254 | Sithe/Independence LLC | 54547 | Sithe Independence Station | NY | Oswego | 1 | Natural Gas Fired Combined Cycle | CT | BLK1 | W | X | N | Sithe_Ind_1 | Sithe_Ind_1 | 169.2 | 0.8 | 159.2 | 191.9 | 90 | N |  |  | OP | X | 10 | 1994 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: T to BLQ
Vintage1994 | natural gas combined cycle | TRUE | 17254 | Sithe/Independence LLC | 54547 | Sithe Independence Station | NY | Oswego | 2 | Natural Gas Fired Combined Cycle | CT | BLK1 | W | X | N | Sithe_Ind_2 | Sithe_Ind_2 | 169.2 | 0.8 | 159.2 | 191.9 | 90 | N |  |  | OP | X | 9 | 1994 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: T to BLQ
Vintage1994 | natural gas combined cycle | TRUE | 17254 | Sithe/Independence LLC | 54547 | Sithe Independence Station | NY | Oswego | 3 | Natural Gas Fired Combined Cycle | CT | BLK2 | W | X | N | Sithe_Ind_3 | Sithe_Ind_3 | 169.2 | 0.8 | 159.2 | 191.9 | 90 | N |  |  | OP | X | 8 | 1994 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: T to BLQ
Vintage1994 | natural gas combined cycle | TRUE | 17254 | Sithe/Independence LLC | 54547 | Sithe Independence Station | NY | Oswego | 4 | Natural Gas Fired Combined Cycle | CT | BLK2 | W | X | N | Sithe_Ind_4 | Sithe_Ind_4 | 169.5 | 0.8 | 159.2 | 191.9 | 90 | N |  |  | OP | X | 9 | 1994 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: T to BLQ
Vintage1994 | natural gas combined cycle | TRUE | 17254 | Sithe/Independence LLC | 54547 | Sithe Independence Station | NY | Oswego | 5 | Natural Gas Fired Combined Cycle | CA | BLK1 | W | Y | X | Sithe_Independ | Sithe_Independ | 204.5 | 0.89 | 171.7 | 206.9 | 45 | N |  |  | OP | X | 10 | 1994 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: T to BLQ
Vintage1994 | natural gas combined cycle | TRUE | 17254 | Sithe/Independence LLC | 54547 | Sithe Independence Station | NY | Oswego | 6 | Natural Gas Fired Combined Cycle | CA | BLK2 | W | Y | X | Sithe_Independ | Sithe_Independ | 204.5 | 0.89 | 171.7 | 206.9 | 45 | N |  |  | OP | X | 9 | 1994 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [20 empty] | N |  |  | N | N | N | bar: T to BLQ
Vintage1991 | hydro | TRUE | 59827 | Ampersand Long Falls Hydro, LLC | 54548 | Longfalls Facility | NY | Jefferson | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.3 | 1 | 3 | 3 | 1 | N |  |  | OP | X | 10 | 1991 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1993 | natural gas combined cycle | FALSE | 57139 | W&T Offshore Inc | 54550 | W&T Onshore Treating Facility (OTF) | AL | Mobile | 901 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 0.9 | 0.95 | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 12 | 1993 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1993 | natural gas combined cycle | FALSE | 57139 | W&T Offshore Inc | 54550 | W&T Onshore Treating Facility (OTF) | AL | Mobile | 901A | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 3.7 | 0.95 | 3.4 | 3.6 | 1.1 | N |  |  | OP | X | 9 | 1993 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1993 | natural gas combined cycle | FALSE | 57139 | W&T Offshore Inc | 54550 | W&T Onshore Treating Facility (OTF) | AL | Mobile | 901B | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 3.7 | 0.95 | 3.4 | 3.6 | 1.1 | N |  |  | OP | X | 9 | 1993 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1993 | natural gas combined cycle | FALSE | 57139 | W&T Offshore Inc | 54550 | W&T Onshore Treating Facility (OTF) | AL | Mobile | 901C | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | Y |  |  | 3.7 | 0.8 | 3.4 | 3.6 | 1.1 | N |  |  | OP | X | 9 | 1993 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | bar: T to BLQ
Vintage1989 | hydro | TRUE | 40613 | Northern California Power Agny | 54554 | Spicer Meadow Project | CA | Tuolumne | GEN1 | Conventional Hydroelectric | HY |  | W | X | X | SPICER_1_UNITS-APND | SPICER_1_UNITS-APND | 2.7 | 0.95 | 2.5 | 2.5 | 0.8 | N |  |  | OP | X | 11 | 1989 |  |  | N | Electric Utility | 1 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1989 | hydro | TRUE | 40613 | Northern California Power Agny | 54554 | Spicer Meadow Project | CA | Tuolumne | GEN2 | Conventional Hydroelectric | HY |  | W | X | X | SPICER_1_UNITS-APND | SPICER_1_UNITS-APND | 2.7 | 0.95 | 2.5 | 2.5 | 0.8 | N |  |  | OP | X | 11 | 1989 |  |  | N | Electric Utility | 1 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1989 | hydro | TRUE | 40613 | Northern California Power Agny | 54554 | Spicer Meadow Project | CA | Tuolumne | GEN3 | Conventional Hydroelectric | HY |  | W | X | X | SPICER_1_UNITS-APND | SPICER_1_UNITS-APND | 0.5 | 0.95 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 11 | 1989 |  |  | N | Electric Utility | 1 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1989 | hydro | TRUE | 40613 | Northern California Power Agny | 54555 | Collierville Powerhouse | CA | Calaveras | GEN1 | Conventional Hydroelectric | HY |  | W | X | X | COLVIL_7_PL1x2-APND | COLVIL_7_PL1x2-APND | 126.5 | 0.95 | 126.5 | 126.5 | 3 | N |  |  | OP | X | 11 | 1989 |  |  | N | Electric Utility | 1 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 1H
Vintage1989 | hydro | TRUE | 40613 | Northern California Power Agny | 54555 | Collierville Powerhouse | CA | Calaveras | GEN2 | Conventional Hydroelectric | HY |  | W | X | X | COLVIL_7_PL1x2-APND | COLVIL_7_PL1x2-APND | 126.5 | 0.95 | 126.5 | 126.5 | 3 | N |  |  | OP | X | 11 | 1989 |  |  | N | Electric Utility | 1 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 1H
Vintage1996 | natural gas peaker | FALSE | 4222 | Ingredion Inc - Illinois | 54556 | Ingredion Incorporated | IL | Cook | TG03 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 4.8 | 0.8 | 4.4 | 4.8 | 0.5 | N |  |  | SB | Y | 2 | 1996 |  |  | N | Industrial CHP | 7 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | bar: T to BLQ
Vintage1996 | natural gas peaker | FALSE | 4222 | Ingredion Inc - Illinois | 54556 | Ingredion Incorporated | IL | Cook | TG04 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 4.8 | 0.8 | 4.4 | 4.8 | 0.5 | N |  |  | SB | Y | 2 | 1996 |  |  | N | Industrial CHP | 7 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | bar: T to BLQ
Vintage1991 | natural gas steam turbine | FALSE | 4222 | Ingredion Inc - Illinois | 54556 | Ingredion Incorporated | IL | Cook | TGO1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 22.5 | 0.8 | 21.1 | 21.2 | 5 | N |  |  | OP | X | 5 | 1991 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: NG; WDS: BIT; NG: NG |  |  |  | N | N |  | 1H | Y |  |  |  |  | Y | [17 empty] | N | N
Vintage1991 | natural gas steam turbine | FALSE | 4222 | Ingredion Inc - Illinois | 54556 | Ingredion Incorporated | IL | Cook | TGO2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 22.5 | 0.8 | 21.1 | 21.2 | 5 | N |  |  | OP | X | 5 | 1991 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: NG; WDS: BIT; NG: NG |  |  |  | N | N |  | 1H | Y |  |  |  |  | Y | [17 empty] | N | N
Vintage1993 | hydro | TRUE | 8365 | Hazelton/Wilson Joint Venture | 54558 | Hazelton B Hydro | ID | Jerome | U1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.8 | 0.9 | 3.8 | 3.8 | 1.4 | N |  |  | OP | X | 4 | 1993 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 1H | [23 empty] | N
Vintage1993 | hydro | TRUE | 8365 | Hazelton/Wilson Joint Venture | 54558 | Hazelton B Hydro | ID | Jerome | U2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.8 | 0.9 | 3.8 | 3.8 | 1.4 | N |  |  | OP | X | 4 | 1993 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 1H | [23 empty] | N
Vintage1958 | biomass | TRUE | 11169 | Longview Fibre Co | 54562 | Longview Fibre | WA | Cowlitz | 6 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 20 | 0.85 | 22 | 22 | 4 | N |  |  | OP | X | 1 | 1958 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | OBL |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1966 | biomass | TRUE | 11169 | Longview Fibre Co | 54562 | Longview Fibre | WA | Cowlitz | 7 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 25 | 0.85 | 25 | 25 | 4 | N |  |  | OP | X | 4 | 1966 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | WDS | OBL |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1996 | petroleum | FALSE | 21116 | YKK USA Inc | 54566 | YKK USA Chestney | GA | Bibb | BWP1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.9 | 0.5 | 0.5 | 0.1 | N |  |  | SB | N | 10 | 1996 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage2015 | petroleum | FALSE | 21116 | YKK USA Inc | 54566 | YKK USA Chestney | GA | Bibb | SEV1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.9 | 0.3 | 0.3 | 0.1 | N |  |  | SB | N | 8 | 2015 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO | [6 empty] | 10M | [23 empty] | N | N
Vintage1992 | petroleum | FALSE | 21116 | YKK USA Inc | 54566 | YKK USA Chestney | GA | Bibb | SLD1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.9 | 0.5 | 0.5 | 0.1 | N |  |  | SB | N | 12 | 1992 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1990 | biomass | TRUE | 61324 | Yolo County Community Services Department | 54567 | MM Yolo Power | CA | Yolo | 1 | Landfill Gas | IC |  | S | X | X |  |  | 0.6 | 0.98 | 0.5 | 0.5 | 0.5 | N |  |  | OP | X | 10 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1990 | biomass | TRUE | 61324 | Yolo County Community Services Department | 54567 | MM Yolo Power | CA | Yolo | 2 | Landfill Gas | IC |  | S | X | X |  |  | 0.6 | 0.98 | 0.5 | 0.5 | 0.5 | N |  |  | OP | X | 10 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1990 | biomass | TRUE | 61324 | Yolo County Community Services Department | 54567 | MM Yolo Power | CA | Yolo | 3 | Landfill Gas | IC |  | S | X | X |  |  | 0.6 | 0.98 | 0.5 | 0.5 | 0.5 | N |  |  | OA | X | 10 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1993 | biomass | TRUE | 61324 | Yolo County Community Services Department | 54567 | MM Yolo Power | CA | Yolo | 4 | Landfill Gas | IC |  | S | X | X |  |  | 0.9 | 0.98 | 0.6 | 0.6 | 0.5 | N |  |  | OP | X | 3 | 1993 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1998 | biomass | TRUE | 61324 | Yolo County Community Services Department | 54567 | MM Yolo Power | CA | Yolo | 5 | Landfill Gas | IC |  | S | X | X |  |  | 0.9 | 0.98 | 0.4 | 0.4 | 0.3 | N |  |  | OP | X | 12 | 1998 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1988 | biomass | TRUE | 13943 | Ocean County Utilities Auth | 54569 | Bayville Central Facility | NJ | Ocean | COG1 | Other Waste Biomass | IC |  | S | X | X |  |  | 0.3 | 0.9 | 0.3 | 0.3 | 0.2 | N |  |  | OP | X | 9 | 1988 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: OBG; WDS: NG |  |  |  | N | N |  | 1H | [5 empty] | N | [17 empty] | Y | Y
Vintage1988 | biomass | TRUE | 13943 | Ocean County Utilities Auth | 54569 | Bayville Central Facility | NJ | Ocean | COG2 | Other Waste Biomass | IC |  | S | X | X |  |  | 0.3 | 0.9 | 0.3 | 0.3 | 0.2 | N |  |  | OP | X | 9 | 1988 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: OBG; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y
Vintage1988 | biomass | TRUE | 13943 | Ocean County Utilities Auth | 54569 | Bayville Central Facility | NJ | Ocean | COG3 | Other Waste Biomass | IC |  | S | X | X |  |  | 0.3 | 0.9 | 0.3 | 0.3 | 0.2 | N |  |  | OP | X | 9 | 1988 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: OBG; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y
Vintage2002 | petroleum | FALSE | 13943 | Ocean County Utilities Auth | 54569 | Bayville Central Facility | NJ | Ocean | COG4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.7 | N |  |  | OP | X | 5 | 2002 |  |  | N | Commercial CHP | 5 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage2002 | petroleum | FALSE | 13943 | Ocean County Utilities Auth | 54569 | Bayville Central Facility | NJ | Ocean | COG5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.7 | N |  |  | OP | X | 5 | 2002 |  |  | N | Commercial CHP | 5 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage2002 | petroleum | FALSE | 13943 | Ocean County Utilities Auth | 54569 | Bayville Central Facility | NJ | Ocean | COG6 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.7 | N |  |  | OP | X | 5 | 2002 |  |  | N | Commercial CHP | 5 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage2002 | petroleum | FALSE | 13943 | Ocean County Utilities Auth | 54569 | Bayville Central Facility | NJ | Ocean | COG7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.7 | N |  |  | OP | X | 5 | 2002 |  |  | N | Commercial CHP | 5 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage2007 | solar pv | FALSE | 13943 | Ocean County Utilities Auth | 54569 | Bayville Central Facility | NJ | Ocean | CPV1 | Solar Photovoltaic | PV |  | S | X | X |  |  | 0.2 |  | 0.2 | 0.1 |  | N |  |  | OP | X | 5 | 2007 |  |  | N | Commercial CHP | 5 | T: X; BLQ: SUN |  |  |  | N
Vintage1984 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 54572 | Lochmere Hydroelectric Plant | NH | Belknap | UNT1 | Conventional Hydroelectric | HY |  | W | X | X | 4392 | 4392 | 0.3 | 0.82 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 12 | 1984 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT | [6 empty] | 10M
Vintage1984 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 54572 | Lochmere Hydroelectric Plant | NH | Belknap | UNT2 | Conventional Hydroelectric | HY |  | W | X | X | 4392 | 4392 | 0.3 | 0.82 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 12 | 1984 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT | [6 empty] | 10M
Vintage1984 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 54572 | Lochmere Hydroelectric Plant | NH | Belknap | UNT3 | Conventional Hydroelectric | HY |  | W | X | X | 4392 | 4392 | 0.3 | 0.82 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 12 | 1984 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT | [6 empty] | 10M
Vintage1984 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 54572 | Lochmere Hydroelectric Plant | NH | Belknap | UNT4 | Conventional Hydroelectric | HY |  | W | X | X | 4392 | 4392 | 0.3 | 0.82 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 12 | 1984 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT | [6 empty] | 10M
Vintage1988 | hydro | TRUE | 54838 | Windsor Machinery Co Inc | 54573 | Wappinger Falls Hydroelectric | NY | Dutchess | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 1 | 1 | 0.9 | 1 | N |  |  | OP | X | 12 | 1988 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1988 | hydro | TRUE | 54838 | Windsor Machinery Co Inc | 54573 | Wappinger Falls Hydroelectric | NY | Dutchess | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 1 | 1 | 0.9 | 1 | N |  |  | SB | Y | 12 | 1988 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N |  | 0 | 10M
Vintage1994 | natural gas combined cycle | TRUE | 16729 | Saranac Power Partners LP | 54574 | Saranac Facility | NY | Clinton | GEN1 | Natural Gas Fired Combined Cycle | CT | CA | S | X | N |  | NYSEG Northend | 95.2 | 0.9 | 73 | 98 | 40 | N |  |  | OP | X | 6 | 1994 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1994 | natural gas combined cycle | TRUE | 16729 | Saranac Power Partners LP | 54574 | Saranac Facility | NY | Clinton | GEN2 | Natural Gas Fired Combined Cycle | CT | CA | S | X | N |  |  | 95.2 | 0.9 | 81.3 | 95 | 40 | N |  |  | OP | X | 6 | 1994 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1994 | natural gas combined cycle | TRUE | 16729 | Saranac Power Partners LP | 54574 | Saranac Facility | NY | Clinton | GEN3 | Natural Gas Fired Combined Cycle | CA | CA | S | Y | X |  |  | 95.2 | 0.9 | 85 | 87 | 10 | N |  |  | OP | X | 6 | 1994 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1986 | hydro | TRUE | 24931 | Palmer Hydroelectric | 54580 | Curtis Palmer Hydroelectric | NY | Saratoga | C1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.6 | 0.8 | 2.5 | 2.5 | 0.9 | N |  |  | OP | X | 3 | 1986 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1986 | hydro | TRUE | 24931 | Palmer Hydroelectric | 54580 | Curtis Palmer Hydroelectric | NY | Saratoga | C2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.6 | 0.8 | 2.5 | 2.5 | 0.9 | N |  |  | OP | X | 1 | 1986 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 24931 | Palmer Hydroelectric | 54580 | Curtis Palmer Hydroelectric | NY | Saratoga | C3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.6 | 0.8 | 2.4 | 2.4 | 2.3 | N |  |  | OP | X | 12 | 1985 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 24931 | Palmer Hydroelectric | 54580 | Curtis Palmer Hydroelectric | NY | Saratoga | C4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.8 | 1.1 | 1.1 | 0.2 | N |  |  | OP | X | 11 | 1985 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1985 | hydro | TRUE | 24931 | Palmer Hydroelectric | 54580 | Curtis Palmer Hydroelectric | NY | Saratoga | C5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1 | 0.8 | 1.1 | 1.1 | 0.2 | N |  |  | OP | X | 10 | 1985 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1986 | hydro | TRUE | 24931 | Palmer Hydroelectric | 54580 | Curtis Palmer Hydroelectric | NY | Saratoga | P1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 24.6 | 0.9 | 25 | 25 | 6 | N |  |  | OP | X | 11 | 1986 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1986 | hydro | TRUE | 24931 | Palmer Hydroelectric | 54580 | Curtis Palmer Hydroelectric | NY | Saratoga | P2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 24.6 | 0.9 | 25 | 25 | 6 | N |  |  | OP | X | 10 | 1986 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2008 | natural gas combined cycle | TRUE | 56171 | Bicent Power | 54586 | Tanner Street Generation | MA | Middlesex | TRENT | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | UN.LENERGIA13.8LENR | 461 | 57.9 | 0.85 | 58 | 58 | 45 | N |  |  | OP | X | 10 | 2008 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: NG; WDS: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1992 | natural gas combined cycle | TRUE | 56171 | Bicent Power | 54586 | Tanner Street Generation | MA | Middlesex | VAX | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X |  |  | 27.1 | 0.85 | 17 | 19 | 10 | N |  |  | OP | X | 10 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: NG; WDS: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1992 | natural gas combined cycle | TRUE | 15253 | Power City Partners LP | 54592 | Massena Energy Facility | NY | St Lawrence | GEN1 | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | 23902 | 23902 | 66.5 | 0.9 | 46 | 56 | 46 | N |  |  | OP | X | 7 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: NG; WDS: DFO; NG: OBL |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1992 | natural gas combined cycle | TRUE | 15253 | Power City Partners LP | 54592 | Massena Energy Facility | NY | St Lawrence | GEN2 | Natural Gas Fired Combined Cycle | CA | CC1 | S | Y | X | 23902 | 23902 | 35.6 | 0.9 | 35 | 35 | 30 | N |  |  | OP | X | 7 | 1992 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1992 | petroleum | TRUE | 15253 | Power City Partners LP | 54592 | Massena Energy Facility | NY | St Lawrence | IC | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.85 | 2 | 2 | 0.1 | N |  |  | SB | Y | 7 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1992 | natural gas combined cycle | TRUE | 16839 | Seneca Power Partners LP | 54593 | Batavia Power Plant | NY | Genesee | GEN1 | Natural Gas Fired Combined Cycle | CT | CC01 | S | X | N | 24024 | 24024 | 47.7 | 0.9 | 34.3 | 44.3 | 34.3 | N |  |  | OP | X | 9 | 1992 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1992 | natural gas combined cycle | TRUE | 16839 | Seneca Power Partners LP | 54593 | Batavia Power Plant | NY | Genesee | GEN2 | Natural Gas Fired Combined Cycle | CA | CC01 | S | N | X | 24024 | 24024 | 18.5 | 0.9 | 14.5 | 14.8 | 14.5 | N |  |  | OP | X | 9 | 1992 |  |  | N | IPP Non-CHP | 2 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1992 | petroleum | TRUE | 16839 | Seneca Power Partners LP | 54593 | Batavia Power Plant | NY | Genesee | GEN3 | Petroleum Liquids | IC |  | S | X | X | 24024 | 24024 | 1.1 | 0.8 | 1 | 1 | 0.5 | N |  |  | SB | Y | 9 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1990 | petroleum | FALSE | 55994 | University of Arizona - Biosphere 2 | 54594 | University of Arizona - Biosphere 2 | AZ | Pinal | G-1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 1 | N |  |  | SB | Y | 11 | 1990 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2000 | natural gas peaker | FALSE | 55994 | University of Arizona - Biosphere 2 | 54594 | University of Arizona - Biosphere 2 | AZ | Pinal | G-4 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 1 | N |  |  | SB | Y | 4 | 2000 |  |  | N | Commercial Non-CHP | 4 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1992 | petroleum | FALSE | 56478 | University of Michigan NCampus Research | 54604 | Warner Lambert | MI | Washtenaw | 016E | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0 | N |  |  | SB | N | 6 | 1992 |  |  | N | Commercial CHP | 5 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2002 | petroleum | FALSE | 56478 | University of Michigan NCampus Research | 54604 | Warner Lambert | MI | Washtenaw | 0550 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0 | N |  |  | SB | N | 6 | 2002 |  |  | N | Commercial CHP | 5 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2005 | petroleum | FALSE | 56478 | University of Michigan NCampus Research | 54604 | Warner Lambert | MI | Washtenaw | 085-1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.3 | 0.8 | 2.3 | 2.3 | 0 | N |  |  | SB | Y | 12 | 2005 |  |  | N | Commercial CHP | 5 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2005 | petroleum | FALSE | 56478 | University of Michigan NCampus Research | 54604 | Warner Lambert | MI | Washtenaw | 085-2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.3 | 0.8 | 2.3 | 2.3 | 0 | N |  |  | SB | Y | 12 | 2005 |  |  | N | Commercial CHP | 5 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1989 | natural gas peaker | FALSE | 56478 | University of Michigan NCampus Research | 54604 | Warner Lambert | MI | Washtenaw | 5164 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3 | 0.8 | 2.8 | 3.2 | 0 | N |  |  | OP | X | 8 | 1989 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: NG; WDS: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage2007 | petroleum | FALSE | 56478 | University of Michigan NCampus Research | 54604 | Warner Lambert | MI | Washtenaw | 800-1 | Petroleum Liquids | IC |  | S | X | X |  |  | 2.3 | 0.8 | 2.3 | 2.3 | 0 | N |  |  | SB | Y | 11 | 2007 |  |  | N | Commercial CHP | 5 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N |  | N
Vintage1992 | natural gas peaker | FALSE | 21621 | United Technologies | 54605 | Pratt & Whitney | CT | Hartford | FT-8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X | 4004 Z Connecticut | 4004 Z Connecticut | 25.8 | 0.85 | 28 | 31 | 12 | N |  |  | OP | X | 1 | 1992 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: NG; WDS: DFO |  |  |  | N | N | 0 | 1H | [23 empty] | Y | N | Y
Vintage1985 | biomass | TRUE | 4417 | Ingredion Inc - Winston Salem | 54618 | Ingredion Winston Salem | NC | Forsyth | 7500 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 7.5 | 0.8 | 6.6 | 6.6 | 1 | N |  |  | OP | X | 12 | 1985 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: WDS; WDS: NG; NG: WDS | BIT |  |  | N | N | 0 | 12H | [23 empty] | Y | Y | N
Vintage1993 | biomass | TRUE | 4417 | Ingredion Inc - Winston Salem | 54618 | Ingredion Winston Salem | NC | Forsyth | 900 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 0.9 | 0.8 | 0.4 | 0.5 | 0.1 | N |  |  | OP | X | 5 | 1993 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: WDS; WDS: NG; NG: WDS | BIT |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1992 | biomass | TRUE | 64003 | Stored Solar Services, LLC | 54620 | Stored Solar Fitchburg, LLC | MA | Worcester | NO-1 | Wood/Wood Waste Biomass | ST |  | W | X | X |  |  | 18 | 1 | 14.9 | 15.1 | 8 | N |  |  | OP | X | 8 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WDS; WDS: NG; NG: NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage2013 | biomass | TRUE | 12411 | Miami Dade Water & Sewer Dept | 54623 | Central District Wastewater Treat Plant | FL | Miami Dade | 3A | Other Waste Biomass | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 1 | N |  |  | OP | X | 3 | 2013 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: OBG |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage2013 | biomass | TRUE | 12411 | Miami Dade Water & Sewer Dept | 54623 | Central District Wastewater Treat Plant | FL | Miami Dade | 4A | Other Waste Biomass | IC |  | S | X | X |  |  | 1.2 | 0.8 | 1.2 | 1.2 | 1 | N |  |  | OP | X | 3 | 2013 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: OBG |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage2015 | biomass | TRUE | 12411 | Miami Dade Water & Sewer Dept | 54623 | Central District Wastewater Treat Plant | FL | Miami Dade | 5 | Other Waste Biomass | IC |  | S | X | X |  |  | 1.2 | 0.86 | 1.2 | 1.2 | 1 | N |  |  | OP | X | 6 | 2015 |  |  | N | Commercial CHP | 5 | T: X; BLQ: OBG |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N
Vintage2015 | biomass | TRUE | 12411 | Miami Dade Water & Sewer Dept | 54623 | Central District Wastewater Treat Plant | FL | Miami Dade | 6 | Other Waste Biomass | IC |  | S | X | X |  |  | 1.2 | 0.86 | 1.2 | 1.2 | 1 | N |  |  | OP | X | 6 | 2015 |  |  | N | Commercial CHP | 5 | T: X; BLQ: OBG |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage2014 | biomass | TRUE | 12411 | Miami Dade Water & Sewer Dept | 54624 | South District Wastewater Treatment Plt | FL | Miami Dade | 1A | Other Waste Biomass | IC |  | S | X | X |  |  | 2 | 0.86 | 2 | 2 | 1.9 | N |  |  | OP | X | 3 | 2014 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: OBG; WDS: NG; NG: LFG |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | Y | Y | N
Vintage2014 | biomass | TRUE | 12411 | Miami Dade Water & Sewer Dept | 54624 | South District Wastewater Treatment Plt | FL | Miami Dade | 2A | Other Waste Biomass | IC |  | S | X | X |  |  | 2 | 0.86 | 2 | 2 | 1.9 | N |  |  | OP | X | 3 | 2014 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: OBG; WDS: NG; NG: LFG |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | Y | Y | N
Vintage2014 | biomass | TRUE | 12411 | Miami Dade Water & Sewer Dept | 54624 | South District Wastewater Treatment Plt | FL | Miami Dade | 3A | Other Waste Biomass | IC |  | S | X | X |  |  | 2 | 0.86 | 2 | 2 | 1.9 | N |  |  | OP | X | 11 | 2014 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: OBG; WDS: NG; NG: LFG |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | Y | Y | N
Vintage2014 | biomass | TRUE | 12411 | Miami Dade Water & Sewer Dept | 54624 | South District Wastewater Treatment Plt | FL | Miami Dade | 4A | Other Waste Biomass | IC |  | S | X | X |  |  | 2 | 0.86 | 2 | 2 | 1.9 | N |  |  | OP | X | 11 | 2014 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: OBG; WDS: NG; NG: LFG |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | Y | Y | N
Vintage1991 | municipal solid waste | FALSE | 56646 | Covanta Plymouth Renewable Energy L P | 54625 | Covanta Plymouth Renewable Energy | PA | Montgomery | TGI | Municipal Solid Waste | ST |  | S | X | X | PECO | PECO | 32.1 | 0.9 | 28 | 28 | 14 | N |  |  | OP | X | 12 | 1991 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: MSW; NG: DFO |  |  |  | N | N |  | 12H |  |  |  |  | N | [18 empty] | N | N | N
Vintage1989 | biomass | TRUE | 13060 | Mt Poso Cogeneration Co | 54626 | Mt Poso Cogeneration | CA | Kern | TG01 | Wood/Wood Waste Biomass | ST |  | J | X | X |  |  | 62 | 0.8 | 42.4 | 42.4 | 20 | N |  |  | OP | X | 5 | 1989 |  |  | Y | IPP CHP | 3 | T: T; BLQ: WDS; WDS: NG; NG: NG |  |  |  | N | N |  | OVER | [23 empty] | Y | Y | N
Vintage1996 | biomass | TRUE | 13492 | New Hope Power Company | 54627 | Okeelanta Cogeneration | FL | Palm Beach | GEN1 | Other Waste Biomass | ST |  | S | X | X |  |  | 74.9 | 0.85 | 74.9 | 74.9 | 5 | N |  |  | OP | X | 1 | 1996 |  |  | Y | IPP CHP | 3 | T | AB | NG | WDS | DFO |  |  | DFO | NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage2006 | biomass | TRUE | 13492 | New Hope Power Company | 54627 | Okeelanta Cogeneration | FL | Palm Beach | GEN2 | Other Waste Biomass | ST |  | S | X | X |  |  | 54 | 0.85 | 30 | 30 | 5 | N |  |  | OP | X | 8 | 2006 |  |  | Y | IPP CHP | 3 | T | AB | NG | WDS | DFO |  |  | DFO | NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1986 | natural gas peaker | FALSE | 14925 | Phelps Dodge Refining Corp | 54628 | Phelps Dodge Refining | TX | El Paso | 2607 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.5 | 0.8 | 2.6 | 3 | 2.6 | N |  |  | OS | X | 10 | 1986 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1986 | natural gas peaker | FALSE | 14925 | Phelps Dodge Refining Corp | 54628 | Phelps Dodge Refining | TX | El Paso | 2608 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.5 | 0.8 | 2.6 | 3 | 2.6 | N |  |  | OS | X | 10 | 1986 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1992 | natural gas peaker | FALSE | 14925 | Phelps Dodge Refining Corp | 54628 | Phelps Dodge Refining | TX | El Paso | 3001 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 4.2 | 0.8 | 3.2 | 3.8 | 3.2 | N |  |  | OP | X | 6 | 1992 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: T to BLQ
Vintage1992 | natural gas peaker | FALSE | 14925 | Phelps Dodge Refining Corp | 54628 | Phelps Dodge Refining | TX | El Paso | 3002 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 4.2 | 0.8 | 3.2 | 3.8 | 3.2 | N |  |  | OP | X | 6 | 1992 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: T to BLQ
Vintage1992 | natural gas peaker | FALSE | 14925 | Phelps Dodge Refining Corp | 54628 | Phelps Dodge Refining | TX | El Paso | 3003 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 4.2 | 0.8 | 3.2 | 3.8 | 3.2 | N |  |  | OP | X | 6 | 1992 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 10M | [23 empty] | N | N | N | bar: T to BLQ
Vintage1990 | petroleum | FALSE | 54839 | Eagle Materials Co LLC | 54630 | American Gypsum Cogeneration | CO | Eagle | D-1 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.2 | 1.4 | 0.3 | N |  |  | SB | N | 3 | 1990 |  |  | N | Industrial CHP | 7 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1990 | petroleum | FALSE | 54839 | Eagle Materials Co LLC | 54630 | American Gypsum Cogeneration | CO | Eagle | D-2 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.2 | 1.4 | 0.3 | N |  |  | SB | N | 3 | 1990 |  |  | N | Industrial CHP | 7 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1990 | natural gas peaker | FALSE | 54839 | Eagle Materials Co LLC | 54630 | American Gypsum Cogeneration | CO | Eagle | T-1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 2.8 | 0.8 | 2.6 | 2.8 | 0.5 | N |  |  | OP | X | 3 | 1990 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1990 | natural gas peaker | FALSE | 54839 | Eagle Materials Co LLC | 54630 | American Gypsum Cogeneration | CO | Eagle | T-2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 3.6 | 0.8 | 2.6 | 2.8 | 0.5 | N |  |  | OP | X | 3 | 1990 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N |  | N | bar: T to BLQ
Vintage1990 | hard coal | TRUE | 16793 | Schuylkill Energy Resource Inc | 54634 | St Nicholas Cogen Project | PA | Schuylkill | SNCP | Conventional Steam Coal | ST |  | S | X | X | 50601 | 50601 | 99.2 | 0.85 | 86 | 86 | 55 | N |  |  | OP | X | 9 | 1990 |  |  | Y | IPP CHP | 3 | T: T; BLQ: WC; WDS: DFO; NG: DFO |  |  |  | N | N |  | OVER | Y |  |  |  | Y | [18 empty] | N |  | N
Vintage1992 | natural gas peaker | FALSE | 30052 | Indorama Ventures | 54637 | JCO Oxides Olefins Plant | TX | Jefferson | GCG1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 36.9 | 0.85 | 30.5 | 35.5 | 10 | N |  |  | OP | X | 9 | 1992 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ; NG
Vintage1992 | natural gas peaker | FALSE | 30052 | Indorama Ventures | 54637 | JCO Oxides Olefins Plant | TX | Jefferson | GCG2 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 36.9 | 0.85 | 30.5 | 35.5 | 10 | N |  |  | OP | X | 9 | 1992 |  |  | Y | Industrial CHP | 7 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1993 | biomass | TRUE | 56137 | Domtar LLC | 54638 | Johnsonburg Mill | PA | Elk | PT1 | Wood/Wood Waste Biomass | ST |  | S | X | X | 50785 | 50785 | 54 | 0.9 | 49 | 49 | 12 | N |  |  | OP | X | 2 | 1993 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: BLQ; WDS: NG; NG: NG |  |  |  | N | N |  | 12H |  | N | [21 empty] | Y | Y | N
Vintage1914 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54639 | Berlin Gorham | NH | Coos | CAS1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.9 | 2.4 | 2.4 | 0.1 | N |  |  | OP | X | 1 | 1914 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1916 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54639 | Berlin Gorham | NH | Coos | CAS2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.9 | 2.4 | 2.4 | 0.1 | N |  |  | OP | X | 1 | 1916 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1918 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54639 | Berlin Gorham | NH | Coos | CAS3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.1 | 0.9 | 3.1 | 3.1 | 0.1 | N |  |  | OP | X | 1 | 1918 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1920 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54639 | Berlin Gorham | NH | Coos | GOR1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.9 | 1.2 | 1.2 | 0.1 | N |  |  | OP | X | 1 | 1920 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1920 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54639 | Berlin Gorham | NH | Coos | GOR2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.9 | 1.2 | 1.2 | 0.1 | N |  |  | OP | X | 1 | 1920 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1920 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54639 | Berlin Gorham | NH | Coos | GOR3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.9 | 1.2 | 1.2 | 0.1 | N |  |  | OP | X | 1 | 1920 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1920 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54639 | Berlin Gorham | NH | Coos | GOR4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 0.9 | 1.2 | 1.2 | 0.1 | N |  |  | OP | X | 1 | 1920 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1920 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54639 | Berlin Gorham | NH | Coos | RS1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.8 | 0.9 | 3.8 | 3.8 | 0.1 | N |  |  | OP | X | 1 | 1920 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1920 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54639 | Berlin Gorham | NH | Coos | RS3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.1 | 0.9 | 4.1 | 4.1 | 0.1 | N |  |  | OP | X | 1 | 1920 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1916 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54639 | Berlin Gorham | NH | Coos | SH2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 1 | 1916 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1916 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54639 | Berlin Gorham | NH | Coos | SHL1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.1 | N |  |  | OP | X | 1 | 1916 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1929 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54639 | Berlin Gorham | NH | Coos | SHL3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.8 | 0.9 | 1.8 | 1.8 | 0.1 | N |  |  | OP | X | 1 | 1929 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1980 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54639 | Berlin Gorham | NH | Coos | SM1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.9 | 0.8 | 0.8 | 0.1 | N |  |  | OP | X | 10 | 1980 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1980 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54639 | Berlin Gorham | NH | Coos | SM2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.9 | 0.8 | 0.8 | 0.1 | N |  |  | OP | X | 10 | 1980 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1980 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54639 | Berlin Gorham | NH | Coos | SM3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.9 | 0.8 | 0.8 | 0.1 | N |  |  | OP | X | 10 | 1980 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1980 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54639 | Berlin Gorham | NH | Coos | SM4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.8 | 0.9 | 0.8 | 0.8 | 0.1 | N |  |  | OP | X | 10 | 1980 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1921 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54639 | Berlin Gorham | NH | Coos | XP1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.9 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 1 | 1921 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1921 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54639 | Berlin Gorham | NH | Coos | XP2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.9 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 1 | 1921 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1921 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54639 | Berlin Gorham | NH | Coos | XP3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.6 | 0.9 | 0.6 | 0.6 | 0.1 | N |  |  | OP | X | 1 | 1921 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1921 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54639 | Berlin Gorham | NH | Coos | XP4 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.9 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 1 | 1921 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1924 | hydro | TRUE | 7595 | Great Lakes Hydro America LLC | 54639 | Berlin Gorham | NH | Coos | XP5 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.7 | 0.9 | 0.7 | 0.7 | 0.1 | N |  |  | OP | X | 1 | 1924 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1994 | natural gas combined cycle | TRUE | 60789 | Essential Power Operating Company, LLC | 54640 | NAEA Lakewood LLC | NJ | Ocean | GEN1 | Natural Gas Fired Combined Cycle | CT | LCLP | W | X | N |  |  | 77.9 | 0.8 | 84.6 | 84.9 | 62.1 | N |  |  | SB | Y | 4 | 1994 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: NG; WDS: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1994 | natural gas combined cycle | TRUE | 60789 | Essential Power Operating Company, LLC | 54640 | NAEA Lakewood LLC | NJ | Ocean | GEN2 | Natural Gas Fired Combined Cycle | CT | LCLP | W | X | N |  |  | 77.9 | 0.8 | 83.6 | 83.9 | 62.1 | N |  |  | SB | Y | 4 | 1994 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: NG; WDS: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1994 | natural gas combined cycle | TRUE | 60789 | Essential Power Operating Company, LLC | 54640 | NAEA Lakewood LLC | NJ | Ocean | GEN3 | Natural Gas Fired Combined Cycle | CA | LCLP | W | N | X |  |  | 81 | 0.8 | 79.7 | 82.2 | 79.7 | N |  |  | SB | Y | 4 | 1994 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: NG; WDS: DFO |  |  |  | N | N |  | 12H | [23 empty] | Y | N | Y
Vintage1989 | petroleum | TRUE | 9989 | Kalaeloa Partners LP | 54646 | Kalaeloa Cogen Plant | HI | Honolulu | CT1 | Petroleum Liquids | CT | CC1 | J | X | N |  |  | 119.2 | 0.85 | 85 | 85 | 40 | N |  |  | OP | X | 10 | 1989 |  |  | Y | IPP CHP | 3 | T: T; BLQ: RFO; WDS: DFO; NG: DFO |  |  |  | N | N |  | 1H |  |  |  |  | N | [18 empty] | Y | N | N
Vintage1991 | petroleum | TRUE | 9989 | Kalaeloa Partners LP | 54646 | Kalaeloa Cogen Plant | HI | Honolulu | CT2 | Petroleum Liquids | CT | CC1 | J | X | N |  |  | 119.2 | 0.85 | 85 | 85 | 40 | N |  |  | OP | X | 1 | 1991 |  |  | Y | IPP CHP | 3 | T: T; BLQ: RFO; WDS: DFO; NG: DFO |  |  |  | N | N |  | 1H | [23 empty] | Y | N | N
Vintage1991 | petroleum | TRUE | 9989 | Kalaeloa Partners LP | 54646 | Kalaeloa Cogen Plant | HI | Honolulu | ST | Petroleum Liquids | CA | CC1 | J | N | X |  |  | 61 | 0.85 | 50 | 50 | 10 | N |  |  | OP | X | 3 | 1991 |  |  | Y | IPP CHP | 3 | T: B; BLQ: DFO |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1986 | onshore wind | TRUE | 2770 | Terra-Gen Operating Co-Wind | 54647 | TPC Windfarms LLC | CA | Kern | EXIS | Onshore Wind Turbine | WT |  | W | X | X |  |  | 28.7 |  | 28.7 | 28.7 | 5.2 | N |  |  | OP | X | 12 | 1986 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WND |  |  |  | N | N | 100
Vintage1989 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 54654 | Kekawaka Power House | CA | Trinity | KEK1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 4.9 | 0.9 | 4.9 | 4.9 | 0.7 | N |  |  | OA | X | 12 | 1989 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT | [5 empty] | 0 | 10M
Vintage1990 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 54655 | Schoolfield Dam | VA | Pittsylvania | SCH1 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.5 | 0.9 | 1.5 | 1.5 | 0.2 | N |  |  | OP | X | 10 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N |  |  | 10M
Vintage1990 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 54655 | Schoolfield Dam | VA | Pittsylvania | SCH2 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.5 | 0.9 | 1.5 | 1.5 | 0.2 | N |  |  | OP | X | 11 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT | [6 empty] | 10M
Vintage1990 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 54655 | Schoolfield Dam | VA | Pittsylvania | SCH3 | Conventional Hydroelectric | HY |  | W | X | X |  |  | 1.5 | 0.9 | 1.5 | 1.5 | 0.2 | N |  |  | OP | X | 12 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT | [6 empty] | 10M
Vintage1951 | biomass | TRUE | 9210 | International Paper Co-Riegelwood | 54656 | International Paper Riegelwood Mill | NC | Columbus | NO 1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 7.5 | 0.8 | 7.8 | 8.3 | 4 | N |  |  | OP | X | 12 | 1951 | 6 | 2022 | Y | Industrial CHP | 7 | T | BLQ | NG | RFO | SLW | WDS |  | RFO | NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage1976 | biomass | TRUE | 9210 | International Paper Co-Riegelwood | 54656 | International Paper Riegelwood Mill | NC | Columbus | NO3 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 44 | 0.8 | 44.5 | 40.7 | 17.3 | N |  |  | OP | X | 12 | 1976 |  |  | Y | Industrial CHP | 7 | T | BLQ | NG | RFO | SLW | WDS |  | RFO | NG |  |  | N | N |  | 12H | [23 empty] | Y | Y | Y
Vintage2002 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54661 | Pheasant Run Landfill Gas Recovery | WI | Kenosha | GE10 | Landfill Gas | IC |  | S | X | X | WE | WE | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 7 | 2002 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2002 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54661 | Pheasant Run Landfill Gas Recovery | WI | Kenosha | GE11 | Landfill Gas | IC |  | S | X | X | WE | WE | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 7 | 2002 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1992 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54661 | Pheasant Run Landfill Gas Recovery | WI | Kenosha | GEN1 | Landfill Gas | IC |  | S | X | X | WE | WE | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 2 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1992 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54661 | Pheasant Run Landfill Gas Recovery | WI | Kenosha | GEN2 | Landfill Gas | IC |  | S | X | X | WE | WE | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 2 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1996 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54661 | Pheasant Run Landfill Gas Recovery | WI | Kenosha | GEN3 | Landfill Gas | IC |  | S | X | X | WE | WE | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 2 | 1996 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2000 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54661 | Pheasant Run Landfill Gas Recovery | WI | Kenosha | GEN4 | Landfill Gas | IC |  | S | X | X | WE | WE | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 2 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2000 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54661 | Pheasant Run Landfill Gas Recovery | WI | Kenosha | GEN5 | Landfill Gas | IC |  | S | X | X | WE | WE | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 2 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2000 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54661 | Pheasant Run Landfill Gas Recovery | WI | Kenosha | GEN6 | Landfill Gas | IC |  | S | X | X | WE | WE | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 2 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2000 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54661 | Pheasant Run Landfill Gas Recovery | WI | Kenosha | GEN7 | Landfill Gas | IC |  | S | X | X | WE | WE | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 2 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2002 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54661 | Pheasant Run Landfill Gas Recovery | WI | Kenosha | GEN8 | Landfill Gas | IC |  | S | X | X | WE | WE | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 7 | 2002 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage2002 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54661 | Pheasant Run Landfill Gas Recovery | WI | Kenosha | GEN9 | Landfill Gas | IC |  | S | X | X | WE | WE | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 7 | 2002 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N | 0 | 1H | [23 empty] | N | N | N
Vintage1992 | biomass | TRUE | 54843 | WM Illinois Renewable Energy LLC | 54662 | Woodland Landfill Gas Recovery | IL | Kane | GEN1 | Landfill Gas | IC |  | S | X | X | Zonal | Zonal | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 5 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1992 | biomass | TRUE | 54843 | WM Illinois Renewable Energy LLC | 54662 | Woodland Landfill Gas Recovery | IL | Kane | GEN2 | Landfill Gas | IC |  | S | X | X | Zonal | Zonal | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 5 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage2010 | biomass | TRUE | 54843 | WM Illinois Renewable Energy LLC | 54662 | Woodland Landfill Gas Recovery | IL | Kane | GEN3 | Landfill Gas | IC |  | S | X | X | Zonal | Zonal | 1.6 | 0.98 | 1.6 | 1.6 | 0.8 | N |  |  | OP | X | 5 | 2010 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage2010 | biomass | TRUE | 54843 | WM Illinois Renewable Energy LLC | 54662 | Woodland Landfill Gas Recovery | IL | Kane | GEN4 | Landfill Gas | IC |  | S | X | X |  |  | 1.6 | 0.98 | 1.6 | 1.6 | 0.8 | N |  |  | OP | X | 5 | 2010 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1992 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54663 | Turnkey Landfill Gas Recovery | NH | Strafford | GEN1 | Landfill Gas | IC |  | S | X | X | SESD # 496 | SESD # 496 | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 2 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1992 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54663 | Turnkey Landfill Gas Recovery | NH | Strafford | GEN2 | Landfill Gas | IC |  | S | X | X | SESD # 496 | SESD # 496 | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 2 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1992 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54663 | Turnkey Landfill Gas Recovery | NH | Strafford | GEN3 | Landfill Gas | IC |  | S | X | X | SESD # 496 | SESD # 496 | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 2 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1993 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54663 | Turnkey Landfill Gas Recovery | NH | Strafford | GEN4 | Landfill Gas | IC |  | S | X | X | SESD # 496 | SESD # 496 | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 9 | 1993 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1997 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54663 | Turnkey Landfill Gas Recovery | NH | Strafford | GEN5 | Landfill Gas | GT |  | S | X | X | SESD # 496 | SESD # 496 | 3 | 0.98 | 2.9 | 3.3 | 1 | N |  |  | OP | X | 12 | 1997 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1997 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54663 | Turnkey Landfill Gas Recovery | NH | Strafford | GEN6 | Landfill Gas | GT |  | S | X | X | SESD # 496 | SESD # 496 | 3 | 0.98 | 2.9 | 3.3 | 1 | N |  |  | OP | X | 12 | 1997 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1992 | geothermal | TRUE | 18031 | Steamboat Development Corp | 54665 | Steamboat II | NV | Washoe | T201 | Geothermal | BT |  | S | X | X |  |  | 9.1 | 0.8 | 5.4 | 8.1 | 5.4 | N |  |  | OP | X | 8 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: GEO |  |  |  | N |  |  | OVER | [23 empty] | N
Vintage1992 | geothermal | TRUE | 18031 | Steamboat Development Corp | 54665 | Steamboat II | NV | Washoe | T202 | Geothermal | BT |  | S | X | X |  |  | 9.1 | 0.8 | 5.4 | 8.1 | 5.4 | N |  |  | OP | X | 8 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: GEO |  |  |  | N |  |  | OVER | [23 empty] | N
Vintage1992 | geothermal | TRUE | 18031 | Steamboat Development Corp | 54666 | Steamboat III | NV | Washoe | T301 | Geothermal | BT |  | S | X | X |  |  | 9.1 | 0.8 | 5.4 | 8.1 | 5.4 | N |  |  | OP | X | 10 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: GEO |  |  |  | N |  |  | OVER | [23 empty] | N
Vintage1992 | geothermal | TRUE | 18031 | Steamboat Development Corp | 54666 | Steamboat III | NV | Washoe | T302 | Geothermal | BT |  | S | X | X |  |  | 9.1 | 0.8 | 5.4 | 8.1 | 5.4 | N |  |  | OP | X | 10 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: GEO |  |  |  | N |  |  | OVER | [23 empty] | N
Vintage1959 | natural gas combined cycle | FALSE | 3670 | FreePort-McMoRan-Corp-Chino Mines | 54667 | Chino Mines | NM | Grant | 7 | Natural Gas Fired Combined Cycle | CA | CTG9 | S | Y | X |  |  | 16.5 | 0.85 | 15.4 | 15.5 | 2 | N |  |  | SB | Y | 10 | 1959 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N | 0 | OVER | [23 empty] | N | N | N | bar: T to BLQ
Vintage2001 | natural gas combined cycle | FALSE | 3670 | FreePort-McMoRan-Corp-Chino Mines | 54667 | Chino Mines | NM | Grant | 9 | Natural Gas Fired Combined Cycle | CT | CTG9 | S | X | Y |  |  | 37.5 | 0.9 | 35 | 40 | 4.5 | N |  |  | SB | Y | 7 | 2001 |  |  | N | Industrial Non-CHP | 6 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1993 | hydro | TRUE | 11782 | Marysville Hydro Partners | 54668 | Falls River Hydro | ID | Fremont | 1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.5 | 0.9 | 4.5 | 4.5 | 1 | N |  |  | OP | X | 8 | 1993 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1993 | hydro | TRUE | 11782 | Marysville Hydro Partners | 54668 | Falls River Hydro | ID | Fremont | 2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 4.5 | 0.9 | 4.5 | 4.5 | 1 | N |  |  | OP | X | 8 | 1993 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N |  |  | 1H | [23 empty] | N
Vintage1988 | hydro | TRUE | 6527 | Ford Hydro Ltd Partnership | 54674 | Ford Hydro LP | ID | Clearwater | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 1 | 0.2 | 0.5 | 0.1 | N |  |  | OP | X | 3 | 1988 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1988 | hydro | TRUE | 6527 | Ford Hydro Ltd Partnership | 54674 | Ford Hydro LP | ID | Clearwater | GEN2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 1 | 0.2 | 0.5 | 0.1 | N |  |  | OP | X | 3 | 1988 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1988 | hydro | TRUE | 6527 | Ford Hydro Ltd Partnership | 54674 | Ford Hydro LP | ID | Clearwater | GEN3 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.4 | 1 | 0.2 | 0.5 | 0.1 | N |  |  | OP | X | 3 | 1988 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage2011 | petroleum | FALSE | 17664 | Spartanburg Commissioners PW | 54675 | Spartanburg Water System | SC | Spartanburg | DI2 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.5 | N |  |  | OP | X | 12 | 2011 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1926 | hydro | FALSE | 17664 | Spartanburg Commissioners PW | 54675 | Spartanburg Water System | SC | Spartanburg | HG1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.4 | N |  |  | SB | Y | 1 | 1926 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1926 | hydro | FALSE | 17664 | Spartanburg Commissioners PW | 54675 | Spartanburg Water System | SC | Spartanburg | HG2 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.4 | N |  |  | SB | Y | 1 | 1926 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 1H | [23 empty] | N
Vintage1994 | natural gas combined cycle | TRUE | 5374 | Dow Chemical Company-Oyster Creek VIII | 54676 | Oyster Creek Unit VIII | TX | Brazoria | G81 | Natural Gas Fired Combined Cycle | CT | CC1 | J | X | N | N/A | N/A | 99 | 1 | 73 | 90 | 70 | N |  |  | OP | X | 10 | 1994 |  |  | Y | IPP CHP | 3 | T: T; BLQ: NG; WDS: OG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1994 | natural gas combined cycle | TRUE | 5374 | Dow Chemical Company-Oyster Creek VIII | 54676 | Oyster Creek Unit VIII | TX | Brazoria | G82 | Natural Gas Fired Combined Cycle | CT | CC1 | J | X | N | N/A | N/A | 99 | 1 | 73 | 90 | 70 | N |  |  | OP | X | 10 | 1994 |  |  | Y | IPP CHP | 3 | T: T; BLQ: NG; WDS: OG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1994 | natural gas combined cycle | TRUE | 5374 | Dow Chemical Company-Oyster Creek VIII | 54676 | Oyster Creek Unit VIII | TX | Brazoria | G83 | Natural Gas Fired Combined Cycle | CT | CC1 | J | X | N | N/A | N/A | 99 | 1 | 73 | 90 | 70 | N |  |  | OP | X | 10 | 1994 |  |  | Y | IPP CHP | 3 | T: T; BLQ: NG; WDS: OG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1994 | natural gas combined cycle | TRUE | 5374 | Dow Chemical Company-Oyster Creek VIII | 54676 | Oyster Creek Unit VIII | TX | Brazoria | G84 | Natural Gas Fired Combined Cycle | CA | CC1 | J | Y | X | N/A | N/A | 200.9 | 1 | 160 | 160 | 50 | N |  |  | OP | X | 10 | 1994 |  |  | Y | IPP CHP | 3 | T: T; BLQ: NG; WDS: OG |  |  |  | N | N |  | 1H | [23 empty] | N | N | N
Vintage1951 | other | FALSE | 4660 | CII Carbon LLC | 54677 | CII Carbon LLC | LA | St Bernard | TG-2 | All Other | ST |  | S | X | X |  |  | 23 | 0.85 | 23 | 23 | 3 | N |  |  | OP | X | 1 | 1951 |  |  | Y | Industrial CHP | 7 | T: B; BLQ: WH; NG: NG |  |  |  | N | N |  | OVER | N |  |  | N | [19 empty] | N | N | N
Vintage1951 | other | FALSE | 4660 | CII Carbon LLC | 54677 | CII Carbon LLC | LA | St Bernard | TG-3 | All Other | ST |  | S | X | X |  |  | 23 | 0.85 | 23 | 23 | 3 | N |  |  | SB | Y | 1 | 1951 |  |  | Y | Industrial CHP | 7 | T: B; BLQ: WH; NG: NG |  |  |  | N | N |  | OVER | N | [22 empty] | N | N | N
Vintage1990 | hydro | TRUE | 6371 | First National Bank-Commerce | 54678 | Sidney A Murray Jr Hydroelectric | LA | Concordia | 01 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 24 | 0.95 | 24 | 24 | 3 | N |  |  | OP | X | 7 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1990 | hydro | TRUE | 6371 | First National Bank-Commerce | 54678 | Sidney A Murray Jr Hydroelectric | LA | Concordia | 02 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 24 | 0.95 | 24 | 24 | 3 | N |  |  | OP | X | 8 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1990 | hydro | TRUE | 6371 | First National Bank-Commerce | 54678 | Sidney A Murray Jr Hydroelectric | LA | Concordia | 03 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 24 | 0.95 | 24 | 24 | 3 | N |  |  | OP | X | 6 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1990 | hydro | TRUE | 6371 | First National Bank-Commerce | 54678 | Sidney A Murray Jr Hydroelectric | LA | Concordia | 04 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 24 | 0.95 | 24 | 24 | 3 | N |  |  | OP | X | 5 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1990 | hydro | TRUE | 6371 | First National Bank-Commerce | 54678 | Sidney A Murray Jr Hydroelectric | LA | Concordia | 05 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 24 | 0.95 | 24 | 24 | 3 | N |  |  | OP | X | 6 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1990 | hydro | TRUE | 6371 | First National Bank-Commerce | 54678 | Sidney A Murray Jr Hydroelectric | LA | Concordia | 06 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 24 | 0.95 | 24 | 24 | 3 | N |  |  | OP | X | 5 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1990 | hydro | TRUE | 6371 | First National Bank-Commerce | 54678 | Sidney A Murray Jr Hydroelectric | LA | Concordia | 07 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 24 | 0.95 | 24 | 24 | 3 | N |  |  | OP | X | 6 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1990 | hydro | TRUE | 6371 | First National Bank-Commerce | 54678 | Sidney A Murray Jr Hydroelectric | LA | Concordia | 08 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 24 | 0.95 | 24 | 24 | 3 | N |  |  | OP | X | 7 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage2004 | hydro | TRUE | 1994 | Boulder City of | 54679 | Boulder City Lakewood Hydro | CO | Boulder | 0001 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3.5 | 0.9 | 3.5 | 3.5 | 0.3 | N |  |  | OP | X | 2 | 2004 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N |  | 10M
Vintage1987 | hydro | TRUE | 1994 | Boulder City of | 54680 | Boulder City Betasso Hydro Plant | CO | Boulder | 0001 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 3 | 0.9 | 3 | 3 | 0.3 | N |  |  | OP | X | 12 | 1987 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N |  | 10M
Vintage1987 | onshore wind | TRUE | 2770 | Terra-Gen Operating Co-Wind | 54686 | Difwind Farms Ltd VI | CA | Kern | EXIS | Onshore Wind Turbine | WT |  | S | X | X |  |  | 27.1 |  | 25.3 | 25.3 | 0 | N |  |  | OP | X | 1 | 1987 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WND |  |  |  | N | N | 251
Vintage1981 | hydro | TRUE | 42890 | Woonsocket City of | 54688 | Thundermist Hydro | RI | Providence | HYD1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 1.2 | 1 | 1.1 | 1.1 | 0.3 | N |  |  | OS | X | 6 | 1981 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT | [6 empty] | 10M | [23 empty] | N
Vintage1985 | geothermal | TRUE | 49748 | ORCAL Geothermal, Inc | 54689 | Heber Geothermal | CA | Imperial | 1 | Geothermal | ST |  | W | X | X |  |  | 52 | 0.8 | 34.3 | 52 | 34.3 | N |  |  | OP | X | 6 | 1985 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: GEO; NG: GEO |  |  |  | N |  |  | OVER | [23 empty] | N
Vintage2006 | geothermal | TRUE | 49748 | ORCAL Geothermal, Inc | 54689 | Heber Geothermal | CA | Imperial | 2 | Geothermal | BT |  | W | X | X |  |  | 7 | 0.8 | 4.5 | 7 | 4.5 | N |  |  | OP | X | 6 | 2006 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: GEO | [6 empty] | OVER | [23 empty] | N
Vintage2006 | geothermal | TRUE | 49748 | ORCAL Geothermal, Inc | 54689 | Heber Geothermal | CA | Imperial | 3 | Geothermal | BT |  | W | X | X |  |  | 3.5 | 0.8 | 3 | 3.5 | 3 | N |  |  | OP | X | 6 | 2006 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: GEO | [6 empty] | OVER | [23 empty] | N
Vintage2018 | geothermal | TRUE | 49748 | ORCAL Geothermal, Inc | 54689 | Heber Geothermal | CA | Imperial | 4 | Geothermal | BT |  | W | X | X |  |  | 19 | 0.8 | 12.5 | 19 | 12.5 | N |  |  | OP | X | 1 | 2018 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: GEO | [6 empty] | OVER
Vintage1948 | natural gas steam turbine | FALSE | 24206 | Amalgamated Sugar Co-Nampa | 54690 | Amalgamated Sugar LLC Nampa | ID | Canyon | 2250 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 2.2 | 0.9 | 2.2 | 2.2 | 1 | N |  |  | OP | X | 10 | 1948 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: NG; WDS: BIT; NG: NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | N | [17 empty] | N |  | N
Vintage1968 | natural gas steam turbine | FALSE | 24206 | Amalgamated Sugar Co-Nampa | 54690 | Amalgamated Sugar LLC Nampa | ID | Canyon | 6500 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 6 | 0.9 | 6 | 6 | 3 | N |  |  | OP | X | 10 | 1968 |  |  | Y | Industrial CHP | 7 | T: T; BLQ: NG; WDS: BIT; NG: NG |  |  |  | N | N |  | 12H |  | Y |  |  | Y | N | [17 empty] | N |  | N
Vintage1979 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 54691 | Lower Beaver Falls Project | NY | Lewis | 2G | Conventional Hydroelectric | HY |  | W | X | X | 23633 | 23633 | 0.5 | 0.95 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 12 | 1979 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT | [6 empty] | 10M
Vintage1979 | hydro | TRUE | 57280 | Eagle Creek Renewable Energy, LLC | 54691 | Lower Beaver Falls Project | NY | Lewis | 3G | Conventional Hydroelectric | HY |  | W | X | X | 23633 | 23633 | 0.5 | 0.95 | 0.5 | 0.5 | 0.1 | N |  |  | OP | X | 12 | 1979 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT | [6 empty] | 10M
Vintage1994 | natural gas combined cycle | TRUE | 49919 | Falcon Power Operating Company | 54694 | Yuma Cogeneration Associates | AZ | Yuma | GEN1 | Natural Gas Fired Combined Cycle | CT | YUCG | S | X | N | NGILA_5 N008 | NGILA 5 N008 | 44.1 | 0.9 | 35.1 | 37.4 | 32 | N |  |  | OP | X | 3 | 1994 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: T to BLQ
Vintage1994 | natural gas combined cycle | TRUE | 49919 | Falcon Power Operating Company | 54694 | Yuma Cogeneration Associates | AZ | Yuma | GEN2 | Natural Gas Fired Combined Cycle | CA | YUCG | S | Y | X | NGILA 5 N008 | NGILA 5 N008 | 18.5 | 0.9 | 17.1 | 16.5 | 5 | N |  |  | OP | X | 3 | 1994 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: T to BLQ
Vintage1998 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54700 | Metro Methane Recovery Facility | IA | Polk | GEN1 | Landfill Gas | IC |  | S | X | X | Zonal | Zonal | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 1 | 1998 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage2014 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54700 | Metro Methane Recovery Facility | IA | Polk | GEN10 | Landfill Gas | IC |  | S | X | X | Zonal | Zonal | 1.6 | 0.98 | 1.6 | 1.6 | 0.8 | N |  |  | OP | X | 3 | 2014 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage2014 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54700 | Metro Methane Recovery Facility | IA | Polk | GEN11 | Landfill Gas | IC |  | S | X | X | Zonal | Zonal | 1.6 | 0.98 | 1.6 | 1.6 | 0.8 | N |  |  | OP | X | 3 | 2014 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N | N
Vintage2014 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54700 | Metro Methane Recovery Facility | IA | Polk | GEN12 | Landfill Gas | IC |  | S | X | X | Zonal | Zonal | 1.6 | 0.98 | 1.6 | 1.6 | 0.8 | N |  |  | OP | X | 3 | 2014 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1998 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54700 | Metro Methane Recovery Facility | IA | Polk | GEN2 | Landfill Gas | IC |  | S | X | X | Zonal | Zonal | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 1 | 1998 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1998 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54700 | Metro Methane Recovery Facility | IA | Polk | GEN3 | Landfill Gas | IC |  | S | X | X | Zonal | Zonal | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 1 | 1998 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1998 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54700 | Metro Methane Recovery Facility | IA | Polk | GEN4 | Landfill Gas | IC |  | S | X | X | Zonal | Zonal | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 1 | 1998 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1998 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54700 | Metro Methane Recovery Facility | IA | Polk | GEN5 | Landfill Gas | IC |  | S | X | X | Zonal | Zonal | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 1 | 1998 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1998 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54700 | Metro Methane Recovery Facility | IA | Polk | GEN6 | Landfill Gas | IC |  | S | X | X | Zonal | Zonal | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 1 | 1998 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1998 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54700 | Metro Methane Recovery Facility | IA | Polk | GEN7 | Landfill Gas | IC |  | S | X | X | Zonal | Zonal | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 1 | 1998 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1998 | biomass | TRUE | 54842 | WM Renewable Energy LLC | 54700 | Metro Methane Recovery Facility | IA | Polk | GEN8 | Landfill Gas | IC |  | S | X | X | Zonal | Zonal | 0.8 | 0.98 | 0.8 | 0.8 | 0.5 | N |  |  | OP | X | 1 | 1998 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N |  |  | 1H | [23 empty] | N | N | N
Vintage1993 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54710 | Alliant SBD 9205 A Y McDonald | IA | Dubuque | 0001 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.1 | N |  |  | SB | Y | 7 | 1993 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1990 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54710 | Alliant SBD 9205 A Y McDonald | IA | Dubuque | 0002 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.1 | N |  |  | SB | Y | 3 | 1990 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2016 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54710 | Alliant SBD 9205 A Y McDonald | IA | Dubuque | 0003 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0.1 | N |  |  | SB | N | 5 | 2016 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2014 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54712 | Alliant SBD 9201 Norplex | IA | Allamakee | 0002 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.1 | N |  |  | SB | N | 7 | 2014 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1988 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54712 | Alliant SBD 9201 Norplex | IA | Allamakee | 0044 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 1.1 | N |  |  | SB | N | 12 | 1988 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1992 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54715 | Alliant SBD 9107 JBS USA | IA | Marshall | 2665 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.1 | N |  |  | SB | Y | 8 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1992 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54715 | Alliant SBD 9107 JBS USA | IA | Marshall | 2688 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.1 | N |  |  | SB | Y | 8 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1992 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54715 | Alliant SBD 9107 JBS USA | IA | Marshall | 2689 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.1 | N |  |  | SB | Y | 8 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1994 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54715 | Alliant SBD 9107 JBS USA | IA | Marshall | 4644 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.1 | N |  |  | SB | Y | 8 | 1994 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1996 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54715 | Alliant SBD 9107 JBS USA | IA | Marshall | 4658 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.1 | N |  |  | SB | Y | 6 | 1996 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1998 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54715 | Alliant SBD 9107 JBS USA | IA | Marshall | 4659 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.1 | N |  |  | SB | Y | 4 | 1998 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2000 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54715 | Alliant SBD 9107 JBS USA | IA | Marshall | 4660 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.1 | N |  |  | SB | Y | 6 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1986 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54716 | Alliant SBD 8602 Marion Sub | IA | Linn | 1536 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.1 | N |  |  | SB | Y | 8 | 1986 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1986 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54716 | Alliant SBD 8602 Marion Sub | IA | Linn | 2734 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.1 | N |  |  | SB | Y | 8 | 1986 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1986 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54716 | Alliant SBD 8602 Marion Sub | IA | Linn | 2741 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.1 | N |  |  | SB | Y | 8 | 1986 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1986 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54716 | Alliant SBD 8602 Marion Sub | IA | Linn | 2785 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.1 | N |  |  | SB | Y | 8 | 1986 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1992 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54717 | Alliant SBD 9106 Rockwell CR | IA | Linn | 2671 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.1 | N |  |  | SB | Y | 6 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1992 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54717 | Alliant SBD 9106 Rockwell CR | IA | Linn | 2672 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.1 | N |  |  | SB | Y | 6 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1992 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54717 | Alliant SBD 9106 Rockwell CR | IA | Linn | 2675 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.1 | N |  |  | SB | Y | 6 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1992 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54717 | Alliant SBD 9106 Rockwell CR | IA | Linn | 2678 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.1 | N |  |  | SB | Y | 6 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1992 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54717 | Alliant SBD 9106 Rockwell CR | IA | Linn | 2679 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.1 | N |  |  | SB | Y | 6 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1992 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54717 | Alliant SBD 9106 Rockwell CR | IA | Linn | 2682 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.1 | N |  |  | SB | Y | 6 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1992 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54717 | Alliant SBD 9106 Rockwell CR | IA | Linn | 2683 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.1 | N |  |  | SB | Y | 6 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1992 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54717 | Alliant SBD 9106 Rockwell CR | IA | Linn | 2684 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.1 | N |  |  | SB | Y | 6 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1992 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54717 | Alliant SBD 9106 Rockwell CR | IA | Linn | 2685 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.1 | N |  |  | SB | Y | 6 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1992 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54717 | Alliant SBD 9106 Rockwell CR | IA | Linn | 2690 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.1 | N |  |  | SB | Y | 6 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1995 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54718 | Alliant SBD 9206 Donaldson | IA | Howard | 4632 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.6 | 0.8 | 1.6 | 1.6 | 0.1 | N |  |  | SB | Y | 11 | 1995 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1996 | petroleum | TRUE | 56189 | American Profol Incorporated | 54719 | Alliant SBD 9203 Profol | IA | Linn | 6916 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.1 | N |  |  | SB | N | 9 | 1996 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2001 | petroleum | TRUE | 56189 | American Profol Incorporated | 54719 | Alliant SBD 9203 Profol | IA | Linn | 6917 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.1 | N |  |  | SB | N | 2 | 2001 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2012 | petroleum | TRUE | 56189 | American Profol Incorporated | 54719 | Alliant SBD 9203 Profol | IA | Linn | 6918 | Petroleum Liquids | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.1 | N |  |  | OP | X | 8 | 2012 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N
Vintage1986 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54720 | Alliant SBD 8601 Quad Graphics | IA | Iowa | 2736 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.1 | N |  |  | SB | Y | 8 | 1986 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1991 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54720 | Alliant SBD 8601 Quad Graphics | IA | Iowa | 3489 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0.1 | N |  |  | SB | Y | 1 | 1991 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1996 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54720 | Alliant SBD 8601 Quad Graphics | IA | Iowa | 7164 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.1 | N |  |  | SB | Y | 5 | 1996 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1982 | hydro | TRUE | 20100 | Warm Springs Power Enterprises | 54721 | Warm Springs Power Enterprises | OR | Jefferson | 0001 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 19.6 | 1 | 18.5 | 18.5 | 1 | N |  |  | OP | X | 6 | 1982 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1993 | biomass | TRUE | 57249 | EPP Renewable Energy | 54723 | I 95 Landfill Phase II | VA | Fairfax | UNT1 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.95 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 3 | 1993 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1993 | biomass | TRUE | 57249 | EPP Renewable Energy | 54723 | I 95 Landfill Phase II | VA | Fairfax | UNT2 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.95 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 3 | 1993 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1993 | biomass | TRUE | 57249 | EPP Renewable Energy | 54723 | I 95 Landfill Phase II | VA | Fairfax | UNT3 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.95 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 3 | 1993 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1993 | biomass | TRUE | 57249 | EPP Renewable Energy | 54723 | I 95 Landfill Phase II | VA | Fairfax | UNT4 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.95 | 0.8 | 0.8 | 0.3 | N |  |  | OP | X | 3 | 1993 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1989 | geothermal | TRUE | 34691 | Ormat Nevada Inc | 54724 | Ormesa II | CA | Imperial | OEC21 | Geothermal | BT |  | S | X | X |  |  | 12 | 0.8 | 8 | 12 | 8 | N |  |  | OP | X | 5 | 1989 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: GEO; NG: GEO |  |  |  | N |  |  | OVER | [23 empty] | N
Vintage2007 | geothermal | TRUE | 34691 | Ormat Nevada Inc | 54724 | Ormesa II | CA | Imperial | OEC22 | Geothermal | BT |  | S | X | X |  |  | 12 | 0.8 | 8 | 12 | 8 | N |  |  | OP | X | 4 | 2007 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: GEO; NG: GEO |  |  |  | N |  |  | OVER | [23 empty] | N
Vintage1993 | hydro | TRUE | 16070 | Rio Blanco Water Conserv Dist | 54729 | Taylor Draw Hydroelectric Facility | CO | Rio Blanco | COX1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.3 | 0.8 | 2 | 2 | 0.2 | N |  |  | OP | X | 4 | 1993 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N |  | 12H
Vintage2010 | petroleum | FALSE | 8453 | Hendricks Regional Health | 54731 | Hendricks Regional Health | IN | Hendricks | GE06 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0 | N |  |  | SB | Y | 5 | 2010 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1992 | petroleum | FALSE | 8453 | Hendricks Regional Health | 54731 | Hendricks Regional Health | IN | Hendricks | GEO1 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0 | N |  |  | SB | Y | 9 | 1992 | 3 | 2023 | N | Commercial Non-CHP | 4 | T: X; BLQ: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1992 | petroleum | FALSE | 8453 | Hendricks Regional Health | 54731 | Hendricks Regional Health | IN | Hendricks | GEO2 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.5 | 0.8 | 0.5 | 0.5 | 0 | N |  |  | SB | Y | 9 | 1992 | 3 | 2023 | N | Commercial Non-CHP | 4 | T: X; BLQ: DFO |  |  |  | N |  |  | 10M | [23 empty] | N
Vintage1992 | petroleum | FALSE | 8453 | Hendricks Regional Health | 54731 | Hendricks Regional Health | IN | Hendricks | GEO3 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.3 | 0.8 | 0.3 | 0.3 | 0 | N |  |  | SB | Y | 9 | 1992 | 3 | 2023 | N | Commercial Non-CHP | 4 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2004 | petroleum | FALSE | 8453 | Hendricks Regional Health | 54731 | Hendricks Regional Health | IN | Hendricks | GEO4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0 | N |  |  | SB | Y | 3 | 2004 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2004 | petroleum | FALSE | 8453 | Hendricks Regional Health | 54731 | Hendricks Regional Health | IN | Hendricks | GEO5 | Petroleum Liquids | IC |  | S | X | X |  |  | 1 | 0.8 | 1 | 1 | 0 | N |  |  | SB | Y | 3 | 2004 |  |  | N | Commercial Non-CHP | 4 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1967 | petroleum | FALSE | 14989 | Freeport McMoRan Inc | 54734 | Freeport McMoRan | NM | Grant | 1 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.8 | 2.9 | 2.9 | 0.5 | N |  |  | SB | Y | 12 | 1967 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO; WDS: NG |  |  |  |  | N |  | 1H | [23 empty] | Y | N | Y
Vintage1971 | petroleum | FALSE | 14989 | Freeport McMoRan Inc | 54734 | Freeport McMoRan | NM | Grant | 11 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.8 | 2.9 | 2.9 | 0.5 | N |  |  | SB | Y | 2 | 1971 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO; WDS: NG |  |  |  |  | N |  | 1H | [23 empty] | Y | N | Y
Vintage1972 | petroleum | FALSE | 14989 | Freeport McMoRan Inc | 54734 | Freeport McMoRan | NM | Grant | 12 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.8 | 2.9 | 2.9 | 0.5 | N |  |  | SB | Y | 7 | 1972 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO; WDS: NG |  |  |  |  | N |  | 1H | [23 empty] | Y | N | Y
Vintage1972 | petroleum | FALSE | 14989 | Freeport McMoRan Inc | 54734 | Freeport McMoRan | NM | Grant | 13 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.8 | 2.9 | 2.9 | 0.5 | N |  |  | SB | Y | 7 | 1972 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO; WDS: NG |  |  |  |  | N |  | 1H | [23 empty] | Y | N | Y
Vintage1972 | petroleum | FALSE | 14989 | Freeport McMoRan Inc | 54734 | Freeport McMoRan | NM | Grant | 14 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.8 | 2.9 | 2.9 | 0.5 | N |  |  | SB | Y | 7 | 1972 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO; WDS: NG |  |  |  |  | N |  | 1H | [23 empty] | Y | N | Y
Vintage1972 | petroleum | FALSE | 14989 | Freeport McMoRan Inc | 54734 | Freeport McMoRan | NM | Grant | 15 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.1 | 0.8 | 2.9 | 2.9 | 0.5 | N |  |  | SB | Y | 8 | 1972 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO; WDS: NG |  |  |  |  | N |  | 1H | [23 empty] | Y | N | Y
Vintage1967 | petroleum | FALSE | 14989 | Freeport McMoRan Inc | 54734 | Freeport McMoRan | NM | Grant | 3 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.1 | 0.8 | 2.9 | 2.9 | 0.5 | N |  |  | SB | Y | 12 | 1967 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO; WDS: NG |  |  |  |  | N |  | 1H | [23 empty] | Y | N | Y
Vintage1967 | petroleum | FALSE | 14989 | Freeport McMoRan Inc | 54734 | Freeport McMoRan | NM | Grant | 4 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.1 | 0.8 | 2.9 | 2.9 | 0.5 | N |  |  | SB | Y | 12 | 1967 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO; WDS: NG |  |  |  |  | N |  | 1H | [23 empty] | Y | N | Y
Vintage1967 | petroleum | FALSE | 14989 | Freeport McMoRan Inc | 54734 | Freeport McMoRan | NM | Grant | 7 | Petroleum Liquids | IC |  | S | X | X |  |  | 3.1 | 0.8 | 2.9 | 2.9 | 0.5 | N |  |  | SB | Y | 12 | 1967 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1967 | petroleum | FALSE | 14989 | Freeport McMoRan Inc | 54734 | Freeport McMoRan | NM | Grant | 8 | Petroleum Liquids | IC |  | S | X | X |  |  | 3 | 0.8 | 2.9 | 2.9 | 0.5 | N |  |  | SB | Y | 12 | 1967 |  |  | N | Industrial Non-CHP | 6 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | N | Y
Vintage1993 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54735 | Alliant SBD 9301 Prairie Farms | IA | Dubuque | 0079 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.8 | 0.8 | 1.8 | 1.8 | 0.1 | N |  |  | SB | N | 7 | 1993 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1998 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54735 | Alliant SBD 9301 Prairie Farms | IA | Dubuque | 0080 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.1 | 0.8 | 1.1 | 1.1 | 0.1 | N |  |  | SB | N | 11 | 1998 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage2019 | petroleum | TRUE | 361 | Industrial Energy Applications Inc | 54735 | Alliant SBD 9301 Prairie Farms | IA | Dubuque | 0081 | Petroleum Liquids | IC |  | S | X | X |  |  | 0.6 | 0.8 | 0.6 | 0.6 | 0.1 | N |  |  | SB | N | 6 | 2019 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N | N | N
Vintage1951 | other | FALSE | 19102 | Transcontinental Gas PL Corp | 54744 | District 70 Transco Gas Pipe Line | MS | Walthall | 001 | All Other | ST |  | S | X | X |  |  | 0.8 | 0.8 | 0.7 | 0.8 | 0.2 | N |  |  | OS | X | 6 | 1951 |  |  | N | Commercial Non-CHP | 4 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | N | bar: T to BLQ; NG
Vintage1951 | other | FALSE | 19102 | Transcontinental Gas PL Corp | 54744 | District 70 Transco Gas Pipe Line | MS | Walthall | 002 | All Other | ST |  | S | X | X |  |  | 0.8 | 0.8 | 0.7 | 0.8 | 0.2 | N |  |  | OS | X | 6 | 1951 |  |  | N | Commercial Non-CHP | 4 | [11 empty] | N | N |  | OVER | [23 empty] | N | N | N | bar: T to BLQ; NG
Vintage1994 | municipal solid waste | TRUE | 20541 | Wheelabrator Environmental Systems | 54746 | Wheelabrator Falls | PA | Bucks | WFI1 | Municipal Solid Waste | ST |  | S | X | X | 50485 | 50485 | 53.3 | 0.85 | 43.9 | 43.6 | 0 | N |  |  | OP | X | 5 | 1994 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: MSW; NG: NG |  |  |  | N | N |  | 12H | [23 empty] | N | N | N
Vintage1994 | natural gas peaker | FALSE | 327 | Air Liquide Large Industries U S LP | 54748 | Port Neches Plant | TX | Jefferson | G1 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 38 | 0.85 | 32 | 30.5 | 27 | N |  |  | OP | X | 2 | 1994 |  |  | Y | Industrial CHP | 7 | [11 empty] | N |  |  | 12H | [23 empty] | N | bar: T to BLQ
Vintage1994 | natural gas combined cycle | TRUE | 22269 | Goal Line LP | 54749 | Goal Line LP | CA | San Diego | CTG | Natural Gas Fired Combined Cycle | CT | CC1 | S | X | N | GOALLINE_6_N001 | CAISO SP-15 | 41.2 | 0.9 | 40 | 40 | 35 | N |  |  | OP | X | 8 | 1994 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 1H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1994 | natural gas combined cycle | TRUE | 22269 | Goal Line LP | 54749 | Goal Line LP | CA | San Diego | STG | Natural Gas Fired Combined Cycle | CA | CC1 | S | N | X |  |  | 10.2 | 0.85 | 9.4 | 9.4 | 6 | N |  |  | OP | X | 8 | 1994 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1992 | onshore wind | TRUE | 63235 | Brookfield Renewable Trading and Marketing LP | 54750 | Coram Tehachapi | CA | Kern | VW1 | Onshore Wind Turbine | WT |  | S | X | X |  |  | 6.5 |  | 6.5 | 6.5 | 1 | N |  |  | OP | X | 9 | 1992 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WND |  |  |  | N | N | 29
Vintage1995 | biomass | TRUE | 3836 | CMS Generation Operating LLC | 54751 | Genesee Power Station LP | MI | Genesee | GEN1 | Wood/Wood Waste Biomass | ST |  | J | X | X | cons.genesee & cons.geneseps | MISO | 39.5 | 0.85 | 35 | 35 | 10 | N |  |  | OP | X | 12 | 1995 |  |  | N | IPP Non-CHP | 2 | X | WDS | TDF | NG |  |  |  | NG |  |  |  | N | N |  | 12H | [23 empty] | Y | Y | N
Vintage1968 | biomass | TRUE | 56291 | International Paper Co. | 54752 | International Paper Pine Hill Mill | AL | Wilcox | NO1 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 40 | 0.85 | 40 | 40 | 10 | N |  |  | OP | X | 8 | 1968 |  |  | Y | Industrial CHP | 7 | B | WDS | NG | BIT |  |  |  | NG |  |  |  | N | N | 0 | 12H | N | N | N |  | N | [18 empty] | Y | Y | N
Vintage1982 | biomass | TRUE | 56291 | International Paper Co. | 54752 | International Paper Pine Hill Mill | AL | Wilcox | NO2 | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 37.4 | 0.85 | 34.8 | 35.1 | 10 | N |  |  | OP | X | 11 | 1982 |  |  | Y | Industrial CHP | 7 | T | BLQ | RFO | NG |  |  |  | NG |  |  |  | N | N |  | 12H |  |  |  |  | N | [18 empty] | Y | Y | N
Vintage1984 | hydro | TRUE | 10723 | Lateral 10 Ventures | 54753 | Lateral 10 Ventures | ID | Twin Falls | GEN1 | Conventional Hydroelectric | HY |  | S | X | X |  |  | 2.4 | 0.8 | 2.3 | 2.2 | 0.2 | N |  |  | OP | X | 11 | 1984 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N |  | 1H
Vintage1994 | biomass | TRUE | 55858 | EDL Inc | 54756 | Coopersville | MI | Ottawa | 3-1 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 1 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 6 | 1994 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1994 | biomass | TRUE | 55858 | EDL Inc | 54756 | Coopersville | MI | Ottawa | 3-2 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 1 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 6 | 1994 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1994 | biomass | TRUE | 55858 | EDL Inc | 54756 | Coopersville | MI | Ottawa | 3-3 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 1 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 6 | 1994 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1994 | biomass | TRUE | 55858 | EDL Inc | 54756 | Coopersville | MI | Ottawa | 3-4 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 1 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 6 | 1994 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1994 | biomass | TRUE | 55858 | EDL Inc | 54756 | Coopersville | MI | Ottawa | 3-5 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 1 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 6 | 1994 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1994 | biomass | TRUE | 55858 | EDL Inc | 54756 | Coopersville | MI | Ottawa | 3-6 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 1 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 6 | 1994 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage2006 | biomass | TRUE | 55858 | EDL Inc | 54756 | Coopersville | MI | Ottawa | 3-7 | Landfill Gas | IC |  | S | X | X |  |  | 1.6 | 1 | 1.6 | 1.6 | 0.6 | N |  |  | OP | X | 2 | 2006 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1994 | biomass | TRUE | 55858 | EDL Inc | 54757 | Grand Blanc Generating Station | MI | Genesee | 4-1 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 1 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 7 | 1994 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1994 | biomass | TRUE | 55858 | EDL Inc | 54757 | Grand Blanc Generating Station | MI | Genesee | 4-2 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 1 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 7 | 1994 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage1994 | biomass | TRUE | 55858 | EDL Inc | 54757 | Grand Blanc Generating Station | MI | Genesee | 4-3 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 1 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 7 | 1994 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage2000 | biomass | TRUE | 55858 | EDL Inc | 54757 | Grand Blanc Generating Station | MI | Genesee | 4-4 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 1 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 10 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage2003 | biomass | TRUE | 55858 | EDL Inc | 54757 | Grand Blanc Generating Station | MI | Genesee | 4-5 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 1 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 1 | 2003 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [23 empty] | N
Vintage2012 | biomass | TRUE | 55858 | EDL Inc | 54757 | Grand Blanc Generating Station | MI | Genesee | 4-7 | Landfill Gas | IC |  | S | X | X |  |  | 1.6 | 1 | 1.6 | 1.6 | 1 | N |  |  | OP | X | 8 | 2012 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage2012 | biomass | TRUE | 55858 | EDL Inc | 54757 | Grand Blanc Generating Station | MI | Genesee | 4-8 | Landfill Gas | IC |  | S | X | X |  |  | 1.6 | 1 | 1.6 | 1.6 | 1 | N |  |  | OP | X | 8 | 2012 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage2010 | biomass | TRUE | 55858 | EDL Inc | 54757 | Grand Blanc Generating Station | MI | Genesee | CIB | Landfill Gas | IC |  | S | X | X |  |  | 0.6 | 1 | 0.6 | 0.6 | 0.6 | N |  |  | OP | X | 8 | 2010 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 12H | [23 empty] | N
Vintage1995 | municipal solid waste | TRUE | 20541 | Wheelabrator Environmental Systems | 54758 | Wheelabrator Lisbon | CT | New London | GEN1 | Municipal Solid Waste | ST |  | W | X | X |  |  | 14.6 | 0.85 | 14 | 14 | 2 | N |  |  | OP | X | 10 | 1995 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: MSW; NG: WO |  |  |  | N | N |  | 12H |  |  |  | N | N | [18 empty] | N | N
Vintage1996 | natural gas combined cycle | TRUE | 8503 | Hermiston Generating Co LP | 54761 | Hermiston Generating Plant | OR | Umatilla | GEN1 | Natural Gas Fired Combined Cycle | CA | CC1 | J | N | X |  |  | 106.1 | 0.98 | 80 | 83 | 65 | N |  |  | OP | X | 6 | 1996 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N | 0 | 12H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1996 | natural gas combined cycle | TRUE | 8503 | Hermiston Generating Co LP | 54761 | Hermiston Generating Plant | OR | Umatilla | GEN2 | Natural Gas Fired Combined Cycle | CT | CC1 | J | X | N |  |  | 204.5 | 0.98 | 152 | 160 | 99 | N |  |  | OP | X | 6 | 1996 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1996 | natural gas combined cycle | TRUE | 8503 | Hermiston Generating Co LP | 54761 | Hermiston Generating Plant | OR | Umatilla | GEN3 | Natural Gas Fired Combined Cycle | CA | CC2 | J | N | X |  |  | 106.1 | 0.98 | 80 | 83 | 65 | N |  |  | OP | X | 6 | 1996 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1996 | natural gas combined cycle | TRUE | 8503 | Hermiston Generating Co LP | 54761 | Hermiston Generating Plant | OR | Umatilla | GEN4 | Natural Gas Fired Combined Cycle | CT | CC2 | J | X | N |  |  | 204.5 | 0.98 | 152 | 160 | 99 | N |  |  | OP | X | 6 | 1996 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | N | N | bar: T to BLQ
Vintage1982 | biomass | TRUE | 59976 | WestRock Mill Company, LLC | 54763 | WestRock Demopolis Mill | AL | Marengo | 2TG | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 12.5 | 0.85 | 8.6 | 10.8 | 2 | N |  |  | OP | X | 10 | 1982 |  |  | Y | Industrial CHP | 7 | T | BLQ | WDS | NG | DFO |  |  | NG |  |  |  | N | N |  | 12H | N |  |  |  | N | [18 empty] | N | N | N
Vintage2014 | biomass | TRUE | 59976 | WestRock Mill Company, LLC | 54763 | WestRock Demopolis Mill | AL | Marengo | 4TG | Wood/Wood Waste Biomass | ST |  | S | X | X |  |  | 34.9 | 0.85 | 34.9 | 34.9 | 3 | N |  |  | OP | X | 3 | 2014 |  |  | N | Industrial CHP | 7 | X | BLQ | WDS | NG | DFO |  |  | NG |  |  |  | N | N |  | 12H | N | N |  |  | N | [18 empty] | N | N | N
Vintage1993 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN1 | Petroleum Liquids | IC |  | S | X | X | 36181309 | 36181309 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 6 | 1993 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1993 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN10 | Petroleum Liquids | IC |  | S | X | X | 36181309 | 36181309 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 6 | 1993 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage2000 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN11 | Petroleum Liquids | IC |  | S | X | X | 36181311 | 36181311 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 5 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage2000 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN12 | Petroleum Liquids | IC |  | S | X | X | 36181311 | 36181311 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 5 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage2000 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN13 | Petroleum Liquids | IC |  | S | X | X | 36181311 | 36181311 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 5 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage2000 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN14 | Petroleum Liquids | IC |  | S | X | X | 36181311 | 36181311 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 5 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage2000 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN15 | Petroleum Liquids | IC |  | S | X | X | 36181311 | 36181311 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 5 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage2000 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN16 | Petroleum Liquids | IC |  | S | X | X | 36181311 | 36181311 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 5 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage2000 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN17 | Petroleum Liquids | IC |  | S | X | X | 36181311 | 36181311 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 5 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage2000 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN18 | Petroleum Liquids | IC |  | S | X | X | 36181311 | 36181311 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 5 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage2000 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN19 | Petroleum Liquids | IC |  | S | X | X | 36181311 | 36181311 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 5 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1993 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN2 | Petroleum Liquids | IC |  | S | X | X | 36181309 | 36181309 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 6 | 1993 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage2000 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN20 | Petroleum Liquids | IC |  | S | X | X | 36181311 | 36181311 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 5 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage2000 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN21 | Petroleum Liquids | IC |  | S | X | X | 36181311 | 36181311 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 5 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage2000 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN22 | Petroleum Liquids | IC |  | S | X | X | 36181311 | 36181311 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 5 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage2000 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN23 | Petroleum Liquids | IC |  | S | X | X | 36181311 | 36181311 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 5 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage2000 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN24 | Petroleum Liquids | IC |  | S | X | X | 36181311 | 36181311 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 5 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage2000 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN25 | Petroleum Liquids | IC |  | S | X | X | 36181311 | 36181311 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 5 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage2000 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN26 | Petroleum Liquids | IC |  | S | X | X | 36181311 | 36181311 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 5 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage2000 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN27 | Petroleum Liquids | IC |  | S | X | X | 36181311 | 36181311 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 5 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage2000 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN28 | Petroleum Liquids | IC |  | S | X | X | 36181311 | 36181311 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 5 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage2000 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN29 | Petroleum Liquids | IC |  | S | X | X | 36181311 | 36181311 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 5 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1993 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN3 | Petroleum Liquids | IC |  | S | X | X | 36181309 | 36181309 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 6 | 1993 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage2000 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN30 | Petroleum Liquids | IC |  | S | X | X | 36181311 | 36181311 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 5 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage2000 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN31 | Petroleum Liquids | IC |  | S | X | X | 36181311 | 36181311 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 5 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage2000 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN32 | Petroleum Liquids | IC |  | S | X | X | 36181311 | 36181311 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 5 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage2000 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN33 | Petroleum Liquids | IC |  | S | X | X | 36181311 | 36181311 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 5 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage2000 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN34 | Petroleum Liquids | IC |  | S | X | X | 36181311 | 36181311 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 5 | 2000 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1993 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN4 | Petroleum Liquids | IC |  | S | X | X | 36181309 | 36181309 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 6 | 1993 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1993 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN5 | Petroleum Liquids | IC |  | S | X | X | 36181309 | 36181309 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 6 | 1993 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1993 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN6 | Petroleum Liquids | IC |  | S | X | X | 36181309 | 36181309 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 6 | 1993 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1993 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN7 | Petroleum Liquids | IC |  | S | X | X | 36181309 | 36181309 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 6 | 1993 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1993 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN8 | Petroleum Liquids | IC |  | S | X | X | 36181309 | 36181309 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 6 | 1993 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1993 | petroleum | TRUE | 5178 | Dinwiddie Power Inc | 54766 | Boydton Plank Road Cogen Plant | VA | Dinwiddie | GEN9 | Petroleum Liquids | IC |  | S | X | X | 36181309 | 36181309 | 0.3 | 1 | 0.3 | 0.3 | 0.1 | N |  |  | OP | X | 6 | 1993 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: DFO; WDS: NG |  |  |  | N | N |  | 1H | [23 empty] | Y | Y | N
Vintage1992 | natural gas peaker | TRUE | 60662 | WCAC Operating Company | 54768 | Live Oak Limited | CA | Kern | GEN1 | Natural Gas Fired Combustion Turbine | GT |  | W | X | X |  |  | 46 | 0.85 | 46 | 48 | 21 | N |  |  | OP | X | 3 | 1992 |  |  | Y | IPP CHP | 3 | [11 empty] | N | N |  | 12H | [23 empty] | N | bar: T to BLQ
Vintage1994 | natural gas peaker | FALSE | 11329 | NYU Langone Health | 54769 | NYU Luthern Medical Center | NY | Kings | GEN1 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.8 | 0.85 | 0.8 | 0.8 | 0.2 | N |  |  | OS | X | 1 | 1994 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: T to BLQ
Vintage1994 | natural gas peaker | FALSE | 11329 | NYU Langone Health | 54769 | NYU Luthern Medical Center | NY | Kings | GEN2 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 0.8 | 0.85 | 0.8 | 0.8 | 0.2 | N |  |  | OS | X | 1 | 1994 |  |  | Y | Commercial CHP | 5 | [11 empty] | N | N |  | 10M | [23 empty] | N | bar: T to BLQ
Vintage2006 | petroleum | FALSE | 11329 | NYU Langone Health | 54769 | NYU Luthern Medical Center | NY | Kings | GEN3 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.5 | N |  |  | SB | Y | 1 | 2006 |  |  | N | Commercial CHP | 5 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage2006 | petroleum | FALSE | 11329 | NYU Langone Health | 54769 | NYU Luthern Medical Center | NY | Kings | GEN4 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.5 | 0.8 | 1.5 | 1.5 | 0.5 | N |  |  | SB | Y | 1 | 2006 |  |  | N | Commercial CHP | 5 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1994 | hydro | TRUE | 55754 | Boralex Hydro Operations Inc | 54772 | South Glens Falls Hydroelectric | NY | Saratoga | GEN1 | Conventional Hydroelectric | HY |  | J | X | X | F | F | 6.9 | 0.95 | 6.9 | 6.9 | 0.1 | N |  |  | OP | X | 8 | 1994 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1994 | hydro | TRUE | 55754 | Boralex Hydro Operations Inc | 54772 | South Glens Falls Hydroelectric | NY | Saratoga | GEN2 | Conventional Hydroelectric | HY |  | J | X | X | F | F | 6.9 | 0.95 | 6.9 | 6.9 | 0.1 | N |  |  | OP | X | 8 | 1994 |  |  | N | IPP Non-CHP | 2 | T: X; BLQ: WAT |  |  |  | N | N | 0 | 10M | [23 empty] | N
Vintage1998 | petroleum | FALSE | 19539 | University of Iowa | 54775 | University of Iowa Main Power Plant | IA | Johnson | DG7 | Petroleum Liquids | IC |  | S | X | X |  |  | 1.7 | 0.8 | 1.7 | 1.7 | 0.5 | N |  |  | OA | X | 6 | 1998 |  |  | N | Commercial CHP | 5 | T: X; BLQ: DFO |  |  |  | N | N |  | 10M | [20 empty] | N |  |  | N
Vintage2014 | natural gas peaker | FALSE | 19539 | University of Iowa | 54775 | University of Iowa Main Power Plant | IA | Johnson | GEN10 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.5 | N |  |  | OP | X | 6 | 2014 |  |  | N | Commercial CHP | 5 | [11 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | N | bar: T to BLQ
Vintage1974 | natural gas steam turbine | FALSE | 19539 | University of Iowa | 54775 | University of Iowa Main Power Plant | IA | Johnson | GEN6 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 15 | 0.8 | 15 | 15 | 1.5 | N |  |  | OA | X | 1 | 1974 |  |  | Y | Commercial CHP | 5 | T | NG | BIT | WDS | OBS |  |  | NG |  |  |  | N | N |  | 12H | Y |  | N | Y | Y | [15 empty] | N |  |  | Y | Y | N
Vintage2014 | natural gas peaker | FALSE | 19539 | University of Iowa | 54775 | University of Iowa Main Power Plant | IA | Johnson | GEN7 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.5 | N |  |  | OP | X | 6 | 2014 |  |  | N | Commercial CHP | 5 | [11 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | bar: T to BLQ
Vintage2014 | natural gas peaker | FALSE | 19539 | University of Iowa | 54775 | University of Iowa Main Power Plant | IA | Johnson | GEN8 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.5 | N |  |  | OP | X | 6 | 2014 |  |  | N | Commercial CHP | 5 | [11 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | bar: T to BLQ
Vintage2014 | natural gas peaker | FALSE | 19539 | University of Iowa | 54775 | University of Iowa Main Power Plant | IA | Johnson | GEN9 | Natural Gas Internal Combustion Engine | IC |  | S | X | X |  |  | 2 | 0.8 | 2 | 2 | 0.5 | N |  |  | OP | X | 6 | 2014 |  |  | N | Commercial CHP | 5 | [11 empty] | N | N |  | 10M | [20 empty] | N |  |  | N | bar: T to BLQ
Vintage1940 | natural gas steam turbine | FALSE | 19528 | University of Illinois | 54780 | University of Illinois Abbott Power Plt | IL | Champaign | T1 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 1 | N |  |  | OP | X | 11 | 1940 |  |  | Y | Commercial CHP | 5 | T | NG | BIT | DFO |  |  |  | NG |  |  |  | N | N |  | 12H |  |  | Y | N | Y | [15 empty] | N |  |  | Y | Y | Y
Vintage2004 | natural gas steam turbine | FALSE | 19528 | University of Illinois | 54780 | University of Illinois Abbott Power Plt | IL | Champaign | T10 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 7.8 | 0.85 | 7.8 | 7.8 | 3 | N |  |  | OP | X | 8 | 2004 |  |  | Y | Commercial CHP | 5 | T | NG | BIT | DFO |  |  |  | NG |  |  |  | N | N |  | 12H |  |  | Y | N | Y | [15 empty] | N |  |  | Y | Y | Y
Vintage2004 | natural gas steam turbine | FALSE | 19528 | University of Illinois | 54780 | University of Illinois Abbott Power Plt | IL | Champaign | T11 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 12.5 | 0.85 | 12.5 | 12.5 | 3 | N |  |  | OP | X | 6 | 2004 |  |  | Y | Commercial CHP | 5 | T | NG | BIT | DFO |  |  |  | NG |  |  |  | N | N |  | 12H |  |  | Y | N | Y | [15 empty] | N |  |  | Y | Y | Y
Vintage2004 | natural gas steam turbine | FALSE | 19528 | University of Illinois | 54780 | University of Illinois Abbott Power Plt | IL | Champaign | T12 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 7 | 0.85 | 7 | 7 | 3 | N |  |  | OP | X | 4 | 2004 |  |  | Y | Commercial CHP | 5 | T | NG | BIT | DFO |  |  |  | NG |  |  |  | N | N |  | 12H |  |  | Y | N | Y | [15 empty] | N |  |  | Y | Y | Y
Vintage1940 | natural gas steam turbine | FALSE | 19528 | University of Illinois | 54780 | University of Illinois Abbott Power Plt | IL | Champaign | T2 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 1 | N |  |  | OP | X | 11 | 1940 |  |  | Y | Commercial CHP | 5 | T | NG | BIT | DFO |  |  |  | NG |  |  |  | N | N |  | 12H |  |  | Y | N | Y | [15 empty] | N |  |  | Y | Y | Y
Vintage1948 | natural gas steam turbine | FALSE | 19528 | University of Illinois | 54780 | University of Illinois Abbott Power Plt | IL | Champaign | T3 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 1 | N |  |  | OP | X | 11 | 1948 |  |  | Y | Commercial CHP | 5 | T | NG | BIT | DFO |  |  |  | NG |  |  |  | N | N |  | 12H |  |  | Y | N | Y | [15 empty] | N |  |  | Y | Y | Y
Vintage1951 | natural gas steam turbine | FALSE | 19528 | University of Illinois | 54780 | University of Illinois Abbott Power Plt | IL | Champaign | T4 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 3 | 0.8 | 3 | 3 | 1 | N |  |  | OP | X | 2 | 1951 |  |  | Y | Commercial CHP | 5 | T | NG | BIT | DFO |  |  |  | NG |  |  |  | N | N |  | 12H |  |  | Y | N | Y | [15 empty] | N |  |  | Y | Y | Y
Vintage1959 | natural gas steam turbine | FALSE | 19528 | University of Illinois | 54780 | University of Illinois Abbott Power Plt | IL | Champaign | T6 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 7.5 | 0.8 | 7.5 | 7.5 | 1.5 | N |  |  | OP | X | 6 | 1959 |  |  | Y | Commercial CHP | 5 | T | NG | BIT | DFO |  |  |  | NG |  |  |  | N | N |  | 12H |  |  | Y | N | Y | [15 empty] | N |  |  | Y | Y | Y
Vintage1962 | natural gas steam turbine | FALSE | 19528 | University of Illinois | 54780 | University of Illinois Abbott Power Plt | IL | Champaign | T7 | Natural Gas Steam Turbine | ST |  | S | X | X |  |  | 7.5 | 0.8 | 7.5 | 7.5 | 1.5 | N |  |  | OP | X | 8 | 1962 |  |  | Y | Commercial CHP | 5 | T | NG | BIT | DFO |  |  |  | NG |  |  |  | N | N |  | 12H |  |  | Y | N | Y | [15 empty] | N |  |  | Y | Y | Y
Vintage2003 | natural gas peaker | FALSE | 19528 | University of Illinois | 54780 | University of Illinois Abbott Power Plt | IL | Champaign | T8 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 13 | 0.85 | 12.5 | 15 | 7 | N |  |  | OP | X | 9 | 2003 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: NG; WDS: DFO; NG: NG |  |  |  | N | N |  | 12H |  |  |  | N | [16 empty] | N |  |  | Y | Y | Y
Vintage2003 | natural gas peaker | FALSE | 19528 | University of Illinois | 54780 | University of Illinois Abbott Power Plt | IL | Champaign | T9 | Natural Gas Fired Combustion Turbine | GT |  | S | X | X |  |  | 13 | 0.85 | 12.5 | 15 | 7 | N |  |  | OP | X | 11 | 2003 |  |  | Y | Commercial CHP | 5 | T: T; BLQ: NG; WDS: DFO; NG: NG |  |  |  | N | N |  | 12H |  |  |  | N | [16 empty] | N |  |  | Y | Y | Y
Vintage1994 | biomass | TRUE | 18190 | Mas Suffolk RNG, LLC | 54781 | Mas Suffolk RNG, LLC | VA | Suffolk City | SU1 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.7 | 0.7 | 0.6 | N |  |  | OP | X | 11 | 1994 | 2 | 2022 | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1994 | biomass | TRUE | 18190 | Mas Suffolk RNG, LLC | 54781 | Mas Suffolk RNG, LLC | VA | Suffolk City | SU4 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.7 | 0.7 | 0.6 | N |  |  | OP | X | 11 | 1994 | 2 | 2022 | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 10M | [23 empty] | N
Vintage1998 | biomass | TRUE | 17283 | Seneca Energy II | 54782 | Seneca Energy | NY | Seneca | GE10 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 8 | 1998 | 12 | 2022 | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1998 | biomass | TRUE | 17283 | Seneca Energy II | 54782 | Seneca Energy | NY | Seneca | GE11 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 8 | 1998 | 12 | 2022 | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1998 | biomass | TRUE | 17283 | Seneca Energy II | 54782 | Seneca Energy | NY | Seneca | GE12 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 8 | 1998 | 12 | 2022 | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N
Vintage1998 | biomass | TRUE | 17283 | Seneca Energy II | 54782 | Seneca Energy | NY | Seneca | GE13 | Landfill Gas | IC |  | S | X | X |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | N |  |  | OP | X | 8 | 1998 | 12 | 2022 | N | IPP Non-CHP | 2 | T: X; BLQ: LFG |  |  |  | N | N |  | 1H | [20 empty] | N |  |  | N | N | N